## Index
Tab Name | Purpose
Final Results | Final incremental costs including first costs, maintenance costs, and replacement costs
Proto Costing | Cost buildup for each prototype and system type
Plant-side Costs | Plant-side component costs
Air-side Costs | Air-side distribution component costs
Sizing | Heating load and AHU cfm from models
MZ HP Costing Approach
Costs are developed for individual system components using RS Means, manufacturer direct quotes, and other data sources. Cost versus capacity regressions are developed for components where possible. This allows costs to be calculated as models are revised.
Model sizing output for a given prototype and case is combined with component costs to develop prototype costs. These costs are applicable to a specific prototype and system configuration. These costs represent the first cost for the system in the context of the proposed measure, i.e., only those components of a system that are changing between the baseline and proposed case are costed.
Finally, present value of maintenance and replacement costs is added to the incremental cost to calculate the total incremental cost of the measure.

## Final Results
Prototype Incremental First Costs and Maintenance and Replacement Costs
Maintenance and Replacement Costs Calculation
| Parameter | Value |  | Source
| Discount Rate | 3% |  | CEC Assumption
| Lrg Office Num Zones | 120 |  | Costing assumes Large Office prototype has more zones than "energy model zones"
| Lrg School Num Zones | 46
| Component | Annual Maint | EUL | Repl Discount | PV of Maint. Cost
| PVAV | 500 | 20 | 0.55368 | -10094.2273
| VRF | 400 | 20 | 0.55368 | -8075.3818
| Boiler | 500 | 25 | 0.47761 | -10094.2273
| AWHP | 300 | 15 | 0.64186 | -6056.5364
| Pump | 50 | 20 | 0.55368 | -1009.4227
| FPFC | 180 | 20 | 0.55368 | -3633.9218
| VAV Terminal Unit | 45 | 20 | 0.55368 | -908.4805
| DOAS | 500 | 20 | 0.55368 | -10094.2273
| Built-up AHU (Note 1) | 500 | 20 | 0.55368 | -10094.2273
| BU AHU Replacement/cfm | 1.109 | 25 | 0.47761
1. O&M for Built-Up VAV assumes replacement of fans and coils without entire cabinet. Pump maintenance cost is neutral for the AWHP case.
2. Annual Maintenance Cost estimates from O&M equipment task lists and an assumed burdened labor rate of $100-$120/hr.
3. EUL = Expected Useful Life of Equipment, from ASHRAE Equipment Life Expectancy Chart
4. Repl Discount = Discount factor for equipment replacement after EUL period.
5. PV of Maint Cost = Total maintenance cost over expected life, per unit, accounting for the discount rate.
6. FPFC estimated annual maintenance (incremental over VAV terminal units) is 2 hours per FPFC unit.
Proposed First Cost - proposed HVAC system first cost of all costed components. Note for some buildings this may not include systems (chiller, tower) that have a neutral cost.
Replacement Cost - replacement cost of all systems in table above applicable to the design, modified by the Replacement Discount factor in colum G.
Maintenance Cost - the total maintenance cost of all system components in the table above, column H, multiplied by the number of components of each type.
Incr Cost - the incremental HVAC system cost over the baseline, per square foot of building floor area.
AGIC Avoided Cost - the avoided cost of gas infrastructure (running gas lines to building, and runnling gas lines to HVAC units). This only applies to office buildings, not to schools.
Net Incremental Cost - the net incremental cost over the standard design (2022 baseline) HVAC system, per square foot of floor area.
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
LrgOff | Proposed First Cost | 6380934.3238 | 6392820.1985 | 6397473.4365 | 6443581.6649 | 6374437.336 | 6321940.0484 | 6323914.6113 | 6339861.3684 | 6401351.0938 | 6384629.7581 | 6526750.8187 | 6423039.8863 | 6443641.9951 | 6528604.8471 | 6438142.8194 | 6651746.1989
AWHP+VAV | Replacement Cost | 842488.8471 | 847647.1432 | 848718.4159 | 872409.5661 | 838234.71 | 810455.1815 | 810879.7798 | 819014.5038 | 848900.803 | 841547.2757 | 912131.6172 | 862080.2344 | 870768.7766 | 911865.9719 | 865954.2721 | 971830.1069
| Maintenance Cost | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551 | 242261.4551
| Total | 7465684.626 | 7482728.7967 | 7488453.3075 | 7558252.6861 | 7454933.5011 | 7374656.685 | 7377055.8463 | 7401137.3272 | 7492513.3519 | 7468438.4889 | 7681143.8909 | 7527381.5757 | 7556672.2268 | 7682732.2741 | 7546358.5466 | 7865837.7609
| Incr Cost | 1.5668 | 1.5249 | 1.4363 | 1.5668 | 1.4783 | 1.2686 | 1.2267 | 1.2686 | 1.3105 | 1.3572 | 1.5668 | 1.5249 | 1.4363 | 1.4783 | 1.2686 | 1.5668
| AGIC Avoided Cost | 0.072308 | 0.072308 | 0.072308 | 0.072308 | 0.072308 | 0.044293 | 0.044887 | 0.044887 | 0.044293 | 0.044293 | 0.072308 | 0.044887 | 0.072308 | 0.044293 | 0.072308 | 0.072308
| Net Incremental Cost | 1.4945 | 1.4526 | 1.364 | 1.4945 | 1.406 | 1.2243 | 1.1818 | 1.2237 | 1.2662 | 1.3129 | 1.4945 | 1.48 | 1.364 | 1.434 | 1.1963 | 1.4945
Large Office | CZ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Base | Baseline First Cost | 5741555.2271 | 5767239.7478 | 5800991.6777 | 5804202.5682 | 5764156.9313 | 5780652.8734 | 5796426.0823 | 5798574.1934 | 5846265.2729 | 5814243.8912 | 5887371.722 | 5797459.4356 | 5847160.2363 | 5918324.4424 | 5896855.6444 | 6012367.1023
| Replacement Cost | 692593.1178 | 704860.1879 | 720980.2977 | 722513.8368 | 703387.8176 | 711152.1596 | 718685.5321 | 719711.4819 | 742489.007 | 727195.4168 | 762235.8879 | 719293.2791 | 743030.6584 | 777019.0795 | 766651.2502 | 821934.3776
| Maintenance Cost | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369 | 250336.8369
| Total | 6684485.1819 | 6722436.7726 | 6772308.8123 | 6777053.242 | 6717881.5858 | 6742141.87 | 6765448.4512 | 6768622.5122 | 6839091.1168 | 6791776.1449 | 6899944.4468 | 6767089.5517 | 6840527.7316 | 6945680.3588 | 6913843.7315 | 7084638.3168
AWHP+FPFC | Baseline First Cost | 5055775.1476 | 5037078.2469 | 4998183.0454 | 5055775.1476 | 5016879.9461 | 4921894.0424 | 4903197.1417 | 4921894.0424 | 4940590.9432 | 4960789.2439 | 5055775.1476 | 5037078.2469 | 4998183.0454 | 5016879.9461 | 4921894.0424 | 5055775.1476
| Replacement Cost | 1016124.2434 | 1006676.0355 | 987779.6198 | 1016124.2434 | 997227.8277 | 949155.4996 | 939707.2917 | 949155.4996 | 958603.7074 | 968051.9153 | 1016124.2434 | 1006676.0355 | 987779.6198 | 997227.8277 | 949155.4996 | 1016124.2434
| Maintenance Cost | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194 | 569314.4194
| Total | 6641213.8105 | 6613068.7019 | 6555277.0846 | 6641213.8105 | 6583422.1933 | 6440363.9614 | 6412218.8528 | 6440363.9614 | 6468509.07 | 6498155.5787 | 6641213.8105 | 6613068.7019 | 6555277.0846 | 6583422.1933 | 6440363.9614 | 6641213.8105
| Incr Cost | -0.086788 | -0.21936 | -0.43529 | -0.27245 | -0.26968 | -0.60526 | -0.70846 | -0.65838 | -0.74326 | -0.5889 | -0.51893 | -0.30891 | -0.57212 | -0.72657 | -0.94964 | -0.88936
| AGIC Avoided Cost | 0.072308 | 0.072308 | 0.072308 | 0.072308 | 0.072308 | 0.044293 | 0.044887 | 0.044887 | 0.044293 | 0.044293 | 0.072308 | 0.044887 | 0.072308 | 0.044293 | 0.072308 | 0.072308
| Net Incremental Cost | -0.1591 | -0.29166 | -0.5076 | -0.34476 | -0.34199 | -0.64956 | -0.75335 | -0.70326 | -0.78755 | -0.6332 | -0.59123 | -0.3538 | -0.64442 | -0.77086 | -1.0219 | -0.96167
LrgSch | Proposed First Cost | 3155859.8729 | 3200721.1483 | 3151975.6278 | 3212327.6869 | 3156202.9946 | 3078252.7714 | 3080934.2228 | 3143312.7036 | 3129738.2994 | 3150564.6436 | 3213853.3134 | 3190372.8269 | 3191169.8083 | 3258351.5011 | 3144509.249 | 3279619.1155
AWHP-VAV | Replacement Cost | 269719.5908 | 279999.0874 | 250823.175 | 279999.0874 | 260271.3829 | 212199.0548 | 212199.0548 | 241374.9672 | 231095.4705 | 241374.9672 | 269719.5908 | 269719.5908 | 260271.3829 | 279999.0874 | 221647.2627 | 279999.0874
| Maintenance Cost | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738 | 53903.1738
| Total | 3479482.6374 | 3534623.4094 | 3456701.9766 | 3546229.9481 | 3470377.5513 | 3344354.9999 | 3347036.4514 | 3438590.8445 | 3414736.9436 | 3445842.7845 | 3537476.0779 | 3513995.5915 | 3505344.3649 | 3592253.7623 | 3420059.6854 | 3613521.3766
| Incr Cost | 1.1634 | 1.2088 | 0.88422 | 1.1783 | 1.0142 | 0.46985 | 0.46281 | 0.75873 | 0.63114 | 0.73969 | 1.0111 | 1.0727 | 0.92242 | 1.0575 | 0.44413 | 1.0017
AGIC Avoided Cost
| Net Incremental Cost | 1.1634 | 1.2088 | 0.88422 | 1.1783 | 1.0142 | 0.46985 | 0.46281 | 0.75873 | 0.63114 | 0.73969 | 1.0111 | 1.0727 | 0.92242 | 1.0575 | 0.44413 | 1.0017
Large School | CZ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Base | Baseline First Cost | 2793903.993 | 2823465.2224 | 2816115.6398 | 2835071.7611 | 2808045.7607 | 2799088.7671 | 2801770.2186 | 2821251.3615 | 2822977.0032 | 2828503.3015 | 2851897.4335 | 2828416.947 | 2843012.5743 | 2881095.5753 | 2851546.5988 | 2902363.1896
| Replacement Cost | 358075.7638 | 374070.4886 | 371950.3252 | 380496.7477 | 366278.3288 | 364013.4032 | 365498.0578 | 375166.4609 | 376494.518 | 379181.6843 | 390185.3257 | 377184.7497 | 385638.6057 | 405979.0177 | 392685.4216 | 417754.3801
| Maintenance Cost | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102 | 82167.0102
| Total | 3234146.7669 | 3279702.7212 | 3270232.9751 | 3297735.5189 | 3256491.0997 | 3245269.1805 | 3249435.2866 | 3278584.8326 | 3281638.5314 | 3289851.996 | 3324249.7694 | 3287768.7069 | 3310818.1902 | 3369241.6031 | 3326399.0306 | 3402284.5799
AWHP+FPFC | Proposed First Cost | 2931522.3449 | 2950219.2456 | 2894128.5434 | 2950219.2456 | 2912825.4442 | 2819340.9404 | 2819340.9404 | 2875431.6427 | 2856734.7419 | 2875431.6427 | 2931522.3449 | 2931522.3449 | 2912825.4442 | 2950219.2456 | 2838037.8412 | 2950219.2456
| Replacement Cost | 608521.0379 | 618800.5345 | 589624.6222 | 618800.5345 | 599072.83 | 551000.5019 | 551000.5019 | 580176.4143 | 569896.9177 | 580176.4143 | 608521.0379 | 608521.0379 | 599072.83 | 618800.5345 | 560448.7098 | 618800.5345
| Maintenance Cost | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768 | 179273.4768
| Total | 3719316.8596 | 3748293.2569 | 3663026.6423 | 3748293.2569 | 3691171.7509 | 3549614.9191 | 3549614.9191 | 3634881.5337 | 3605905.1363 | 3634881.5337 | 3719316.8596 | 3719316.8596 | 3691171.7509 | 3748293.2569 | 3577760.0277 | 3748293.2569
| Incr Cost | 2.3006 | 2.222 | 1.8626 | 2.1365 | 2.0612 | 1.4432 | 1.4234 | 1.6895 | 1.5376 | 1.6361 | 1.8734 | 2.0464 | 1.8036 | 1.7974 | 1.1919 | 1.6407
AGIC Avoided Cost
| Net Incremental Cost | 2.3006 | 2.222 | 1.8626 | 2.1365 | 2.0612 | 1.4432 | 1.4234 | 1.6895 | 1.5376 | 1.6361 | 1.8734 | 2.0464 | 1.8036 | 1.7974 | 1.1919 | 1.6407

## Proto Costing
Conditioned Floor Area
| Large Office | 498589 | ft2
| Large School | 210886 | ft2
Large Office Prototype - VAV+Gas Boiler (Base Case)
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Gas Boiler | Capacity | 4800 | 4560 | 4080 | 4800 | 4320 | 3120 | 2880 | 3120 | 3360 | 3600 | 4800 | 4560 | 4080 | 4320 | 3120 | 4800 | MBH | Capacity, MBH, sizing from energy model heating load
Qty | bar: CZ1 to CZ16
| Mat Cost | 62948.2 | 59883.64 | 53754.52 | 62948.2 | 56819.08 | 41496.28 | 38431.72 | 41496.28 | 44560.84 | 47625.4 | 62948.2 | 59883.64 | 53754.52 | 56819.08 | 41496.28 | 62948.2 |  | RS Means Online 2023
| Labor Cost | 25401.54 | 24206.748 | 21817.164 | 25401.54 | 23011.956 | 17037.996 | 15843.204 | 17037.996 | 18232.788 | 19427.58 | 25401.54 | 24206.748 | 21817.164 | 23011.956 | 17037.996 | 25401.54 |  | RS Means Online 2023
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 101602.201 | 96703.9462 | 86907.4366 | 101602.201 | 91805.6914 | 67314.4174 | 62416.1626 | 67314.4174 | 72212.6722 | 77110.927 | 101602.201 | 96703.9462 | 86907.4366 | 91805.6914 | 67314.4174 | 101602.201 |  | Gas Boiler Cost with Overhead and Profit
VAV AHU | Capacity | [17 empty] | Capacity in tons is not used - use airflow from sizing run for built-up AHU
| Qty (CFM) | 354536 | 367002 | 384753 | 380072 | 367742 | 385061 | 393487 | 392366 | 409809 | 394760 | 413973 | 379320 | 403572 | 430583 | 432427 | 464923 | CFM | Design airflow of built-up AHUs from model (built-up unit with CHW and HW coils)
Unit Cost
| Mat Cost | 764820.8488 | 791414.5666 | 829282.7749 | 819296.7976 | 792993.2086 | 829939.8313 | 847915.0171 | 845523.5878 | 882734.7397 | 850630.708 | 891617.8009 | 817692.556 | 869429.3476 | 927051.9139 | 930985.7191 | 1000309.4359 |  | RS Means Online (2023) - cost regression as a function of design airflow (cfm)
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 879543.9761 | 910126.7516 | 953675.1911 | 942191.3172 | 911942.1899 | 954430.806 | 975102.2697 | 972352.126 | 1015144.9507 | 978225.3142 | 1025360.471 | 940346.4394 | 999843.7497 | 1066109.701 | 1070633.577 | 1150355.8513
HW Ductwork | Capacity
| Qty (ft) | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | 10200 | ft | Length of ductwork in ft - trunk ducts and btanches to all 120 zones
| Unit Cost | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 |  | Installed Ductwork Cost per linear foot, MEP CA Office Project Avg (NORESCO), combined material and labor cost [- see Sheet1
| Mat Cost | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 | 2763486 |  | Duct system installed cost
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 | 3178008.9 |  | Duct system installed cost with OH&P
HW Piping | Capacity (ft) | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | ft | Length of jhydronic piping, CHW and HW
| Qty | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Unit Cost | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800 | 34800
| Mat Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 | 40020 |  | HW Piping Cost
VAV Box | Subtotal | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 |  | Installed Cost of 120 VAV Boxes, MEP CA Office Project Avg (NORESCO)
All (120 zones)
Circ Pump | Pump Motorhorsepower | 8 | 8 | 8 | 8 | 8 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8 | 6 | 8 | hp | Pump Nameplate HP, using ACM gpm/ton and W/gpm standard design assumptions
| Subtotal | 15118.9 | 15118.9 | 15118.9 | 15118.9 | 15118.9 | 13617.5 | 13617.5 | 13617.5 | 13617.5 | 13617.5 | 15118.9 | 15118.9 | 15118.9 | 15118.9 | 13617.5 | 15118.9
SUBTOTAL | No controls, Cx | 4603729.9771 | 4629414.4978 | 4663166.4277 | 4666377.3182 | 4626331.6813 | 4642827.6234 | 4658600.8323 | 4660748.9434 | 4708440.0229 | 4676418.6412 | 4749546.472 | 4659634.1856 | 4709334.9863 | 4780499.1924 | 4759030.3944 | 4874541.8523
| Controls | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 | 1121825.25 |  | Feng, J. and Hwakong Cheng 2018. Construction and Energy Costs for Radiant vs. VAV Systems in the California Bay Area, Final Report, Taylor Engineering and UC Berkeley, EPIC-14-009, November 15, 2018.
| Commissioning (Htg System) | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 |  | Cx Costs are differential function testing estimates for bours (NORESCO), using a loaded Cx labor rate of $160/hr.
| Subtotal | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25 | 1137825.25
TOTAL | Project Total (Costed Portion) | 5741555.2271 | 5767239.7478 | 5800991.6777 | 5804202.5682 | 5764156.9313 | 5780652.8734 | 5796426.0823 | 5798574.1934 | 5846265.2729 | 5814243.8912 | 5887371.722 | 5797459.4356 | 5847160.2363 | 5918324.4424 | 5896855.6444 | 6012367.1023
Large Office Prototype - AWHP with FPFC (Proposed Case)
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
AWHP | Capacity | 200 | 190 | 170 | 200 | 180 | 130 | 120 | 130 | 140 | 150 | 200 | 190 | 170 | 180 | 130 | 200 | tons | System Heating Capacity for 50% of heating load from energy model
Qty | bar: CZ1 to CZ16
| Unit Cost | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | $/ton | Distributor cost, Trane Ascend ACX, unit only with no desuperheater
| Mat Cost | 256000 | 243200 | 217600 | 256000 | 230400 | 166400 | 153600 | 166400 | 179200 | 192000 | 256000 | 243200 | 217600 | 230400 | 166400 | 256000 |  | Unit cost (rquipment only)
| Labor Cost | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 |  | RS Means Online
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 306544 | 291824 | 262384 | 306544 | 277104 | 203504 | 188784 | 203504 | 218224 | 232944 | 306544 | 291824 | 262384 | 277104 | 203504 | 306544
DOAS | Capacity | [17 empty] | Note that Capacity in tons is not used - source has DOAS installed cost as a function of CFM
w/ ductwork | Qty (CFM) | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | 74788 | CFM | DOAS AHU design CFM, from model.
| Unit Cost | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | $/cfm | VHE DOAS Study Final Report 2002, Red Car Analytics
| Mat Cost | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880 | 747880
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062 | 860062
CHW Piping | Capacity
| Qty (ft) | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | Linear ft | Linear Feet of Ductwork, assumes trunk duct around perimeter, with branch ductwork to each of 120 zones
| Unit Cost | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | $/LF | MEP CA Office Project Avg (NORESCO), combined material and labor cost
| Mat Cost | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190 | 487190
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5 | 560268.5
HW Piping | Capacity
| Qty (ft) | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | Linrar ft | Linear feet of Hydronic Piping
| Unit Cost | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | $/LF | MEP CA Office Project Avg (NORESCO), combined material and labor cost [- see Sheet1
| Mat Cost | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711
FPFC Unit | Number of Zones | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | Num Zones
| Subtotal | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988 | 1202988
| Pump Nameplate HP | 12 | 12 | 10 | 12 | 10 | 8 | 8 | 8 | 8 | 10 | 12 | 12 | 10 | 10 | 8 | 12 | hp | Circulation Pump Nameplate HP - gpm/ton and W/gpm from ACM standard design assumptions (Note: no code requirement on pump power)
Circ Pump | Subtotal | 18121.7 | 18121.7 | 16620.3 | 18121.7 | 16620.3 | 15118.9 | 15118.9 | 15118.9 | 15118.9 | 16620.3 | 18121.7 | 18121.7 | 16620.3 | 16620.3 | 15118.9 | 18121.7 |  | RS Means Online 2023
Storage | Capacity (gal) | 1458.7028 | 1358.7028 | 1158.7028 | 1458.7028 | 1258.7028 | 758.7028 | 658.7028 | 758.7028 | 858.7028 | 958.7028 | 1458.7028 | 1358.7028 | 1158.7028 | 1258.7028 | 758.7028 | 1458.7028 | gal | Assumes 10 gal/ton total volume, less volume in piping (conversion estimate of 21.43 ft piping holds 1 gal)
| Qty (gal) | 1475 | 1375 | 1175 | 1475 | 1275 | 775 | 675 | 775 | 875 | 975 | 1475 | 1375 | 1175 | 1275 | 775 | 1475 | gal | Round up to nearest 25 gal for indirect storage tank
Unit Cost
| Mat Cost + Labor Cost | 30667.885 | 28618.585 | 24519.985 | 30667.885 | 26569.285 | 16322.785 | 14273.485 | 16322.785 | 18372.085 | 20421.385 | 30667.885 | 28618.585 | 24519.985 | 26569.285 | 16322.785 | 30667.885 |  | RS Means Online 2023 (regression of total costs, material and labor) against storage volume in gallons
Labor Cost (not used)
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 35268.0677 | 32911.3727 | 28197.9827 | 35268.0677 | 30554.6777 | 18771.2027 | 16414.5077 | 18771.2027 | 21127.8977 | 23484.5927 | 35268.0677 | 32911.3727 | 28197.9827 | 30554.6777 | 18771.2027 | 35268.0677 |  | Storage Cost with OH&P
`
Suppl Htr | Capacity (kW) | 703.3998 | 668.2298 | 597.8898 | 703.3998 | 633.0598 | 457.2098 | 422.0399 | 457.2098 | 492.3798 | 527.5498 | 703.3998 | 668.2298 | 597.8898 | 633.0598 | 457.2098 | 703.3998 | kW | Supplemental Heater, kW, sized from energy model
Qty | bar: CZ1 to CZ16
| Total Cost (Mat + Labor) | 33338.5912 | 31929.7166 | 29111.9675 | 33338.5912 | 30520.8421 | 23476.4693 | 22067.5947 | 23476.4693 | 24885.3438 | 26294.2184 | 33338.5912 | 31929.7166 | 29111.9675 | 30520.8421 | 23476.4693 | 33338.5912 |  | RS Means Online 2023
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 38339.3799 | 36719.1741 | 33478.7627 | 38339.3799 | 35098.9684 | 26997.9397 | 25377.7339 | 26997.9397 | 28618.1454 | 30238.3512 | 38339.3799 | 36719.1741 | 33478.7627 | 35098.9684 | 26997.9397 | 38339.3799 |  | Supplemental Electric Boiler Cost with OH&P
SUBTOTAL | No controls, Cx | 3777302.6476 | 3758605.7469 | 3719710.5454 | 3777302.6476 | 3738407.4461 | 3643421.5424 | 3624724.6417 | 3643421.5424 | 3662118.4432 | 3682316.7439 | 3777302.6476 | 3758605.7469 | 3719710.5454 | 3738407.4461 | 3643421.5424 | 3777302.6476
| Controls | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 |  | Feng, J. and Hwakong Cheng 2018. Construction and Energy Costs for Radiant vs. VAV Systems in the California Bay Area, Final Report, Taylor Engineering and UC Berkeley, EPIC-14-009, November 15, 2018.
| Commissioning (Htg System) | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 |  | Cx Costs are differential function testing estimates for bours (NORESCO), using a loaded Cx labor rate of $160/hr.
TOTAL | Project Total (Costed Portion) | 5055775.1476 | 5037078.2469 | 4998183.0454 | 5055775.1476 | 5016879.9461 | 4921894.0424 | 4903197.1417 | 4921894.0424 | 4940590.9432 | 4960789.2439 | 5055775.1476 | 5037078.2469 | 4998183.0454 | 5016879.9461 | 4921894.0424 | 5055775.1476
| Large School Prototype - VAV+Gas Boiler (Base Case) | CZ4: Distribution Length:; CZ6: 4412
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Gas Boiler | Capacity | 4320 | 4560 | 3840 | 4560 | 4080 | 2880 | 2880 | 3600 | 3360 | 3600 | 4320 | 4320 | 4080 | 4560 | 3120 | 4560 | MBH | Gas Boiler Heating Capacity for heating load from energy model
Qty | bar: CZ1 to 4412 CZ16
| Mat Cost | 56819.08 | 59883.64 | 50689.96 | 59883.64 | 53754.52 | 38431.72 | 38431.72 | 47625.4 | 44560.84 | 47625.4 | 56819.08 | 56819.08 | 53754.52 | 59883.64 | 41496.28 | 59883.64 |  | Unit Cost, Equipment (RS Means Online(
| Labor Cost | 23011.956 | 24206.748 | 20622.372 | 24206.748 | 21817.164 | 15843.204 | 15843.204 | 19427.58 | 18232.788 | 19427.58 | 23011.956 | 23011.956 | 21817.164 | 24206.748 | 17037.996 | 24206.748 |  | Unit Cost, (RS Means Online)
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 91805.6914 | 96703.9462 | 82009.1818 | 96703.9462 | 86907.4366 | 62416.1626 | 62416.1626 | 77110.927 | 72212.6722 | 77110.927 | 91805.6914 | 91805.6914 | 86907.4366 | 96703.9462 | 67314.4174 | 96703.9462 |  | Component Installed Cost with OH&P
VAV AHU | Capacity
| Qty (CFM) | 166505 | 176558 | 180164 | 181289 | 174266 | 181210 | 182303 | 184254 | 186954 | 187210 | 190144 | 180573 | 188519 | 200049 | 200596 | 208718 | cfm | VAV AHU design CFM, from model.
Unit Cost
| Mat Cost | 363694.3165 | 385140.3814 | 392833.0612 | 395233.0237 | 380250.8578 | 395064.493 | 397396.1899 | 401558.2582 | 407318.1682 | 407864.293 | 414123.3952 | 393705.5809 | 410656.7827 | 435253.7317 | 436420.6468 | 453747.3094 |  | RS Means Online (2023), Cost for Built-up VAV Air Handling Unit
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 418248.464 | 442911.4386 | 451758.0204 | 454517.9773 | 437288.4865 | 454324.167 | 457005.6184 | 461791.9969 | 468415.8934 | 469043.937 | 476241.9045 | 452761.418 | 472255.3001 | 500541.7915 | 501883.7438 | 521809.4058 |  | VAV AHU Cost with OH&P
HW Ductwork | Capacity
| Qty (ft) | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | Linear feet | Linear Feet of Ductwork, assumes trunk duct around perimeter, with branch ductwork to each of 120 zones
| Unit Cost | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | $/LF | MEP CA Office Project Avg (NORESCO), combined material and labor cost
| Mat Cost | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 |  | Heating Hot Water Ductwork Cost
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 |  | Heating Hot Water Ductwork Cost with OH&P
HW Piping | Capacity (ft) | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | Linear feet | Linear feet of Hydronic Piping
| Unit Cost | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | $/LF | MEP CA Office Project Avg (NORESCO), combined material and labor cost [- see Sheet1
| Mat Cost | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264 | 221138.264
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036 | 254309.0036
VAV Box | Subtotal | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 |  | Piping Installed Cost with OH&P
All (46 zones)
Circ Pump | Pump Motorhorsepower | 8 | 8 | 6 | 8 | 8 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8 | 6 | 8 | Motor HP | Circulation Pump Nameplate HP - gpm/ton and W/gpm from ACM standard design assumptions (Note: no code requirement on pump power)
| Subtotal | 15118.9 | 15118.9 | 13617.5 | 15118.9 | 15118.9 | 13617.5 | 13617.5 | 13617.5 | 13617.5 | 13617.5 | 15118.9 | 15118.9 | 15118.9 | 15118.9 | 13617.5 | 15118.9 | $ | RS Means Online 2023
SUBTOTAL | No controls, Cx | 2303410.493 | 2332971.7224 | 2325622.1398 | 2344578.2611 | 2317552.2607 | 2308595.2671 | 2311276.7186 | 2330757.8615 | 2332483.5032 | 2338009.8015 | 2361403.9335 | 2337923.447 | 2352519.0743 | 2390602.0753 | 2361053.0988 | 2411869.6896
| Controls | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 | 474493.5 |  | Feng, J. and Hwakong Cheng 2018. Construction and Energy Costs for Radiant vs. VAV Systems in the California Bay Area, Final Report, Taylor Engineering and UC Berkeley, EPIC-14-009, November 15, 2018.
| Commissioning (Htg System) | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 |  | Cx Costs are differential function testing estimates for bours (NORESCO), using a loaded Cx labor rate of $160/hr.
| Subtotal | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5 | 490493.5
TOTAL | Project Total (Costed Portion) | 2793903.993 | 2823465.2224 | 2816115.6398 | 2835071.7611 | 2808045.7607 | 2799088.7671 | 2801770.2186 | 2821251.3615 | 2822977.0032 | 2828503.3015 | 2851897.4335 | 2828416.947 | 2843012.5743 | 2881095.5753 | 2851546.5988 | 2902363.1896
Large School Prototype - AWHP with FPFC (Proposed Case)
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
AWHP | Capacity | 180 | 190 | 160 | 190 | 170 | 120 | 120 | 150 | 140 | 150 | 180 | 180 | 170 | 190 | 130 | 190 | Nominal tons | System Heating Capacity for 50% of heating load from energy model
Qty | bar: CZ1 to CZ16
| Unit Cost | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | $/ton | Distributor cost, Trane Ascend ACX, unit only with no desuperheater
| Mat Cost | 230400 | 243200 | 204800 | 243200 | 217600 | 153600 | 153600 | 192000 | 179200 | 192000 | 230400 | 230400 | 217600 | 243200 | 166400 | 243200 |  | Unit cost (rquipment only)
| Labor Cost | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 |  | RS Means Online
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 277104 | 291824 | 247664 | 291824 | 262384 | 188784 | 188784 | 232944 | 218224 | 232944 | 277104 | 277104 | 262384 | 291824 | 203504 | 291824
DOAS | Capacity
w/ ductwork | Qty (CFM) | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | 85729 | cfm | VAV AHU design CFM, from model.
| Unit Cost | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | $/cfm | VHE DOAS Study Final Report 2002, Red Car Analytics
| Mat Cost | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 | 857290 |  | DOAS Unit Installed Cost
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 | 985883.5 |  | VAV AHU Cost with OH&P
CHW Piping | Capacity
| Qty (ft) | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | Linear feet | Linear Feet of Ductwork, assumes trunk duct around perimeter, with branch ductwork to each of 120 zones
| Unit Cost | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | $/LF | MEP CA Office Project Avg (NORESCO), combined material and labor cost
| Mat Cost | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 |  | Heating Hot Water Ductwork Cost, Total Installed Cost
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | n/a (cost abvoe is installed cost)
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 |  | Heating Hot Water Ductwork Cost with OH&P
HW Piping | Capacity
| Qty (ft) | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | Linear feet | Linear feet of Hydronic Piping
| Unit Cost | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | $/LF | MEP CA Office Project Avg (NORESCO), combined material and labor cost [- see Sheet1
| Mat Cost | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 |  | HW Piping Installed Cost
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | n/a
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 |  | Piping Installed Cost with OH&P
FPFC Unit | Number of Zone | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | Number of Zones
| Subtotal | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 | 461145.4 |  | Fan coil unit total costs, with unit costs from MEP CA Office Project Avg (NORESCO)
| Pump Nameplate HP | 10 | 12 | 10 | 12 | 10 | 8 | 8 | 10 | 8 | 10 | 10 | 10 | 10 | 12 | 8 | 12 | hp | Circulation Pump Nameplate HP - gpm/ton and W/gpm from ACM standard design assumptions (Note: no code requirement on pump power)
Circ Pump | All (3/4 HP) | 16620.3 | 18121.7 | 16620.3 | 18121.7 | 16620.3 | 15118.9 | 15118.9 | 16620.3 | 15118.9 | 16620.3 | 16620.3 | 16620.3 | 16620.3 | 18121.7 | 15118.9 | 18121.7 |  | RS Means Online 2023
Storage | Capacity (gal) | 1594.1204 | 1694.1204 | 1394.1204 | 1694.1204 | 1494.1204 | 994.1204 | 994.1204 | 1294.1204 | 1194.1204 | 1294.1204 | 1594.1204 | 1594.1204 | 1494.1204 | 1694.1204 | 1094.1204 | 1694.1204 | gal | Storage Requirement, 10 gal/ton, less volume in hydronic loop
| Qty (gal) | 1600 | 1700 | 1400 | 1700 | 1500 | 1000 | 1000 | 1300 | 1200 | 1300 | 1600 | 1600 | 1500 | 1700 | 1100 | 1700 | gal | Storage Requirement rounded to nominal size
Unit Cost
| Mat Cost + Labor Cost | 33229.51 | 35278.81 | 29130.91 | 35278.81 | 31180.21 | 20933.71 | 20933.71 | 27081.61 | 25032.31 | 27081.61 | 33229.51 | 33229.51 | 31180.21 | 35278.81 | 22983.01 | 35278.81 |  | RS Means Online (2023)
Labor Cost (not used)
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 38213.9365 | 40570.6315 | 33500.5465 | 40570.6315 | 35857.2415 | 24073.7665 | 24073.7665 | 31143.8515 | 28787.1565 | 31143.8515 | 38213.9365 | 38213.9365 | 35857.2415 | 40570.6315 | 26430.4615 | 40570.6315
Suppl Htr | Capacity (kW) | 633.0598 | 668.2298 | 562.7198 | 668.2298 | 597.8898 | 422.0399 | 422.0399 | 527.5498 | 492.3798 | 527.5498 | 633.0598 | 633.0598 | 597.8898 | 668.2298 | 457.2098 | 668.2298 | kW | Supplemental Electric Boiler Size Requirement at 50% of design heating load
Qty | bar: CZ1 to CZ16
| Total Cost (Mat + Labor) | 30520.8421 | 31929.7166 | 27703.093 | 31929.7166 | 29111.9675 | 22067.5947 | 22067.5947 | 26294.2184 | 24885.3438 | 26294.2184 | 30520.8421 | 30520.8421 | 29111.9675 | 31929.7166 | 23476.4693 | 31929.7166 |  | Electric Boiler Installed Cost, RS Means Online (2023)
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 35098.9684 | 36719.1741 | 31858.5569 | 36719.1741 | 33478.7627 | 25377.7339 | 25377.7339 | 30238.3512 | 28618.1454 | 30238.3512 | 35098.9684 | 35098.9684 | 33478.7627 | 36719.1741 | 26997.9397 | 36719.1741
SUBTOTAL | No controls, Cx | 2372307.3449 | 2391004.2456 | 2334913.5434 | 2391004.2456 | 2353610.4442 | 2260125.9404 | 2260125.9404 | 2316216.6427 | 2297519.7419 | 2316216.6427 | 2372307.3449 | 2372307.3449 | 2353610.4442 | 2391004.2456 | 2278822.8412 | 2391004.2456
| Controls | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 |  | Feng, J. and Hwakong Cheng 2018. Construction and Energy Costs for Radiant vs. VAV Systems in the California Bay Area, Final Report, Taylor Engineering and UC Berkeley, EPIC-14-009, November 15, 2018.
| Commissioning (Htg System) | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 |  | Cx Costs are differential function testing estimates for bours (NORESCO), using a loaded Cx labor rate of $160/hr.
TOTAL | Project Total (Costed Portion) | 2931522.3449 | 2950219.2456 | 2894128.5434 | 2950219.2456 | 2912825.4442 | 2819340.9404 | 2819340.9404 | 2875431.6427 | 2856734.7419 | 2875431.6427 | 2931522.3449 | 2931522.3449 | 2912825.4442 | 2950219.2456 | 2838037.8412 | 2950219.2456
Large Office Prototype - VAV+AWHP (Proposed Case)
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Units
AWHP | Capacity | 200 | 190 | 170 | 200 | 180 | 130 | 120 | 130 | 140 | 150 | 200 | 190 | 170 | 180 | 130 | 200 | tons | Heating Capacity, tons (rounded up to nearest 10 tons)
Qty | bar: CZ1 to CZ16
| Unit Cost | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | $/ton | Distributor cost, Trane Ascend ACX, unit only with no desuperheater
| Mat Cost | 256000 | 243200 | 217600 | 256000 | 230400 | 166400 | 153600 | 166400 | 179200 | 192000 | 256000 | 243200 | 217600 | 230400 | 166400 | 256000 |  | Unit cost (rquipment only)
| Labor Cost | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 |  | RS Means Online
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 306544 | 291824 | 262384 | 306544 | 277104 | 203504 | 188784 | 203504 | 218224 | 232944 | 306544 | 291824 | 262384 | 277104 | 203504 | 306544
VAV AHU | Capacity
| Qty (CFM) | 354536 | 367002 | 384753 | 380072 | 367742 | 385061 | 393487 | 392366 | 409809 | 394760 | 413973 | 379320 | 403572 | 430583 | 432427 | 464923 | CFM | Built-Up VAV AHU design CFM, from model.
| Unit Cost | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Mat Cost | 764820.8488 | 791414.5666 | 829282.7749 | 819296.7976 | 792993.2086 | 829939.8313 | 847915.0171 | 845523.5878 | 882734.7397 | 850630.708 | 891617.8009 | 817692.556 | 869429.3476 | 927051.9139 | 930985.7191 | 1000309.4359 |  | RS Means Online, regression of system costs
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 879543.9761 | 910126.7516 | 953675.1911 | 942191.3172 | 911942.1899 | 954430.806 | 975102.2697 | 972352.126 | 1015144.9507 | 978225.3142 | 1025360.471 | 940346.4394 | 999843.7497 | 1066109.701 | 1070633.577 | 1150355.8513
HW Ductwork | Capacity
| Qty (ft) | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | 8600 | ft | Linear Feet of Ductwork, assumes trunk duct around perimeter, with branch ductwork to each of 120 zones
| Unit Cost | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | $/ft | MEP CA Office Project Avg (NORESCO), combined material and labor cost
| Mat Cost | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998 | 2329998
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7 | 2679497.7
HW Piping | Capacity
| Qty (ft) | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | ft | Linear feet of Hydronic Piping
| Unit Cost | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | $/ft | MEP CA Office Project Avg (NORESCO), combined material and labor cost [- see Sheet1
| Mat Cost | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140 | 657140
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711 | 755711
VAV Box | Subtotal | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436 | 389436
120 zones
| Pump Nameplate HP | 12 | 12 | 10 | 12 | 10 | 8 | 8 | 8 | 8 | 10 | 12 | 12 | 10 | 10 | 8 | 12 |  | Circulation Pump Nameplate HP - gpm/ton and W/gpm from ACM standard design assumptions (Note: no code requirement on pump power)
Circ Pump | Subtotal | 18121.7 | 18121.7 | 16620.3 | 18121.7 | 16620.3 | 15118.9 | 15118.9 | 15118.9 | 15118.9 | 16620.3 | 18121.7 | 18121.7 | 16620.3 | 16620.3 | 15118.9 | 18121.7 |  | RS Means Online 2023
Storage | Capacity (gal) | 1458.7028 | 1358.7028 | 1158.7028 | 1458.7028 | 1258.7028 | 758.7028 | 658.7028 | 758.7028 | 858.7028 | 958.7028 | 1458.7028 | 1358.7028 | 1158.7028 | 1258.7028 | 758.7028 | 1458.7028 | gal | Assumes 10 gal/ton total volume, less volume in piping (conversion estimate of 21.43 ft piping holds 1 gal)
| Qty (gal) | 1475 | 1375 | 1175 | 1475 | 1275 | 775 | 675 | 775 | 875 | 975 | 1475 | 1375 | 1175 | 1275 | 775 | 1475 | gal | Round up to nearest 25 gal for indirect storage tank
Unit Cost
| Mat Cost | 30667.885 | 28618.585 | 24519.985 | 30667.885 | 26569.285 | 16322.785 | 14273.485 | 16322.785 | 18372.085 | 20421.385 | 30667.885 | 28618.585 | 24519.985 | 26569.285 | 16322.785 | 30667.885 |  | RS Means Online 2023
| Labor Cost | included | included | included | included | included | included | included | included | included | included | included | included | included | included | included | included
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 35268.0677 | 32911.3727 | 28197.9827 | 35268.0677 | 30554.6777 | 18771.2027 | 16414.5077 | 18771.2027 | 21127.8977 | 23484.5927 | 35268.0677 | 32911.3727 | 28197.9827 | 30554.6777 | 18771.2027 | 35268.0677 |  | Storage Cost with OH&P
Suppl Htr | Capacity (kW) | 703.3998 | 668.2298 | 597.8898 | 703.3998 | 633.0598 | 457.2098 | 422.0399 | 457.2098 | 492.3798 | 527.5498 | 703.3998 | 668.2298 | 597.8898 | 633.0598 | 457.2098 | 703.3998 | kW | Supplemental Heater, kW, sized from energy model
Qty | bar: CZ1 to CZ16
| Total Cost (Mat + Labor) | 33338.5912 | 31929.7166 | 29111.9675 | 33338.5912 | 30520.8421 | 23476.4693 | 22067.5947 | 23476.4693 | 24885.3438 | 26294.2184 | 33338.5912 | 31929.7166 | 29111.9675 | 30520.8421 | 23476.4693 | 33338.5912 |  | RS Means Online 2023
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 38339.3799 | 36719.1741 | 33478.7627 | 38339.3799 | 35098.9684 | 26997.9397 | 25377.7339 | 26997.9397 | 28618.1454 | 30238.3512 | 38339.3799 | 36719.1741 | 33478.7627 | 35098.9684 | 26997.9397 | 38339.3799 |  | Supplemental Electric Boiler Cost with OH&P
SUBTOTAL | No controls, Cx | 5102461.8238 | 5114347.6985 | 5119000.9365 | 5165109.1649 | 5095964.836 | 5043467.5484 | 5045442.1113 | 5061388.8684 | 5122878.5938 | 5106157.2581 | 5248278.3187 | 5144567.3863 | 5165169.4951 | 5250132.3471 | 5159670.3194 | 5373273.6989
| Controls | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 | 1246472.5 |  | Feng, J. and Hwakong Cheng 2018. Construction and Energy Costs for Radiant vs. VAV Systems in the California Bay Area, Final Report, Taylor Engineering and UC Berkeley, EPIC-14-009, November 15, 2018.
| Commissioning (Htg System) | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 |  | Cx Costs are differential function testing estimates for bours (NORESCO), using a loaded Cx labor rate of $160/hr.
TOTAL | Project Total (Costed Portion) | 6380934.3238 | 6392820.1985 | 6397473.4365 | 6443581.6649 | 6374437.336 | 6321940.0484 | 6323914.6113 | 6339861.3684 | 6401351.0938 | 6384629.7581 | 6526750.8187 | 6423039.8863 | 6443641.9951 | 6528604.8471 | 6438142.8194 | 6651746.1989
Large School Prototype - VAV+AWHP (Proposed Case)
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
AWHP | Capacity | 180 | 190 | 160 | 190 | 170 | 120 | 120 | 150 | 140 | 150 | 180 | 180 | 170 | 190 | 130 | 190 | Nominal tons | System Heating Capacity for 50% of heating load from energy model
Qty | bar: CZ1 to CZ16
| Unit Cost | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | $/ton | Distributor cost, Trane Ascend ACX, unit only with no desuperheater
| Mat Cost | 230400 | 243200 | 204800 | 243200 | 217600 | 153600 | 153600 | 192000 | 179200 | 192000 | 230400 | 230400 | 217600 | 243200 | 166400 | 243200 |  | Unit cost (rquipment only)
| Labor Cost | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 | 10560 |  | RS Means Online
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 277104 | 291824 | 247664 | 291824 | 262384 | 188784 | 188784 | 232944 | 218224 | 232944 | 277104 | 277104 | 262384 | 291824 | 203504 | 291824
VAV AHU | Capacity | [17 empty] | Capacity (tons) not used for built-up AHU. Cost is a function of design airflow (cfm).
| Qty (CFM) | 166505 | 176558 | 180164 | 181289 | 174266 | 181210 | 182303 | 184254 | 186954 | 187210 | 190144 | 180573 | 188519 | 200049 | 200596 | 208718 | cfm | VAV AHU design CFM, from model.
Unit Cost (not used)
| Mat Cost | 363694.3165 | 385140.3814 | 392833.0612 | 395233.0237 | 380250.8578 | 395064.493 | 397396.1899 | 401558.2582 | 407318.1682 | 407864.293 | 414123.3952 | 393705.5809 | 410656.7827 | 435253.7317 | 436420.6468 | 453747.3094 |  | RS Means Online (2023), Cost for Built-up VAV Air Handling Unit
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 418248.464 | 442911.4386 | 451758.0204 | 454517.9773 | 437288.4865 | 454324.167 | 457005.6184 | 461791.9969 | 468415.8934 | 469043.937 | 476241.9045 | 452761.418 | 472255.3001 | 500541.7915 | 501883.7438 | 521809.4058 |  | VAV AHU Cost with OH&P
HW Ductwork
| Qty (ft) | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | Linear feet | Linear Feet of Ductwork, assumes trunk duct around perimeter, with branch ductwork to each of 120 zones
| Unit Cost | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | $/LF | MEP CA Office Project Avg (NORESCO), combined material and labor cost
| Mat Cost | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 | 1195343.16 |  | Heating Hot Water Ductwork Cost
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 | 1374644.634 |  | Heating Hot Water Ductwork Cost with OH&P
HW Piping
| Qty (ft) | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | 4412 | Linear feet | Linear feet of Hydronic Piping
| Unit Cost | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | 56.65 | $/LF | MEP CA Office Project Avg (NORESCO), combined material and labor cost [- see Sheet1
| Mat Cost | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8 | 249939.8
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77 | 287430.77
VAV Box | Subtotal | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8 | 149283.8
| Pump Nameplate HP | 10 | 12 | 10 | 12 | 10 | 8 | 8 | 10 | 8 | 10 | 10 | 10 | 10 | 12 | 8 | 12 | hp | Circulation Pump Nameplate HP - gpm/ton and W/gpm from ACM standard design assumptions (Note: no code requirement on pump power)
Circ Pump | Subtotal | 16620.3 | 18121.7 | 16620.3 | 18121.7 | 16620.3 | 15118.9 | 15118.9 | 16620.3 | 15118.9 | 16620.3 | 16620.3 | 16620.3 | 16620.3 | 18121.7 | 15118.9 | 18121.7 |  | RS Means Online 2023
Storage | Capacity (gal) | 1594.1204 | 1694.1204 | 1394.1204 | 1694.1204 | 1494.1204 | 994.1204 | 994.1204 | 1294.1204 | 1194.1204 | 1294.1204 | 1594.1204 | 1594.1204 | 1494.1204 | 1694.1204 | 1094.1204 | 1694.1204 | gal | Storage Requirement, 10 gal/ton, less volume in hydronic loop
| Qty (gal) | 1600 | 1700 | 1400 | 1700 | 1500 | 1000 | 1000 | 1300 | 1200 | 1300 | 1600 | 1600 | 1500 | 1700 | 1100 | 1700 | gal | Storage Requirement rounded to nominal size
Unit Cost
| Mat Cost | 33229.51 | 35278.81 | 29130.91 | 35278.81 | 31180.21 | 20933.71 | 20933.71 | 27081.61 | 25032.31 | 27081.61 | 33229.51 | 33229.51 | 31180.21 | 35278.81 | 22983.01 | 35278.81 |  | RS Means Online (2023). Regression of installed cost with storage capacity in gallons.
Labor Cost
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 38213.9365 | 40570.6315 | 33500.5465 | 40570.6315 | 35857.2415 | 24073.7665 | 24073.7665 | 31143.8515 | 28787.1565 | 31143.8515 | 38213.9365 | 38213.9365 | 35857.2415 | 40570.6315 | 26430.4615 | 40570.6315
Suppl Htr | Capacity (kW) | 633.0598 | 668.2298 | 562.7198 | 668.2298 | 597.8898 | 422.0399 | 422.0399 | 527.5498 | 492.3798 | 527.5498 | 633.0598 | 633.0598 | 597.8898 | 668.2298 | 457.2098 | 668.2298 | kW | Supplemental Electric Boiler Size Requirement at 50% of design heating load
Qty | bar: CZ1 to CZ16
| Total Cost (Mat + Labor) | 30520.8421 | 31929.7166 | 27703.093 | 31929.7166 | 29111.9675 | 22067.5947 | 22067.5947 | 26294.2184 | 24885.3438 | 26294.2184 | 30520.8421 | 30520.8421 | 29111.9675 | 31929.7166 | 23476.4693 | 31929.7166 |  | Electric Boiler Installed Cost, RS Means Online (2023)
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 35098.9684 | 36719.1741 | 31858.5569 | 36719.1741 | 33478.7627 | 25377.7339 | 25377.7339 | 30238.3512 | 28618.1454 | 30238.3512 | 35098.9684 | 35098.9684 | 33478.7627 | 36719.1741 | 26997.9397 | 36719.1741
SUBTOTAL | No controls, Cx | 2596644.8729 | 2641506.1483 | 2592760.6278 | 2653112.6869 | 2596987.9946 | 2519037.7714 | 2521719.2228 | 2584097.7036 | 2570523.2994 | 2591349.6436 | 2654638.3134 | 2631157.8269 | 2631954.8083 | 2699136.5011 | 2585294.249 | 2720404.1155
| Controls | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 | 527215 |  | Feng, J. and Hwakong Cheng 2018. Construction and Energy Costs for Radiant vs. VAV Systems in the California Bay Area, Final Report, Taylor Engineering and UC Berkeley, EPIC-14-009, November 15, 2018.
| Commissioning (Htg System) | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 |  | Cx Costs are differential function testing estimates for bours (NORESCO), using a loaded Cx labor rate of $160/hr.
TOTAL | Project Total (Costed Portion) | 3155859.8729 | 3200721.1483 | 3151975.6278 | 3212327.6869 | 3156202.9946 | 3078252.7714 | 3080934.2228 | 3143312.7036 | 3129738.2994 | 3150564.6436 | 3213853.3134 | 3190372.8269 | 3191169.8083 | 3258351.5011 | 3144509.249 | 3279619.1155

## Plant-side Costs
Plant-side components and regressions
| Storage = (10gal/ton x tons) - (length pipe x 1 gal/21.43 ft pipe) | [5 empty] | Required storage volume is 10 gal/ton less the volume in the hydronic piping
Storage Tank, Stainless Steel Unlined
Source: RS Means
| Cap | Mat | Labor | Total
| 15 | 1075 | 46.5 | 1121.5
| 30 | 1200 | 51 | 1251
| 80 | 1775 | 62 | 1837
| 135 | 2625 | 93 | 2718
| 240 | 4900 | 140 | 5040
| 300 | 6875 | 186 | 7061
| 400 | 8350 | 251 | 8601
| 500 | 10400 | 335 | 10735
Electric Boiler
Source: RSMeans #235213102040
| MBH | Mat | Labor | Total
| 30 | 5525 | 1275 | 6800
| 45 | 5400 | 1275 | 6675
| 60 | 5775 | 1275 | 7050
| 75 | 6100 | 1400 | 7500
| 90 | 6150 | 1400 | 7550
| 105 | 7125 | 1550 | 8675
| 120 | 6800 | 1725 | 8525
| 135 | 7550 | 2050 | 9600
| 150 | 7950 | 2375 | 10325
| 165 | 8175 | 2575 | 10750
| 296 | 16200 | 2800 | 19000
| 370 | 18000 | 3850 | 21850
| 444 | 21600 | 4400 | 26000
| 518 | 23900 | 4775 | 28675
| 592 | 26200 | 4900 | 31100
| 666 | 28400 | 5275 | 33675
| 740 | 28600 | 5400 | 34000
| 814 | 30800 | 5550 | 36350
| 888 | 33300 | 5700 | 39000
| 962 | 35300 | 5850 | 41150
Commercial NG Boilers
Source: AF Supply, Distributor
RS Means for Labor
| Make | Eff | Capacity | Cost |  | MBH | Labor Cost
| Well-McLain | 85.1 | 400 | 7413 |  | 102 | 1650
| Well-McLain | 85.1 | 650 | 10679 |  | 122 | 2150
| Well-McLain | 85.1 | 910 | 13720 |  | 163 | 2375
| Well-McLain | 85.1 | 1040 | 15005 |  | 203 | 2375
| Well-McLain | 85.1 | 1170 | 16622 |  | 240 | 2525
| Well-McLain | 85.1 | 1300 | 17967 |  | 280 | 2675
| Lochinvar Cu |  | 495 | 6661 |  | 320 | 3050
| Lochinvar | 82 | 315 | 4266 |  | 360 | 3425
| Lochinvar |  | 360 | 4455 |  | 400 | 3800
| Lochinvar |  | 399 | 4893 |  | 440 | 4175
| Lochinvar |  | 500 | 6427 |  | 544 | 4800
| LAARS | 85 | 500 | 13121 |  | 765 | 4975
| LAARS | 85 | 750 | 14700 |  | 892 | 5650
| LAARS | 85 | 1250 | 15456
Pump Costs
Pump Sizing
| Large Office | [5 empty] | Pump Sizing gas
| Load | 200 | tons |  | Model |  | Load | 2400
| GPM | 480 | gpm |  | Calc = f (10F delta T) |  |  | 160 | gpm
| Pump Efficacy | 19 | W/gpm | App G | Constant |  |  | 19 | W/gpm
| Pump Power | 9120 | W/gpm |  | Conversion |  |  | 3040 | W/gpm
| Pump bhp | 11.0027 | [5 empty] | 3.6676
| BHP per ton | 0.055013 | [5 empty] | 0.0015282 | Conversion Factor, Pump HP per gpm
From RS Means: assume base mounted pump with coupling guard for easier service (more expensive than close mounted)
RS Means#232123135040
| Size Range |  | Material | Total Installed | HP | $
| 2 HP to 50 gpm |  | 8625 | 10125 | 2 | 10125
| 3 HP to 90 gpm |  | 8525 | 10125 | 3 | 10125
| 5 HP to 225 gpm |  | 12400 | 14635 | 5 | 14635
| 7 1/2 HP to 350 gpm |  | 12000 | 14200 | 7.5 | 14200
| 10 HP to 600 gpm |  | 15200 | 18150 | 10 | 18150
| 15 H to 1000 gpm |  | 16300 | 19350 | 15 | 19350
AWHP Cost
Source: Email correspondence with manufacturer
| Model | Nominal Tons | Htg Cap MBh | Htg Tons | COP@47 | Water Flow (gpm) | Tin | Tout | HX Loss (ft) | Strainer Head Loss (ft) | COST | Cost/Ton | Source
| ACSA | 140 | 1457.58 | 121.465 | 2.89 | 294.55 | 110 | 120 | 4.63 | 3.92 | 175100 | 1441.5675 | Todd Elmgren, Trane, quote on 1/3/2023
| ACSA | 180 | 1992.04 | 166.0033 | 2.8 | 402.55 | 110 | 120 | 11.64 | 1.28 | 214900 | 1294.5523 | Todd Elmgren, Trane, quote on 1/3/2023
| ACSA | 200 | 2148.36 | 179.03 | 2.81 | 434.14 | 110 | 120 | 13.4 | 1.59 | 225300 | 1258.4483 | Todd Elmgren, Trane, quote on 1/3/2023
| ACSA | 230 | 2506.36 | 208.8633 | 2.87 | 506.29 | 110 | 120 | 12.41 | 2.4 | 252400 | 1208.4457 | Todd Elmgren, Trane, quote on 1/3/2023
Quotation Email:
Pricing including : standard safety and operating controls, disconnects, BACnet, insulation, conv outlet, 1st year parts, labor, and refrigerant wty, start-up , freight , no tax
NOTE: Units are heat or cool - not simultaneous
ACSA-140 ……………………………… $ 175,100
ACSA-180………………………………$ 214,800
ACSA-200……………………………..$ 225,300
ACSA- 230……………………………..$ 252,400
Todd Elmgren
Trane Technologies
5335 College Ave. Oakland CA 94618
tjelmgren@trane.com
510-433-8946

## Air-side Costs
Four-Pipe Fan Coil Units
Source: Distributiors. 1-ton $1713, 2 ton $1926, 3 ton $2778
Capacity | Cost (No Heat) | FPFC Mat | Labor | Total
0.5 | 765 | 1071 | 131 | 1202
1 | 880 | 1232 | 174 | 1406
1.5 | 920 | 1288 | 190 | 1478
2 | 1250 | 1750 | 199 | 1949
2.5 | 2450 | 3430 | 209 | 3639
3 | 2675 | 3745 | 261 | 4006
VAV Built-Up Units
Source: RS Means
RS Means Code: 237313102318
CFM | Total Cost
5000 | 16050
6500 | 20550
7500 | 22550
9200 | 28975
11500 | 31925
13200 | 36500
16500 | 45225
19500 | 53225
22000 | 60200
22500 | 60950
27000 | 64250
34000 | 81075
40000 | 88925
Labor Costs - PVAV
Source: RS Means
Nominal Tons | Bare Labor | Eqp Cost (Ref only)
7.5 | 2100 | 6525
10 | 2425 | 8050
12.5 | 2575 | 9100
15 | 2850 | 12200
20 | 3325 | 15700
25 | 3975 | 36900
30 | 4725 | 37200
40 | 6300 | 45400
50 | 7875 | 51500
Distribution System Costs
Source: Adapted from MEP project data of California office buildings, NORESCO (Singer)
These costs are used to determine ductwork and piping installed costs per linear foot (LF).
Distribution Costs - J. Singer (Northern California recent Large Office MEP projects)
Component | Material Cost per ft | Labor | Total Cost
Duct | 24.6 | 246.33 | 270.93
Pipe | 16.32 | 40.33 | 56.65
Pipe Base | 9.792 | 40.33 | 50.122
Duct 32.80 - 16" round with labor
Assume 24.50 with fittings - $50
Duct Insulation - $4.77
Total: $54.77/LF
Terminal Unit Costs
Average Capacity |  | 3.5ton/1250cfm |  | RSMeans |  |  | Terminal Unit Costs
VAV Terminal Unit |  | 3245.3 |  | 233616105660 |  |  | VAV Box, 1250 cfm avg | 3245.3
FPFC |  | 10024.9 |  | 238219103150 |  |  | FPFC, 3.5 ton avg. | 10024.9
Built-Up AHU Replacement Estimate:
1. Replace Centrifugal Fan
RS Means 233416104260 - Belt-Driven Fan. Cost with labor for 40,980 cfm, 25 HP | [5 empty] | 18811.2
[5 empty] | Cost per cfm | 0.45903
2. Repair replace Coils |  |  |  |  | Estimate per cfm | 0.25
3. Repair or replace dampers |  |  |  |  | Estimate per cfm | 0.4
Total | [5 empty] | 1.109

## Sizing
Sizing info from models
Large Office
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Heating Load, tons | 194.6144 | 187.6657 | 162.7542 | 199.9519 | 174.4151 | 122.3392 | 117.4976 | 126.3698 | 131.9117 | 144.9757 | 190.2957 | 180.5482 | 160.5167 | 178.1443 | 124.8733 | 191.5946
AHU CFM | 354536 | 367002 | 384753 | 380072 | 367742 | 385061 | 393487 | 392366 | 409809 | 394760 | 413973 | 379320 | 403572 | 430583 | 432427 | 464923
Secondary School
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Heating Load, tons | 180 | 190 | 160 | 190 | 170 | 120 | 120 | 150 | 140 | 150 | 180 | 180 | 170 | 190 | 130 | 190
AHU CFM | 166505 | 176558 | 180164 | 181289 | 174266 | 181210 | 182303 | 184254 | 186954 | 187210 | 190144 | 180573 | 188519 | 200049 | 200596 | 208718

## Rough Work (hidden)
Sch Floor | Plan Dim 1 | Plan Dim 2 | Run 30' from ends | Run 30' from ends
105443 | 400 | 263.6075 | 340 | 203.6075 | 1087.215 | Avg 50' supply return duct per zone
[5 empty] | 2174.43 | 2300
Maintenance Tasks for FCUs.

## AGIC (hidden)
Avoided Gas Infrstructure Costs |  |  | Source: CPUC
Medium Office
| Amount |  | Included?
Gas T&D Avoided Costs | 0.1 | therm
GHG Abatement Cost | 114 | ton
Service Extension PG&E | 15535 | bldg | Service line including trenching
Service Extension PG&E | 3330 | bldg | Service line including trenching (greenfield)
Meter | 1309 | bldg | Meter
Submeters | 1434 | x 3 | Submeter, Leviton GMP 10-251, with installation
Medium Office - Total
Large Office
Gas T&D Avoided Costs | 0.1 | therm
GHG Abatement Cost | 114 | ton
Service Extension PG&E | 15535 | bldg | Service line including trenching
Service Extension PG&E | 3330 | bldg | Service line including trenching (greenfield) |  |  |  |  | SCE: $1567
Meter | 11714 | bldg | Per Meter
Avoided Gas Lines to Boiler | 2000 | bldg
Submeters | 1434 | 12 | Submeter, Leviton GMP 10-251, with installation
Subtotal | 29249
With Submetering | 46457
Medium Office
| CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Service Line (high) | 15535 | 15535 | 15535 | 15535 | 15535 | 1567 | 1863 | 1863 | 1567 | 1567 | 15535 | 1863 | 15535 | 1567 | 15535 | 15535
Service line (rural, no trenching) | 2814 | 2814 | 2814 | 2814 | 2814 | 1567 | 1863 | 1863 | 1567 | 1567 | 2814 | 1863 | 2814 | 1567 | 1567 | 2814
Meter | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309
Submeters (qty 3) | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302
Avoided Gas Lines | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
AGIC Cost High Estimate | 23146 | 23146 | 23146 | 23146 | 23146 | 9178 | 9474 | 9474 | 9178 | 9178 | 23146 | 9474 | 23146 | 9178 | 23146 | 23146
AGIC Cost Low Estimate | 10425 | 10425 | 10425 | 10425 | 10425 | 9178 | 9474 | 9474 | 9178 | 9178 | 10425 | 9474 | 10425 | 9178 | 9178 | 10425
AGIC Cost High Est (per sf) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
AGIC Cost Low Est (per sf) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Large Office
| CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Service Line (high) | 15535 | 15535 | 15535 | 15535 | 15535 | 1567 | 1863 | 1863 | 1567 | 1567 | 15535 | 1863 | 15535 | 1567 | 15535 | 15535
Service line (rural, no trenching) | 2814 | 2814 | 2814 | 2814 | 2814 | 1567 | 1863 | 1863 | 1567 | 1567 | 2814 | 1863 | 2814 | 1567 | 1567 | 2814
Meter | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309
Submeters (qty 12) | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208 | 17208
Avoided Gas Lines | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
AGIC Cost High Estimate | 36052 | 36052 | 36052 | 36052 | 36052 | 22084 | 22380 | 22380 | 22084 | 22084 | 36052 | 22380 | 36052 | 22084 | 36052 | 36052
AGIC Cost Low Estimate | 23331 | 23331 | 23331 | 23331 | 23331 | 22084 | 22380 | 22380 | 22084 | 22084 | 23331 | 22380 | 23331 | 22084 | 22084 | 23331
AGIC Cost High Est (per sf) | 0.072308 | 0.072308 | 0.072308 | 0.072308 | 0.072308 | 0.044293 | 0.044887 | 0.044887 | 0.044293 | 0.044293 | 0.072308 | 0.044887 | 0.072308 | 0.044293 | 0.072308 | 0.072308
AGIC Cost Low Est (per sf) | 0.046794 | 0.046794 | 0.046794 | 0.046794 | 0.046794 | 0.044293 | 0.044887 | 0.044887 | 0.044293 | 0.044293 | 0.046794 | 0.044887 | 0.046794 | 0.044293 | 0.044293 | 0.046794
Large School | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Service Line (high) | 15535 | 15535 | 15535 | 15535 | 15535 | 1567 | 1863 | 1863 | 1567 | 1567 | 15535 | 1863 | 15535 | 1567 | 15535 | 15535
Service line (rural, no trenching) | 2814 | 2814 | 2814 | 2814 | 2814 | 1567 | 1863 | 1863 | 1567 | 1567 | 2814 | 1863 | 2814 | 1567 | 1567 | 2814
Meter | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309
Submeters (qty 1) | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434 | 1434
Avoided Gas Lines | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
AGIC Cost High Estimate | 20278 | 20278 | 20278 | 20278 | 20278 | 6310 | 6606 | 6606 | 6310 | 6310 | 20278 | 6606 | 20278 | 6310 | 20278 | 20278
AGIC Cost Low Estimate | 7557 | 7557 | 7557 | 7557 | 7557 | 6310 | 6606 | 6606 | 6310 | 6310 | 7557 | 6606 | 7557 | 6310 | 6310 | 7557
AGIC Cost High Est (per sf) | 0.096156 | 0.096156 | 0.096156 | 0.096156 | 0.096156 | 0.029921 | 0.031325 | 0.031325 | 0.029921 | 0.029921 | 0.096156 | 0.031325 | 0.096156 | 0.029921 | 0.096156 | 0.096156
AGIC Cost Low Est (per sf) | 0.015157 | 0.015157 | 0.015157 | 0.015157 | 0.015157 | 0.012656 | 0.013249 | 0.013249 | 0.012656 | 0.012656 | 0.015157 | 0.013249 | 0.015157 | 0.012656 | 0.012656 | 0.015157
Ealier Distribution Gas Line Install estimate from Colby Jones of AES (large GC of retail projects)
John,
There is a lot of different factors that could increase or decrease the prices.
Below is an average that we typically use.
Sch. 40 Steel Pipe.
¾” Gas Pipe - $12.50/ft
1” Gas Pipe - $15.30/ft
1-1/4” Gas Pipe - $17.25/ft
1-1/2" Gas Pipe - $20/ft
Fiorentini Regulator
¾” Gas Regulator - $72/ea
The pipe support depends on what you’re wanting to use. You will need one every 6-8ft depending on the size of the pipe.
Target Pipe support is around $65 each.
Basic 2x4 will run you about $10 each.

## Implan_Costs (hidden)
Space Type | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Large Office | 0 | 0 | 3.234 | 1.578 | 0 | 1.422 | 0.825 | 2.288 | 4.152 | 0.3916 | 0.1088 | 0.5747 | 0 | 0.2002 | 0.01303 | 0.04995
Medium Office | 0.1302 | 0.4761 | 1.372 | 0.7442 | 0.3705 | 1.201 | 0.8046 | 1.646 | 3.184 | 1.174 | 0.2685 | 2.799 | 0.5859 | 0.3482 | 0.2629 | 0.102
Small Office | 0.01306 | 0.4369 | 0.1869 | 0.02019 | 0.06423 | 0.1481 | 0.2339 | 0.1594 | 0.36 | 0.4167 | 0.0933 | 0.5443 | 0.3852 | 0.04404 | 0.1051 | 0.03313
Large Retail | 0 | 0 | 1.097 | 0.5497 | 0.1491 | 0.6978 | 0.3746 | 0.8316 | 1.664 | 0.6327 | 0.2997 | 1.303 | 0.3564 | 0.1442 | 0.1803 | 0.05547
Medium Retail | 0.08421 | 0.348 | 0.7947 | 0.4459 | 0.08574 | 0.6027 | 0.2856 | 0.8641 | 1.424 | 0.8224 | 0.142 | 0.6274 | 0.379 | 0.18 | 0.1242 | 0.08122
Strip Mall | 0.001146 | 0.1543 | 0.504 | 0.2256 | 0.007439 | 0.5629 | 0.4878 | 0.9855 | 1.065 | 1.345 | 0.07164 | 0.5928 | 0.3253 | 0.3206 | 0.1001 | 0.0602
Mixed-use Retail | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large School | 0.006476 | 0.1273 | 0.8761 | 0.4418 | 0.03636 | 0.5941 | 0.6084 | 0.9052 | 1.421 | 0.8535 | 0.3545 | 1.152 | 0.6149 | 0.1661 | 0.08573 | 0.0681
Small School | 0.0665 | 0.2698 | 0.4566 | 0.2294 | 0.1395 | 0.3155 | 0.2944 | 0.3516 | 0.6581 | 0.3481 | 0.09881 | 0.7763 | 0.3025 | 0.107 | 0.03728 | 0.04489
Non-refrigerated Warehouse | 0.06177 | 0.3672 | 2.16 | 1.118 | 0.1776 | 1.363 | 0.7108 | 1.948 | 3.01 | 1.36 | 0.6315 | 2.844 | 0.8203 | 0.3618 | 0.3673 | 0.1381
Hotel | 0.03627 | 0.2154 | 1.033 | 0.5306 | 0.1095 | 0.5527 | 0.4822 | 0.7835 | 1.183 | 0.5716 | 0.1534 | 0.8029 | 0.2557 | 0.1375 | 0.1248 | 0.04395
Assembly | 0.01028 | 0.3935 | 1.583 | 0.5574 | 0.05869 | 0.7868 | 0.7991 | 1.431 | 1.824 | 1.144 | 0.1669 | 1.414 | 0.3043 | 0.2453 | 0.118 | 0.08429
Hospital | 0.02939 | 0.1746 | 0.8416 | 0.4358 | 0.07972 | 0.3285 | 0.549 | 0.4412 | 0.7894 | 0.8128 | 0.1459 | 0.8253 | 0.2729 | 0.1417 | 0.115 | 0.04813
Laboratory | 0.000819 | 0.0531 | 0.6313 | 0.3632 | 0.02078 | 0.07327 | 0.05265 | 0.1017 | 0.1214 | 0.06227 | 0.008372 | 0.04996 | 0.009723 | 0.01063 | 0.006101 | 0.003518
Restaurant | 0.0139 | 0.08256 | 0.3269 | 0.1667 | 0.03403 | 0.3365 | 0.2036 | 0.4933 | 0.8189 | 0.4129 | 0.07099 | 0.3135 | 0.1414 | 0.1015 | 0.04739 | 0.0296
Enclosed Parking Garage | 0.000176 | 0.009137 | 1.83 | 1.245 | 0.004558 | 2.585 | 0.7059 | 2.265 | 1.527 | 0.05053 | 0.001585 | 0.04116 | 0.002972 | 0.0152 | 0.003691 | 0.007247
Open Parking Garage | 0.002272 | 0.1182 | 2.474 | 1.682 | 0.05894 | 3.648 | 1.201 | 3.197 | 2.155 | 0.6535 | 0.0205 | 0.5323 | 0.03843 | 0.1965 | 0.04773 | 0.09372
Incremental Costs for IMPLAN Input
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | $/sf
Large Off | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Med Off | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Large Sch | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[17 empty] | #REF! | Cost $/sf
[17 empty] | 38.6179 | Square ft (x 10^6)