## Index
Tab Name | Purpose
Final Results | Final incremental costs including first costs, maintenance costs, and replacement costs
Proto Costing | Cost buildup for each prototype and system type
Air-side Component Costs | Air-side distribution component costs
Plant Equipment Costs | Plant component data and regressions
VRF Costing Approach
Costs are developed for individual system components using RS Means, manufacturer direct quotes, and other data sources. Cost versus capacity regressions are developed for components where possible. This allows costs to be calculated as models are revised.
Model sizing output for a given prototype and case is combined with component costs to develop prototype costs. These costs are applicable to a specific prototype and system configuration. These costs represent the first cost for the system in the context of the proposed measure, i.e., only those components of a system that are changing between the baseline and proposed case are costed.
Finally, present value of maintenance and replacement costs is added to the incremental cost to calculate the total incremental cost of the measure.

## Final Results
Small School Prototype Incremental First Costs and Maintenance and Replacement Costs
Maintenance and Replacement Costs Calculation
|  | Parameter | Value |  | Source
|  | Discount Rate | 3% |  | CEC Assumption
|  | Small School Num Zones | 24 |  | Assume 1 zone per classroom; avg approximately 1,000 SF/zone
|  | Small School Floor Area | 24403 |  | Prototype Definition
|  | Component | Annual Maint | EUL | Repl Discount | PV of Maint. Cost
|  | PVAV | 500 | 20 | 0.55368 | -10094.2273
|  | VRF | 300 | 20 | 0.55368 | -6056.5364
|  | Boiler | 500 | 25 | 0.47761 | -10094.2273
|  | AWHP | 300 | 15 | 0.64186 | -6056.5364
|  | Pump | 50 | 20 | 0.55368 | -1009.4227
|  | FPFC | 120 | 20 | 0.55368 | -2422.6146
|  | VAV Terminal Unit | 45 | 20 | 0.55368 | -908.4805
|  | DOAS | 500 | 20 | 0.55368 | -10094.2273
1. O&M for Built-Up VAV assumes replacement of fans and coils without entire cabinet. Pump maintenance cost is neutral for the AWHP case.
2. Annual Maintenance Cost estimates from O&M equipment task lists and an assumed burdened labor rate of $100-$120/hr.
3. EUL = Expected Useful Life of Equipment, from ASHRAE Equipment Life Expectancy Chart
4. Repl Discount = Discount factor for equipment replacement after EUL period.
5. PV of Maint Cost = Total maintenance cost over expected life, per unit, accounting for the discount rate.
6. FPFC estimated annual maintenance (incremental over VAV terminal units) is 2 hours per FPFC unit.
Proposed First Cost - proposed HVAC system first cost of all costed components. Note for some buildings this may not include systems (chiller, tower) that have a neutral cost.
Replacement Cost - replacement cost of all systems in table above applicable to the design, modified by the Replacement Discount factor in colum G.
For VRF/DOAS, Replacement Cost includes condenser unit replacement at $1620/ton and energy recovery section of DOAS replacement at $14,585, with discount rate aplpied..
Maintenance Cost - the total maintenance cost of all system components in the table above, column H, multiplied by the number of components of each type.
Incr Cost - the incremental HVAC system cost over the baseline, per square foot of building floor area.
AGIC Avoided Cost - the avoided cost of gas infrastructure (running gas lines to building, and runnling gas lines to HVAC units). This only applies to office buildings, not to schools.
Net Incremental Cost - the net incremental cost over the standard design (2022 baseline) HVAC system, per square foot of floor area.
Small School VRF/DOAS Cost-Effectiveness
|  | CZ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
| Base | Baseline First Cost | 744155.4227 | 755868.8107 | 749689.5353 | 758206.4378 | 752856.6822 | 753796.291 | 748586.588 | 757873.8284 | 757214.413 | 758580.5857 | 759831.1947 | 750430.5313 | 751825.0448 | 759783.4897 | 761884.2299 | 759521.7197
|  | Replacement Cost | 82251.0291 | 88724.0277 | 85291.8448 | 89965.5285 | 87152.543 | 87745.7513 | 84873.6854 | 89900.9168 | 89559.1027 | 90301.5465 | 90931.8765 | 85779.7437 | 86598.4284 | 90820.0734 | 92234.7148 | 90634.7714
|  | Maintenance Cost | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356 | 53095.6356
|  | Total | 879502.0873 | 897688.4739 | 888077.0157 | 901267.6019 | 893104.8608 | 894637.6778 | 886555.909 | 900870.3807 | 899869.1512 | 901977.7678 | 903858.7068 | 889305.9106 | 891519.1088 | 903699.1987 | 907214.5803 | 903252.1267
| VRF/DOAS | Baseline First Cost | 722039.5976 | 793659.8795 | 755889.0826 | 803575.8405 | 753049.5119 | 775135.0615 | 789468.1323 | 802854.6797 | 784510.1519 | 791135.8167 | 802313.8091 | 769906.6456 | 785366.5303 | 795237.4188 | 834630.8274 | 793299.2991
|  | Replacement Cost | 70177.6627 | 84425.8743 | 76911.7136 | 86398.5656 | 76346.8065 | 80740.5282 | 83591.9638 | 86255.0971 | 82605.6182 | 83923.7346 | 86147.4958 | 79700.3818 | 82775.987 | 84739.7115 | 92576.6762 | 84354.14
|  | Maintenance Cost | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129 | 74293.5129
|  | Total | 866510.7731 | 952379.2667 | 907094.3091 | 964267.919 | 903689.8314 | 930169.1025 | 947353.6091 | 963403.2897 | 941409.2829 | 949353.0642 | 962754.8178 | 923900.5404 | 942436.0301 | 954270.6432 | 1001501.0166 | 951946.952
| Cost-Effectiveness | Incremental Cost | -12991.3142 | 54690.7927 | 19017.2934 | 63000.3171 | 10584.9706 | 35531.4247 | 60797.7001 | 62532.909 | 41540.1317 | 47375.2965 | 58896.111 | 34594.6297 | 50916.9214 | 50571.4445 | 94286.4363 | 48694.8253
|  | Incremental Cost / SF | -0.53237 | 2.2412 | 0.7793 | 2.5817 | 0.43376 | 1.456 | 2.4914 | 2.5625 | 1.7023 | 1.9414 | 2.4135 | 1.4176 | 2.0865 | 2.0723 | 3.8637 | 1.9954
|  | LSC Energy Model Savings | 3.7179 | 2.4817 | 1.3742 | 4.8512 | 1.3105 | 0.73931 | 0.35402 | 3.3377 | 3.3174 | 4.6902 | 7.5208 | 4.8209 | 6.6574 | 7.1409 | 9.5638 | 2.7811
|  | BCR, Small School LCC | Infinite | 1.1073 | 1.7634 | 1.8791 | 3.0213 | 0.50776 | 0.14209 | 1.3025 | 1.9488 | 2.4159 | 3.1162 | 3.4006 | 3.1907 | 3.4458 | 2.4753 | 1.3937
Infinite
|  | -0.53237 | 1.1073
|  | 2.2412 | 1.7634
|  | 0.7793 | 1.8791
|  | 2.5817 | 3.0213
|  | 0.43376 | 0.50776
|  | 1.456 | 0.14209
|  | 2.4914 | 1.3025
|  | 2.5625 | 1.9488
|  | 1.7023 | 2.4159
|  | 1.9414 | 3.1162
|  | 2.4135 | 3.4006
|  | 1.4176 | 3.1907
|  | 2.0865 | 3.4458
|  | 2.0723 | 2.4753
|  | 3.8637 | 1.3937
1.9954

## Proto Costing
| Small School | FloorArea | 24404 | sf
Small School Prototype - Base Case
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Gas Boiler | Capacity | 625 | 633 | 640 | 667 | 571 | 524 | 516 | 590 | 575 | 584 | 624 | 590 | 560 | 679 | 517 | 705
Qty | bar: CZ1 to CZ16
| Mat Cost | 9637.625 | 9739.777 | 9829.16 | 10173.923 | 8948.099 | 8347.956 | 8245.804 | 9190.71 | 8999.175 | 9114.096 | 9624.856 | 9190.71 | 8807.64 | 10327.151 | 8258.573 | 10659.145
| Labor Cost | 4617.1375 | 4656.9639 | 4691.812 | 4826.2261 | 4348.3093 | 4114.3292 | 4074.5028 | 4442.897 | 4368.2225 | 4413.0272 | 4612.1592 | 4442.897 | 4293.548 | 4885.9657 | 4079.4811 | 5015.4015
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 16392.9769 | 16556.252 | 16699.1178 | 17250.1715 | 15290.8695 | 14331.628 | 14168.3528 | 15678.648 | 15372.5071 | 15556.1917 | 16372.5675 | 15678.648 | 15066.3662 | 17495.0842 | 14188.7622 | 18025.7285
PVAV | Capacity | 35 | 54 | 46 | 60 | 47 | 49 | 47 | 61 | 61 | 62 | 65 | 59 | 61 | 68 | 74 | 44
| Qty (CFM) | 14735 | 19443 | 16866 | 20113 | 18731 | 19505 | 17448 | 20618 | 20474 | 20956 | 21133 | 17584 | 18402 | 20656 | 22860 | 20333
| Unit Cost | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Mat Cost | 39923.3755 | 49966.9519 | 44469.4378 | 51396.2629 | 48448.0423 | 50099.2165 | 45711.0184 | 52473.5794 | 52166.3842 | 53194.6348 | 53572.2289 | 46001.1472 | 47746.1866 | 52554.6448 | 57256.438 | 51865.5889
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 45911.8818 | 57461.9947 | 51139.8535 | 59105.7023 | 55715.2486 | 57614.099 | 52567.6712 | 60344.6163 | 59991.3418 | 61173.83 | 61608.0632 | 52901.3193 | 54908.1146 | 60437.8415 | 65844.9037 | 59645.4272
HW Ductwork | Capacity
| Qty (ft) | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440
| Unit Cost | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93 | 270.93
| Mat Cost | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2 | 390139.2
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08 | 448660.08
HW Piping | Capacity (ft) | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280 | 1280
| Unit Cost | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122 | 50.122
| Mat Cost | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16 | 64156.16
| Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584 | 73779.584
VAV Box | Subtotal | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2 | 77887.2
Number Zones | 24
Circ Pump | Pump Motorhorsepower | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Subtotal | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7 | 10614.7
SUBTOTAL | No controls, Cx | 673246.4227 | 684959.8107 | 678780.5353 | 687297.4378 | 681947.6822 | 682887.291 | 677677.588 | 686964.8284 | 686305.413 | 687671.5857 | 688922.1947 | 679521.5313 | 680916.0448 | 688874.4897 | 690975.2299 | 688612.7197
| Controls | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909 | 54909
| Commissioning (Htg System) | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000
| Subtotal | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909 | 70909
TOTAL | Project Total (Costed Portion) | 744155.4227 | 755868.8107 | 749689.5353 | 758206.4378 | 752856.6822 | 753796.291 | 748586.588 | 757873.8284 | 757214.413 | 758580.5857 | 759831.1947 | 750430.5313 | 751825.0448 | 759783.4897 | 761884.2299 | 759521.7197
Small School Prototype - VRF/DOAS (Proposed Case)
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
VRF | Capacity | 32.21 | 48.1 | 39.72 | 50.3 | 39.09 | 43.99 | 47.17 | 50.14 | 46.07 | 47.54 | 50.02 | 42.83 | 46.26 | 48.45 | 57.19 | 48.02
Qty
| Mat Cost (per ton) | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5
| Labor Cost (per ton) | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 86728.9681 | 129514.541 | 106950.4692 | 135438.283 | 105254.1249 | 118447.9139 | 127010.4137 | 135007.4654 | 124048.5427 | 128006.6794 | 134684.3522 | 115324.4863 | 124560.1386 | 130456.9545 | 153990.3659 | 129299.1322
Condensate Line | Qty | 32.21 | 48.1 | 39.72 | 50.3 | 39.09 | 43.99 | 47.17 | 50.14 | 46.07 | 47.54 | 50.02 | 42.83 | 46.26 | 48.45 | 57.19 | 48.02
| Subtotal | 10210.57 | 15247.7 | 12591.24 | 15945.1 | 12391.53 | 13944.83 | 14952.89 | 15894.38 | 14604.19 | 15070.18 | 15856.34 | 13577.11 | 14664.42 | 15358.65 | 18129.23 | 15222.34
Rx Piping | Capacity | 32.21 | 48.1 | 39.72 | 50.3 | 39.09 | 43.99 | 47.17 | 50.14 | 46.07 | 47.54 | 50.02 | 42.83 | 46.26 | 48.45 | 57.19 | 48.02
Qty
Unit Cost
| Mat Cost | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4
| Labor Cost | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 48239.1454 | 72036.7245 | 59486.4594 | 75331.5435 | 58542.943 | 65881.4036 | 70643.9146 | 75091.9203 | 68996.5051 | 71198.0433 | 74912.2029 | 64144.1353 | 69281.0577 | 72560.9003 | 85650.3175 | 71916.9129
Indoor Units | Capacity
Qty
| Installed Cost per Unit | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
| Labor Cost (per ton) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000
DOAS Unit | Capacity
"Std Package" | Qty | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285 | 7285
110% multiplier | Unit Cost
on Std HRV Cost | Mat Cost | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14
for bypass | Labor Cost | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85 | 72922.85
DOAS Ductwork | DOAS vs. VAV Ductwork (Note 1) | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
| Qty (LF) | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440 | 1440
| Mat Cost | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68
| Labor Cost | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064 | 358928.064
SUBTOTAL | No controls, Cx | 637029.5976 | 708649.8795 | 670879.0826 | 718565.8405 | 668039.5119 | 690125.0615 | 704458.1323 | 717844.6797 | 699500.1519 | 706125.8167 | 717303.8091 | 684896.6456 | 700356.5303 | 710227.4188 | 749620.8274 | 708289.2991
| Controls | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010 | 61010
| Commissioning (Htg System) | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000 | 24000
TOTAL | Project Total (Costed Portion) | 722039.5976 | 793659.8795 | 755889.0826 | 803575.8405 | 753049.5119 | 775135.0615 | 789468.1323 | 802854.6797 | 784510.1519 | 791135.8167 | 802313.8091 | 769906.6456 | 785366.5303 | 795237.4188 | 834630.8274 | 793299.2991
Note 1. DOAS Ductwork installation costs discounted by 20% in comparison to central AHU VAV ductwork costs. DOAS ductwork serving only ventiation will be much smaller than conventional ductwork.
Table 1-08162024. Incremental First Cost, Small School, PVAV to VRF/DOAS
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
| Incr First Cost, less controls, Cx | -36216.8251 | 23690.0688 | -7901.4527 | 31268.4027 | -13908.1702 | 7237.7705 | 26780.5444 | 30879.8513 | 13194.7389 | 18454.231 | 28381.6144 | 5375.1143 | 19440.4855 | 21352.929 | 58645.5975 | 19676.5794
| Incr Cost/SF, less controls, Cx | -1.4841 | 0.97075 | -0.32378 | 1.2813 | -0.56991 | 0.29658 | 1.0974 | 1.2654 | 0.54068 | 0.7562 | 1.163 | 0.22026 | 0.79661 | 0.87498 | 2.4031 | 0.80629
| Incr First Cost | -22115.8251 | 37791.0688 | 6199.5473 | 45369.4027 | 192.8298 | 21338.7705 | 40881.5444 | 44980.8513 | 27295.7389 | 32555.231 | 42482.6144 | 19476.1143 | 33541.4855 | 35453.929 | 72746.5975 | 33777.5794
| Incr First Cost/SF | -0.90624 | 1.5486 | 0.25404 | 1.8591 | 0.0079016 | 0.8744 | 1.6752 | 1.8432 | 1.1185 | 1.334 | 1.7408 | 0.79807 | 1.3744 | 1.4528 | 2.9809 | 1.3841
Assumptions:
1. Prototype Model of 24,404 SF floor area, single story assumed.
2.Assume similar zoning as energy model, but with each classroom as having its own zone, for a total of 24 zones (energy model has 12).
3. Duct Layout assumes perimeter band of ductwork as ~20 feet from exterior for 480 LF of ductwork; assumes 40 LF of ductwork for each zone, for duct costing purposes.
4. All zones except corridor zones and MEP/elec room assumed to require reheat. HW piping length is 20/24 times the duct length.
5. Ductwork and piping instlled costs per LF the same as other building types.
6. Revised Indoor Unit average installation cost of $2500 per unit (zone)as a conservativ estimate.
7. VRF Condensate Piping at $317 per ton.
8. Maintenace Costs not included in this estimate.
9. Controls costs assumes slight increment for VRF system ($2.25-$2.50/sf). Commissioning assumes 50% labor increment for VRF system, depending on Cx agent familiarity.

## Airside Component Costs
Airside Component Costs
Terminal Unit Costs
Average Capacity | 3.5ton/1250cfm | Source
VAV Terminal Unit | 3245.3 | RSMeans 233616105660
Labor Costs - PVAV (RSMeansOnline), gas heat
Nominal Tons | Bare Labor | Eqp Cost (Ref only)
7.5 | 2100 | 6525
10 | 2425 | 8050
12.5 | 2575 | 9100
15 | 2850 | 12200
20 | 3325 | 15700
25 | 3975 | 36900
30 | 4725 | 37200
40 | 6300 | 45400
50 | 7875 | 51500
Distribution Costs - J. Singer (Northern California recent Large Office MEP projects)
Component | Material Cost per ft | Labor | Total Cost
Duct | 24.6 | 246.33 | 270.93
Pipe | 16.32 | 40.33 | 56.65
Pipe Base | 9.792 | 40.33 | 50.122
Duct 32.80 - 16" round with labor
Assume 24.50 with fittings - $50
Duct Insulation - $4.77
Total: $54.77/LF

## Plant Equipment Costs
Component Data and Regressions
Electric Boiler |  | RSMeans #235213102040
MBH | Mat | Labor | Total
30 | 5525 | 1275 | 6800
45 | 5400 | 1275 | 6675
60 | 5775 | 1275 | 7050
75 | 6100 | 1400 | 7500
90 | 6150 | 1400 | 7550
105 | 7125 | 1550 | 8675
120 | 6800 | 1725 | 8525
135 | 7550 | 2050 | 9600
150 | 7950 | 2375 | 10325
165 | 8175 | 2575 | 10750
296 | 16200 | 2800 | 19000
370 | 18000 | 3850 | 21850
444 | 21600 | 4400 | 26000
518 | 23900 | 4775 | 28675
592 | 26200 | 4900 | 31100
666 | 28400 | 5275 | 33675
740 | 28600 | 5400 | 34000
814 | 30800 | 5550 | 36350
888 | 33300 | 5700 | 39000
962 | 35300 | 5850 | 41150
Commercial NG Boilers - AF Supply, Distributor
RS Means for Labor
Make | Eff | Capacity | Cost |  | MBH | Labor Cost
Well-McLain | 85.1 | 400 | 7413 |  | 102 | 1650
Well-McLain | 85.1 | 650 | 10679 |  | 122 | 2150
Well-McLain | 85.1 | 910 | 13720 |  | 163 | 2375
Well-McLain | 85.1 | 1040 | 15005 |  | 203 | 2375
Well-McLain | 85.1 | 1170 | 16622 |  | 240 | 2525
Well-McLain | 85.1 | 1300 | 17967 |  | 280 | 2675
Lochinvar Cu |  | 495 | 6661 |  | 320 | 3050
Lochinvar | 82 | 315 | 4266 |  | 360 | 3425
Lochinvar |  | 360 | 4455 |  | 400 | 3800
Lochinvar |  | 399 | 4893 |  | 440 | 4175
Lochinvar |  | 500 | 6427 |  | 544 | 4800
LAARS | 85 | 500 | 13121 |  | 765 | 4975
LAARS | 85 | 750 | 14700 |  | 892 | 5650
LAARS | 85 | 1250 | 15456
Pump Sizing
Load | 2400
| 160 | gpm
| 19 | W/gpm
| 3040 | W/gpm
3.6676
0.0015282
From RS Means: assume base mounted pump with coupling guard for easier service (more expensive than close mounted)
|  | Material | Total Installed
2 HP to 50 gpm | 232123135040 | 8625 | 10125 | 2 | 10125
3 HP to 90 gpm |  | 8525 | 10125 | 3 | 10125
5 HP to 225 gpm |  | 12400 | 14635 | 5 | 14635
7 1/2 HP to 350 gpm |  | 12000 | 14200 | 7.5 | 14200
10 HP to 600 gpm |  | 15200 | 18150 | 10 | 18150
15 H to 1000 gpm |  | 16300 | 19350 | 15 | 19350