## Index
Tab Name | Purpose
Final Results | Final incremental costs including first costs, maintenance costs, and replacement costs
Proto Costing | Cost buildup for each prototype and system type
Air-side Component Costs | Air-side distribution component costs
Plant Equipment Costs | Plant component data and regressions
AGIC | Avoided Gas Infrastructure Costs
VRF Costing Approach
Costs are developed for individual system components using RS Means, manufacturer direct quotes, and other data sources. Cost versus capacity regressions are developed for components where possible. This allows costs to be calculated as models are revised.
Model sizing output for a given prototype and case is combined with component costs to develop prototype costs. These costs are applicable to a specific prototype and system configuration. These costs represent the first cost for the system in the context of the proposed measure, i.e., only those components of a system that are changing between the baseline and proposed case are costed.
Finally, present value of maintenance and replacement costs is added to the incremental cost to calculate the total incremental cost of the measure.
AGIC: Avoided gas infrastructure costs were estimated from CPUC technical documentation and from general contractor estaimtes. The avoided costs consist of the elimination of required gas lines to rooftop units, avoided gas main service to buiding and avoided costs for submetering. The costs are developed for each climate zone based on costs provided by utility service providers in the 2022 report.

## Final Results
Medium Office Prototype Incremental First Costs and Maintenance and Replacement Costs
Maintenance and Replacement Costs Calculation
|  | Parameter | Value |  | Source
|  | Discount Rate | 3% |  | CEC Assumption
|  | Medium Office Num Zones | 60 |  | Assumption based on zoning layout
|  | Medium Office Floor Area | 53628 |  | Prototype Definition
|  |  | Annual Maint | EUL | Repl Discount | Annual Conv Factor
|  | PVAV | 500 | 20 | 0.55368 | -10094.2273
|  | VRF | 400 | 20 | 0.55368 | -8075.3818
|  | Boiler | 500 | 25 | 0.47761 | -10094.2273
|  | Pump | 50 | 20 | 0.55368 | -1009.4227
|  | VRF Indoor Unit | 180 | 20 | 0.55368 | -3633.9218
|  | VAV Terminal Unit | 45 | 20 | 0.55368 | -908.4805
|  | DOAS | 500 | 20 | 0.55368 | -10094.2273
|  | ERV / HRV price | 12064.905 | 15 | 0.64186
1. O&M for DOAS unit mainly consists of mainteance and replacement of airside energy recovery.
2. Annual Maintenance Cost estimates from O&M equipment task lists and an assumed burdened labor rate of $100-$120/hr.
3. EUL = Expected Useful Life of Equipment, from ASHRAE Equipment Life Expectancy Chart
4. Repl Discount = Discount factor for equipment replacement after EUL period.
5. PV of Maint Cost = Total maintenance cost over expected life, per unit, accounting for the discount rate.
6. VRF Maintenance Costs use estimated maintenance costs from four-pipe fan coil units.
Proposed First Cost - proposed HVAC system first cost of all costed components. Note for some buildings this may not include systems (chiller, tower) that have a neutral cost.
Replacement Cost - replacement cost of all systems in table above applicable to the design, modified by the Replacement Discount factor in colum G.
Maintenance Cost - the total maintenance cost of all system components in the table above, column H, multiplied by the number of components of each type.
Incr Cost = the incremental HVAC system cost over the baseline, per square foot of building floor area.
AGIC Avoided Cost - the avoided cost of gas infrastructure (running gas lines to building, and runnling gas lines to HVAC units). This only applies to office buildings, not to schools. See AGIC Worksheet tab for details.
Net Incremental Cost - the net incremental cost over the standard design (2022 baseline) HVAC system, per square foot of floor area.
Medium Office VRF/DOAS Cost-Effectiveness
|  | CZ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
| Base Case | Baseline First Cost | 1549693.9499 | 1596677.7602 | 1594542.1324 | 1605220.2711 | 1581728.366 | 1600949.0157 | 1605220.2711 | 1614513.4821 | 1612377.8544 | 1623055.9931 | 1620920.3653 | 1596677.7602 | 1609491.5266 | 1635869.7595 | 1640141.015 | 1665768.5479
|  | Replacement Cost | 160675.0139 | 185550.5224 | 184419.8174 | 190073.3421 | 177635.5878 | 187811.9322 | 190073.3421 | 195011.8062 | 193881.1013 | 199534.6259 | 198403.921 | 185550.5224 | 192334.752 | 206318.8555 | 208580.2654 | 222148.7246
|  | Maintenance Cost | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683 | 47442.8683
|  | Total | 1757811.832 | 1829671.1508 | 1826404.8182 | 1842736.4815 | 1806806.8221 | 1836203.8162 | 1842736.4815 | 1856968.1566 | 1853701.8239 | 1870033.4873 | 1866767.1546 | 1829671.1508 | 1849269.1469 | 1889631.4833 | 1896164.1487 | 1935360.1407
| VRF/DOAS | Proposed First Cost | 1407564.5177 | 1520131.1277 | 1515623.8727 | 1538160.1477 | 1488580.3427 | 1529145.6377 | 1538160.1477 | 1556189.1677 | 1551681.9127 | 1574218.1877 | 1569710.9327 | 1520131.1277 | 1547174.6577 | 1601261.7177 | 1610276.2277 | 1664363.2877
|  | Replacement Cost | 209006.4412 | 234060.761 | 232569.9281 | 240024.0925 | 223624.9309 | 237042.4267 | 240024.0925 | 245987.424 | 244496.5911 | 251950.7554 | 250459.9226 | 234060.761 | 243005.7582 | 260895.7527 | 263877.4184 | 281767.4129
|  | Maintenance Cost | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091 | 18169.6091
|  | Total | 1634740.568 | 1772361.4978 | 1766363.4099 | 1796353.8493 | 1730374.8827 | 1784357.6736 | 1796353.8493 | 1820346.2008 | 1814348.1129 | 1844338.5523 | 1838340.4644 | 1772361.4978 | 1808350.025 | 1880327.0795 | 1892323.2553 | 1964300.3097
| Cost-Effectiveness | Incremental Cost | -2.2949 | -1.0687 | -1.1196 | -0.8649 | -1.4252 | -0.96677 | -0.8649 | -0.68289 | -0.73383 | -0.47913 | -0.53007 | -1.0687 | -0.76302 | -0.1735 | -0.071621 | 0.53965
|  | AGIC Avoided Cost | 0.4316 | 0.4316 | 0.4316 | 0.4316 | 0.4316 | 0.17114 | 0.17666 | 0.17666 | 0.17114 | 0.17114 | 0.4316 | 0.17666 | 0.4316 | 0.17114 | 0.4316 | 0.4316
|  | Net Incremental Cost | -2.7265 | -1.5003 | -1.5512 | -1.2965 | -1.8568 | -1.1379 | -1.0416 | -0.85955 | -0.90497 | -0.65027 | -0.96167 | -1.2453 | -1.1946 | -0.34464 | -0.50322 | 0.10804
|  | LSC Energy Model Savings | 2.44 | 4.15 | 0.22 | 7.23 | 0.56 | 0.82 | 4.25 | 5.17 | 5.84 | 5.59 | 10.28 | 6.07 | 9.04 | 9.64 | 12.97 | 5.91
|  | BCR, Medium Office LCC' | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | Infinite | 54.7001
Note on E10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Annual Maintenance Cost estimates from O&M equipment task lists and an assumed burdened labor rate of $100-$120/hr.
Note on F10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Expected Useful Life of Equipment, from ASHRAE Life Expectancy Chart
Note on G10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Discount factor for equipment replacement after EUL period.
Note on H10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total maintenance cost over expected life, per unit, accounting for the discount rate.

## Proto Costing
Medium Office Cost Components
| Floor Area | 53628 | sf
| Medium Office Prototype - Base Case | [16 empty] | Data Source / Notes
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
PVAV | Capacity | 135 | 157 | 156 | 161 | 150 | 159 | 161 | 165 | 164 | 169 | 168 | 157 | 163 | 175 | 177 | 189 | Size, tons, from model runs
Qty
| Mat Cost (per ton) | 191700 | 222940 | 221520 | 228620 | 213000 | 225780 | 228620 | 234300 | 232880 | 239980 | 238560 | 222940 | 231460 | 248500 | 251340 | 268380 | RS Means Equipment Cost
| Labor Cost (per ton) | 23233.5 | 27019.7 | 26847.6 | 27708.1 | 25815 | 27363.9 | 27708.1 | 28396.5 | 28224.4 | 29084.9 | 28912.8 | 27019.7 | 28052.3 | 30117.5 | 30461.7 | 32526.9 | RS Means Online Labor Cost
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 247173.525 | 287453.655 | 285622.74 | 294777.315 | 274637.25 | 291115.485 | 294777.315 | 302100.975 | 300270.06 | 309424.635 | 307593.72 | 287453.655 | 298439.145 | 320410.125 | 324071.955 | 346042.935
Condensate Line | Qty | 135 | 157 | 156 | 161 | 150 | 159 | 161 | 165 | 164 | 169 | 168 | 157 | 163 | 175 | 177 | 189
| Subtotal | 8073 | 9388.6 | 9328.8 | 9627.8 | 8970 | 9508.2 | 9627.8 | 9867 | 9807.2 | 10106.2 | 10046.4 | 9388.6 | 9747.4 | 10465 | 10584.6 | 11302.2 | Cost per ton for installing condensate lines
Ductwork | Capacity | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | Ductwork for VAV AHU, linear feet
Qty
| Mat Cost (per LF) | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | MEP CA Office Project Avg (NORESCO)
| Labor Cost (per LF) | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | 246.33 | MEP CA Office Project Avg (NORESCO)
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95 | 654295.95
VAV Boxes | Capacity
| Qty (Num Zones) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Number of Zones, Medium Office
| Mat Cost (per ton) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | Average Cost per Terminal Unit: See Airside Component Costs
Labor Cost (per ton)
O&P
| Subtotal | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718 | 194718
Gas Boiler | Capacity | 1620 | 1884 | 1872 | 1932 | 1800 | 1908 | 1932 | 1980 | 1968 | 2028 | 2016 | 1884 | 1956 | 2100 | 2124 | 2268 | Central Gas Boiler from model sizing, MBH
Qty | bar: CZ1 to CZ16
| Mat Cost | 22342.78 | 25713.796 | 25560.568 | 26326.708 | 24641.2 | 26020.252 | 26326.708 | 26939.62 | 26786.392 | 27552.532 | 27399.304 | 25713.796 | 26633.164 | 28471.9 | 28778.356 | 30617.092 | RS Means Online 2023
| Labor Cost | 9570.546 | 10884.8172 | 10825.0776 | 11123.7756 | 10466.64 | 11004.2964 | 11123.7756 | 11362.734 | 11302.9944 | 11601.6924 | 11541.9528 | 10884.8172 | 11243.2548 | 11960.13 | 12079.6092 | 12796.4844 | RS Means Online 2023
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 36700.3249 | 42088.4052 | 41843.4924 | 43068.0561 | 40374.016 | 42578.2307 | 43068.0561 | 44047.7071 | 43802.7944 | 45027.3581 | 44782.4453 | 42088.4052 | 43557.8816 | 46496.8345 | 46986.66 | 49925.6129
HW Piping | Capacity
| Qty | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | Linear Feet of Piping
Unit Cost
| Mat Cost | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | 16.32 | MEP CA Office Project Avg (NORESCO)
| Labor Cost | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | 40.33 | MEP CA Office Project Avg (NORESCO)
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75 | 267104.75
| Installed First Cost | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 4 | 4 | 4 | Nameplate HP, Calculated from (a) gpm requirement, (b) standard design W/cfm, roudned up to nearest motor nameplate HP for costing
Circ Pump | Subtotal | 11365.4 | 11365.4 | 11365.4 | 11365.4 | 11365.4 | 11365.4 | 11365.4 | 12116.1 | 12116.1 | 12116.1 | 12116.1 | 11365.4 | 11365.4 | 12116.1 | 12116.1 | 12116.1 | RS Means Online 2023
SUBTOTAL | No controls, Cx | 1419430.9499 | 1466414.7602 | 1464279.1324 | 1474957.2711 | 1451465.366 | 1470686.0157 | 1474957.2711 | 1484250.4821 | 1482114.8544 | 1492792.9931 | 1490657.3653 | 1466414.7602 | 1479228.5266 | 1505606.7595 | 1509878.015 | 1535505.5479 | Includes all Costs except Controls and Cx
| Controls | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | 120663 | Feng, J. and Hwakong Cheng 2018. Construction and Energy Costs for Radiant vs. VAV Systems in the California Bay Area, Final Report, Taylor Engineering and UC Berkeley, EPIC-14-009, November 15, 2018.
| Commissioning (Htg System) | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | 9600 | Cx Costs are differential function testing estimates for bours (NORESCO), using a loaded Cx labor rate of $160/hr.
TOTAL | Project Total (Costed Portion) | 1549693.9499 | 1596677.7602 | 1594542.1324 | 1605220.2711 | 1581728.366 | 1600949.0157 | 1605220.2711 | 1614513.4821 | 1612377.8544 | 1623055.9931 | 1620920.3653 | 1596677.7602 | 1609491.5266 | 1635869.7595 | 1640141.015 | 1665768.5479 | Total Project Costs for ~50ksf building
Medium Office Prototype - VRF/DOAS (Proposed Case)
|  | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
VRF | Capacity | 135 | 157 | 156 | 161 | 150 | 159 | 161 | 165 | 164 | 169 | 168 | 157 | 163 | 175 | 177 | 189 | Size, tons, from model runs
Qty
| Mat Cost (per ton) | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | 1619.5 | Red Car Analytics, 2050 Partners, VHE DOAS Study. 2022.
| Labor Cost (per ton) | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | 721.9 | Red Car Analytics, 2050 Partners, VHE DOAS Study. 2022.
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 363502.35 | 422739.77 | 420047.16 | 433510.21 | 403891.5 | 428124.99 | 433510.21 | 444280.65 | 441588.04 | 455051.09 | 452358.48 | 422739.77 | 438895.43 | 471206.75 | 476591.97 | 508903.29
Condensate Line | Qty | 135 | 157 | 156 | 161 | 150 | 159 | 161 | 165 | 164 | 169 | 168 | 157 | 163 | 175 | 177 | 189 | Condensate Line Cost, Indoor fan coils
| Subtotal | 42795 | 49769 | 49452 | 51037 | 47550 | 50403 | 51037 | 52305 | 51988 | 53573 | 53256 | 49769 | 51671 | 55475 | 56109 | 59913
Rx Piping | Capacity | 135 | 157 | 156 | 161 | 150 | 159 | 161 | 165 | 164 | 169 | 168 | 157 | 163 | 175 | 177 | 189
Qty
Unit Cost
| Mat Cost | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | 388.4 | Red Car Analytics, 2050 Partners, VHE DOAS Study. 2022.
| Labor Cost | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | 913.9 | Red Car Analytics, 2050 Partners, VHE DOAS Study. 2022.
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 202182.075 | 235130.265 | 233632.62 | 241120.845 | 224646.75 | 238125.555 | 241120.845 | 247111.425 | 245613.78 | 253102.005 | 251604.36 | 235130.265 | 244116.135 | 262087.875 | 265083.165 | 283054.905
Indoor Units | Capacity
Qty
| Mat Cost (per SF) | [16 empty] | Indoor Unit cost per ton from VHE DOAS Study, with 30 zones as a reference. Indoor units will be proportional to the number of zones. | bar: CZ1 to CZ16
| Labor Cost (per ton) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2 | 61672.2
DOAS Unit | Capacity
"Std Package" | Qty (cfm) | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | 8043.27 | Design ventilation airlfow for Medium Office, CFM.
110% multiplier | Unit Cost
on Std HRV Cost | Mat Cost | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | 8.14 | Red Car Analytics, 2050 Partners, VHE DOAS Study. 2022. Costed as $/cfm of ventilation airflow.
for bypass | Labor Cost | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | Red Car Analytics, 2050 Partners, VHE DOAS Study. 2022. Costed as $/cfm of ventilation airflow.
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327 | 80513.1327
DOAS Ductwork | DOAS vs. VAV Ductwork (Note 1) | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | Reduction of 20% for Smaller duct size compared to VAV AHU, since lower cfm (Assumption)
| Qty (LF) | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100
| Mat Cost | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | 19.68 | MEP CA Office Project Avg (NORESCO), with 20% reduction applied
| Labor Cost | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | 197.064 | MEP CA Office Project Avg (NORESCO), with 20% reduction applied
| O&P | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Subtotal | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76 | 523436.76
SUBTOTAL | No controls, Cx | 1274101.5177 | 1373261.1277 | 1368753.8727 | 1391290.1477 | 1341710.3427 | 1382275.6377 | 1391290.1477 | 1409319.1677 | 1404811.9127 | 1427348.1877 | 1422840.9327 | 1373261.1277 | 1400304.6577 | 1454391.7177 | 1463406.2277 | 1517493.2877
| Controls | 120663 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | 134070 | Feng, J. and Hwakong Cheng 2018. Construction and Energy Costs for Radiant vs. VAV Systems in the California Bay Area, Final Report, Taylor Engineering and UC Berkeley, EPIC-14-009, November 15, 2018.
| Commissioning (Htg System) | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | 12800 | Cx Costs are differential function testing estimates for bours (NORESCO), using a loaded Cx labor rate of $160/hr.
TOTAL | Project Total (Costed Portion) | 1407564.5177 | 1520131.1277 | 1515623.8727 | 1538160.1477 | 1488580.3427 | 1529145.6377 | 1538160.1477 | 1556189.1677 | 1551681.9127 | 1574218.1877 | 1569710.9327 | 1520131.1277 | 1547174.6577 | 1601261.7177 | 1610276.2277 | 1664363.2877

## Airside Component Costs
Airside Component Costs
Labor Costs - PVAV (RSMeansOnline), gas heat
Nominal Tons | Bare Labor | Eqp Cost (Ref only)
7.5 | 2100 | 6525
10 | 2425 | 8050
12.5 | 2575 | 9100
15 | 2850 | 12200
20 | 3325 | 15700
25 | 3975 | 36900
30 | 4725 | 37200
40 | 6300 | 45400
50 | 7875 | 51500
Airflow Sizing for Built-Up Air Handling Units, from Energy Model
# of Fans Represented | 1 | 1 | 1 | 1 | 5 | 5 | 5 | 5 | 1 | 1
Climate Zone | BASESYS RETFAN | BASESYS6 SUPFAN | BASESYS RETFAN-2 | BASESYS6 SUPFAN-2 | BASESYS RETFAN-3 | BASESYS6 SUPFAN-3 | BASESYS RETFAN-4 | BASESYS6 SUPFAN-4 | BASESYS RETFAN-5 | BASESYS6 SUPFAN-5 | TotalCFM
1 | 24733 | 24733 | 25614 | 25614 | 27962 | 27962 | 27804 | 27804 | 25359 | 25359 | 354536
2 | 25713 | 25713 | 26300 | 26300 | - | 28866 | - | 28787 | 26724 | 26724 | 367002
3 | - | 24964 | - | 26495 | - | 30596 | - | 30495 | - | 27839 | 384753
4 | - | 26061 | - | 27291 | - | 29914 | - | 29831 | - | 27995 | 380072
5 | - | 24831 | - | 26335 | - | 28999 | - | 28895 | - | 27106 | 367742
6 | - | 25313 | - | 27233 | - | 30421 | - | 30381 | - | 28505 | 385061
7 | - | 25960 | - | 27950 | - | 31054 | - | 31028 | - | 29167 | 393487
8 | - | 25394 | - | 27681 | - | 31020 | - | 31011 | - | 29136 | 392366
9 | - | 25915 | - | 28148 | - | 32566 | - | 32537 | - | 30231 | 409809
10 | - | 26495 | - | 28037 | - | 31102 | - | 31062 | - | 29408 | 394760
11 | 26658 | 26658 | - | 28989 | - | 32728 | - | 32704 | - | 31166 | 413973
12 | 25655 | 25655 | 27035 | 27035 | - | 29884 | - | 29817 | 28125 | 28125 | 379320
13 | 26697 | 26697 | 27936 | 27936 | - | 31864 | - | 31838 | - | 30429 | 403572
14 | 28320 | 28320 | - | 30590 | - | 33915 | - | 33882 | - | 32688 | 430583
15 | 27439 | 27439 | - | 30806 | - | 34006 | - | 34047 | - | 33917 | 432427
16 | - | 29915 | - | 33504 | - | 37061 | - | 36396 | - | 34219 | 464923
Distribution System Costs - adapted from MEP project data of California office buildings, NORESCO (Singer)
These costs are used to determine ductwork and piping installed costs per linear foot (LF).
Distribution Costs - J. Singer (Northern California recent Large Office MEP projects)
Component | Material Cost per ft | Labor | Total Cost
Duct | 24.6 | 246.33 | 270.93
Pipe | 16.32 | 40.33 | 56.65
Pipe Base | 9.792 | 40.33 | 50.122
Duct 32.80 - 16" round with labor
Assume 24.50 with fittings - $50
Duct Insulation - $4.77
Total: $54.77/LF
VAV Terminal Unit Cost Assumptions for Base Case
Terminal Unit Costs | Value | Source
RS Means Cost | 1909 | RSMeans 233616105660
CA Union rate multiplier | 1.7
VAV Box, 1250 cfm avg | 3245.3

## Plant Equipment Costs
Plant Equipment Costs
Commercial NG Boilers - AF Supply, Distributor
Make | Eff | Capacity | Cost |  | RS Means for Labor
Well-McLain | 85.1 | 400 | 7413 |  | MBH | Labor Cost
Well-McLain | 85.1 | 650 | 10679 |  | 102 | 1650
Well-McLain | 85.1 | 910 | 13720 |  | 122 | 2150
Well-McLain | 85.1 | 1040 | 15005 |  | 163 | 2375
Well-McLain | 85.1 | 1170 | 16622 |  | 203 | 2375
Well-McLain | 85.1 | 1300 | 17967 |  | 240 | 2525
Lochinvar Cu |  | 495 | 6661 |  | 280 | 2675
Lochinvar | 82 | 315 | 4266 |  | 320 | 3050
Lochinvar |  | 360 | 4455 |  | 360 | 3425
Lochinvar |  | 399 | 4893 |  | 400 | 3800
Lochinvar |  | 500 | 6427 |  | 440 | 4175
LAARS | 85 | 500 | 13121 |  | 544 | 4800
LAARS | 85 | 750 | 14700 |  | 765 | 4975
LAARS | 85 | 1250 | 15456 |  | 892 | 5650
Pump Sizing | [5 empty] | Pump Sizing gas
Large Office
Load | 200 | tons |  | Model |  | Load | 2400
GPM | 480 | gpm |  | Calc = f (10F delta T) |  |  | 160 | gpm
Pump Efficacy | 19 | W/gpm | App G | Constant |  |  | 19 | W/gpm
Pump Power | 9120 | W/gpm |  | Conversion |  |  | 3040 | W/gpm
Pump bhp | 11.0027 | [5 empty] | 3.6676
BHP per ton | 0.055013 | [5 empty] | 0.0015282 | Conversion Factor, Pump HP per gpm
From RS Means: assume base mounted pump with coupling guard for easier service (more expensive than close mounted)
|  | Material | Total Installed
2 HP to 50 gpm | 232123135040 | 8625 | 10125 | 2 | 10125
3 HP to 90 gpm |  | 8525 | 10125 | 3 | 10125
5 HP to 225 gpm |  | 12400 | 14635 | 5 | 14635
7 1/2 HP to 350 gpm |  | 12000 | 14200 | 7.5 | 14200
10 HP to 600 gpm |  | 15200 | 18150 | 10 | 18150
15 H to 1000 gpm |  | 16300 | 19350 | 15 | 19350

## AGIC
Avoided Gas Infrstructure Costs |  |  | Source: CPUC
Medium Office
Amount
Gas T&D Avoided Costs | 0.1 | therm
GHG Abatement Cost | 114 | ton
Utility-Specific Costs (Note 1)
Service Extension PG&E | 15535 | bldg | Service line including trenching
Service Extension PG&E | 3330 | bldg | Service line including trenching (greenfield)
Meter | 1309 | bldg | Meter
Submeters | 1434 | x 3 | Submeter, Leviton GMP 10-251, with installation
Medium Office - Total
| CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Service Line (high) | 15535 | 15535 | 15535 | 15535 | 15535 | 1567 | 1863 | 1863 | 1567 | 1567 | 15535 | 1863 | 15535 | 1567 | 15535 | 15535
Meter | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309 | 1309
Submeters (qty 3) | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302 | 4302
Avoided Gas Lines (Note 2) | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
AGIC Cost | 23146 | 23146 | 23146 | 23146 | 23146 | 9178 | 9474 | 9474 | 9178 | 9178 | 23146 | 9474 | 23146 | 9178 | 23146 | 23146
AGIC Cost (per sf) | 0.4316 | 0.4316 | 0.4316 | 0.4316 | 0.4316 | 0.17114 | 0.17666 | 0.17666 | 0.17114 | 0.17114 | 0.4316 | 0.17666 | 0.4316 | 0.17114 | 0.4316 | 0.4316
Notes
1. Avoided gas infrastructure costs from Wildan 2022. 2022 Distributed Energy Resources Avoided Cost Caculator Documentation, prepared for the California Public Utilities Commission, June 22, 2022.
2. Avoided Gas Line cost savings is derived from general contractor estimates of avoided gas pipe lines to rooftop equipment. Gas line quotes are $15.30/ft, $17.25/ft and $20/ft for 1", 1 1/4" and 1 1/2" gas pipies
repsecitvely. Gas pressure regulators at $72 each would be required, and pipe supports ($10-$65 depending upon type) every 6 to 8 feet would also be required.