To qualify as a low leakage air-handling unit for use for compliance with applicable performance compliance credits, the air-handling unit shall be certified to the Energy Commission according to the following requirements:

JA9.2.1 Method of Test

The air-handling unit shall be tested in accordance with the requirements given in ASHRAE Standard 193.

JA9.2.2 Testing Laboratory Requirements

The Air-Handling Unit shall be tested in a laboratory that has demonstrated compliance with ISO Standard 17025, General Criteria for the Competence of Testing and Calibration Laboratories, and is accredited for the ASHRAE Standard 193 test methods. The accreditation body shall be a signatory to the International Laboratory Accreditation Cooperation Mutual Recognition Arrangement www.ilac.org.

JA9.2.3 Nominal Air-Handling Unit Airflow

The nominal air-handling unit airflow used for determining the leakage criterion for qualification shall be as follows:

(a) For heating-only systems the nominal air-handling unit airflow shall be 21.7 cfm per kBtu/hr of rated heating output capacity.

(b) For systems that provide space cooling, the nominal air-handling unit airflow shall be 400 cfm per nominal ton of cooling capacity as specified by the manufacturer, or the heating-only value, whichever is greater.

JA9.2.4 Leakage Criterion for Qualification

Allowable leakage for qualification as a Low Leakage Air-Handling Unit shall be equal to or less than 1.4 percent of the nominal air-handling unit airflow determined by Section JA9.2.3.

Complete and submit electronically to CertifiedtoCEC@energy.ca.gov.

List of Models offered for Certification (insert additional lines as needed)

| Manufacturer | Brand | Model No. | AHU Type1 | Heating or Cooling (H or C) | Nominal AHU Airflow Rate2 (CFM) | AHU Leakage Rate3 (CFM) | Leakage Rate4 (%) |
| --- | --- | --- | --- | --- | --- | --- | --- |

Table Notes:

- For AHU Types, please use the following codes (F) Furnace, (FC) Fan-Coil Unit,  (HP) Heat Pump, (AC) Air Conditioner.

- Nominal AHU Airflow Rate (cfm)  for heating is based on 21.7 cfm per kBtu/hr of rated heating output capacity and for cooling is based on 400 cfm per nominal ton of cooling capacity.

- Certified AHU Leakage Rate (cfm) when pressurized to 125 Pa (0.5 inches of water).

- Certified Leakage Rate expressed as % of Nominal AHU Airflow Rate.

Name of the accredited laboratory(s), which performed the required ASHRAE Standard 193 test methods for the devices, listed above.

| Test Laboratory Name *** | Phone |
| --- | --- |
| Address | Fax |
| (Address) | E-mail |
| (Address) | Laboratory's EPA-Issued Organization ID |

When providing the information below, be sure to enter complete mailing addresses, including postal/zip codes.

Certifying Company

| Contact Person Name * | Phone 1 |
| --- | --- |
| Certifying Company Name ** | Phone 2 |
| Address | Fax |
| (Address) | E-mail |
| (Address) | Company Website (URL) |

* If the contact person named above is NOT the person whose signature is on the Declaration, then the full contact information for the person whose signature is on the Declaration must also be provided on a separate page.

** If the company named above is: A) a parent entity filing on behalf of a subsidiary entity; B) a subsidiary entity filing on behalf of a parent entity; or C) an affiliate entity filing on behalf of an affiliate entity, the above contact information must be provided for any additional entities on a separate page.

Manufacturer (if different from Certifying Company)

| Contact Person Name | Phone 1 |
| --- | --- |
| Manufacturing Company Name | Phone 2 |
| Address | Fax |
| (Address) | E-mail |
| (Address) | Company Website (URL) |

- Declaration

I declare under penalty of perjury under the laws of the State of California that:

- All the information in this statement and in any attachment(s) is true, complete, accurate, and in compliance with all applicable provisions in the Performance Standards as set forth in 2019 California Title 24, Part 6, Section 150.1; Joint Appendix JA9; Residential ACM Reference Manual Section 2.4.6.12; Reference Residential Appendix Sections RA3.1.4.3.9, and RA3.1.4.2.2.

- Each Low Leakage Air Handling Unit has been tested in accordance with all applicable requirements of Section 150.1; Joint Appendix JA9; Residential ACM Reference Manual Section 2.4.6.12; Reference Residential Appendix Sections RA3.1.4.3.9, and RA3.1.4.2.2.

- [If the party submitting this statement is a corporation, partnership, or other business entity] I am authorized to make this declaration, and to file this statement, on behalf of the company named below.

| Certifying Company Name |  | Date |
| --- | --- | --- |
| Name/Title (please print) |  | Signature |