{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Solar_Inverters","Battery_Inverters"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Solar_Inverters","index":0,"n_rows":1191,"n_cols":60,"rows_kept":1191,"cut":false,"hidden":false,"merged":[]}
["Grid Support Solar Inverter List (Full Data)"]
["Data has not changed since October 21, 2021"]
["This list contains an extensive amount of equipment information. If you require any assistance, please reach out to us at SolarEquipment@energy.ca.gov or 916-654-4120."]
["Inverter List Notes"]
["This row is intentionally left blank."]
["% Equipment is in the process of being removed from the list of eligible equipment pursuant to Appendix A, Section B, of the Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1) at:  "]
["Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1)"]
["(1) Any text in brackets at the end of the Model Number is not part of the Manufacturer's Model Number.  Part of the text in brackets indicates the specified voltage option for that model number, if provided; models with multiple voltage options will have multiple row entries, with one for each eligible option."]
["(2) Hybrid inverters are capable of taking DC power input from both a solar system and an energy storage system. These models are listed on both the solar and battery inverter lists to reflect the dual functionality. Refer to the manufacturer's documentation for more information on the exact functionality and limitations."]
["(3) RPP: UL 1741 SA13 tested with reactive power priority enabled (when operating at apparent power capacity, inverter will reduce active power as needed to ensure curve-required reactive power is provided)"]
["(4) A Y* notes the inverter has not been certified according to CSIP, but instead NRTL reported inverter was connected to a gateway during compatibility testing."]
["(5) The listed Firmware Version is the version used during the inverter's UL 1741 Supplement SA (SA8-SA13) testing and certified on the listed Certificate Date; multiple firmware versions may be listed for a single certificate date if all are required to comply with Supplement SA. Multiple certificate dates with different firmware versions may be listed if new firmware versions were certified under Supplement SA and reported by the manufacturer. Additional firmware versions may be certified but not reported. Check with NRTL for the most current information."]
["(6) Inverter CSIP conformance information refers to the entity responsible for the documentation provided to the manufacturer. If the inverter is certified to CSIP, then the information refers to the certifying entity and the certificate date. Otherwise, the information refers to the NRTL that issued the compatibility report and the date of the report."]
["Blue colored text indicates that the model number occurs multiple times on the list under different manufacturer names."]
["Manufacturer Name","Model Number1","Hybrid Inverter2","UL 1741 Supplement SA Testing","UL 1741 SA13 Volt-Var","UL 1741 SA\nFreq-Watt\nVolt-Watt","UL 1741 SA\nDisable Permit Service\nLimit Active Power","Common Smart Inverter Profile Conformance","Monitor Key Data\nScheduling","Description","Maximum Continuous Output Power at Unity Power Factor","Nominal Voltage","Weighted Efficiency","UL 1741 Supplement SA \nCertification (SA8-SA13)5",null,null,"UL 1741 SA13  Volt-Var","UL 1741 SA\nFreq-Watt\nVolt-Watt","UL 1741 SA\nDisable Permit Service\nLimit Active Power","Inverter CSIP Conformance6",null,"Monitor Key Data\nScheduling\nAttestation","Notes","Built-In Meter","Microinverter","Night Tare Loss","Power Rating, Continuous, 40 deg C","Night\nTare Loss, 40 deg C","Voltage Minimum","Voltage Nominal","Voltage Maximum","Power Level","Power Level","Power Level","Power Level","Power Level","Power Level","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Grid Support Listing Date","Last Update"]
[null,null,"PV and Battery","SA8-SA13","RPP3","SA14-SA15","SA17-SA18","CSIP4","Attestation",null,"(kW)","(Vac)","(%)","Certifying Entity","Certificate Date [mo/day/yr]","Firmware Version(s) Tested","Listing Date (mo/day/yr)","Certificate Date [mo/day/yr]","Listing Date (mo/day/yr)","Issuing Entity","Document Date (mo/day/yr)","Listing Date",null,null,null,"(W)","(kW)","(W)","(Vdc)","(Vdc)","(Vdc)","10% (kW)","20% (kW)","30% (kW)","50% (kW)","75% (kW)","100% (kW)","10% Pwr Lvl (%)","20% Pwr Lvl (%)","30% Pwr Lvl (%)","50% Pwr Lvl (%)","75% Pwr Lvl (%)","100% Pwr Lvl (%)","Wtd (%)","10% Pwr Lvl (%)","20% Pwr Lvl (%)","30% Pwr Lvl (%)","50% Pwr Lvl (%)","75% Pwr Lvl (%)","100% Pwr Lvl (%)","Wtd (%)","10% Pwr Lvl (%)","20% Pwr Lvl (%)","30% Pwr Lvl (%)","50% Pwr Lvl (%)","75% Pwr Lvl (%)","100% Pwr Lvl (%)","Wtd (%)"]
["ABB","PVI-3.0-OUTD-S-US-A [208V]","N","Y","Y","N","N","N","N","3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector",3,208,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,310,480,0.3,0.6,0.9,1.5,2.25,3,93.1,95.5,96,95.9,95.7,95.1,95.6,93.3,95.9,96.4,96.4,96.2,95.8,96.1,91,94.9,95.7,96,95.8,95.5,95.6,"2017-07-01","2018-10-15"]
["ABB","PVI-3.0-OUTD-S-US-A [240V]","N","Y","Y","N","N","N","N","3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector",3,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,340,480,0.25,0.6,0.9,1.5,2.25,3,92.5,95.2,95.9,96.1,95.9,95.5,95.7,93.1,95.9,96.5,96.7,96.7,96.4,96.5,91.1,95.1,96,96.4,96.4,96.2,96.1,"2017-07-01","2018-10-15"]
["ABB","PVI-3.0-OUTD-S-US-A [277V]","N","Y","Y","N","N","N","N","3 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector",3,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,390,480,0.3,0.6,0.9,1.5,2.25,3,91.4,94.7,95.5,96.1,95.9,95.6,95.7,92.5,95.8,96.5,96.9,96.9,96.8,96.6,91.1,95.2,96.2,96.7,96.8,96.7,96.4,"2017-07-01","2018-10-15"]
["ABB","PVI-3.0-OUTD-S-US-Z-A [208V]","N","Y","Y","N","N","N","N","3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector",3,208,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,310,480,0.3,0.6,0.9,1.5,2.25,3,93.1,95.5,96,95.9,95.7,95.1,95.6,93.3,95.9,96.4,96.4,96.2,95.8,96.1,91,94.9,95.7,96,95.8,95.5,95.6,"2017-07-01","2018-10-15"]
["ABB","PVI-3.0-OUTD-S-US-Z-A [240V]","N","Y","Y","N","N","N","N","3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector",3,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,340,480,0.25,0.6,0.9,1.5,2.25,3,92.5,95.2,95.9,96.1,95.9,95.5,95.7,93.1,95.9,96.5,96.7,96.7,96.4,96.5,91.1,95.1,96,96.4,96.4,96.2,96.1,"2017-07-01","2018-10-15"]
["ABB","PVI-3.0-OUTD-S-US-Z-A [277V]","N","Y","Y","N","N","N","N","3 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector",3,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,390,480,0.3,0.6,0.9,1.5,2.25,3,91.4,94.7,95.5,96.1,95.9,95.6,95.7,92.5,95.8,96.5,96.9,96.9,96.8,96.6,91.1,95.2,96.2,96.7,96.8,96.7,96.4,"2017-07-01","2018-10-15"]
["ABB","PVI-3.0-OUTD-S-US-Z-M-A [208V]","N","Y","Y","N","N","N","N","3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",3,208,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,310,480,0.3,0.6,0.9,1.5,2.25,3,93.1,95.5,96,95.9,95.7,95.1,95.6,93.3,95.9,96.4,96.4,96.2,95.8,96.1,91,94.9,95.7,96,95.8,95.5,95.6,"2017-07-01","2018-10-15"]
["ABB","PVI-3.0-OUTD-S-US-Z-M-A [240V]","N","Y","Y","N","N","N","N","3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",3,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,340,480,0.25,0.6,0.9,1.5,2.25,3,92.5,95.2,95.9,96.1,95.9,95.5,95.7,93.1,95.9,96.5,96.7,96.7,96.4,96.5,91.1,95.1,96,96.4,96.4,96.2,96.1,"2017-07-01","2018-10-15"]
["ABB","PVI-3.0-OUTD-S-US-Z-M-A [277V]","N","Y","Y","N","N","N","N","3 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",3,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,390,480,0.3,0.6,0.9,1.5,2.25,3,91.4,94.7,95.5,96.1,95.9,95.6,95.7,92.5,95.8,96.5,96.9,96.9,96.8,96.6,91.1,95.2,96.2,96.7,96.8,96.7,96.4,"2017-07-01","2018-10-15"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SB-RA [208V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.3,0.6,0.9,1.5,2.25,3,92.3,95,95.4,95.8,95.7,95.3,95.5,93.2,95.6,96.1,96.4,96.4,96.2,96.2,91.4,94.7,95.6,96.1,96.1,95.9,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SB-RA-Q [208V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",0.9,null,null,200,340,480,0.3,0.6,0.9,1.5,2.25,3,92.3,95,95.4,95.8,95.7,95.3,95.5,93.2,95.6,96.1,96.4,96.4,96.2,96.2,91.4,94.7,95.6,96.1,96.1,95.9,95.8,"2020-08-21"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SE-RA [208V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply",3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.3,0.6,0.9,1.5,2.25,3,92.3,95,95.4,95.8,95.7,95.3,95.5,93.2,95.6,96.1,96.4,96.4,96.2,96.2,91.4,94.7,95.6,96.1,96.1,95.9,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SZM-RA [208V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply",3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.3,0.6,0.9,1.5,2.25,3,92.3,95,95.4,95.8,95.7,95.3,95.5,93.2,95.6,96.1,96.4,96.4,96.2,96.2,91.4,94.7,95.6,96.1,96.1,95.9,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SZ-RA [208V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply",3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.3,0.6,0.9,1.5,2.25,3,92.3,95,95.4,95.8,95.7,95.3,95.5,93.2,95.6,96.1,96.4,96.4,96.2,96.2,91.4,94.7,95.6,96.1,96.1,95.9,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SB-RA [240V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",3.3,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,355,480,0.33,0.66,0.99,1.65,2.48,3.3,92.8,95.3,95.8,96.1,96.1,95.7,95.9,93.6,96,96.6,96.9,96.8,96.7,96.6,92.2,95.3,96,96.6,96.6,96.5,96.3,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SB-RA-Q [240V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",3.3,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",0.9,null,null,200,355,480,0.33,0.66,0.99,1.65,2.48,3.3,92.8,95.3,95.8,96.1,96.1,95.7,95.9,93.6,96,96.6,96.9,96.8,96.7,96.6,92.2,95.3,96,96.6,96.6,96.5,96.3,"2020-08-21"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SE-RA [240V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply",3.3,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,355,480,0.33,0.66,0.99,1.65,2.48,3.3,92.8,95.3,95.8,96.1,96.1,95.7,95.9,93.6,96,96.6,96.9,96.8,96.7,96.6,92.2,95.3,96,96.6,96.6,96.5,96.3,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SZM-RA [240V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply",3.3,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,355,480,0.33,0.66,0.99,1.65,2.48,3.3,92.8,95.3,95.8,96.1,96.1,95.7,95.9,93.6,96,96.6,96.9,96.8,96.7,96.6,92.2,95.3,96,96.6,96.6,96.5,96.3,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.3-TL-PLUS-US-SZ-RA [240V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply",3.3,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,355,480,0.33,0.66,0.99,1.65,2.48,3.3,92.8,95.3,95.8,96.1,96.1,95.7,95.9,93.6,96,96.6,96.9,96.8,96.7,96.6,92.2,95.3,96,96.6,96.6,96.5,96.3,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SB-RA [208V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",3.3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.33,0.66,0.99,1.65,2.48,3.3,91.5,94.7,95.4,95.7,95.5,95.2,95.3,92.9,95.7,96.2,96.6,96.6,96.5,96.4,90.5,94.5,95.7,96.2,96.1,96,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SB-RA-Q [208V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",3.3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",0.9,null,null,200,340,480,0.33,0.66,0.99,1.65,2.48,3.3,91.5,94.7,95.4,95.7,95.5,95.2,95.3,92.9,95.7,96.2,96.6,96.6,96.5,96.4,90.5,94.5,95.7,96.2,96.1,96,95.8,"2020-08-21"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SE-RA [208V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply",3.3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.33,0.66,0.99,1.65,2.48,3.3,91.5,94.7,95.4,95.7,95.5,95.2,95.3,92.9,95.7,96.2,96.6,96.6,96.5,96.4,90.5,94.5,95.7,96.2,96.1,96,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SZM-RA [208V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply",3.3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.33,0.66,0.99,1.65,2.48,3.3,91.5,94.7,95.4,95.7,95.5,95.2,95.3,92.9,95.7,96.2,96.6,96.6,96.5,96.4,90.5,94.5,95.7,96.2,96.1,96,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SZ-RA [208V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply",3.3,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.33,0.66,0.99,1.65,2.48,3.3,91.5,94.7,95.4,95.7,95.5,95.2,95.3,92.9,95.7,96.2,96.6,96.6,96.5,96.4,90.5,94.5,95.7,96.2,96.1,96,95.8,"2017-07-01","2020-08-21"]
["ABB","PVI-3.6-OUTD-S-US-A [208V]","N","Y","Y","N","N","N","N","3.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector",3.6,208,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,310,480,0.36,0.72,1.08,1.8,2.7,3.6,92.2,94.7,95.4,95.9,95.9,95.6,95.6,92.7,95.5,96.1,96.4,96.4,96.1,96.1,90.3,94.5,95.3,95.9,96,95.7,95.6,"2017-07-01","2018-10-15"]
["ABB","PVI-3.6-OUTD-S-US-A [240V]","N","Y","Y","N","N","N","N","3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector",3.6,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,340,480,0.3,0.72,1.08,1.8,2.7,3.6,91.1,94.1,94.9,95.6,95.8,95.7,95.4,92.4,95.5,96.3,96.7,96.7,96.6,96.5,90.2,94.6,95.6,96.2,96.4,96.3,95.9,"2017-07-01","2018-10-15"]
["ABB","PVI-3.6-OUTD-S-US-A [277V]","N","Y","Y","N","N","N","N","3.6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector",3.6,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,395,480,0.36,0.72,1.08,1.8,2.7,3.6,90,93.4,94.4,95.4,95.7,95.6,95.1,91.9,95.4,96.3,96.9,97,96.9,96.6,90.4,94.9,95.9,96.6,96.8,96.8,96.3,"2017-07-01","2018-10-15"]
["ABB","PVI-3.6-OUTD-S-US-Z-A [208V]","N","Y","Y","N","N","N","N","3.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector",3.6,208,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,310,480,0.36,0.72,1.08,1.8,2.7,3.6,92.2,94.7,95.4,95.9,95.9,95.6,95.6,92.7,95.5,96.1,96.4,96.4,96.1,96.1,90.3,94.5,95.3,95.9,96,95.7,95.6,"2017-07-01","2018-10-15"]
["ABB","PVI-3.6-OUTD-S-US-Z-A [240V]","N","Y","Y","N","N","N","N","3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector",3.6,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,340,480,0.3,0.72,1.08,1.8,2.7,3.6,91.1,94.1,94.9,95.6,95.8,95.7,95.4,92.4,95.5,96.3,96.7,96.7,96.6,96.5,90.2,94.6,95.6,96.2,96.4,96.3,95.9,"2017-07-01","2018-10-15"]
["ABB","PVI-3.6-OUTD-S-US-Z-A [277V]","N","Y","Y","N","N","N","N","3.6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector",3.6,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,395,480,0.36,0.72,1.08,1.8,2.7,3.6,90,93.4,94.4,95.4,95.7,95.6,95.1,91.9,95.4,96.3,96.9,97,96.9,96.6,90.4,94.9,95.9,96.6,96.8,96.8,96.3,"2017-07-01","2018-10-15"]
["ABB","PVI-3.6-OUTD-S-US-Z-M-A [208V]","N","Y","Y","N","N","N","N","3.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",3.6,208,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,310,480,0.36,0.72,1.08,1.8,2.7,3.6,92.2,94.7,95.4,95.9,95.9,95.6,95.6,92.7,95.5,96.1,96.4,96.4,96.1,96.1,90.3,94.5,95.3,95.9,96,95.7,95.6,"2017-07-01","2018-10-15"]
["ABB","PVI-3.6-OUTD-S-US-Z-M-A [240V]","N","Y","Y","N","N","N","N","3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",3.6,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,340,480,0.3,0.72,1.08,1.8,2.7,3.6,91.1,94.1,94.9,95.6,95.8,95.7,95.4,92.4,95.5,96.3,96.7,96.7,96.6,96.5,90.2,94.6,95.6,96.2,96.4,96.3,95.9,"2017-07-01","2018-10-15"]
["ABB","PVI-3.6-OUTD-S-US-Z-M-A [277V]","N","Y","Y","N","N","N","N","3.6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",3.6,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,395,480,0.36,0.72,1.08,1.8,2.7,3.6,90,93.4,94.4,95.4,95.7,95.6,95.1,91.9,95.4,96.3,96.9,97,96.9,96.6,90.4,94.9,95.9,96.6,96.8,96.8,96.3,"2017-07-01","2018-10-15"]
["ABB","PVI-3.8-OUTD-S-US-A [208V]","N","Y","Y","N","N","N","N","3.3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector",3.8,208,95.5,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.12,null,null,100,310,480,0.33,0.66,0.99,1.65,2.48,3.3,91.5,94.3,95.1,95.6,95.6,95.4,95.3,92.1,95.1,95.9,96.3,96.4,96.2,96.1,89.1,93.9,95,95.7,95.9,95.8,95.4,"2017-07-01","2018-10-15"]
["ABB","PVI-3.8-OUTD-S-US-A [240V]","N","Y","Y","N","N","N","N","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector",3.8,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.16,null,null,100,340,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,91.4,94.2,94.9,95.5,95.6,95.5,95.3,92.6,95.5,96.2,96.6,96.7,96.6,96.4,90.3,94.5,95.5,96.2,96.3,96.3,95.9,"2017-07-01","2018-10-15"]
["ABB","PVI-3.8-OUTD-S-US-A [277V]","N","Y","Y","N","N","N","N","3.8 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector",3.8,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.22,null,null,100,395,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,90.3,93.6,94.5,95.3,95.6,95.5,95.1,92,95.3,96.2,96.8,96.9,96.9,96.5,90.4,94.7,95.8,96.5,96.7,96.8,96.2,"2017-07-01","2018-10-15"]
["ABB","PVI-3.8-OUTD-S-US-Z-A [208V]","N","Y","Y","N","N","N","N","3.3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector",3.8,208,95.5,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.12,null,null,100,310,480,0.33,0.66,0.99,1.65,2.48,3.3,91.5,94.3,95.1,95.6,95.6,95.4,95.3,92.1,95.1,95.9,96.3,96.4,96.2,96.1,89.1,93.9,95,95.7,95.9,95.8,95.4,"2017-07-01","2018-10-15"]
["ABB","PVI-3.8-OUTD-S-US-Z-A [240V]","N","Y","Y","N","N","N","N","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector",3.8,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.16,null,null,100,340,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,91.4,94.2,94.9,95.5,95.6,95.5,95.3,92.6,95.5,96.2,96.6,96.7,96.6,96.4,90.3,94.5,95.5,96.2,96.3,96.3,95.9,"2017-07-01","2018-10-15"]
["ABB","PVI-3.8-OUTD-S-US-Z-A [277V]","N","Y","Y","N","N","N","N","3.8 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector",3.8,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.22,null,null,100,395,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,90.3,93.6,94.5,95.3,95.6,95.5,95.1,92,95.3,96.2,96.8,96.9,96.9,96.5,90.4,94.7,95.8,96.5,96.7,96.8,96.2,"2017-07-01","2018-10-15"]
["ABB","PVI-3.8-OUTD-S-US-Z-M-A [208V]","N","Y","Y","N","N","N","N","3.3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",3.8,208,95.5,"TUV Rheinland of North America","[3/9/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.12,null,null,100,310,480,0.33,0.66,0.99,1.65,2.48,3.3,91.5,94.3,95.1,95.6,95.6,95.4,95.3,92.1,95.1,95.9,96.3,96.4,96.2,96.1,89.1,93.9,95,95.7,95.9,95.8,95.4,"2017-07-01","2018-10-15"]
["ABB","PVI-3.8-OUTD-S-US-Z-M-A [240V]","N","Y","Y","N","N","N","N","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",3.8,240,96,"TUV Rheinland of North America","[3/9/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.16,null,null,100,340,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,91.4,94.2,94.9,95.5,95.6,95.5,95.3,92.6,95.5,96.2,96.6,96.7,96.6,96.4,90.3,94.5,95.5,96.2,96.3,96.3,95.9,"2017-07-01","2018-10-15"]
["ABB","PVI-3.8-OUTD-S-US-Z-M-A [277V]","N","Y","Y","N","N","N","N","3.8 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",3.8,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.22,null,null,100,395,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,90.3,93.6,94.5,95.3,95.6,95.5,95.1,92,95.3,96.2,96.8,96.9,96.9,96.5,90.4,94.7,95.8,96.5,96.7,96.8,96.2,"2017-07-01","2018-10-15"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SB-RA [240V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",3.8,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,92,95,95.7,95.9,96,95.8,95.7,93.7,96,96.6,96.9,97,96.8,96.7,91.7,95.2,96,96.6,96.7,96.5,96.3,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SB-RA-Q [240V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",3.8,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",1,null,null,200,355,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,92,95,95.7,95.9,96,95.8,95.7,93.7,96,96.6,96.9,97,96.8,96.7,91.7,95.2,96,96.6,96.7,96.5,96.3,"2020-08-21"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SE-RA [240V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply",3.8,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,92,95,95.7,95.9,96,95.8,95.7,93.7,96,96.6,96.9,97,96.8,96.7,91.7,95.2,96,96.6,96.7,96.5,96.3,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SZM-RA [240V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac Grid Support Interactive Utility Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply",3.8,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,92,95,95.7,95.9,96,95.8,95.7,93.7,96,96.6,96.9,97,96.8,96.7,91.7,95.2,96,96.6,96.7,96.5,96.3,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-3.8-TL-PLUS-US-SZ-RA [240V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and Rapid Shutdown power supply",3.8,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,92,95,95.7,95.9,96,95.8,95.7,93.7,96,96.6,96.9,97,96.8,96.7,91.7,95.2,96,96.6,96.7,96.5,96.3,"2017-07-01","2020-08-21"]
["ABB","PVI-4.2-OUTD-S-US-A [208V]","N","Y","Y","N","N","N","N","4.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector",4.2,208,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,310,480,0.42,0.84,1.26,2.1,3.15,4.2,92.9,95,95.6,95.9,95.8,95.4,95.6,93.5,95.8,96.3,96.4,96.3,95.9,96.1,91.4,94.9,95.6,95.9,95.8,95.5,95.6,"2017-07-01","2018-10-15"]
["ABB","PVI-4.2-OUTD-S-US-A [240V]","N","Y","Y","N","N","N","N","4.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector",4.2,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,340,480,0.42,0.84,1.26,2.1,3.15,4.2,91.8,94.4,95.2,95.8,95.8,95.4,95.5,93.3,95.9,96.5,96.7,96.7,96.5,96.5,91.3,95.1,95.9,96.3,96.4,96.2,96,"2017-07-01","2018-10-15"]
["ABB","PVI-4.2-OUTD-S-US-A [277V]","N","Y","Y","N","N","N","N","4.2 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector",4.2,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,395,480,0.42,0.84,1.26,2.1,3.15,4.2,90.8,93.9,94.8,95.6,95.7,95.6,95.3,92.8,95.8,96.6,97,97,96.9,96.7,91.6,95.4,96.2,96.7,96.8,96.7,96.4,"2017-07-01","2018-10-15"]
["ABB","PVI-4.2-OUTD-S-US-Z-A [208V]","N","Y","Y","N","N","N","N","4.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector",4.2,208,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,310,480,0.42,0.84,1.26,2.1,3.15,4.2,92.9,95,95.6,95.9,95.8,95.4,95.6,93.5,95.8,96.3,96.4,96.3,95.9,96.1,91.4,94.9,95.6,95.9,95.8,95.5,95.6,"2017-07-01","2018-10-15"]
["ABB","PVI-4.2-OUTD-S-US-Z-A [240V]","N","Y","Y","N","N","N","N","4.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector",4.2,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,340,480,0.42,0.84,1.26,2.1,3.15,4.2,91.8,94.4,95.2,95.8,95.8,95.4,95.5,93.3,95.9,96.5,96.7,96.7,96.5,96.5,91.3,95.1,95.9,96.3,96.4,96.2,96,"2017-07-01","2018-10-15"]
["ABB","PVI-4.2-OUTD-S-US-Z-A [277V]","N","Y","Y","N","N","N","N","4.2 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector",4.2,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,395,480,0.42,0.84,1.26,2.1,3.15,4.2,90.8,93.9,94.8,95.6,95.7,95.6,95.3,92.8,95.8,96.6,97,97,96.9,96.7,91.6,95.4,96.2,96.7,96.8,96.7,96.4,"2017-07-01","2018-10-15"]
["ABB","PVI-4.2-OUTD-S-US-Z-M-A [208V]","N","Y","Y","N","N","N","N","4.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",4.2,208,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.1,null,null,100,310,480,0.42,0.84,1.26,2.1,3.15,4.2,92.9,95,95.6,95.9,95.8,95.4,95.6,93.5,95.8,96.3,96.4,96.3,95.9,96.1,91.4,94.9,95.6,95.9,95.8,95.5,95.6,"2017-07-01","2018-10-15"]
["ABB","PVI-4.2-OUTD-S-US-Z-M-A [240V]","N","Y","Y","N","N","N","N","4.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",4.2,240,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,340,480,0.42,0.84,1.26,2.1,3.15,4.2,91.8,94.4,95.2,95.8,95.8,95.4,95.5,93.3,95.9,96.5,96.7,96.7,96.5,96.5,91.3,95.1,95.9,96.3,96.4,96.2,96,"2017-07-01","2018-10-15"]
["ABB","PVI-4.2-OUTD-S-US-Z-M-A [277V]","N","Y","Y","N","N","N","N","4.2 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",4.2,277,96,"TUV Rheinland of North America","[03/09/2017]","[A.4.0.B, B.4.2.2, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.2,null,null,100,395,480,0.42,0.84,1.26,2.1,3.15,4.2,90.8,93.9,94.8,95.6,95.7,95.6,95.3,92.8,95.8,96.6,97,97,96.9,96.7,91.6,95.4,96.2,96.7,96.8,96.7,96.4,"2017-07-01","2018-10-15"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SB-RA [208V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",4.2,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.42,0.84,1.26,2.1,3.15,4.2,92.6,95,95.7,95.6,95.2,95,95.2,94.1,96,96.4,96.6,96.5,96.1,96.4,92.3,95.2,96,96.2,96,95.8,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SB-RA-Q [208V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",4.2,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",0.9,null,null,200,340,480,0.42,0.84,1.26,2.1,3.15,4.2,92.6,95,95.7,95.6,95.2,95,95.2,94.1,96,96.4,96.6,96.5,96.1,96.4,92.3,95.2,96,96.2,96,95.8,95.8,"2020-08-21"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SE-RA [208V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply",4.2,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.42,0.84,1.26,2.1,3.15,4.2,92.6,95,95.7,95.6,95.2,95,95.2,94.1,96,96.4,96.6,96.5,96.1,96.4,92.3,95.2,96,96.2,96,95.8,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SZM-RA [208V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply",4.2,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.42,0.84,1.26,2.1,3.15,4.2,92.6,95,95.7,95.6,95.2,95,95.2,94.1,96,96.4,96.6,96.5,96.1,96.4,92.3,95.2,96,96.2,96,95.8,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SZ-RA [208V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply",4.2,208,96,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",0.9,null,null,200,340,480,0.42,0.84,1.26,2.1,3.15,4.2,92.6,95,95.7,95.6,95.2,95,95.2,94.1,96,96.4,96.6,96.5,96.1,96.4,92.3,95.2,96,96.2,96,95.8,95.8,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SB-RA [240V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",4.5999999999999996,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93.1,95.3,95.9,96,95.9,95.5,95.8,94.5,96.3,96.8,97,96.9,96.6,96.8,92.6,95.6,96.3,96.6,96.6,96.3,96.4,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SB-RA-Q [240V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",4.5999999999999996,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",1,null,null,200,355,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93.1,95.3,95.9,96,95.9,95.5,95.8,94.5,96.3,96.8,97,96.9,96.6,96.8,92.6,95.6,96.3,96.6,96.6,96.3,96.4,"2020-08-21"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SE-RA [240V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply",4.5999999999999996,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93.1,95.3,95.9,96,95.9,95.5,95.8,94.5,96.3,96.8,97,96.9,96.6,96.8,92.6,95.6,96.3,96.6,96.6,96.3,96.4,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SZM-RA [240V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply",4.5999999999999996,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93.1,95.3,95.9,96,95.9,95.5,95.8,94.5,96.3,96.8,97,96.9,96.6,96.8,92.6,95.6,96.3,96.6,96.6,96.3,96.4,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-4.6-TL-PLUS-US-SZ-RA [240V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and Rapid Shutdown power supply",4.5999999999999996,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93.1,95.3,95.9,96,95.9,95.5,95.8,94.5,96.3,96.8,97,96.9,96.6,96.8,92.6,95.6,96.3,96.6,96.6,96.3,96.4,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SB-RA [208V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",4.5999999999999996,208,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,240,340,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93,95.4,96.2,96.4,96.3,96.1,96.1,93.6,95.9,96.5,96.8,96.8,96.6,96.6,90.8,94.9,95.8,96.4,96.4,96.3,96,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SB-RA-QU [208V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",4.5999999999999996,208,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",1,null,null,240,340,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93,95.4,96.2,96.4,96.3,96.1,96.1,93.6,95.9,96.5,96.8,96.8,96.6,96.6,90.8,94.9,95.8,96.4,96.4,96.3,96,"2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SE-RA [208V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply",4.5999999999999996,208,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,240,340,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93,95.4,96.2,96.4,96.3,96.1,96.1,93.6,95.9,96.5,96.8,96.8,96.6,96.6,90.8,94.9,95.8,96.4,96.4,96.3,96,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SZM-RA [208V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply",4.5999999999999996,208,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,240,340,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93,95.4,96.2,96.4,96.3,96.1,96.1,93.6,95.9,96.5,96.8,96.8,96.6,96.6,90.8,94.9,95.8,96.4,96.4,96.3,96,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SZ-RA [208V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply",4.5999999999999996,208,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,240,340,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93,95.4,96.2,96.4,96.3,96.1,96.1,93.6,95.9,96.5,96.8,96.8,96.6,96.6,90.8,94.9,95.8,96.4,96.4,96.3,96,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SZ-RA-U [208V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply",4.5999999999999996,208,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,240,340,480,0.46,0.92,1.38,2.2999999999999998,3.45,4.5999999999999996,93,95.4,96.2,96.4,96.3,96.1,96.1,93.6,95.9,96.5,96.8,96.8,96.6,96.6,90.8,94.9,95.8,96.4,96.4,96.3,96,"2020-08-21"]
["ABB","PVI-5000-OUTD-US-A [208V]","N","Y","Y","N","N","N","N","5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector",5,208,96,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.18,null,null,100,310,480,0.5,1,1.5,2.5,3.75,5,93.4,95.7,96.2,96.4,96.2,95.8,96.1,93.6,95.9,96.5,96.7,96.6,96.3,96.4,90.9,94.7,95.6,96.1,96.1,95.9,95.8,"2017-07-01","2018-10-15"]
["ABB","PVI-5000-OUTD-US-A [240V]","N","Y","Y","N","N","N","N","5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector",5,240,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.24,null,null,100,345,480,0.5,1,1.5,2.5,3.75,5,92.5,95.5,96.1,96.4,96.3,96,96.1,93.8,96.2,96.7,97,96.9,96.6,96.7,91.5,95,95.9,96.4,96.5,96.3,96.1,"2017-07-01","2018-10-15"]
["ABB","PVI-5000-OUTD-US-A [277V]","N","Y","Y","N","N","N","N","5 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector",5,277,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.32,null,null,100,400,480,0.5,1,1.5,2.5,3.75,5,91.6,95,95.9,96.4,96.5,96.3,96.1,92.5,95.7,96.5,97.1,97.1,97,96.8,90.9,95,95.9,96.7,96.9,96.9,96.4,"2017-07-01","2018-10-15"]
["ABB","PVI-5000-OUTD-US-Z-A [208V]","N","Y","Y","N","N","N","N","5 kW, 208 Vac Grid Support Utility Interactive Inverter",5,208,96,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.18,null,null,100,310,480,0.5,1,1.5,2.5,3.75,5,93.4,95.7,96.2,96.4,96.2,95.8,96.1,93.6,95.9,96.5,96.7,96.6,96.3,96.4,90.9,94.7,95.6,96.1,96.1,95.9,95.8,"2017-07-01","2018-10-15"]
["ABB","PVI-5000-OUTD-US-Z-A [240V]","N","Y","Y","N","N","N","N","5 kW, 240 Vac Grid Support Utility Interactive Inverter",5,240,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.24,null,null,100,345,480,0.5,1,1.5,2.5,3.75,5,92.5,95.5,96.1,96.4,96.3,96,96.1,93.8,96.2,96.7,97,96.9,96.6,96.7,91.5,95,95.9,96.4,96.5,96.3,96.1,"2017-07-01","2018-10-15"]
["ABB","PVI-5000-OUTD-US-Z-A [277V]","N","Y","Y","N","N","N","N","5 kW, 277 Vac Grid Support Utility Interactive Inverter",5,277,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.32,null,null,100,400,480,0.5,1,1.5,2.5,3.75,5,91.6,95,95.9,96.4,96.5,96.3,96.1,92.5,95.7,96.5,97.1,97.1,97,96.8,90.9,95,95.9,96.7,96.9,96.9,96.4,"2017-07-01","2018-10-15"]
["ABB","PVI-5000-OUTD-US-Z-M-A [208V]","N","Y","Y","N","N","N","N","5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",5,208,96,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.18,null,null,100,310,480,0.5,1,1.5,2.5,3.75,5,93.4,95.7,96.2,96.4,96.2,95.8,96.1,93.6,95.9,96.5,96.7,96.6,96.3,96.4,90.9,94.7,95.6,96.1,96.1,95.9,95.8,"2017-07-01","2018-10-15"]
["ABB","PVI-5000-OUTD-US-Z-M-A [240V]","N","Y","Y","N","N","N","N","5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",5,240,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.24,null,null,100,345,480,0.5,1,1.5,2.5,3.75,5,92.5,95.5,96.1,96.4,96.3,96,96.1,93.8,96.2,96.7,97,96.9,96.6,96.7,91.5,95,95.9,96.4,96.5,96.3,96.1,"2017-07-01","2018-10-15"]
["ABB","PVI-5000-OUTD-US-Z-M-A [277V]","N","Y","Y","N","N","N","N","5 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",5,277,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.32,null,null,100,400,480,0.5,1,1.5,2.5,3.75,5,91.6,95,95.9,96.4,96.5,96.3,96.1,92.5,95.7,96.5,97.1,97.1,97,96.8,90.9,95,95.9,96.7,96.9,96.9,96.4,"2017-07-01","2018-10-15"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SB-RA [240V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",5,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.5,1,1.5,2.5,3.75,5,93.1,95.5,96.1,96.4,96.4,96.1,96.2,94,96.3,96.9,97.2,97.2,97,97,91.5,95.3,96.3,96.8,96.9,96.8,96.5,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SB-RA-QU [240V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",5,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",1,null,null,200,355,480,0.5,1,1.5,2.5,3.75,5,93.1,95.5,96.1,96.4,96.4,96.1,96.2,94,96.3,96.9,97.2,97.2,97,97,91.5,95.3,96.3,96.8,96.9,96.8,96.5,"2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SE-RA [240V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply",5,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.5,1,1.5,2.5,3.75,5,93.1,95.5,96.1,96.4,96.4,96.1,96.2,94,96.3,96.9,97.2,97.2,97,97,91.5,95.3,96.3,96.8,96.9,96.8,96.5,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SZM-RA [240V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply",5,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.5,1,1.5,2.5,3.75,5,93.1,95.5,96.1,96.4,96.4,96.1,96.2,94,96.3,96.9,97.2,97.2,97,97,91.5,95.3,96.3,96.8,96.9,96.8,96.5,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SZ-RA [240V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply",5,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2018-10-15","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.5,1,1.5,2.5,3.75,5,93.1,95.5,96.1,96.4,96.4,96.1,96.2,94,96.3,96.9,97.2,97.2,97,97,91.5,95.3,96.3,96.8,96.9,96.8,96.5,"2017-07-01","2020-08-21"]
["ABB","UNO-DM-5.0-TL-PLUS-US-SZ-RA-U [240V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and Rapid Shutdown power supply",5,240,96.5,"TUV Rheinland of North America","[06/10/2020]","[1913B]","2020-08-21","[06/10/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1,null,null,200,355,480,0.5,1,1.5,2.5,3.75,5,93.1,95.5,96.1,96.4,96.4,96.1,96.2,94,96.3,96.9,97.2,97.2,97,97,91.5,95.3,96.3,96.8,96.9,96.8,96.5,"2020-08-21"]
["ABB","PVI-6000-OUTD-US-A [208V]","N","Y","Y","N","N","N","N","6 kW, 208 Vac Grid Support Utility Interactive Inverter",6,208,96,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.18,null,null,100,310,480,0.6,1.2,1.8,3,4.5,6,94,96,96.4,96.3,96,95.5,96,94.3,96.2,96.6,96.7,96.4,96,96.4,92.1,95.1,95.9,96.1,96,95.7,95.8,"2017-07-01","2018-10-15"]
["ABB","PVI-6000-OUTD-US-A [240V]","N","Y","Y","N","N","N","N","6 kW, 240 Vac Grid Support Utility Interactive Inverter",6,240,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.24,null,null,100,345,480,0.6,1.2,1.8,3,4.5,6,93.5,95.8,96.3,96.4,96.2,95.8,96.1,94.6,96.5,96.9,96.9,96.8,96.5,96.7,92.6,95.5,96.1,96.5,96.4,96.2,96.2,"2017-07-01","2018-10-15"]
["ABB","PVI-6000-OUTD-US-A [277V]","N","Y","Y","N","N","N","N","6 kW, 277 Vac Grid Support Utility Interactive Inverter",6,277,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.32,null,null,100,400,480,0.6,1.2,1.8,3,4.5,6,92.5,95.5,96.2,96.4,96.4,96.1,96.1,93.5,96.2,96.8,97.1,97.1,97,96.9,92.2,95.5,96.3,96.8,96.9,96.9,96.5,"2017-07-01","2018-10-15"]
["ABB","PVI-6000-OUTD-US-Z-A [208V]","N","Y","Y","N","N","N","N","6 kW, 208 Vac Grid Support Utility Interactive Inverter",6,208,96,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.18,null,null,100,310,480,0.6,1.2,1.8,3,4.5,6,94,96,96.4,96.3,96,95.5,96,94.3,96.2,96.6,96.7,96.4,96,96.4,92.1,95.1,95.9,96.1,96,95.7,95.8,"2017-07-01","2018-10-15"]
["ABB","PVI-6000-OUTD-US-Z-A [240V]","N","Y","Y","N","N","N","N","6 kW, 240 Vac Grid Support Utility Interactive Inverter",6,240,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.24,null,null,100,345,480,0.6,1.2,1.8,3,4.5,6,93.5,95.8,96.3,96.4,96.2,95.8,96.1,94.6,96.5,96.9,96.9,96.8,96.5,96.7,92.6,95.5,96.1,96.5,96.4,96.2,96.2,"2017-07-01","2018-10-15"]
["ABB","PVI-6000-OUTD-US-Z-A [277V]","N","Y","Y","N","N","N","N","6 kW, 277 Vac Grid Support Utility Interactive Inverter",6,277,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.32,null,null,100,400,480,0.6,1.2,1.8,3,4.5,6,92.5,95.5,96.2,96.4,96.4,96.1,96.1,93.5,96.2,96.8,97.1,97.1,97,96.9,92.2,95.5,96.3,96.8,96.9,96.9,96.5,"2017-07-01","2018-10-15"]
["ABB","PVI-6000-OUTD-US-Z-M-A [208V]","N","Y","Y","N","N","N","N","6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",6,208,96,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.18,null,null,100,310,480,0.6,1.2,1.8,3,4.5,6,94,96,96.4,96.3,96,95.5,96,94.3,96.2,96.6,96.7,96.4,96,96.4,92.1,95.1,95.9,96.1,96,95.7,95.8,"2017-07-01","2018-10-15"]
["ABB","PVI-6000-OUTD-US-Z-M-A [240V]","N","Y","Y","N","N","N","N","6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",6,240,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.24,null,null,100,345,480,0.6,1.2,1.8,3,4.5,6,93.5,95.8,96.3,96.4,96.2,95.8,96.1,94.6,96.5,96.9,96.9,96.8,96.5,96.7,92.6,95.5,96.1,96.5,96.4,96.2,96.2,"2017-07-01","2018-10-15"]
["ABB","PVI-6000-OUTD-US-Z-M-A [277V]","N","Y","Y","N","N","N","N","6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter",6,277,96.5,"TUV Rheinland of North America","[2/7/2017]","[A.4.1.0, B.4.2.0, C.2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.32,null,null,100,400,480,0.6,1.2,1.8,3,4.5,6,92.5,95.5,96.2,96.4,96.4,96.1,96.1,93.5,96.2,96.8,97.1,97.1,97,96.9,92.2,95.5,96.3,96.8,96.9,96.9,96.5,"2017-07-01","2018-10-15"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SB-RA [208V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU",6,208,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,240,340,480,0.6,1.2,1.8,3,4.5,6,94.3,96.3,96.7,96.8,96.6,96.3,96.6,94.9,96.7,97,97.1,97,96.7,96.9,93.7,96.2,96.7,97.1,97.1,96.8,96.8,"2017-11-01","2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SB-RA [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU",6,240,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,200,355,480,0.6,1.2,1.8,3,4.5,6,94.1,96.3,96.6,96.8,96.7,96.4,96.6,95.1,96.9,97.3,97.4,97.4,97.2,97.3,93.8,96.4,97.1,97.4,97.5,97.4,97.2,"2017-11-01","2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SB-RA-QU [208V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",6,208,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2020-08-21","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",1.3,null,null,240,340,480,0.6,1.2,1.8,3,4.5,6,94.3,96.3,96.7,96.8,96.6,96.3,96.6,94.9,96.7,97,97.1,97,96.7,96.9,93.7,96.2,96.7,97.1,97.1,96.8,96.8,"2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SB-RA-QU [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply",6,240,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2020-08-21","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"N","N",1.3,null,null,200,355,480,0.6,1.2,1.8,3,4.5,6,94.1,96.3,96.6,96.8,96.7,96.4,96.6,95.1,96.9,97.3,97.4,97.4,97.2,97.3,93.8,96.4,97.1,97.4,97.5,97.4,97.2,"2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SC-RA [208V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, cellular, RSD PSU",6,208,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,240,340,480,0.6,1.2,1.8,3,4.5,6,94.3,96.3,96.7,96.8,96.6,96.3,96.6,94.9,96.7,97,97.1,97,96.7,96.9,93.7,96.2,96.7,97.1,97.1,96.8,96.8,"2017-11-01","2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SC-RA [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, cellular, RSD PSU",6,240,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,200,355,480,0.6,1.2,1.8,3,4.5,6,94.1,96.3,96.6,96.8,96.7,96.4,96.6,95.1,96.9,97.3,97.4,97.4,97.2,97.3,93.8,96.4,97.1,97.4,97.5,97.4,97.2,"2017-11-01","2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SE-RA [208V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, Ethernet card, RSD PSU",6,208,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,240,340,480,0.6,1.2,1.8,3,4.5,6,94.3,96.3,96.7,96.8,96.6,96.3,96.6,94.9,96.7,97,97.1,97,96.7,96.9,93.7,96.2,96.7,97.1,97.1,96.8,96.8,"2017-11-01","2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SE-RA [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, Ethernet card, RSD PSU",6,240,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,200,355,480,0.6,1.2,1.8,3,4.5,6,94.1,96.3,96.6,96.8,96.7,96.4,96.6,95.1,96.9,97.3,97.4,97.4,97.2,97.3,93.8,96.4,97.1,97.4,97.5,97.4,97.2,"2017-11-01","2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-S-XRA [208V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU",6,208,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,240,340,480,0.6,1.2,1.8,3,4.5,6,94.3,96.3,96.7,96.8,96.6,96.3,96.6,94.9,96.7,97,97.1,97,96.7,96.9,93.7,96.2,96.7,97.1,97.1,96.8,96.8,"2017-11-01","2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-S-XRA [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU",6,240,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,200,355,480,0.6,1.2,1.8,3,4.5,6,94.1,96.3,96.6,96.8,96.7,96.4,96.6,95.1,96.9,97.3,97.4,97.4,97.2,97.3,93.8,96.4,97.1,97.4,97.5,97.4,97.2,"2017-11-01","2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SZM-RA [208V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, Zigbee, Revenue Grade Meter, RSD PSU",6,208,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/2020]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,240,340,480,0.6,1.2,1.8,3,4.5,6,94.3,96.3,96.7,96.8,96.6,96.3,96.6,94.9,96.7,97,97.1,97,96.7,96.9,93.7,96.2,96.7,97.1,97.1,96.8,96.8,"2017-11-01","2020-08-21"]
["ABB","UNO-DM-6.0-TL-PLUS-US-SZM-RA [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, Zigbee, Revenue Grade Meter, RSD PSU",6,240,97,"TUV Rheinland of North America","[06/09/202]","[1913D]","2018-10-15","[06/09/202]","2020-08-21","PCTEST","2020-01-16","2020-08-21",null,"Y","N",1.3,null,null,200,355,480,0.6,1.2,1.8,3,4.5,6,94.1,96.3,96.6,96.8,96.7,96.4,96.6,95.1,96.9,97.3,97.4,97.4,97.2,97.3,93.8,96.4,97.1,97.4,97.5,97.4,97.2,"2017-11-01","2020-08-21"]
["ABB","UNO-7.6-TL-OUTD-S-US-A [208V]","N","Y","Y","Y","N","N","N","7.6 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",7.6,208,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","[2/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.3,null,null,200,340,480,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,93.9,96,96.4,96.5,96.4,96.1,96.3,95.6,97.1,97.4,97.4,97.3,97,97.2,93.8,96.3,96.8,97.1,97,96.7,96.8,"2017-07-01","2019-02-15"]
["ABB","UNO-7.6-TL-OUTD-S-US-A [240V]","N","Y","Y","Y","N","N","N","7.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",7.6,240,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","[2/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.4,null,null,200,380,480,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,93.1,95.7,96.3,96.6,96.5,96.3,96.3,95.4,97.1,97.5,97.7,97.6,97.4,97.5,93.9,96.5,97.1,97.4,97.4,97.2,97.2,"2017-07-01","2019-02-15"]
["ABB","UNO-7.6-TL-OUTD-S-US-A [277V]","N","Y","Y","Y","N","N","N","7.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",7.6,277,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","[2/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.5,null,null,200,380,480,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,92.1,95.3,96.1,96.6,96.6,96.4,96.3,93.9,96.4,97,97.4,97.4,97.3,97.2,94.2,96.7,97.3,97.7,97.7,97.7,97.5,"2017-07-01","2019-02-15"]
["ABB","UNO-7.6-TL-OUTD-S-US-Z-A [208V]","N","Y","Y","Y","N","N","N","7.6 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",7.6,208,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","[2/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.3,null,null,200,340,480,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,93.9,96,96.4,96.5,96.4,96.1,96.3,95.6,97.1,97.4,97.4,97.3,97,97.2,93.8,96.3,96.8,97.1,97,96.7,96.8,"2017-07-01","2019-02-15"]
["ABB","UNO-7.6-TL-OUTD-S-US-Z-A [240V]","N","Y","Y","Y","N","N","N","7.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",7.6,240,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","[2/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.4,null,null,200,380,480,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,93.1,95.7,96.3,96.6,96.5,96.3,96.3,95.4,97.1,97.5,97.7,97.6,97.4,97.5,93.9,96.5,97.1,97.4,97.4,97.2,97.2,"2017-07-01","2019-02-15"]
["ABB","UNO-7.6-TL-OUTD-S-US-Z-A [277V]","N","Y","Y","Y","N","N","N","7.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",7.6,277,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","[2/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.5,null,null,200,380,480,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,92.1,95.3,96.1,96.6,96.6,96.4,96.3,93.9,96.4,97,97.4,97.4,97.3,97.2,94.2,96.7,97.3,97.7,97.7,97.7,97.5,"2017-07-01","2019-02-15"]
["ABB","UNO-7.6-TL-OUTD-S-US-Z-M-A [208V]","N","Y","Y","Y","N","N","N","7.6 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",7.6,208,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","[2/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.3,null,null,200,340,480,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,93.9,96,96.4,96.5,96.4,96.1,96.3,95.6,97.1,97.4,97.4,97.3,97,97.2,93.8,96.3,96.8,97.1,97,96.7,96.8,"2017-07-01","2019-02-15"]
["ABB","UNO-7.6-TL-OUTD-S-US-Z-M-A [240V]","N","Y","Y","Y","N","N","N","7.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",7.6,240,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","[2/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.4,null,null,200,380,480,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,93.1,95.7,96.3,96.6,96.5,96.3,96.3,95.4,97.1,97.5,97.7,97.6,97.4,97.5,93.9,96.5,97.1,97.4,97.4,97.2,97.2,"2017-07-01","2019-02-15"]
["ABB","UNO-7.6-TL-OUTD-S-US-Z-M-A [277V]","N","Y","Y","Y","N","N","N","7.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",7.6,277,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","[2/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.5,null,null,200,380,480,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,92.1,95.3,96.1,96.6,96.6,96.4,96.3,93.9,96.4,97,97.4,97.4,97.3,97.2,94.2,96.7,97.3,97.7,97.7,97.7,97.5,"2017-07-01","2019-02-15"]
["ABB","UNO-8.6-TL-OUTD-S-US-A [240V]","N","Y","Y","Y","N","N","N","8.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",8.6,240,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.4,null,null,200,380,480,0.86,1.72,2.58,4.3,6.45,8.6,93.7,95.9,96.4,96.6,96.4,96.2,96.3,95.7,97.3,97.6,97.7,97.6,97.4,97.5,94.5,96.7,97.2,97.4,97.4,97.2,97.2,"2017-07-01","2019-02-15"]
["ABB","UNO-8.6-TL-OUTD-S-US-A [277V]","N","Y","Y","Y","N","N","N","8.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",8.6,277,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.5,null,null,200,380,480,0.86,1.72,2.58,4.3,6.45,8.6,92.8,95.6,96.3,96.6,96.5,96.3,96.3,94.5,96.6,97.1,97.4,97.4,97.3,97.2,94.8,96.9,97.5,97.8,97.7,97.6,97.5,"2017-07-01","2019-02-15"]
["ABB","UNO-8.6-TL-OUTD-S-US-Z-A [240V]","N","Y","Y","Y","N","N","N","8.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",8.6,240,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.4,null,null,200,380,480,0.86,1.72,2.58,4.3,6.45,8.6,93.7,95.9,96.4,96.6,96.4,96.2,96.3,95.7,97.3,97.6,97.7,97.6,97.4,97.5,94.5,96.7,97.2,97.4,97.4,97.2,97.2,"2017-07-01","2019-02-15"]
["ABB","UNO-8.6-TL-OUTD-S-US-Z-A [277V]","N","Y","Y","Y","N","N","N","8.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",8.6,277,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.5,null,null,200,380,480,0.86,1.72,2.58,4.3,6.45,8.6,92.8,95.6,96.3,96.6,96.5,96.3,96.3,94.5,96.6,97.1,97.4,97.4,97.3,97.2,94.8,96.9,97.5,97.8,97.7,97.6,97.5,"2017-07-01","2019-02-15"]
["ABB","UNO-8.6-TL-OUTD-S-US-Z-M-A [240V]","N","Y","Y","Y","N","N","N","8.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",8.6,240,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.4,null,null,200,380,480,0.86,1.72,2.58,4.3,6.45,8.6,93.7,95.9,96.4,96.6,96.4,96.2,96.3,95.7,97.3,97.6,97.7,97.6,97.4,97.5,94.5,96.7,97.2,97.4,97.4,97.2,97.2,"2017-07-01","2019-02-15"]
["ABB","UNO-8.6-TL-OUTD-S-US-Z-M-A [277V]","N","Y","Y","Y","N","N","N","8.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector",8.6,277,97,"TUV Rheinland of North America","[2/7/2017]","[A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.5,null,null,200,380,480,0.86,1.72,2.58,4.3,6.45,8.6,92.8,95.6,96.3,96.6,96.5,96.3,96.3,94.5,96.6,97.1,97.4,97.4,97.3,97.2,94.8,96.9,97.5,97.8,97.7,97.6,97.5,"2017-07-01","2019-02-15"]
["ABB","TRIO-50.0-TL-OUTD-US-480 [480V]","N","Y","Y","N","N","N","N","50 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector",50,480,98,"TUV Rheinland of North America","[1/27/2017]","[A.0.9.A, B.1.E.1, C.1.8.8]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1,null,null,520,720,800,5,10,15,25,37.5,50,96.342590866613719,97.39411188523512,97.730509677227218,97.849372845857189,97.864151934162123,97.735773713628447,97.8,96.858957935821849,98.003347675106397,98.335107750948936,98.526031796946754,98.551492631407513,98.493346758272125,98.422163741220473,95.922612669418839,97.568344051090364,98.034086986063684,98.317886765684975,98.343247316145977,98.304327830005803,98.163305837510407,"2017-07-01","2018-10-15"]
["ABB","TRIO-60.0-TL-OUTD-US-480 [480V]","N","Y","Y","N","N","N","N","60 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector",60,480,98,"TUV Rheinland of North America","[1/27/2017]","[A.0.9.A, B.1.E.1, C.1.8.8]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.8,null,null,570,720,800,6,12,18,30,45,60,96.7,97.7,97.9,98,98,97.8,97.9,97.2,98.1,98.4,98.5,98.5,98.4,98.4,96.4,97.8,98.1,98.3,98.3,98.2,98.2,"2017-07-01","2018-10-15"]
["ABB","TRIO-TM-60.0-US-480 [480V]","N","Y","Y","Y","N","N","N","60 kVA, 480 Vac Grid Support Utility Interactive Inverter with arc detector",60,480,98,"TUV Rheinland of North America","[04/12/2018]","[A.0.2.7, B.0.2.9, C.0.5.1]","2018-10-15","[04/12/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.6,null,null,570,720,800,6,12,18,30,45,60,96.7,97.6,97.8,97.9,97.8,97.6,97.8,97.3,98.3,98.5,98.6,98.6,98.4,98.5,96.7,98,98.3,98.4,98.4,98.3,98.3,"2018-06-01","2018-10-15"]
["ABB","PVS-60-TL-R-US [480V]","N","Y","Y","Y","Y","Y*","Y","60 kVA 480Vac transformerless Grid Support Utility Inverter with arc detection.",60.033000000000001,480,98,"TUV Rheinland of North America","[06/15/2020]","[1945E]","2020-09-01","[06/15/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",0.9,null,null,570,720,800,6.0032800000000002,12.00656,18.009840000000001,30.016400000000001,45.0246,60.032800000000002,96.517815523973198,97.597234851715442,97.843304075726479,97.847374722694454,97.828467471784052,97.643075558723922,97.760961082379453,97.189852584467914,98.252714951518371,98.497527870131293,98.589146548256778,98.563054633865718,98.428766538933857,98.48351125339984,96.486801145112508,97.903693085731078,98.241722278149084,98.399571216601657,98.390504803724113,98.251739960357867,98.267127872946958,"2020-09-01"]
["ABB","PVS-60-TL-SC-R-US [480V]","N","Y","Y","Y","Y","Y*","Y","60 kVA 480Vac transformerless Grid Support Utility Inverter with arc detection.",60.033000000000001,480,98,"TUV Rheinland of North America","[06/15/2020]","[1945E]","2020-09-01","[06/15/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",0.9,null,null,570,720,800,6.0032800000000002,12.00656,18.009840000000001,30.016400000000001,45.0246,60.032800000000002,96.517815523973198,97.597234851715442,97.843304075726479,97.847374722694454,97.828467471784052,97.643075558723922,97.760961082379453,97.189852584467914,98.252714951518371,98.497527870131293,98.589146548256778,98.563054633865718,98.428766538933857,98.48351125339984,96.486801145112508,97.903693085731078,98.241722278149084,98.399571216601657,98.390504803724113,98.251739960357867,98.267127872946958,"2020-09-01"]
["ABB","PVS-60-TL-SC-US [480V]","N","Y","Y","Y","Y","Y*","Y","60 kW, 480 V transformerless Grid Support Uitlity Interactive Inverter",60.033000000000001,480,98,"TUV Rheinland of North America","[06/15/2020]","[1945E]","2019-06-03","[06/15/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",0.9,null,null,570,720,800,6.0032800000000002,12.00656,18.009840000000001,30.016400000000001,45.0246,60.032800000000002,96.517815523973198,97.597234851715442,97.843304075726479,97.847374722694454,97.828467471784052,97.643075558723922,97.760961082379453,97.189852584467914,98.252714951518371,98.497527870131293,98.589146548256778,98.563054633865718,98.428766538933857,98.48351125339984,96.486801145112508,97.903693085731078,98.241722278149084,98.399571216601657,98.390504803724113,98.251739960357867,98.267127872946958,"2019-06-03","2020-09-01"]
["ABB","PVS-60-TL-S-R-US [480V]","N","Y","Y","Y","Y","Y*","Y","60 kVA 480Vac transformerless Grid Support Utility Inverter with arc detection.",60.033000000000001,480,98,"TUV Rheinland of North America","[06/15/2020]","[1945E]","2020-09-01","[06/15/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",0.9,null,null,570,720,800,6.0032800000000002,12.00656,18.009840000000001,30.016400000000001,45.0246,60.032800000000002,96.517815523973198,97.597234851715442,97.843304075726479,97.847374722694454,97.828467471784052,97.643075558723922,97.760961082379453,97.189852584467914,98.252714951518371,98.497527870131293,98.589146548256778,98.563054633865718,98.428766538933857,98.48351125339984,96.486801145112508,97.903693085731078,98.241722278149084,98.399571216601657,98.390504803724113,98.251739960357867,98.267127872946958,"2020-09-01"]
["ABB","PVS-60-TL-S-US [480V]","N","Y","Y","Y","Y","Y*","Y","60 kW, 480 V transformerless Grid Support Uitlity Interactive Inverter",60.033000000000001,480,98,"TUV Rheinland of North America","[06/15/2020]","[1945E]","2019-06-03","[06/15/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",0.9,null,null,570,720,800,6.0032800000000002,12.00656,18.009840000000001,30.016400000000001,45.0246,60.032800000000002,96.517815523973198,97.597234851715442,97.843304075726479,97.847374722694454,97.828467471784052,97.643075558723922,97.760961082379453,97.189852584467914,98.252714951518371,98.497527870131293,98.589146548256778,98.563054633865718,98.428766538933857,98.48351125339984,96.486801145112508,97.903693085731078,98.241722278149084,98.399571216601657,98.390504803724113,98.251739960357867,98.267127872946958,"2019-06-03","2020-09-01"]
["ABB","PVS-60-TL-US [480V]","N","Y","Y","Y","Y","Y*","Y","60 kW, 480 V transformerless Grid Support Uitlity Interactive Inverter",60.033000000000001,480,98,"TUV Rheinland of North America","[06/15/2020]","[1945E]","2019-06-03","[06/15/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",0.9,null,null,570,720,800,6.0032800000000002,12.00656,18.009840000000001,30.016400000000001,45.0246,60.032800000000002,96.517815523973198,97.597234851715442,97.843304075726479,97.847374722694454,97.828467471784052,97.643075558723922,97.760961082379453,97.189852584467914,98.252714951518371,98.497527870131293,98.589146548256778,98.563054633865718,98.428766538933857,98.48351125339984,96.486801145112508,97.903693085731078,98.241722278149084,98.399571216601657,98.390504803724113,98.251739960357867,98.267127872946958,"2019-06-03","2020-09-01"]
["ABB","PVS-166-TL-POWER-MODULE-1-US [800V]","N","Y","Y","Y","Y","Y*","Y","166 kW, 800 V transformerless Grid Support Utility Interactive inverter",165.95400000000001,800,98.5,"TUV Rheinland of North America","[07/13/2020]","[1923D]","2019-12-23","[07/13/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",12,null,null,850,1100,1200,16.594999999999999,33.191000000000003,49.786000000000001,82.977000000000004,124.46599999999999,165.95400000000001,96.77,98.03,98.27,98.39,98.32,98.15,98.25,96.7,98.08,98.39,98.53,98.48,98.34,98.38,95.77,97.71,98.11,98.23,98.33,98.25,98.15,"2019-12-23","2020-09-01"]
["ABB","PVS-166-TL-POWER-MODULE-2-US [800V]","N","Y","Y","Y","Y","Y*","Y","166 kW, 800 V transformerless Grid Support Utility Interactive inverter",165.95400000000001,800,98.5,"TUV Rheinland of North America","[07/13/2020]","[1923D]","2019-12-23","[07/13/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",12,null,null,850,1100,1200,16.594999999999999,33.191000000000003,49.786000000000001,82.977000000000004,124.46599999999999,165.95400000000001,96.77,98.03,98.27,98.39,98.32,98.15,98.25,96.7,98.08,98.39,98.53,98.48,98.34,98.38,95.77,97.71,98.11,98.23,98.33,98.25,98.15,"2019-12-23","2020-09-01"]
["ABB","PVS-175-TL-POWER-MODULE-1-US [800V]","N","Y","Y","Y","Y","Y*","Y","175 kW, 800 V transformerless Grid Support Utility Interactive inverter",179.57400000000001,800,98.5,"TUV Rheinland of North America","[07/13/2020]","[1923D]","2019-12-23","[07/13/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",12,null,null,850,1100,1200,17.957000000000001,35.914999999999999,53.872,89.787000000000006,134.68100000000001,179.57400000000001,95.65,97.31,97.7,97.83,97.59,97.24,97.54,95.6,97.4,97.8,97.94,97.76,97.52,97.69,94.83,97.05,97.53,97.62,97.61,97.36,97.45,"2019-12-23","2020-09-01"]
["ABB","PVS-175-TL-POWER-MODULE-2-US [800V]","N","Y","Y","Y","Y","Y*","Y","175 kW, 800 V transformerless Grid Support Utility Interactive inverter",179.57400000000001,800,98.5,"TUV Rheinland of North America","[07/13/2020]","[1923D]","2019-12-23","[07/13/2020]","2020-09-01","UL","2020-07-29","2020-09-01",null,"Y","N",12,null,null,850,1100,1200,17.957000000000001,35.914999999999999,53.872,89.787000000000006,134.68100000000001,179.57400000000001,95.65,97.31,97.7,97.83,97.59,97.24,97.54,95.6,97.4,97.8,97.94,97.76,97.52,97.69,94.83,97.05,97.53,97.62,97.61,97.36,97.45,"2019-12-23","2020-09-01"]
["Altenergy Power System Inc.","YC600 [240V]","N","Y","Y","Y","Y","Y*","Y","548 W, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted",0.55000000000000004,240,96.5,"CSA Group","[02/10/2018]","[V5]","2018-10-15","[01/25/2019]","2020-04-13","CSA Group","2020-02-21","2020-04-13",null,"N","Y",0.02,null,null,24,36,45,5.4800000000000001E-2,0.1096,0.16439999999999999,0.27400000000000002,0.41099999999999998,0.54800000000000004,94.4,95.9,96,96.4,96.3,96.1,96.2,94.1,95.8,96.2,96.5,96.7,96.6,96.4,93.7,95.7,95.8,96.4,96.7,96.7,96.4,"2018-03-01","2020-04-13"]
["Altenergy Power System Inc.","QS1 [208V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 208 Vac  Grid Support Utility Interactive Microinverter",1.2182999999999999,208,96.5,"CSA Group","[02/07/2021]","[V5]","2021-03-11","[02/07/2021]","2021-03-11","CSA Group","2021-02-05","2021-03-11",null,"N","Y",4.5999999999999999E-2,null,null,27,37.5,48,0.12182899999999999,0.24365799999999999,0.36548699999999995,0.60914499999999994,0.91371749999999996,1.2182899999999999,95.462910782173736,96.450833571740759,96.576360547365155,96.569657121850355,96.139232614085742,95.492677150212742,96.238276514122461,95.150922104487478,96.390729994634597,96.716405426350349,96.716840111542652,96.377527091193897,95.933901276587122,96.418862880659361,94.853952526999166,96.162858852267263,96.057573094891055,96.578732483713011,96.378738534572932,95.993899432846192,96.291170031625953,"2021-03-11"]
["Altenergy Power System Inc.","QS1 [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted",1.2250000000000001,240,96.5,"CSA Group","[01/28/2019]","[V5]","2019-03-01","[01/28/2019]","2020-04-21","CSA Group","2020-03-18","2020-04-21",null,"N","Y",0.09,null,null,27,37.5,48,0.12251585203999998,0.24503170407999997,0.3675475561199999,0.61257926019999986,0.91886889029999974,1.2251585203999997,93.497015299373786,96.030198868558386,96.291805605462031,96.516377648924689,96.18970599969785,95.636820794062331,96.127231753875478,93.489077418155247,96.010152340904128,96.472039013204679,96.70926293039534,96.540734712474077,96.125506711745189,96.398525343937521,92.818802764414372,95.857275302642961,96.491627254570773,96.652233435545639,96.629689629012688,96.294175176843083,96.410024429940677,"2019-03-01","2020-04-21"]
["Altenergy Power System Inc.","QS1200 [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted",1.2250000000000001,240,96.5,"CSA Group","[01/28/2019]","[V5]","2019-03-01","[01/28/2019]","2020-04-21","CSA Group","2020-03-18","2020-04-21",null,"N","Y",0.09,null,null,27,37.5,48,0.12251585203999998,0.24503170407999997,0.3675475561199999,0.61257926019999986,0.91886889029999974,1.2251585203999997,93.497015299373786,96.030198868558386,96.291805605462031,96.516377648924689,96.18970599969785,95.636820794062331,96.127231753875478,93.489077418155247,96.010152340904128,96.472039013204679,96.70926293039534,96.540734712474077,96.125506711745189,96.398525343937521,92.818802764414372,95.857275302642961,96.491627254570773,96.652233435545639,96.629689629012688,96.294175176843083,96.410024429940677,"2019-03-01","2020-04-21"]
["Altenergy Power System Inc.","QS1A [240V]","N","Y ","Y ","Y ","N","N","N","1.5 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.516,240,96.5,"CSA Group","[07/02/2021]","[V7]","2021-08-23","[07/02/2021]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",3.7999999999999999E-2,null,null,30,41,52,0.152,0.30299999999999999,0.45500000000000002,0.75800000000000001,1.137,1.516,95.51,96.54,96.63,96.65,96.14,95.39,96.26,95.29,96.49,96.46,96.74,96.36,95.82,96.39,94.75,96.22,96.1,96.61,96.35,95.99,96.28,"2021-08-23"]
["Apparent Inc.","SG424U CA, 120VAC, 60Hz [120V]","N","Y","Y","Y","N","N","Y","250 W, 120 Vac Grid Support Utility Interactive Microinverter",0.25,120,91.5,"TUV Rheinland of North America","[08/24/2018]","[R313]","2019-04-02","[08/24/2018]","No Information Submitted","No Information Submitted","No Information Submitted","2021-01-11",null,"N","Y",0.45,null,null,31.2,36.4,48.9,0.03,0.05,0.08,0.13,0.19,0.25,85.4,91.1,91.5,92.1,91.8,90.6,91.5,87,90.8,91.5,92.4,92.2,91.2,91.8,86.1,90.9,92,92.2,92.4,92,92,"2019-04-02","2021-01-11"]
["Aptos Solar Technology LLC","MAC-400R [240V]","N","Y","Y ","Y ","Y ","Y*","Y","382W, 240 Vac Grid Support Utility Interactive Microinverter",0.38253999999999999,240,96.5,"CSA Group","[08/12/2021]","[V01.01.00]","2021-09-21","[08/12/2021]","2021-09-21","CSA Group","2021-08-13","2021-09-21",null,"N","Y",0.105,null,null,34,42,48,3.8254200000000002E-2,7.6508400000000004E-2,0.11476259999999999,0.191271,0.28690650000000001,0.38254199999999999,95.22842857142858,96.218428571428589,96.257238095238108,96.545714285714283,96.783523809523814,96.193761904761899,96.550482857142867,95.679523809523815,96.12704761904763,96.407190476190493,96.343142857142865,96.775857142857134,96.531571428571425,96.552239047619054,96.036380952380952,95.973476190476177,96.408523809523814,96.204571428571427,96.698857142857165,96.608857142857147,96.492949047619049,"2021-09-21"]
["Aptos Solar Technology LLC","MAC-800R [240V]","N","Y","Y ","Y ","Y ","Y*","Y"," 766W, 240 Vac Grid Support Utility Interactive Microinverter",0.76700000000000002,240,96.5,"CSA Group","[08/12/2021]","[V01.01.00]","2021-09-21","[08/12/2021]","2021-09-21","CSA Group","2021-08-13","2021-09-21",null,"N","Y",0.11,null,null,34,42,48,7.6708800000000008E-2,0.15341760000000002,0.23012639999999998,0.383544,0.57531599999999994,0.76708799999999999,95.466952380952392,96.173380952380967,96.22742857142859,96.490142857142885,96.694571428571422,96.149809523809523,96.493181904761911,95.793190476190475,96.05585714285715,96.384380952380951,96.331904761904767,96.700714285714298,96.490285714285719,96.506239047619061,95.702809523809506,95.90157142857143,96.412190476190474,96.194571428571436,96.70052380952383,96.574952380952382,96.473539047619056,"2021-09-21"]
["Canadian Solar Inc.","CSI-25K-T480GL01-UB [480V]","N","Y","Y","Y","Y","Y*","Y","25 kW, 480 Vac, Long Separate Wiring Box, Three-Phase Grid Support Utility Interactive Inverter ",24.957999999999998,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,347,470,800,2.4958062000000001,4.9916124000000002,7.4874185999999989,12.479030999999999,18.718546499999999,24.958061999999998,97.853771727652003,98.386845403985191,98.419952387549216,98.566500213491139,98.410525960115365,98.354027246196793,98.418132591815365,98.000100000000003,98.427499999999981,98.417400000000015,98.665900000000008,98.423000000000002,98.347599999999986,98.452876000000003,97.893000000000001,98.418700000000015,98.492999999999995,98.685000000000002,98.465900000000005,98.373000000000005,98.485242,"2020-11-23"]
["Canadian Solar Inc.","CSI-25KTL-GS-FL [480V]","N","Y","Y","Y","N","N","N","25 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter",25,480,98,"Intertek","[01/31/2018]","[1D]","2018-11-01","[01/31/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",14,null,null,580,650,780,2.5,5,7.5,12.5,18.75,25,97.1,97.4,97.6,97.9,98,97.8,97.9,97.1,97.3,97.6,97.8,98.3,97.6,98,97.2,97.4,97.7,97.8,98,97.5,97.9,"2018-02-15","2019-11-15"]
["Canadian Solar Inc.","CSI-25KTL-GS-FLB [480V]","N","Y","Y","Y","Y","Y*","Y","25 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box",25,480,98,"Intertek","[03/29/2019]","[1D]","2019-05-01","[03/29/2019]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",14,null,null,580,650,770,2.5,5,7.5,12.5,18.75,25,97.142964722609719,97.310266944970607,97.558210787909843,97.902019188713425,98.186266472133454,97.785643565531629,97.945644668839236,97.136908002620146,97.294740203904553,97.401291401475831,97.883743867106773,98.295370114052176,97.750866187372679,97.978043980385848,97.236056040998633,97.395994266218807,97.543490263387042,97.692214831859445,98.001190746739226,97.48550403188284,97.794732198613758,"2019-05-01","2020-11-23"]
["Canadian Solar Inc.","CSI-30K-T480GL01-UB [480V]","N","Y","Y","Y","Y","Y*","Y","30 kW, 480 Vac, Long Separate Wiring Box, Three-Phase Grid Support Utility Interactive Inverter ",29.948,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,417,700,800,2.9947656600000001,5.9895313200000002,8.9842969799999999,14.973828299999999,22.460742449999998,29.947656599999998,97.768902305203113,98.391990453870477,98.434352470454385,98.566898759988248,98.412125272315521,98.316637698776148,98.415784930219743,97.813999999999993,98.424199999999999,98.504000000000005,98.650999999999996,98.419999999999987,98.356000000000023,98.451359999999994,97.890000000000015,98.427900000000022,98.516999999999996,98.6982,98.451000000000008,98.365000000000009,98.482937000000007,"2020-11-23"]
["Canadian Solar Inc.","CSI-30KTL-GS-FL [480V]","N","Y","Y","Y","N","N","N","30 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter",30,480,98,"Intertek","[01/31/2018]","[1D]","2018-11-01","[01/31/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",15,null,null,580,650,780,3,6,9,15,22.5,30,97.1,97.9,97.9,98.3,97.5,97.9,97.8,97.4,98.1,98.1,98.4,98.1,97.9,98.1,97.1,97.9,98,98.3,98,97.8,98,"2018-02-15","2019-11-15"]
["Canadian Solar Inc.","CSI-30KTL-GS-FLB [480V]","N","Y","Y","Y","Y","Y*","Y","30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box",30,480,98,"Intertek","[03/29/2019]","[1D]","2019-05-01","[03/29/2019]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",15,null,null,580,650,780,3,6,9,15,22.5,30,97.136729034962897,97.91235168892814,97.904963869081769,98.308894833573305,97.870536038966534,97.917405124902231,97.94180468208252,97.378314041689322,98.038837889530924,98.035886776299634,98.347723576110241,98.11389303563567,97.915010820497599,98.110516670195011,97.119954609958342,97.865597999954872,97.961685543933498,98.238894650235139,97.96866928700517,97.810325302197526,97.977559213440088,"2019-05-01","2020-11-23"]
["Canadian Solar Inc.","CSI-36K-T480GL01-UB [480V]","N","Y","Y","Y","Y","Y*","Y","36 kW, 480 Vac, Long Separate Wiring Box, Three-Phase Grid Support Utility Interactive Inverter ",35.924999999999997,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,500,700,800,3.592505800000001,7.1850116000000019,10.777517400000002,17.962529000000004,26.943793500000005,35.925058000000007,97.743542748672965,98.364995951458212,98.406126214457615,98.579027787829361,98.430897196517691,98.307273880710142,98.42206169688879,97.796000000000006,98.347400000000022,98.464999999999989,98.635999999999981,98.468000000000004,98.334000000000003,98.463310000000007,97.826000000000008,98.403800000000004,98.495999999999995,98.662100000000009,98.48299999999999,98.319000000000003,98.483730999999992,"2020-11-23"]
["Canadian Solar Inc.","CSI-36KTL-CT [480V]","N","Y","Y","N","N","N","N","36 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000 Vdc",36,480,98,"CSA Group","[8/2/2017]","[V0.60]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",0,null,null,540,730,800,3.6,7.2,10.8,18,27,36,95.5,96.8,97.2,97.5,97.5,97.3,97.3,97.4,98.3,98.5,98.5,98.5,98.3,98.4,97.1,98,98.3,98.4,98.3,98.2,98.3,"2017-10-01","2018-11-01"]
["Canadian Solar Inc.","CSI-36KTL-GS-FL [480V]","N","Y","Y","Y","N","N","N","36 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter",36,480,98,"Intertek","[01/31/2018]","[1D]","2018-11-01","[01/31/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",15,null,null,580,650,780,3.6,7.2,10.8,18,27,36,97.3,98.2,98.1,98.4,97.6,98.1,97.9,97.7,98.3,98.3,98.4,98.3,98.1,98.3,97.4,98.1,98.2,98.3,98.2,98.1,98.2,"2018-02-15","2019-11-15"]
["Canadian Solar Inc.","CSI-36KTL-GS-FLB [480V]","N","Y","Y","Y","Y","Y*","Y","36 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box",36,480,98,"Intertek","[03/29/2019]","[1D]","2019-05-01","[03/29/2019]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",15,null,null,580,650,780,3.6,7.2,10.799999999999999,18,27,36,97.355578045132162,98.146917292221246,98.113242472029853,98.345701137831327,98.021452704297786,98.148305437610048,98.086540527162839,97.654488278356141,98.316398063259214,98.259121423086086,98.438016064841605,98.34302453004014,98.1379196196186,98.313776360586488,97.362390657069383,98.153961833334407,98.213796105992046,98.374901951968553,98.171535410091963,98.075769292291866,98.18128089254526,"2019-05-01","2020-11-23"]
["Canadian Solar Inc.","CSI-40K-T480GL01-UB [480V]","N","Y","Y","Y","Y","Y*","Y","40 kW, 480 Vac, Long Separate Wiring Box, Three-Phase Grid Support Utility Interactive Inverter",39.926000000000002,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,556,700,800,3.9925869200000004,7.9851738400000007,11.977760760000001,19.962934600000001,29.944401900000003,39.925869200000001,97.756568472373232,98.349904317363411,98.430978331530511,98.565106380262918,98.43188587334069,98.327263423100959,98.423410378427576,97.786999999999992,98.366899999999987,98.458999999999989,98.628,98.441000000000003,98.347000000000008,98.447865000000007,97.832000000000008,98.414799999999985,98.466000000000008,98.635000000000005,98.515000000000001,98.335999999999999,98.493040000000008,"2020-11-23"]
["Canadian Solar Inc.","CSI-40KTL-GS [480V]","N","Y","Y","Y","N","N","N","40 kW, 480 Vac, 3-phase Utility Interactive Inverter, with external fan",40,480,98.5,"Intertek","[01/31/2018]","[1D]","2018-11-01","[01/31/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,780,4,8,12,20,30,40,97.5,98,98.1,98.2,98.1,97.7,98.1,97.8,98.3,98.4,98.6,98.5,98.3,98.5,97.6,98.1,98.2,98.4,98.3,98,98.3,"2018-02-15","2019-11-15"]
["Canadian Solar Inc.","CSI-40KTL-GS-B [480V]","N","Y","Y","Y","N","N","N","40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box and external Fan ",40,480,98.5,"Intertek","[03/29/2019]","[1D]","2019-05-15","[03/29/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,780,4,8,12,20,30,40,97.470025307598263,98.006823686121322,98.057428071819388,98.197211562051521,98.113980664562945,98.029180485035397,98.089316769729265,97.925867299237069,98.308888937177215,98.392001764941469,98.714528238058236,98.572481627994733,98.34230976222382,98.530101031561941,97.582250848768538,98.156490052565275,98.193182081593463,98.435303308923267,98.348895960607109,98.244441064517957,98.302846993591785,"2019-05-15"]
["Canadian Solar Inc.","CSI-40KTL-GS-FL [480V]","N","Y","Y","Y","N","N","N","40 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter",40,480,98.5,"Intertek","[01/31/2018]","[1D]","2018-11-01","[01/31/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,780,4,8,12,20,30,40,97.5,98,98.1,98.2,98.1,98,98.1,97.9,98.3,98.4,98.7,98.6,98.3,98.5,97.6,98.2,98.2,98.4,98.3,98.2,98.3,"2018-02-15","2019-11-15"]
["Canadian Solar Inc.","CSI-40KTL-GS-FLB [480V]","N","Y","Y","Y","Y","Y*","Y","40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box",40,480,98.5,"Intertek","[03/29/2019]","[1D]","2019-05-01","[03/29/2019]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,580,650,780,4,8,12,20,30,40,97.47774059338056,98.003904274929724,98.056390714442401,98.19522213581763,98.12583970822547,98.027356845132402,98.095131259352613,97.924650523872657,98.310478358411089,98.400182583606565,98.72105900754346,98.578524443130533,98.342023806171653,98.535673385660147,97.576353190610263,98.150441636686395,98.179486696378575,98.433666102320259,98.342812395871789,98.244022499188716,98.297076189282905,"2019-05-01","2020-11-23"]
["Canadian Solar Inc.","CSI-50K-T480GL01-UB [480V]","N","Y","Y","Y","Y","Y*","Y"," 50 kW, 480 Vac Grid Support Utility Interactive Inverter    ",49.915999999999997,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,568,720,850,4.9916124000000002,9.9832248000000003,14.974837199999998,24.958061999999998,37.437092999999997,49.916123999999996,97.751999999999995,98.364199999999997,98.433999999999997,98.585000000000008,98.419999999999987,98.313000000000002,98.421469999999999,97.790999999999997,98.380900000000011,98.446999999999989,98.644999999999982,98.443000000000012,98.352000000000004,98.452165000000008,97.84,98.411000000000001,98.483000000000004,98.679999999999993,98.493000000000009,98.320099999999996,98.492204999999998,"2020-11-23"]
["Canadian Solar Inc.","CSI-50KTL-CT [480V]","N","Y","Y","N","N","N","N","50 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc",50,480,98.5,"CSA Group","[7/6/2017]","[V5.00]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",0.88,null,null,480,730,850,5,10,15,25,37.5,50,95.608866666666671,96.843033333333338,97.481599999999986,97.854866666666666,97.832722222222202,97.690433333333345,97.649684777777765,98.018411111111092,98.627466666666663,98.774899999999988,98.802266666666668,98.719577777777744,98.610844444444439,98.705492222222205,97.733900000000006,98.458566666666655,98.622255555555569,98.659377777777792,98.586888888888865,98.469777777777765,98.559964333333326,"2017-10-01","2018-11-01"]
["Canadian Solar Inc.","CSI-50KTL-GS [480V]  ","N","Y","Y","Y","N","N","N","50 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter,",50,480,98.5,"Intertek","[01/08/2018]","[19/01]","2018-11-01","[01/08/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,720,5,10,15,25,37.5,50,97.7,98.4,98.5,98.6,98.5,98.4,98.4,97.8,98.5,98.6,98.7,98.5,98.4,98.5,97.9,98.6,98.7,98.8,98.6,98.5,98.6,"2018-02-01","2019-11-15"]
["Canadian Solar Inc.","CSI-50KTL-GS-B [480V]","N","Y","Y","Y","Y","Y*","Y","50 kW, 480 Vac, Seperated Wiring Box, 3-phase Grid Support Utility Interactive Inverter,",50,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,580,650,720,5,10,15,25,37.5,50,97.73621,98.444220000000001,98.455920000000006,98.582179999999994,98.449969999999993,98.347470000000001,98.444490000000002,97.798339999999996,98.53134,98.552109999999999,98.700419999999994,98.512280000000004,98.395949999999999,98.523150000000001,97.876750000000001,98.578149999999994,98.650589999999994,98.759609999999995,98.567750000000004,98.464439999999996,98.585700000000003,"2018-02-01","2020-11-23"]
["Canadian Solar Inc.","CSI-50KTL-GS-FL [480V] ","N","Y","Y","Y","N","N","N","50 kW, 480 Vac, Fanless, 3-phase Grid Support Utility Interactive Inverter,",50,480,98.5,"Intertek","[01/08/2018]","[19/01]","2018-11-01","[01/08/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,720,5,10,15,25,37.5,50,97.5,98.5,98.4,98.6,98.3,98.5,98.4,97.8,98.6,98.5,98.7,98.4,98.5,98.5,98,98.7,98.8,98.8,98.6,98.5,98.6,"2018-02-01","2019-11-15"]
["Canadian Solar Inc.","CSI-50KTL-GS-FLB [480V]","N","Y","Y","Y","Y","Y*","Y","50 kW, 480 Vac, Seperated Wiring Box, Fanless, 3-phase Grid Support Utility Interactive Inverter,",50,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,580,650,720,5,10,15,25,37.5,50,97.516660000000002,98.527910000000006,98.440969999999993,98.556190000000001,98.322069999999997,98.44641,98.369799999999998,97.746949999999998,98.550470000000004,98.522189999999995,98.653930000000003,98.433809999999994,98.488839999999996,98.47175,97.980519999999999,98.699969999999993,98.804749999999999,98.791889999999995,98.567930000000004,98.500640000000004,98.62312,"2018-02-01","2020-11-23"]
["Canadian Solar Inc.","CSI-60K-T480GL01-UB [480V]","N","Y","Y","Y","Y","Y*","Y"," 60 kW, 480 Vac Grid Support Utility Interactive Inverter    ",59.933,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,526,720,850,5.993277120000001,11.986554240000002,17.979831360000002,29.966385600000002,44.949578400000007,59.932771200000005,97.739000000000004,98.411000000000016,98.443999999999988,98.579000000000008,98.411999999999992,98.280000000000015,98.41734000000001,97.786999999999992,98.4024,98.465000000000003,98.622,98.441000000000003,98.341999999999985,98.448850000000007,97.808999999999997,98.433999999999997,98.521999999999991,98.688999999999993,98.47999999999999,98.325999999999993,98.49208999999999,"2020-11-23"]
["Canadian Solar Inc.","CSI-60KTL-CT [480V]","N","Y","Y","N","N","N","N","60 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc",60,480,98.5,"CSA Group","[7/6/2017]","[V5.00]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",0.88,null,null,540,730,850,6,12,18,30,45,60,96.510377777777791,97.476077777777775,97.885233333333332,98.052477777777781,97.943411111111089,97.727133333333313,97.867831888888873,98.222722222222217,98.711588888888883,98.791055555555559,98.779022222222224,98.654766666666688,98.498144444444435,98.674943222222225,98.000833333333347,98.550600000000003,98.663277777777779,98.658800000000014,98.522800000000018,98.354055555555547,98.540291444444463,"2017-10-01","2018-11-01"]
["Canadian Solar Inc.","CSI-60KTL-GS [480V]","N","Y","Y","Y","N","N","N","60 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter,",60,480,98.5,"Intertek","[01/08/2018]","[19/01]","2018-11-01","[01/08/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,720,6,12,18,30,45,60,97.7,98.3,98.4,98.6,98.4,98.2,98.4,97.8,98.5,98.5,98.6,98.5,98.3,98.5,97.9,98.5,98.6,98.7,98.6,98.5,98.6,"2018-02-01","2019-11-15"]
["Canadian Solar Inc.","CSI-60KTL-GS-B [480V]","N","Y","Y","Y","Y","Y*","Y","60 kW, 480 Vac, Seperated Wiring Box, 3-phase Grid Support Utility Interactive Inverter,",60,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,580,650,720,6,12,18,30,45,60,97.725110000000001,98.310810000000004,98.418899999999994,98.550129999999996,98.371089999999995,98.223780000000005,98.378209999999996,97.822659999999999,98.449550000000002,98.540400000000005,98.626189999999994,98.49897,98.329369999999997,98.492649999999998,97.862219999999994,98.525220000000004,98.586510000000004,98.699969999999993,98.55256,98.449910000000003,98.553479999999993,"2018-02-01","2020-11-23"]
["Canadian Solar Inc.","CSI-66K-T480GL01-UB [480V]","N","Y","Y","Y","Y","Y*","Y"," 66 kW, 480 Vac Grid Support Utility Interactive Inverter    ",65.926000000000002,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,579,720,850,6.592550720000002,13.185101440000004,19.777652160000002,32.962753600000006,49.444130400000006,65.925507200000013,97.751999999999995,98.350999999999999,98.412999999999997,98.587999999999994,98.419999999999987,98.309999999999988,98.418769999999981,97.772999999999996,98.342999999999989,98.47999999999999,98.676999999999992,98.436000000000007,98.318999999999988,98.45487,97.806999999999988,98.368999999999986,98.501000000000005,98.657000000000011,98.487000000000009,98.320999999999998,98.482980000000012,"2020-11-23"]
["Canadian Solar Inc.","CSI-66KTL-GS [480V]","N","Y","Y","Y","N","N","N","66 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter.",66,480,98.5,"Intertek","[01/08/2018]","[19/01]","2018-11-01","[01/08/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,720,6.6,13.2,19.8,33,49.5,66,97.6,98.4,98.5,98.6,98.4,98.3,98.4,97.7,98.5,98.6,98.7,98.5,98.4,98.5,97.8,98.7,98.7,98.8,98.6,98.5,98.6,"2018-02-01","2019-11-15"]
["Canadian Solar Inc.","CSI-66KTL-GS-B [480V]","N","Y","Y","Y","Y","Y*","Y","66 kW, 480 Vac, Seperated Wiring Box, 3-phase Grid Support Utility Interactive Inverter     ",66,480,98.5,"Intertek","[03/06/2020]","[1D]","2020-11-23","[03/06/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,580,650,720,6.6,13.2,19.8,33,49.5,66,97.571680000000001,98.376260000000002,98.476309999999998,98.563289999999995,98.421390000000002,98.311779999999999,98.416049999999998,97.744069999999994,98.500609999999995,98.553719999999998,98.7042,98.498869999999997,98.390150000000006,98.513030000000001,97.772109999999998,98.671279999999996,98.653779999999998,98.773750000000007,98.556129999999996,98.491799999999998,98.584729999999993,"2018-02-01","2020-11-23"]
["Canadian Solar Inc.","CSI-75K-T480GL02-U [480V]","N","Y","Y","Y","Y","Y*","Y","75 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter ",75,480,98.5,"CSA Group","[10/16/2020]","[V1C]","2020-11-23","[10/16/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,550,720,850,7.5002329129464727,15.000465825892945,22.500698738839418,37.501164564732363,56.251746847098545,75.002329129464727,98.147025032417488,98.538297364749269,98.524999107031618,98.623779108232739,98.379194007296135,98.216237003843389,98.438574049165965,98.17746730354655,98.521488547158611,98.543858150753337,98.666551658550517,98.444472139663873,98.238359986110964,98.485900179213203,98.244021361705535,98.573713583958948,99.014770545419339,98.621144781425926,98.5743288559581,98.294002446800633,98.609753819213765,"2020-11-23"]
["Canadian Solar Inc.","CSI-80K-T480GL02-U [480V]","N","Y","Y","Y","Y","Y*","Y","85 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter",80,480,98.5,"CSA Group","[10/16/2020]","[V1C]","2020-11-23","[10/16/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,550,720,850,8.0003050776117188,16.000610155223438,24.000915232835151,40.001525388058589,60.002288082087887,80.003050776117178,98.144056766704836,98.536304442013858,98.524086928927204,98.626467261140164,98.379382268335164,98.212328397713335,98.438715071182898,98.176411874265156,98.523181299386493,98.543033514575981,98.665352417337218,98.444660833820109,98.242401261303542,98.4858938743197,98.245072716984239,98.577628018526184,99.014921894647586,98.627129098799657,98.575015590597445,98.289762113147972,98.611418416385362,"2020-11-23"]
["Canadian Solar Inc.","CSI-90K-T480GL02-U [480V]","N","Y","Y","Y","Y","Y*","Y","90 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter ",90,480,98.5,"CSA Group","[10/16/2020]","[V1C]","2020-11-23","[10/16/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,550,720,850,9.0004863717252821,18.000972743450564,27.001459115175845,45.002431858626409,67.503647787939613,90.004863717252817,98.142462468207924,98.530089186513663,98.517514631575267,98.620241445136358,98.381968147783681,98.212915859518517,98.437644328622937,98.167699369061353,98.520772502298982,98.536703570264194,98.657051898547635,98.44293645368937,98.229611437880564,98.481368819353506,98.240022511847229,98.571329194013131,99.015803036201163,98.619661805706784,98.571478964294428,98.291391257797599,98.607646117683032,"2020-11-23"]
["Canadian Solar Inc.","CSI-100K-T480GL02-U [480V]","N","Y","Y","Y","Y","Y*","Y","100 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter ",100,480,98.5,"CSA Group","[10/16/2020]","[V1C]","2020-11-23","[10/16/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,550,720,850,10.000404076371181,20.000808152742362,30.001212229113538,50.0020203818559,75.003030572783842,100.0040407637118,98.140564410825306,98.526079453185915,98.519674341535762,98.618874231032336,98.379626790887073,98.210929571364574,98.43599973633178,98.16926795541994,98.524401802932246,98.538788389017313,98.658248405104047,98.442025680353225,98.230123739739625,98.481657377691548,98.242034120221604,98.571351197024953,99.013935310145271,98.618839828970707,98.571012971722467,98.288911860939493,98.606959994021295,"2020-11-23"]
["Canadian Solar Inc.","CSI-125KTL-GS-E [600V]","N","Y","Y","Y","Y","Y*","Y","125 kW, 600 Vac, 3-phase Grid Support Utility Interactive Inverter, single input",125,600,98.5,"CSA Group","[10/16/2020]","[V08]","2020-11-23","[10/16/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,860,950,1250,12.508265174439627,25.016530348879254,37.524795523318879,62.541325872198129,93.811988808297201,125.08265174439626,98.91665522812005,99.027907871118359,98.940968438394933,98.94618560587287,98.85207356138136,98.746414168721444,98.888596488489611,98.5469464246206,98.840474251603069,98.772193840490829,98.80392771433803,98.633809068909542,98.62883538295489,98.692750226104664,98.280518048463477,98.699974088322037,98.794745388070737,98.661885226486504,98.467930647761705,98.300639692202196,98.543619998409113,"2019-08-15","2020-11-23"]
["Canadian Solar Inc.","CSI-125K-T600GL02-U [600V]","N","Y","Y","Y","Y","Y*","Y","125 kW, 600 Vac, 3-phase Grid Support Utility Interactive Inverter, single input",125.083,600,98.5,"CSA Group","[10/16/2020]","[V08]","2020-11-23","[10/16/2020]","2020-11-23","CSA Group","2020-10-16","2020-11-23",null,"N","N",1,null,null,860,1080,1250,12.508265174439641,25.016530348879282,37.524795523318922,62.5413258721982,93.811988808297301,125.0826517443964,98.244150078788806,98.633881987410717,98.622049586795669,98.725008043697628,98.477330413578301,98.313568328361839,98.537021277728655,98.273504152953748,98.629869980182661,98.646207777090751,98.760872825293617,98.546891900995405,98.335963954530357,98.586412796943918,98.343571962692792,98.673361179391733,99.115933131286468,98.721105260927743,98.67586508935122,98.396605109774001,98.710793770871362,"2020-11-23"]
["Canadian Solar Inc.","CSI-185K-T600GL02-U [600V]","N","Y","Y","Y","Y","Y*","Y","185 kW, 600 Vac Grid Support Utility Interactive Inverter",185.005,600,98.5,"CSA Group","[11/10/2020]","[V18]","2021-01-21","[11/10/2020]","2021-01-21","CSA Group","2020-11-10","2021-01-21",null,"N","N",1,null,null,850,1080,1300,18.500525910334222,37.001051820668444,55.501577731002662,92.502629551671106,138.75394432750664,185.00525910334221,97.817999999999984,98.477000000000018,98.621000000000009,98.626999999999995,98.457000000000022,98.25,98.477470000000011,97.932000000000016,98.565999999999988,98.653999999999982,98.581999999999994,98.403999999999996,98.181000000000012,98.449450000000013,97.649999999999991,98.488,98.579000000000008,98.893000000000001,98.698000000000022,98.444000000000031,98.659550000000024,"2021-01-21"]
["Canadian Solar Inc.","CSI-255K-T800GL02-U [800V]","N","Y","Y","Y","Y","Y*","Y","255 kW, 800 Vac Grid Support Utility Interactive Inverter\n",255.01300000000001,800,98.5,"CSA Group","[11/10/2020]","[V18]","2021-01-21","[11/10/2020]","2021-01-21","CSA Group","2020-11-10","2021-01-21",null,"N","N",1,null,null,850,1080,1300,25.501261036265959,51.002522072531917,76.503783108797876,127.50630518132979,191.25945777199468,255.01261036265959,97.817999999999984,98.477000000000004,98.621000000000009,98.626999999999995,98.457000000000022,98.25,98.477470000000011,97.64500000000001,98.298999999999978,98.49499999999999,98.545999999999978,98.427000000000007,98.254999999999995,98.413869999999989,98.058999999999997,98.701000000000008,98.84,98.834999999999994,98.696000000000026,98.520999999999987,98.708490000000012,"2021-01-21"]
["CE+T Energy Solutions Inc.","30C3 [480V]","Y","Y","Y","Y","N","N","N","30 kW, 480 Vac Grid Support Utility Interactive Battery Charge controller with additional Photovoltaic input",29.99,480,95,"UL","[10/31/2018];[10/31/2018];[10/31/2018];[10/31/2018];[03/22/2019]","[3.2.42];[3.2.60];[3.2.90];[3.2.91];[3.2.106]","2018-10-15","[03/22/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Formerly Ideal Power Inc. 30C3 [480V]","N","N",56.8,null,null,550,700,850,3,6,9,15,22.49,29.99,92.7,94.3,94.8,95.2,95.1,94.8,94.9,92.2,94.2,94.6,95.3,95.4,95.5,95.1,89.6,92.8,93.3,94.8,95.2,95.4,94.6,"2018-02-01","2020-03-11"]
["Chilicon Power, LLC","CP-250E-60/72-208/240-MC4 [208V]","N","Y","Y","Y","Y","Y*","Y","277 W, 208 Vac Grid Support Utility Interactive Inverter",0.27700000000000002,208,95.5,"Intertek","[01/08/2020]","[3542]","2018-10-15","[02/19/2019]","2020-02-11","Intertek","2020-01-07","2020-02-11",null,"N","Y",0.02,null,null,28,30,32,0.03,0.06,0.08,0.14000000000000001,0.21,0.28000000000000003,92,95.1,95.9,96,95.6,94.9,95.5,91.2,94.8,95.7,96,95.6,95.1,95.5,90.6,94.5,95.6,96,95.7,95.2,95.4,"2017-12-15","2020-02-11"]
["Chilicon Power, LLC","CP-250E-60/72-208/240-MC4 [240V]","N","Y","Y","Y","Y","Y*","Y","289 W, 240 Vac Grid Support Utility Interactive Inverter",0.28899999999999998,240,96,"Intertek","[01/08/2020]","[3542]","2018-10-15","[02/19/2019]","2020-02-11","Intertek","2020-01-07","2020-02-11",null,"N","Y",0.06,null,null,28,30,32,0.03,0.06,0.09,0.14000000000000001,0.22,0.28999999999999998,92.3,95.4,96.1,96.2,95.9,95.2,95.8,91.6,95.2,96,96.3,96,95.4,95.8,91,95.1,95.9,96.3,96.1,95.6,95.8,"2017-12-15","2020-02-11"]
["Chilicon Power, LLC","CP-720-60/72/96-208/240-MC4 [240V]","N","Y","Y","Y","Y","Y*","Y","720 W, 240 Vac, Grid Support Utility Interactive Twin Microinverter (2 PV modules per inverter)",0.72099999999999997,240,96,"Intertek","[01/13/2020]","[3541]","2019-02-01","[02/15/2019]","2020-02-11","Intertek","2020-01-07","2020-02-11",null,"N","Y",0.1,null,null,60,65,70,7.2121866666666673E-2,0.14424373333333335,0.21636559999999999,0.36060933333333334,0.54091400000000001,0.72121866666666667,93.132533333333342,95.850773333333336,96.484973333333329,96.66358666666666,96.312706666666671,95.434200000000004,96.212834533333336,92.506166666666687,95.53543333333333,96.34790666666666,96.695073333333312,96.259353333333337,95.397799999999989,96.1320798,91.717346666666657,95.219053333333321,96.14567333333332,96.611386666666675,96.027659999999997,95.18540666666668,95.909448666666663,"2019-02-01","2020-02-11"]
["Chilicon Power, LLC","CP-720-60/72/96-208/240-MC4 [208V]","N","Y","Y","Y","Y","Y*","Y","720 W, 208 Vac, Grid Support Utility Interactive Twin Microinverter (2 PV modules per inverter)",0.72499999999999998,208,95.5,"Intertek","[01/13/2020]","[3541]","2019-02-01","[02/15/2019]","2020-02-11","Intertek","2020-01-07","2020-02-11",null,"N","Y",0.1,null,null,60,65,70,7.254300000000001E-2,0.14508600000000002,0.21762899999999999,0.36271500000000001,0.54407249999999996,0.72543000000000002,93.072133333333326,95.575999999999993,96.237066666666664,96.324399999999997,95.675333333333342,94.843733333333347,95.728370666666677,93.002266666666657,95.359733333333324,96.085999999999984,96.33593333333333,95.730400000000003,94.913666666666671,95.731738666666658,92.399799999999999,94.870333333333335,95.874399999999994,96.234199999999987,95.68846666666667,94.621066666666678,95.599559333333332,"2019-02-01","2020-02-11"]
["Chint Power Systems America","CPS SCA20KTL-DO-R/US-480 [480V]","N","Y","Y","Y","Y","Y*","Y","20 kVA, 1000 Vdc, 480 Vac, 3-phase, non-isolated Grid Support Utility Interactive Inverter",20,480,98,"Intertek","[11/28/2019]","[00.02.00]","2020-01-13","[11/28/2019]","2020-08-03","Intertek","2020-03-19","2020-08-03",null,"N","N",3,null,null,560,735,850,2.0111933333333334,4.0223866666666668,6.0335799999999997,10.055966666666666,15.08395,20.111933333333333,96.981509777777802,97.665209777777775,97.801241333333337,97.831345777777784,97.602279111111102,97.256001333333302,97.635260448888886,97.901590222222211,98.330456888888875,98.481923555555554,98.413890222222236,98.295634666666686,98.149012444444466,98.321471222222243,97.53970133333334,98.21510099999999,98.312145777777772,98.268437999999975,98.198667999999998,97.988923555555544,98.190912794444444,"2020-01-13","2020-08-03"]
["Chint Power Systems America","CPS SCA25KTL-DO-R/US-480 [480V]","N","Y","Y","Y","Y","Y*","Y","25 kVA, 1000 Vdc, 480 Vac, 3 phase, non-isolated Grid Support Utility Interactive Inverter",25,480,98,"Intertek","[11/28/2019]","[00.02.00]","2020-01-13","[11/28/2019]","2020-08-03","Intertek","2020-03-19","2020-08-03",null,"N","N",3,null,null,560,735,850,2.5258733333333332,5.0517466666666664,7.5776199999999996,12.629366666666666,18.944049999999997,25.258733333333332,96.911910371269158,97.698228393841575,97.82952991949324,97.839929437398695,97.597147898886149,97.286821705426348,97.638146078416753,97.89734543415868,98.32561756529762,98.477298970263973,98.408187377201003,98.281658579248486,98.094613938471952,98.309179665200418,97.500273558455632,98.156221457435635,98.313740711134443,98.279290178911168,98.185350638522294,97.996273689551259,98.182171361011868,"2020-01-13","2020-08-03"]
["Chint Power Systems America","CPS SCA25KTL-DO/US-208 [208V]","N","Y","Y","Y","Y","Y*","Y","25 kVA, 1000 Vdc, 208 Vac, 3-phase, non-isolated Grid Support Utility Interactive Inverter",25.431999999999999,208,96.5,"CSA Group","[09/10/2020]","[V01.01.00]","2020-10-12","[09/10/2020]","2020-10-12","Intertek","2020-08-28","2020-10-12",null,"N","N",2.9,null,null,480,575,850,2.5432000000000001,5.0864000000000003,7.629599999999999,12.715999999999999,19.073999999999998,25.431999999999999,95.686990530657496,96.805469029935551,97.031082017127943,97.042352525770227,96.776890574103703,96.473458639563972,96.805801881443344,95.307142857142864,96.284285714285716,96.787142857142854,96.781428571428577,96.482857142857142,96.118571428571428,96.506899999999987,93.594285714285704,95.617142857142866,96.122857142857143,96.335714285714289,96.151428571428568,95.850000000000023,96.04262857142858,"2020-10-12"]
["Chint Power Systems America","CPS SCA36KTL-DO/US [480V]","N","Y","Y","Y","Y","Y*","Y","36 kVA, 480 Vac, 1000 Vdc, 3-phase, non-isolated Grid Support Utility Interactive Inverter",36,480,98,"CSA Group","[12/10/2020]","[V0.90]","2018-10-15","[12/10/2020]","2021-01-21","CSA Group","2020-12-07","2021-01-21",null,"Y","N",0,null,null,540,730,800,3.6,7.2,10.8,18,27,36,95.5,96.8,97.2,97.5,97.5,97.3,97.3,97.4,98.3,98.5,98.5,98.5,98.3,98.4,97.1,98,98.3,98.4,98.3,98.2,98.3,"2017-09-01","2021-01-21"]
["Chint Power Systems America","CPS SCA50KTL-DO/US-480 [480V]","N","Y","Y","Y","Y","Y*","Y","50 kVA , 1000 Vdc, 480 Vac,  3-phase, non-isolated Grid Support Utility Interactive Inverter",50,480,98.5,"CSA Group","[7/6/2017]; [3/15/2019];[09/10/2020]","[V5.00]; [V01.09.00];[V01.12.00]","2018-10-15","[3/15/2019];[09/10/2020]","2020-08-03","Intertek","2020-03-19","2020-08-03",null,"N","N",0.88,null,null,480,730,850,5,10,15,25,37.5,50,95.6,96.8,97.5,97.9,97.8,97.7,97.6,98,98.6,98.8,98.8,98.7,98.6,98.7,97.7,98.5,98.6,98.7,98.6,98.5,98.6,"2017-08-01","2020-10-12"]
["Chint Power Systems America","CPS SCA60KTL-DO/US-480 [480V]","N","Y","Y","Y","Y","Y*","Y","60 kVA , 1000 Vdc, 480 Vac,  3-phase, non-isolated Grid Support Utility Interactive Inverter",60,480,98.5,"CSA Group","[7/6/2017]; [03/15/2019];[09/10/2020]","[V5.00]; [V01.09.00];[V01.12.00]","2018-10-15","[3/15/2019];[09/10/2020]","2020-08-03","Intertek","2020-03-19","2020-08-03",null,"N","N",0.88,null,null,540,730,850,6,12,18,30,45,60,96.5,97.5,97.9,98.1,97.9,97.7,97.9,98.2,98.7,98.8,98.8,98.7,98.5,98.7,98,98.6,98.7,98.7,98.5,98.4,98.5,"2017-08-01","2020-10-12"]
["Chint Power Systems America","CPS SCH100KTL-AIO/US-600 [600V]","N","Y","Y","Y","Y","Y*","Y","100 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter",100,600,98.5,"CSA Group","[09/26/2019]","[V4.00]","2019-11-01","[09/26/2019]","2020-08-03","Intertek","2020-03-19","2020-08-03",null,"N","N",0.33,null,null,870,1000,1300,10.055999999999999,20.111999999999998,30.167999999999999,50.28,75.42,100.56,98.51,99,99.01,99.09,98.94,98.78,98.96,98.03,98.44,98.61,98.6,98.48,98.29,98.49,97.25,97.82,98.17,98.19,98.14,97.93,98.09,"2019-11-01","2020-08-03"]
["Chint Power Systems America","CPS SCH100KTL-DO/US-600 [600V]","N","Y","Y","Y","Y","Y*","Y","100 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter",100,600,98.5,"CSA Group","[06/08/2018];[06/17/2020]","[V2.00];[V4.00]","2018-10-15","[06/08/2018];[06/17/2020]","2020-08-03","Intertek","2020-03-19","2020-08-03",null,"N","N",4.5,null,null,870,1000,1300,10,20,30,50,75,100,98.551913170550606,98.997154065699576,99.061972328956216,99.00078048409739,98.873762893254693,98.745242502108027,98.909891269772601,97.902550474383133,98.484857507533135,98.532225912684183,98.567385583558817,98.447013080233702,98.281050897108159,98.454332453800717,97.097950071451592,97.901048246755153,98.071044058010003,98.105298659618327,98.080044777547087,97.905368682202621,98.027300586886966,"2018-08-01","2020-08-03"]
["Chint Power Systems America","CPS SCH100KTL-DO/US-480 [480V]","N","Y","Y ","Y ","Y ","Y*","Y","100 kVA , 1500 Vdc, 480 Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter",100.20399999999999,480,98,"CSA Group","[06/01/2021]","[V1.09.00]","2021-10-01","[06/01/2021]","2021-10-01","CSA Group","2021-08-11","2021-10-01",null,"N","N",1.6,null,null,760,1000,1300,10.02037,20.04074,30.061109999999999,50.101849999999999,75.152774999999991,100.2037,98.541428571428568,98.92,98.891428571428563,98.752857142857138,98.44714285714285,98.122857142857143,98.575857142857146,98.031428571428577,98.501428571428576,98.55285714285715,98.41857142857144,98.13,97.778571428571439,98.238400000000013,97.242857142857133,97.88,98.087142857142837,98.018571428571406,97.744285714285724,97.358571428571437,97.810471428571432,"2021-10-01"]
["Chint Power Systems America","CPS SCH125KTL-AIO/US-600 [600V]","N","Y","Y","Y","Y","Y*","Y","125 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter",125,600,98.5,"CSA Group","[09/26/2019]","[V4.00]","2019-11-01","[09/26/2019]","2020-08-03","Intertek","2020-03-19","2020-08-03",null,"N","N",0.33,null,null,870,1000,1300,12.555,25.109000000000002,37.664000000000001,62.773000000000003,94.16,125.54600000000001,98.79,99.03,99.05,99.01,98.81,98.58,98.88,98.2,98.51,98.6,98.54,98.33,98.01,98.39,97.56,98.01,98.15,98.17,97.96,97.63,98,"2019-11-01","2020-08-03"]
["Chint Power Systems America","CPS SCH125KTL-DO/US-600 [600V]","N","Y","Y","Y","Y","Y*","Y","125 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter",125,600,98.5,"CSA Group","[06/08/2018];[06/17/2020]","[V2.00];[V4.00]","2018-10-15","[06/08/2018];[06/17/2020]","2020-08-03","Intertek","2020-03-19","2020-08-03",null,"N","N",4.9000000000000004,null,null,870,1000,1300,12.5,25,37.5,62.5,93.75,125,98.707684820160623,99.032876683015886,99.06907867202689,98.952307926326014,98.789908624320944,98.561327097315782,98.854943257884798,98.100765115696163,98.562967124892893,98.584147101616665,98.538352052196359,98.35202881328668,98.051253876208165,98.404468508880086,97.417075240097319,98.038277017220338,98.140012382549841,98.141131689216635,97.978233161124621,97.699223726568917,97.998460762830888,"2018-08-01","2020-08-03"]
["Darfon Electronics Corp.","H5001xxxxxx [240V]","Y","Y","Y","Y","Y","Y*","Y","5000 W, 240 Vac, Hybrid PV and Battery Grid Support Utility Interactive Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality.",4.8440000000000003,240,94.5,"Intertek","[07/28/2020]","[82,372]","2020-11-02","[07/28/2020]","2020-11-02","Intertek","2020-08-12","2020-11-02",null,"N","N",28.48,null,null,300,360,380,0.4844174,0.9688348,1.4532521999999999,2.4220869999999999,3.6331305,4.8441739999999998,86.673553799999993,92.816092799999979,94.3501902,95.2023346,95.057924999999983,94.444936200000001,94.525206941999997,87.1365476,93.167628599999986,94.647862400000008,95.485913400000001,95.379741600000003,94.801270200000005,94.844955193999994,87.172866200000001,93.194648799999996,94.652253000000002,95.484140800000006,95.349433199999993,94.771366400000005,94.830354931999992,"2020-11-02","2021-01-11"]
["Darfon Electronics Corp.","H5000xxxxxx [240V]","Y","Y","Y","Y","Y","Y*","Y","5000 W, 240 Vac, Hybrid PV and Battery Grid support Utility Interactive Inverter with PCS functionality, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality.",5.0739999999999998,240,95.5,"Intertek","[07/28/2020]","[82,372]","2018-10-15","[07/28/2020]","2020-09-11","Intertek","2020-09-02","2020-09-11",null,"N","N",0.43,null,null,300,360,380,0.50800000000000001,1.016,1.524,2.54,3.81,5.0759999999999996,89.228338400000013,93.736259799999999,94.907423600000001,95.751822599999997,95.886322399999997,95.612956999999994,95.353118825999999,89.489125199999989,93.948561799999993,95.256629000000004,95.913850999999994,96.033797399999997,95.885842800000006,95.54190204999999,89.3176694,94.004821399999997,95.202498000000006,95.947675400000008,96.0160956,95.91960379999999,95.530770297999993,"2018-03-15","2021-01-11"]
["Delta Electronics","SOLIVIA 3.8 NA G4 TL [208V]","N","Y","Y","Y","Y","Y*","Y","3800 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type.",3.32,208,97.5,"CSA Group","[10/15/2020]","[02.05.01]","2018-10-15","[10/15/2020]","2020-11-12","Intertek","2020-09-30","2020-11-12",null,"Y","N",1.1399999999999999,null,null,100,380,500,0.33,0.66,1,1.66,2.4900000000000002,3.32,94.6,96.1,97,97.3,97.1,96.8,97,96.3,96.9,97.8,97.9,98.1,97.5,97.8,95.9,95.8,96.9,97.4,97.4,97.1,97.2,"2017-10-16","2020-11-12"]
["Delta Electronics","M4-TL-US [208V]","N","Y","Y","Y","Y","Y*","Y","3648 W, 208 Vac transformerless Grid Support Utility Interactive Inverter",3.33,208,97,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.92,null,null,180,380,480,0.33279999999999998,0.66559999999999997,0.99839999999999995,1.6639999999999999,2.496,3.3279999999999998,92,94.6,95.7,96.5,96.7,96.5,96.2,93,95.7,97.3,97.3,97.8,97.4,97.3,92.9,95.9,96.8,97.5,97.6,97.5,97.2,"2018-03-01","2020-08-11"]
["Delta Electronics","E4-TL-US [208V]","Y","Y","Y","Y","Y","Y*","Y","3328 W, 208 Vac, transformerless, Bi-directional, Multi-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",3.36,208,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2020-08-11","[07/07/2020]","2020-08-11","CSA Group","2020-05-27","2020-08-11",null,"Y","N",1.21,null,null,200,380,480,0.33598600000000001,0.67197200000000001,1.0079579999999999,1.6799299999999999,2.519895,3.3598599999999998,92.7057619047619,95.315952380952382,96.079380952380944,96.937476190476204,97.260999999999996,97.257904761904769,96.771649047619036,94.671571428571426,96.743333333333325,97.430952380952377,97.883190476190478,97.934238095238101,97.830571428571417,97.667888571428577,93.533380952380966,96.078619047619057,96.919190476190479,97.56452380952382,97.760333333333321,97.674666666666681,97.360829047619063,"2020-08-11"]
["Delta Electronics","SOLIVIA 3.8 NA G4 TL [240V]","N","Y","Y","Y","Y","Y*","Y","3800 W, 240 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type.",3.81,240,97.5,"CSA Group","[10/15/2020]","[02.05.01]","2018-10-15","[10/15/2020]","2020-11-12","Intertek","2020-09-30","2020-11-12",null,"Y","N",1.19,null,null,100,380,500,0.38,0.76,1.1399999999999999,1.91,2.86,3.81,94.1,95.9,96.9,97.3,97.2,96.8,97,95.5,96.9,98,98.3,98.1,98,98,94.6,95.6,97.3,97.8,97.8,97.6,97.5,"2017-10-16","2020-11-12"]
["Delta Electronics","M4-TL-US [240V]","N","Y","Y","Y","Y","Y*","Y","4000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter",3.84,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",2.0299999999999998,null,null,180,380,480,0.38400000000000001,0.76800000000000002,1.1519999999999999,1.92,2.88,3.84,92.9,95.1,96.1,96.9,96.9,96.7,96.6,95.7,97.4,97.8,98.1,98.1,98,98,93.6,96.4,97.2,97.7,97.8,97.7,97.5,"2018-03-01","2020-08-11"]
["Delta Electronics","E4-TL-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3840 W, 240 Vac, transformerless, Bi-directional, Multi-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",3.87,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2020-08-11","[07/07/2020]","2020-08-11","CSA Group","2020-05-27","2020-08-11",null,"Y","N",1.27,null,null,200,380,400,0.38695799999999997,0.77391599999999994,1.1608739999999997,1.9347899999999998,2.9021849999999998,3.8695799999999996,92.857285714285709,95.303238095238086,96.081619047619043,97.007952380952389,97.343285714285713,97.360904761904749,96.840904285714288,95.302476190476199,97.104857142857128,97.726142857142847,98.093285714285713,98.142904761904759,98.111380952380941,97.915377619047632,94.284999999999997,96.453619047619028,97.277333333333345,97.860761904761901,98.00376190476193,97.944809523809525,97.657355238095249,"2020-08-11"]
["Delta Electronics","M5-TL-US [208V]","N","Y","Y","Y","Y","Y*","Y","4560 W, 208 Vac transformerless Grid Support Utility Interactive Inverter",4.16,208,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.24,null,null,220,380,480,0.41599999999999998,0.83199999999999996,1.248,2.08,3.12,4.16,94.5,96.1,96.9,97.3,97.2,96.9,97,95.8,97.3,97.8,98,97.8,97.6,97.7,95,96.8,97.4,97.7,97.7,97.4,97.5,"2018-03-01","2020-08-11"]
["Delta Electronics","M5-TL-US [240V]","N","Y","Y","Y","Y","Y*","Y","5000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter",4.8600000000000003,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.26,null,null,220,380,480,0.48,0.96,1.44,2.4,3.6,4.8,94.3,96.1,96.9,97.3,97.2,96.9,97,96.3,97.6,98,98.2,98,97.8,97.9,95.6,97.2,97.7,98,97.9,97.7,97.8,"2018-03-01","2020-08-11"]
["Delta Electronics","M6-TL-US [208V]","N","Y","Y","Y","Y","Y*","Y","5472 W, 208 Vac transformerless Grid Support Utility Interactive Inverter.",4.99,208,97,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.86,null,null,200,380,480,0.49919999999999998,0.99839999999999995,1.4976,2.496,3.7440000000000002,4.992,94,95.6,96.5,97,97,96.7,96.7,95.7,97.2,97.7,97.8,97.7,97.3,97.6,94.6,96.5,97.2,97.5,97.5,97.2,97.3,"2018-03-01","2020-08-11"]
["Delta Electronics","E6-TL-US [208V]","Y","Y","Y","Y","Y","Y*","Y","4992 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",4.992,208,97,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.86,null,null,200,380,480,0.49920000000000003,0.99840000000000007,1.4976,2.496,3.7439999999999998,4.992,94.001552279710452,95.64854413845292,96.470502310715119,97.031778029948327,96.98839431139308,96.678915967705834,96.733417745109648,95.696002839548186,97.220439644049392,97.652205765380231,97.83623139070302,97.667061705813495,97.349085557061244,97.583732361611879,94.631669734067614,96.516985505297939,97.173540834476398,97.541628657333121,97.47105873269301,97.173936814249188,97.274040951844484,"2018-08-01","2020-08-11"]
["Delta Electronics","SOLIVIA 5.2 NA G4 TL [208V]","N","Y","Y","Y","Y","Y*","Y","5200 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type.",5.2,208,97.5,"CSA Group","[10/15/2020]","[02.05.01]","2018-10-15","[10/15/2020]","2020-11-12","Intertek","2020-09-30","2020-11-12",null,"Y","N",1.31,null,null,100,380,500,0.52,1.04,1.56,2.6,3.9,5.2,93.6,95.6,96.3,97.2,97.1,96.8,96.8,95.2,96.6,97.5,98,98,97.7,97.7,93.6,96.3,97,97.7,97.7,97.5,97.4,"2017-10-16","2020-11-12"]
["Delta Electronics","SOLIVIA 5.2 NA G4 TL [240V]","N","Y","Y","Y","Y","Y*","Y","5200 W, 240 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type.",5.2,240,97.5,"CSA Group","[10/15/2020]","[02.05.01]","2018-10-15","[10/15/2020]","2020-11-12","Intertek","2020-09-30","2020-11-12",null,"Y","N",1.42,null,null,100,380,500,0.52,1.04,1.56,2.6,3.9,5.2,94,95.8,96.4,97.3,97.4,97.1,97,95.2,97,97.5,98.2,98.3,98.1,98,93.8,96.6,97.2,97.9,98,98,97.7,"2017-10-16","2020-11-12"]
["Delta Electronics","E6-TL-US [240V]","Y","Y","Y","Y","Y","Y*","Y","5760 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",5.76,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",2.25,null,null,200,380,480,0.57599999999999996,1.1519999999999999,1.728,2.88,4.32,5.76,93.963625969438439,95.732446384706193,96.532807684212585,97.118348653429621,97.062377987109016,96.774553568769321,96.805745508944824,96.257434448555912,97.61499418821316,97.981948161933175,98.081440619035661,97.680440613673383,97.626730315988667,97.737953437828693,95.238569980658667,96.982509064759839,97.535664405666651,97.834209595941928,97.754794153662942,97.458502206940707,97.591098008080536,"2018-08-01","2020-08-11"]
["Delta Electronics","M6-TL-US [240V]","N","Y","Y","Y","Y","Y*","Y","6000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter",5.76,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",2.25,null,null,200,380,480,0.57599999999999996,1.1519999999999999,1.728,2.88,4.32,5.76,94,95.7,96.5,97.1,97.1,96.8,96.8,96.3,97.6,98,98.1,97.7,97.6,97.7,95.2,97,97.5,97.8,97.8,97.5,97.6,"2018-03-01","2020-08-11"]
["Delta Electronics","SOLIVIA 6.6 NA G4 TL [208V]","N","Y","Y","Y","Y","Y*","Y","6600 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type.",6.6,208,97.5,"CSA Group","[10/15/2020]","[02.05.01]","2018-10-15","[10/15/2020]","2020-11-12","Intertek","2020-09-30","2020-11-12",null,"Y","N",1.23,null,null,100,380,500,0.66,1.32,1.98,3.3,4.95,6.6,94.4,96.1,97,97.2,96.9,96.2,96.8,95.9,96.9,97.8,98,97.7,97.3,97.7,95,96.4,97.4,97.7,97.6,97.1,97.4,"2017-10-16","2020-11-12"]
["Delta Electronics","SOLIVIA 6.6 NA G4 TL [240V]","N","Y","Y","Y","Y","Y*","Y","6600W, 208Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type.",6.6,240,97.5,"CSA Group","[10/15/2020]","[02.05.01]","2018-10-15","[10/15/2020]","2020-11-12","Intertek","2020-09-30","2020-11-12",null,"Y","N",1.45,null,null,100,380,500,0.66,1.32,1.98,3.3,4.95,6.6,94.3,96.2,96.9,97.4,97.2,96.8,97,96,97.3,97.9,98.3,98.2,97.9,98,95,96.8,97.6,98,98,97.7,97.7,"2017-10-16","2020-11-12"]
["Delta Electronics","SOLIVIA 7.6 NA G4 TL [208V]","N","Y","Y","Y","Y","Y*","Y","7600 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type.",6.6,208,97.5,"CSA Group","[10/15/2020]","[02.05.01]","2018-10-15","[10/15/2020]","2020-11-12","Intertek","2020-09-30","2020-11-12",null,"Y","N",1.23,null,null,100,380,500,0.66,1.32,1.98,3.3,4.95,6.6,94.4,96.1,97,97.2,96.9,96.2,96.8,95.9,96.9,97.8,98,97.7,97.3,97.7,95,96.4,97.4,97.7,97.6,97.1,97.4,"2017-10-16","2020-11-12"]
["Delta Electronics","E8-TL-US [208V]","Y","Y","Y","Y","Y","Y*","Y","6656 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter\n",6.6559999999999997,208,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.1499999999999999,null,null,270,380,480,0.66559999999999997,1.3311999999999999,1.9967999999999999,3.3279999999999998,4.992,6.6559999999999997,95.230826251614573,96.891036349418002,97.383516545836727,97.634333677831506,97.427625078509706,97.050617106357407,97.332189072308523,95.947578725965741,97.410382433977375,97.794550069017504,97.948730653616494,97.699721373214217,97.39175599472415,97.663441843818802,94.854996124491507,96.776328670410962,97.373903337051033,97.660373266831044,97.517427624777397,97.162060564850904,97.36890273435543,"2018-08-01","2020-08-11"]
["Delta Electronics","M8-TL-US [208V]","N","Y","Y","Y","Y","Y*","Y","7296 W, 208 Vac transformerless Grid Support Utility Interactive Inverter",6.66,208,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.1499999999999999,null,null,270,380,480,0.66559999999999997,1.3311999999999999,1.9967999999999999,3.3279999999999998,4.992,6.6559999999999997,95.2,96.9,97.4,97.6,97.4,97.1,97.3,95.9,97.4,97.8,97.9,97.7,97.4,97.7,94.9,96.8,97.4,97.7,97.5,97.2,97.4,"2018-03-01","2020-08-11"]
["Delta Electronics","SOLIVIA 7.6 NA G4 TL [240V]","N","Y","Y","Y","Y","Y*","Y","7600 W, 240 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type.",7.6,240,97.5,"CSA Group","[10/15/2020]","[02.05.01]","2018-10-15","[10/15/2020]","2020-11-12","Intertek","2020-09-30","2020-11-12",null,"Y","N",1.43,null,null,100,380,500,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,95,96.4,97.3,97.4,97,96.4,97,96.3,97.4,98.1,98.3,98,97.7,98,95.5,97.2,97.7,98,97.9,97.5,97.7,"2017-10-16","2020-11-12"]
["Delta Electronics","E8-TL-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",7.68,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.19,null,null,270,380,480,0.76800000000000002,1.536,2.3039999999999998,3.84,5.76,7.68,95.220244762392653,96.786476523169469,97.360484342448359,97.661527866722594,97.514706743622483,97.063283332614333,97.376271330510363,96.557058272771911,97.768154171688977,98.091693567287209,98.164435292147104,97.997075218849318,97.640443280171482,97.956696708919409,95.553280568100988,97.213562614555073,97.733873018671247,97.947621890495725,97.848069433399232,97.50177995994143,97.714440510395107,"2018-08-01","2020-08-11"]
["Delta Electronics","M8-TL-US [240V]","N","Y","Y","Y","Y","Y*","Y","8000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter",7.68,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.19,null,null,270,380,480,0.76800000000000002,1.536,2.3039999999999998,3.84,5.76,7.68,95.2,96.8,97.4,97.7,97.5,97.1,97.4,96.6,97.8,98.1,98.2,98,97.6,98,95.6,97.2,97.7,97.9,97.8,97.5,97.7,"2018-03-01","2020-08-11"]
["Delta Electronics","M10-TL-US [208V]","N","Y","Y","Y","Y","Y*","Y","9.6 kW, 208 Vac Transformerless, Bi-directional Grid Support Utility Interactive Inverter",8.36,208,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2019-05-15","[07/07/2020]","2020-02-11","CSA Group","2020-01-16","2020-02-11",null,"Y","N",1.35,null,null,280,380,480,0.83599999999999997,1.6719999999999999,2.5079999999999996,4.18,6.27,8.36,95.658185806883793,97.203682700547461,97.62750266213348,97.693930841760704,97.333105719377528,96.718887587060649,97.340027774151622,96.10372934124652,97.46838032604667,97.842267846012263,97.87999564578169,97.481483377157048,96.938989093049173,97.525575061633518,95.323105508116171,96.969870400837721,97.495059999481398,97.675787377583774,97.378973313071157,96.798898585815508,97.323541074815395,"2019-05-15","2020-08-11"]
["Delta Electronics","M10-4-TL-US [208V]","N","Y","Y","Y","Y","Y*","Y","8320 W, 208 Vac transformerless Grid Support Utility Interactive Inverter",8.3849999999999998,208,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2020-08-11","[07/07/2020]","2020-08-11","CSA Group","2020-05-27","2020-08-11",null,"Y","N",1.35,null,null,280,350,480,0.83847999999999989,1.6769599999999998,2.5154399999999995,4.1923999999999992,6.2885999999999989,8.3847999999999985,95.976333333333329,97.034904761904755,97.294428571428583,97.382476190476183,97.179952380952372,96.844333333333324,97.164041428571437,96.73504761904762,97.560666666666663,97.698476190476171,97.602190476190472,97.360809523809522,97.068476190476204,97.422365238095239,95.525095238095233,96.980523809523802,97.343428571428575,97.440952380952368,97.211476190476205,96.927333333333337,97.182290476190488,"2020-08-11"]
["Delta Electronics","M10-TL-US [240V]","N","Y","Y","Y","Y","Y*","Y","9.6 kW, 240 Vac Transformerless, Bi-directional Grid Support Utility Interactive Inverter",9.6199999999999992,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2019-05-15","[07/07/2020]","2020-02-11","CSA Group","2020-01-16","2020-02-11",null,"Y","N",1.41,null,null,280,380,480,0.96202800000000011,1.9240560000000002,2.8860840000000003,4.8101400000000005,7.2152100000000008,9.6202800000000011,95.84342055824014,97.245438616621456,97.69515442161071,97.781490663550827,97.454725058638886,96.868552625224183,97.447972235439451,96.623569444844307,97.788546590551988,98.091504579773868,98.107867810513099,97.728629745090558,97.07935975246771,97.778144649623371,95.916568441616164,97.359272556313599,97.801908821247793,97.956240147070503,97.657547674867473,97.22182842848008,97.631257544018638,"2019-05-15","2020-08-11"]
["Delta Electronics","M10-4-TL-US [240V]","N","Y","Y","Y","Y","Y*","Y","9600 W, 240 Vac transformerless Grid Support Utility Interactive Inverter",9.6739999999999995,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2020-08-11","[07/07/2020]","2020-08-11","CSA Group","2020-05-27","2020-08-11",null,"Y","N",1.38,null,null,280,380,480,0.96742000000000017,1.9348400000000003,2.9022600000000001,4.8371000000000004,7.255650000000001,9.6742000000000008,96.074095238095239,97.098761904761901,97.361523809523788,97.492523809523817,97.321047619047633,96.997571428571419,97.284748571428594,97.043952380952376,97.773238095238085,97.926904761904765,97.834761904761905,97.606142857142842,97.366619047619039,97.666535238095236,96.155095238095228,97.377952380952379,97.675714285714278,97.725238095238083,97.497047619047635,97.260095238095246,97.494927142857151,"2020-08-11"]
["Delta Electronics","M24U_120 [480V]","N","Y","Y","Y","Y","N","N","24 kW, 480 Vac Grid Support Utility Interactive Inverter",26.402999999999999,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.6,null,null,415,710,830,2.64,5.28,7.92,13.2,19.8,26.4,95.28,96.42,97.03,97.41,97.46,97.3,97.25,97.39,98.27,98.56,98.65,98.65,98.57,98.57,96.51,97.77,98.06,98.35,98.36,98.27,98.21,"2017-12-15","2020-03-02"]
["Delta Electronics","M24U_121 [480V]","N","Y","Y","Y","Y","N","N","24 kW, 480 Vac Grid Support Utility Interactive Inverter",26.402999999999999,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.6,null,null,415,710,830,2.64,5.28,7.92,13.2,19.8,26.4,95.28,96.42,97.03,97.41,97.46,97.3,97.25,97.39,98.27,98.56,98.65,98.65,98.57,98.57,96.51,97.77,98.06,98.35,98.36,98.27,98.21,"2017-12-15","2020-03-02"]
["Delta Electronics","M24U_122 [480V]","N","Y","Y","Y","Y","N","N","24 kW, 480 Vac Grid Support Utility Interactive Inverter",26.402999999999999,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.6,null,null,415,710,830,2.64,5.28,7.92,13.2,19.8,26.4,95.28,96.42,97.03,97.41,97.46,97.3,97.25,97.39,98.27,98.56,98.65,98.65,98.57,98.57,96.51,97.77,98.06,98.35,98.36,98.27,98.21,"2017-12-15","2020-03-02"]
["Delta Electronics","E30-TL [277V]","Y","Y","Y","Y","N","N","N","30 kW, 277 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter",30.488,277,98,"CSA Group","[07/01/2019]","[Controller A: V1.1.3, Controller B: V1.1.1]","2019-08-01","[07/01/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.59,null,null,515,750,830,3.048756,6.097512,9.1462679999999992,15.243779999999999,22.865669999999998,30.487559999999998,95.922154835817892,97.135291210035561,97.544908906393758,97.751463175700522,97.700984927947204,97.479578495437408,97.582348026182757,97.446064997289312,98.320910511694706,98.555546035701482,98.626573936177579,98.580992908231693,98.464732043126773,98.523297019876921,96.972530703660837,98.105529055929964,98.382049606322511,98.480939986559989,98.451648843723589,98.316574438180396,98.366223639961746,"2019-08-01"]
["Delta Electronics","M28U_120 [480V]","N","Y","Y","Y","Y","N","N","28 kW, 480 Vac Grid Support Utility Interactive Inverter",30.709,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.4,null,null,485,710,830,3.07,6.14,9.2100000000000009,15.35,23.03,30.71,95.98,97.06,97.64,97.78,97.74,97.52,97.62,97.67,98.38,98.6,98.65,98.6,98.49,98.56,96.9,97.95,98.21,98.35,98.32,98.18,98.23,"2017-12-15","2020-03-02"]
["Delta Electronics","M28U_121 [480V]","N","Y","Y","Y","Y","N","N","28 kW, 480 Vac Grid Support Utility Interactive Inverter",30.709,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.4,null,null,485,710,830,3.07,6.14,9.2100000000000009,15.35,23.03,30.71,95.98,97.06,97.64,97.78,97.74,97.52,97.62,97.67,98.38,98.6,98.65,98.6,98.49,98.56,96.9,97.95,98.21,98.35,98.32,98.18,98.23,"2017-12-15","2020-03-02"]
["Delta Electronics","M28U_122 [480V]","N","Y","Y","Y","Y","N","N","28 kW, 480 Vac Grid Support Utility Interactive Inverter",30.709,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.4,null,null,485,710,830,3.07,6.14,9.2100000000000009,15.35,23.03,30.71,95.98,97.06,97.64,97.78,97.74,97.52,97.62,97.67,98.38,98.6,98.65,98.6,98.49,98.56,96.9,97.95,98.21,98.35,98.32,98.18,98.23,"2017-12-15","2020-03-02"]
["Delta Electronics","M36U_120 [480V]","N","Y","Y","Y","Y","Y*","Y","36 kW, 480 Vac Grid Support Utility Interactive Inverter",39.737000000000002,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","CSA Group","2020-10-07","2020-11-12",null,"N","N",2.9,null,null,520,710,830,3.97,7.95,11.92,19.87,29.8,39.74,96.36,97.47,97.83,97.97,97.81,97.59,97.76,97.75,98.45,98.6,98.6,98.43,98.28,98.45,96.89,97.92,98.22,98.3,98.16,97.95,98.12,"2017-12-15","2020-11-12"]
["Delta Electronics","M36U_121 [480V]","N","Y","Y","Y","Y","Y*","Y","36 kW, 480 Vac Grid Support Utility Interactive Inverter",39.737000000000002,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","CSA Group","2020-10-07","2020-04-21",null,"N","N",2.9,null,null,520,710,830,3.97,7.95,11.92,19.87,29.8,39.74,96.36,97.47,97.83,97.97,97.81,97.59,97.76,97.75,98.45,98.6,98.6,98.43,98.28,98.45,96.89,97.92,98.22,98.3,98.16,97.95,98.12,"2017-12-15","2020-11-12"]
["Delta Electronics","M36U_122 [480V]","N","Y","Y","Y","Y","Y*","Y","36 kW, 480 Vac Grid Support Utility Interactive Inverter",39.737000000000002,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","CSA Group","2020-10-07","2020-11-12",null,"N","N",2.9,null,null,520,710,830,3.97,7.95,11.92,19.87,29.8,39.74,96.36,97.47,97.83,97.97,97.81,97.59,97.76,97.75,98.45,98.6,98.6,98.43,98.28,98.45,96.89,97.92,98.22,98.3,98.16,97.95,98.12,"2017-12-15","2020-11-12"]
["Delta Electronics","M42U_120 [480V]","N","Y","Y","Y","Y","Y*","Y","42 kW, 480 Vac Grid Support Utility Interactive Inverter",45.972000000000001,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","CSA Group","2020-10-07","2020-11-12",null,"N","N",2.9,null,null,545,710,830,4.5999999999999996,9.19,13.79,22.99,34.479999999999997,45.97,96.83,97.76,97.97,98.02,97.8,97.54,97.81,97.98,98.53,98.6,98.55,98.35,98.16,98.41,97.21,98.04,98.26,98.26,98.07,97.86,98.09,"2017-12-15","2020-11-12"]
["Delta Electronics","M42U_121 [480V]","N","Y","Y","Y","Y","Y*","Y","42 kW, 480 Vac Grid Support Utility Interactive Inverter",45.972000000000001,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","CSA Group","2020-10-07","2020-04-21",null,"N","N",2.9,null,null,545,710,830,4.5999999999999996,9.19,13.79,22.99,34.479999999999997,45.97,96.83,97.76,97.97,98.02,97.8,97.54,97.81,97.98,98.53,98.6,98.55,98.35,98.16,98.41,97.21,98.04,98.26,98.26,98.07,97.86,98.09,"2017-12-15","2020-11-12"]
["Delta Electronics","M42U_122 [480V]","N","Y","Y","Y","Y","Y*","Y","42 kW, 480 Vac Grid Support Utility Interactive Inverter",45.972000000000001,480,98,"Intertek","[10/27/2017]","[V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X\n]","2018-10-15","[03/11/2019]","2020-03-02","CSA Group","2020-10-07","2020-11-12",null,"N","N",2.9,null,null,545,710,830,4.5999999999999996,9.19,13.79,22.99,34.479999999999997,45.97,96.83,97.76,97.97,98.02,97.8,97.54,97.81,97.98,98.53,98.6,98.55,98.35,98.16,98.41,97.21,98.04,98.26,98.26,98.07,97.86,98.09,"2017-12-15","2020-11-12"]
["Delta Electronics","M60U_120 [480V]","N","Y","Y","Y","Y","Y*","Y","60 kW, 480 Vac Grid Support Utility Interactive Inverter",65.47,480,98.5,"Intertek","[01/21/2020]","[V1.47, V1.5X, V1.6X, V1.7X, V1.8X]","2018-10-15","[01/21/2020]","2020-02-11","CSA Group","2020-10-07","2020-11-12",null,"N","N",2.8630300000000002,null,null,540,710,800,6.55,13.09,19.64,32.74,49.1,65.47,96.77,97.69,97.62,98.1,98.02,97.46,97.89,98.52,98.59,98.63,98.71,98.46,98.29,98.54,97.76,98.59,98.41,98.51,98.32,98.14,98.35,"2017-12-15","2020-11-12"]
["Delta Electronics","M60U_121 [480V]","N","Y","Y","Y","Y","Y*","Y","60 kW, 480 Vac Grid Support Utility Interactive Inverter",65.47,480,98.5,"Intertek","[01/21/2020]","[V1.47, V1.5X, V1.6X, V1.7X, V1.8X]","2018-10-15","[01/21/2020]","2020-02-11","CSA Group","2020-10-07","2020-04-21",null,"N","N",2.8630300000000002,null,null,540,710,800,6.55,13.09,19.64,32.74,49.1,65.47,96.77,97.69,97.62,98.1,98.02,97.46,97.89,98.52,98.59,98.63,98.71,98.46,98.29,98.54,97.76,98.59,98.41,98.51,98.32,98.14,98.35,"2017-12-15","2020-11-12"]
["Delta Electronics","M60U_122 [480V]","N","Y","Y","Y","Y","Y*","Y","60 kW, 480 Vac Grid Support Utility Interactive Inverter",65.47,480,98.5,"Intertek","[01/21/2020]","[V1.47, V1.5X, V1.6X, V1.7X, V1.8X]","2018-10-15","[01/21/2020]","2020-02-11","CSA Group","2020-10-07","2020-11-12",null,"N","N",2.8630300000000002,null,null,540,710,800,6.55,13.09,19.64,32.74,49.1,65.47,96.77,97.69,97.62,98.1,98.02,97.46,97.89,98.52,98.59,98.63,98.71,98.46,98.29,98.54,97.76,98.59,98.41,98.51,98.32,98.14,98.35,"2017-12-15","2020-11-12"]
["Delta Electronics","M80U_120 [480V]","N","Y","Y","Y","Y","Y*","Y","80 kW, 480 Vac Grid Support Utility Interactive Inverter",82.763999999999996,480,98.5,"Intertek","[01/21/2020]","[V1.47, V1.5X, V1.6X, V1.7X, V1.8X]","2018-10-15","[01/21/2020]","2020-02-11","CSA Group","2020-10-07","2020-11-12",null,"N","N",2.6,null,null,600,710,800,8.2799999999999994,16.55,24.83,41.38,62.07,82.76,97.48,98.39,98.4,98.22,97.97,97.79,98.06,98.31,98.79,98.85,98.69,98.54,98.18,98.59,98.37,98.68,98.69,98.49,98.23,98.09,98.36,"2017-12-15","2020-11-12"]
["Delta Electronics","M80U_121 [480V]","N","Y","Y","Y","Y","Y*","Y","80 kW, 480 Vac Grid Support Utility Interactive Inverter",82.763999999999996,480,98.5,"Intertek","[01/21/2020]","[V1.47, V1.5X, V1.6X, V1.7X, V1.8X]","2018-10-15","[01/21/2020]","2020-02-11","CSA Group","2020-10-07","2020-04-21",null,"N","N",2.6,null,null,600,710,800,8.2799999999999994,16.55,24.83,41.38,62.07,82.76,97.48,98.39,98.4,98.22,97.97,97.79,98.06,98.31,98.79,98.85,98.69,98.54,98.18,98.59,98.37,98.68,98.69,98.49,98.23,98.09,98.36,"2017-12-15","2020-11-12"]
["Delta Electronics","M80U_122 [480V]","N","Y","Y","Y","Y","Y*","Y","80 kW, 480 Vac Grid Support Utility Interactive Inverter",82.763999999999996,480,98.5,"Intertek","[01/21/2020]","[V1.47, V1.5X, V1.6X, V1.7X, V1.8X]","2018-10-15","[01/21/2020]","2020-02-11","CSA Group","2020-10-07","2020-11-12",null,"N","N",2.6,null,null,600,710,800,8.2799999999999994,16.55,24.83,41.38,62.07,82.76,97.48,98.39,98.4,98.22,97.97,97.79,98.06,98.31,98.79,98.85,98.69,98.54,98.18,98.59,98.37,98.68,98.69,98.49,98.23,98.09,98.36,"2017-12-15","2020-11-12"]
["Delta Electronics","M125HV [600V]","N","Y","Y","Y","Y","Y*","Y","125 kw, 600 Vac Grid Support Utility Interactive Inverter",124.468,600,99,"TUV Rheinland of North America","[03/25/2019]","[DSP: 1.15, RED: 1.12, COMM: 1.2, ARC: 1.12, SCM: 1.12]","2019-05-01","[03/25/2019]","2020-06-01","CSA Group","2020-10-07","2020-11-12",null,"N","N",0,null,null,860,1000,1200,12.446844121876001,24.893688243752003,37.340532365628,62.234220609380003,93.351330914070004,124.46844121876001,98.918000000000006,99.156000000000006,99.18971024495724,99.102000000000004,98.847999999999999,98.528000000000006,98.944545229394862,98.344800000000006,98.785999999999987,98.866000000000014,98.908199999999994,98.804199999999994,98.34399999999998,98.791159999999991,97.694000000000003,98.373999999999995,98.507599999999996,98.647999999999996,98.583600000000004,98.244461999999999,98.524983100000014,"2019-05-01","2020-11-12"]
["Destin Power Inc.","SAVEEN1000-ES02H.US [440V]","N","Y","N","N","N","N","N","1000 kW, 440 Vac, Grid Support Utility Interactive Inverter ESS for Indoor ESS PCS",1000,440,98,"TUV SUD America","[01/11/2018]","[1.00.4]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 3 kVA ABB Korea distribution transformer.","N","N",149.25,null,null,740,830,900,100,200,300,500,750,1000,94.976199999999992,97.210200000000015,97.951599999999999,98.4084,98.506999999999991,98.421000000000006,98.209273999999994,94.25200000000001,96.764399999999995,97.581600000000009,98.185599999999994,98.325400000000002,98.260799999999989,97.962569999999999,93.58720000000001,96.477400000000003,97.383799999999994,98.005799999999994,98.208799999999997,98.169399999999996,97.793765999999991,"2018-11-01"]
["Enphase Energy Inc.","IQ7PD-72-2-US [208V]","N","Y","Y","Y","Y","Y*","Y","190 W, 208 Vac Grid Support Utility Interactive Microinverter",0.191,208,97,"UL","[11/25/2020]","[V04.20.04];[V04.20.03];[V04.18.02];[V04.17.01]","2021-03-11","[11/25/2020]","2021-03-11","UL","2020-01-24","2021-03-11",null,"N","Y",0.02,null,null,22,31,40,1.9078200000000003E-2,3.8156400000000007E-2,5.7234599999999997E-2,9.5391000000000004E-2,0.14308650000000001,0.19078200000000001,93.45796,94.612220000000008,96.540809999999993,97.224339999999998,97.130349999999993,96.678169999999994,96.783931999999993,94.189160000000001,95.570039999999992,95.945599999999999,97.242520000000013,97.430389999999989,97.325060000000022,96.984829300000001,93.176430000000011,94.429760000000002,95.402129999999985,96.921140000000008,97.222160000000002,97.205390000000008,96.638254500000002,"2021-03-11"]
["Enphase Energy Inc.","IQ7PD-72-2-US [240V]","N","Y","Y","Y","Y","Y*","Y","190 W, 240 Vac Grid Support Utility Interactive Microinverter",0.191,240,96.5,"UL","[11/25/2020]","[V04.20.04];[V04.20.03];[V04.18.02];[V04.17.01]","2021-01-11","[11/25/2020]","2021-01-11","UL","2020-01-24","2021-01-11",null,"N","Y",0.02,null,null,22,31,40,1.9147700000000004E-2,3.8295400000000007E-2,5.7443099999999997E-2,9.5738500000000004E-2,0.14360775000000001,0.19147700000000001,92.969599999999986,93.859989999999996,96.119039999999998,97.06853000000001,96.997150000000005,96.581649999999996,96.568031599999998,94.322469999999981,95.618900000000011,95.397349999999989,97.220559999999992,97.520020000000017,97.529340000000005,96.979921000000004,93.159599999999998,94.448370000000011,94.789130000000014,96.812350000000009,97.275229999999993,97.406859999999995,96.580306500000006,"2021-01-11","2021-03-11"]
["Enphase Energy Inc.","IQ7PD-84-2-US [208V]","N","Y","Y","Y","Y","Y*","Y","210 W, 208 Vac Grid Support Utility Interactive Microinverter",0.21099999999999999,208,96.5,"UL","[11/25/2020]","[V04.20.04];[V04.20.03];[V04.18.02];[V04.17.01]","2021-03-11","[11/25/2020]","2021-03-11","UL","2020-01-24","2021-03-11",null,"N","Y",2.1000000000000001E-2,null,null,31,40,50,2.1144099999999999E-2,4.2288199999999998E-2,6.3432299999999997E-2,0.1057205,0.15858074999999999,0.21144099999999999,93.831239999999994,95.028869999999984,96.092290000000006,97.093069999999997,97.167730000000006,96.942820000000012,96.771350500000011,93.189589999999981,94.807159999999996,95.586339999999993,96.808790000000016,96.980699999999999,96.846189999999993,96.510228799999993,92.385350000000017,93.926290000000023,95.005420000000001,96.513870000000011,96.779350000000008,96.72308000000001,96.189501100000001,"2021-03-11"]
["Enphase Energy Inc.","IQ7PD-84-2-US [240V]","N","Y","Y","Y","Y","Y*","Y","210 W, 240 Vac Grid Support Utility Interactive Microinverter",0.21099999999999999,240,96.5,"UL","[11/25/2020]","[V04.20.04];[V04.20.03];[V04.18.02];[V04.17.01]","2021-01-11","[11/25/2020]","2021-01-11","UL","2020-01-24","2021-01-11",null,"N","Y",2.1999999999999999E-2,null,null,31,40,50,2.1136700000000001E-2,4.2273400000000003E-2,6.3410099999999997E-2,0.1056835,0.15852525000000001,0.211367,94.001859999999994,95.096379999999996,96.220529999999982,97.334189999999992,97.529579999999996,97.427089999999993,97.063568799999985,93.54983,95.230589999999992,95.688459999999992,96.974520000000012,97.303149999999988,97.358329999999995,96.789373100000006,92.52037,94.327549999999974,94.897409999999994,96.641870000000011,97.050250000000005,97.185190000000006,96.395566200000019,"2021-01-11","2021-03-11"]
["Enphase Energy Inc.","S230-60-LL-x [208V]","N","Y","Y","Y","N","N","N","230 W, 240 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US\n\n",0.22,208,97,"UL","[8/14/2017]","[v00.36.01]","2018-10-15","[8/14/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",5.0999999999999997E-2,null,null,27,32,37,0.02,0.04,7.0000000000000007E-2,0.11,0.17,0.22,94.9,96.5,96.4,97.2,97.2,96.9,97,94.9,96.4,96.1,97.1,97.1,96.8,96.8,94.8,96.3,95.8,96.9,97,96.7,96.7,"2017-10-16","2018-10-15"]
["Enphase Energy Inc.","S230-60-LL-x [240V]","N","Y","Y","Y","N","N","N","230 W, 240 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US",0.22,240,97,"UL","[8/14/2017]","[v00.36.01]","2018-10-15","[8/14/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",5.0999999999999997E-2,null,null,27,32,37,0.02,0.04,7.0000000000000007E-2,0.11,0.17,0.22,95,96.4,96.2,97.4,97.5,97.4,97.2,95,96.5,95.8,97.2,97.3,97.2,97,94.9,96.4,95.4,96.9,97.2,97.2,96.8,"2017-10-16","2018-10-15"]
["Enphase Energy Inc.","IQ6-60-2-US [208V]","N","Y","Y","Y","Y","Y*","Y","230 W, 208 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 2",0.23,208,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11",null,"N","Y",0.02,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.197490000000002,95.712479999999999,96.348519999999994,97.262550000000005,97.260339999999999,96.917450000000002,96.934330000000003,94.452510000000004,95.864980000000003,96.241010000000003,97.119309999999999,97.198210000000003,96.97448,96.879099999999994,94.1798,95.690380000000005,96.083370000000002,96.967740000000006,97.087569999999999,96.917450000000002,96.747230000000002,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ6-60-2-US [240V]","N","Y","Y","Y","Y","Y*","Y","230 W, 240 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 2",0.23,240,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11",null,"N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ6-60-5-US [208V]","N","Y","Y","Y","Y","Y*","Y","230 W, 208 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 5",0.23,208,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11",null,"N","Y",0.02,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.197490000000002,95.712479999999999,96.348519999999994,97.262550000000005,97.260339999999999,96.917450000000002,96.934330000000003,94.452510000000004,95.864980000000003,96.241010000000003,97.119309999999999,97.198210000000003,96.97448,96.879099999999994,94.1798,95.690380000000005,96.083370000000002,96.967740000000006,97.087569999999999,96.917450000000002,96.747230000000002,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ6-60-5-US [240V]","N","Y","Y","Y","Y","Y*","Y","230 W, 240 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 5",0.23,240,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11",null,"N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ6-60-ACM-US [208V]","N","Y","Y","Y","Y","Y*","Y","230 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications",0.23,208,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.197490000000002,95.712479999999999,96.348519999999994,97.262550000000005,97.260339999999999,96.917450000000002,96.934330000000003,94.452510000000004,95.864980000000003,96.241010000000003,97.119309999999999,97.198210000000003,96.97448,96.879099999999994,94.1798,95.690380000000005,96.083370000000002,96.967740000000006,97.087569999999999,96.917450000000002,96.747230000000002,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ6-60-ACM-US [240V]","N","Y","Y","Y","Y","Y*","Y","230W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications",0.23,240,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ7-60-2-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.24,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7-60-x-US-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999998,97.021460000000005,97.553880000000007,97.414230000000003,96.959760000000003,97.185913099999993,93.324759999999998,95.734390000000005,96.756339999999994,97.463930000000005,97.415279999999996,97.056359999999998,97.080812399999999,92.419210000000007,95.095889999999997,96.538390000000007,97.353759999999994,97.337370000000007,97.025310000000005,96.920530900000003,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.24,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7-60-x-US-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999997,97.474630000000005,97.419160000000005,97.028769999999994,97.132815300000004,92.990710000000007,95.658749999999998,96.504930000000002,97.552279999999996,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026439999999994,96.230879999999999,97.381270000000001,97.543800000000005,97.410730000000001,96.998094800000004,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-5-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.24,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7-60-x-US-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999998,97.021460000000005,97.553880000000007,97.414230000000003,96.959760000000003,97.185913099999993,93.324759999999998,95.734390000000005,96.756339999999994,97.463930000000005,97.415279999999996,97.056359999999998,97.080812399999999,92.419210000000007,95.095889999999997,96.538390000000007,97.353759999999994,97.337370000000007,97.025310000000005,96.920530900000003,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-5-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.24,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7-60-x-US-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999997,97.474630000000005,97.419160000000005,97.028769999999994,97.132815300000004,92.990710000000007,95.658749999999998,96.504930000000002,97.552279999999996,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026439999999994,96.230879999999999,97.381270000000001,97.543800000000005,97.410730000000001,96.998094800000004,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 208 Vac Grid Support Utility Interactive microinverter",0.24,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& [208V].","N","Y",2.5000000000000001E-2,2.5000000000000001E-2,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive microinverter",0.24,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999997,97.474630000000005,97.419160000000005,97.028769999999994,97.132815300000004,92.990710000000007,95.658749999999998,96.504930000000002,97.552279999999996,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026439999999994,96.230879999999999,97.381270000000001,97.543800000000005,97.410730000000001,96.998094800000004,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 208 Vac Grid Support Utility Interactive microinverter",0.24,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& [208V].","N","Y",2.5000000000000001E-2,2.5000000000000001E-2,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive microinverter",0.24,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999997,97.474630000000005,97.419160000000005,97.028769999999994,97.132815300000004,92.990710000000007,95.658749999999998,96.504930000000002,97.552279999999996,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026439999999994,96.230879999999999,97.381270000000001,97.543800000000005,97.410730000000001,96.998094800000004,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-E-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 208 Vac Grid Support Utility Interactive microinverter",0.24,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& [208V].","N","Y",2.5000000000000001E-2,2.5000000000000001E-2,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-E-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive microinverter",0.24,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999997,97.474630000000005,97.419160000000005,97.028769999999994,97.132815300000004,92.990710000000007,95.658749999999998,96.504930000000002,97.552279999999996,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026439999999994,96.230879999999999,97.381270000000001,97.543800000000005,97.410730000000001,96.998094800000004,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-E-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 208 Vac Grid Support Utility Interactive microinverter",0.24,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& [208V].","N","Y",2.5000000000000001E-2,2.5000000000000001E-2,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-E-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive microinverter",0.24,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999997,97.474630000000005,97.419160000000005,97.028769999999994,97.132815300000004,92.990710000000007,95.658749999999998,96.504930000000002,97.552279999999996,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026439999999994,96.230879999999999,97.381270000000001,97.543800000000005,97.410730000000001,96.998094800000004,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-E-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.24,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7-60-x-US-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999998,97.021460000000005,97.553880000000007,97.414230000000003,96.959760000000003,97.185913099999993,93.324759999999998,95.734390000000005,96.756339999999994,97.463930000000005,97.415279999999996,97.056359999999998,97.080812399999999,92.419210000000007,95.095889999999997,96.538390000000007,97.353759999999994,97.337370000000007,97.025310000000005,96.920530900000003,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-E-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.24,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7-60-x-US-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999997,97.474630000000005,97.419160000000005,97.028769999999994,97.132815300000004,92.990710000000007,95.658749999999998,96.504930000000002,97.552279999999996,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026439999999994,96.230879999999999,97.381270000000001,97.543800000000005,97.410730000000001,96.998094800000004,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7-60-M-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.24,208,97,"UL","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2021-09-01","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","2021-09-01","UL","2021-08-04","2021-09-01",null,"N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999998,97.021460000000005,97.553880000000007,97.414230000000003,96.959760000000003,97.185913099999993,93.324759999999998,95.734390000000005,96.756339999999994,97.463930000000005,97.415279999999996,97.056359999999998,97.080812399999999,92.419210000000007,95.095889999999997,96.538390000000007,97.353759999999994,97.337370000000007,97.025310000000005,96.920530900000003,"2021-09-01"]
["Enphase Energy Inc.","IQ7-60-M-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.24,240,97,"UL","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2021-09-01","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","2021-09-01","UL","2021-08-04","2021-09-01",null,"N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999997,97.474630000000005,97.419160000000005,97.028769999999994,97.132815300000004,92.990710000000007,95.658749999999998,96.504930000000002,97.552279999999996,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026439999999994,96.230879999999999,97.381270000000001,97.543800000000005,97.410730000000001,96.998094800000004,"2021-09-01"]
["Enphase Energy Inc.","XACM-IQ7-LR6-60PB-300M [208V]","N","Y ","Y ","Y ","Y","Y*","Y","300 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: LR6-60PB-300M. Microinverter: IQ7-60-x-ACM-US-y [208V] ",0.24,208,97,"UL","[2/12/2020]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04]","2020-03-11","[02/12/2020]","2020-05-11","UL","2020-03-18","2020-05-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-03-11","2021-06-21"]
["Enphase Energy Inc.","XACM-IQ7-LR6-60PB-300M [240V]","N","Y ","Y ","Y ","Y","Y*","Y","300 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: LR6-60PB-300M. Microinverter: IQ7-60-x-ACM-US-y [240V] ",0.24,240,97,"UL","[2/12/2020]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04]","2020-03-11","[02/12/2020]","2020-05-11","UL","2020-03-18","2020-05-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-03-11","2021-06-21"]
["Enphase Energy Inc.","XACM-IQ7-LR6-60PB-305M [208V]","N","Y ","Y ","Y ","Y","Y*","Y","305 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: LR6-60PB-305M. Microinverter: IQ7-60-x-ACM-US-y [208V] ",0.24,208,97,"UL","[2/12/2020]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04]","2020-03-11","[02/12/2020]","2020-05-11","UL","2020-03-18","2020-05-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-03-11","2021-06-21"]
["Enphase Energy Inc.","XACM-IQ7-LR6-60PB-305M [240V]","N","Y ","Y ","Y ","Y","Y*","Y","305 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: LR6-60PB-305M. Microinverter: IQ7-60-x-ACM-US-y [240V] ",0.24,240,97,"UL","[2/12/2020]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04]","2020-03-11","[02/12/2020]","2020-05-11","UL","2020-03-18","2020-05-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-03-11","2021-06-21"]
["Enphase Energy Inc.","IQ8-60-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.24199999999999999,240,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-05-03","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-05-03","UL","2021-03-17","2021-05-03",null,"N","Y",3.3000000000000002E-2,null,null,27,32,40,2.4243060302700001E-2,4.8486120605400002E-2,7.2729180908099988E-2,0.12121530151349999,0.18182295227024997,0.24243060302699998,93.466697730749999,93.587469779210011,95.830005182160022,96.822933835430007,96.574597064979997,95.954855479140008,96.232737343886399,95.058602197859997,96.421537498310002,96.76041673700999,97.167878740670005,97.174654836740004,96.861668403039999,96.985575990436004,95.562521347940006,96.525811072780002,96.873856566940006,97.263848261850015,97.493638880340001,97.414042867390009,97.241393080527601,"2021-05-03","2021-10-21"]
["Enphase Energy Inc.","IQ8-60-M-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","240 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.24199999999999999,240,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-09-13","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-09-13","UL","2021-08-10","2021-09-13",null,"N","Y",3.3000000000000002E-2,null,null,27,32,40,2.4243060302700001E-2,4.8486120605400002E-2,7.2729180908099988E-2,0.12121530151349999,0.18182295227024997,0.24243060302699998,93.466697730749999,93.587469779210011,95.830005182160022,96.822933835430007,96.574597064979997,95.954855479140008,96.232737343886399,95.058602197859997,96.421537498310002,96.76041673700999,97.167878740670005,97.174654836740004,96.861668403039999,96.985575990436004,95.562521347940006,96.525811072780002,96.873856566940006,97.263848261850015,97.493638880340001,97.414042867390009,97.241393080527601,"2021-09-13","2021-10-21"]
["Enphase Energy Inc.","IQ6PLUS-ACB-LL [240V]","N","Y","Y","Y","N","N","N","270 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.27,240,95.5,"UL","[12/28/2017]","[v02.12.00]","2018-10-15","[12/28/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",7.0000000000000007E-2,null,null,23,25,28,2.7E-2,5.3999999999999999E-2,8.1000000000000003E-2,0.13500000000000001,0.20250000000000001,0.27,85.890320000000003,93.616439999999997,95.462680000000006,95.976870000000005,95.578299999999999,94.803150000000002,95.123760000000004,85.800269999999998,93.469059999999999,95.405839999999998,96.148520000000005,95.876450000000006,95.229470000000006,95.321349999999995,85.518879999999996,93.118340000000003,95.190380000000005,96.192750000000004,96.066869999999994,95.595110000000005,95.395189999999999,"2018-05-15","2018-10-15"]
["Enphase Energy Inc.","S280-60-LL-x [208V]","N","Y","Y","Y","N","N","N","270 W, 208 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4 , or 5 and may be followed by -US",0.27,208,96.5,"UL","[8/14/2017]","[v00.36.01]","2018-10-15","[8/14/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",5.0999999999999997E-2,null,null,27,32,37,0.03,0.05,0.08,0.14000000000000001,0.2,0.27,95,96.1,96.5,96.9,96.7,96.2,96.6,95,96.1,96.1,96.7,96.6,96.2,96.5,94.9,95.7,95.8,96.6,96.5,96.1,96.3,"2017-10-16","2018-10-15"]
["Enphase Energy Inc.","S280-60-LL-x [240V]","N","Y","Y","Y","N","N","N","270 W, 240 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US\n\n",0.27,240,97,"UL","[8/14/2017]","[v00.36.01]","2018-10-15","[8/14/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",6.2E-2,null,null,27,32,37,0.03,0.05,0.08,0.14000000000000001,0.2,0.27,95.2,96.5,96.9,97.3,97.3,97,97.1,95.3,96.5,96.7,97.1,97.2,96.9,97,95.1,96.1,96,96.9,97.1,96.9,96.8,"2017-10-16","2018-10-15"]
["Enphase Energy Inc.","IQ6PLUS-72-2-US [208V]","N","Y","Y","Y","Y","Y*","Y","280 W, 208 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 2",0.28000000000000003,208,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11",null,"N","Y",0.02,null,null,27,36,45,2.8000000000000001E-2,5.6000000000000001E-2,8.4000000000000005E-2,0.14000000000000001,0.21,0.28000000000000003,94.636139999999997,96.340069999999997,96.930220000000006,97.37612,97.14246,96.578599999999994,96.997494500000002,94.562870000000004,95.684449999999998,96.451030000000003,97.149680000000004,97.092020000000005,96.683809999999994,96.835254800000001,93.928889999999996,95.027100000000004,95.970730000000003,96.918509999999998,96.913079999999994,96.59496,96.571565699999994,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ6PLUS-72-2-US [240V]","N","Y","Y","Y","Y","Y*","Y","280 W, 240 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 2",0.28000000000000003,240,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11",null,"N","Y",0.03,null,null,27,36,45,2.8000000000000001E-2,5.6000000000000001E-2,8.4000000000000005E-2,0.14000000000000001,0.21,0.28000000000000003,94.253060000000005,96.163120000000006,96.81711,97.302610000000001,97.145589999999999,96.716480000000004,96.952866400000005,94.554839999999999,95.744399999999999,96.281419999999997,97.254900000000006,97.333410000000001,97.170069999999996,96.991923799999995,93.905879999999996,95.090100000000007,95.744929999999997,96.971980000000002,97.148679999999999,97.038430000000005,96.704969500000004,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ6PLUS-72-5-US [208V]","N","Y","Y","Y","Y","Y*","Y","280 W, 208 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 5",0.28000000000000003,208,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11",null,"N","Y",0.02,null,null,27,36,45,2.8000000000000001E-2,5.6000000000000001E-2,8.4000000000000005E-2,0.14000000000000001,0.21,0.28000000000000003,94.636139999999997,96.340069999999997,96.930220000000006,97.37612,97.14246,96.578599999999994,96.997494500000002,94.562870000000004,95.684449999999998,96.451030000000003,97.149680000000004,97.092020000000005,96.683809999999994,96.835254800000001,93.928889999999996,95.027100000000004,95.970730000000003,96.918509999999998,96.913079999999994,96.59496,96.571565699999994,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ6PLUS-72-5-US [240V]","N","Y","Y","Y","Y","Y*","Y","280 W, 240 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 5",0.28000000000000003,240,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11",null,"N","Y",0.03,null,null,27,36,45,2.8000000000000001E-2,5.6000000000000001E-2,8.4000000000000005E-2,0.14000000000000001,0.21,0.28000000000000003,94.253060000000005,96.163120000000006,96.81711,97.302610000000001,97.145589999999999,96.716480000000004,96.952866400000005,94.554839999999999,95.744399999999999,96.281419999999997,97.254900000000006,97.333410000000001,97.170069999999996,96.991923799999995,93.905879999999996,95.090100000000007,95.744929999999997,96.971980000000002,97.148679999999999,97.038430000000005,96.704969500000004,"2017-08-01","2021-03-11"]
["Enphase Energy Inc.","IQ6PLUS-72-ACM-US [208V]","N","Y","Y","Y","Y","Y*","Y","280 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications",0.28000000000000003,208,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11","This microinverter is sold as an individual unit but is only for ACPV modules including LG Electronics Inc. LGxxxE1K-A5 and LGxxxE1C-A5, where xxx = 315, 32, 325, 33, or 335.","N","Y",0.02,null,null,27,36,45,2.8000000000000001E-2,5.6000000000000001E-2,8.4000000000000005E-2,0.14000000000000001,0.21,0.28000000000000003,94.636139999999997,96.340069999999997,96.930220000000006,97.37612,97.14246,96.578599999999994,96.997494500000002,94.562870000000004,95.684449999999998,96.451030000000003,97.149680000000004,97.092020000000005,96.683809999999994,96.835254800000001,93.928889999999996,95.027100000000004,95.970730000000003,96.918509999999998,96.913079999999994,96.59496,96.571565699999994,"2017-08-15","2021-03-11"]
["Enphase Energy Inc.","IQ6PLUS-72-ACM-US [240V]","N","Y","Y","Y","Y","Y*","Y","280 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications",0.28000000000000003,240,97,"UL","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","[v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05]","2018-10-15","[06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021]","2021-02-11","UL","2021-01-24","2021-02-11","This microinverter is sold as an individual unit but is only for ACPV modules including LG Electronics Inc. LGxxxE1K-A5 and LGxxxE1C-A5, where xxx = 315, 32, 325, 33, or 335.","N","Y",0.02,null,null,27,36,45,2.8000000000000001E-2,5.6000000000000001E-2,8.4000000000000005E-2,0.14000000000000001,0.21,0.28000000000000003,94.253060000000005,96.163120000000006,96.81711,97.302610000000001,97.145589999999999,96.716480000000004,96.952866400000005,94.554839999999999,95.744399999999999,96.281419999999997,97.254900000000006,97.333410000000001,97.170069999999996,96.991923799999995,93.905879999999996,95.090100000000007,95.744929999999997,96.971980000000002,97.148679999999999,97.038430000000005,96.704969500000004,"2017-08-15","2021-03-11"]
["Enphase Energy Inc.","IQ7PLUS-72-2-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.28999999999999998,208,96.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7PLUS-72-x-US-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,94.911249999999995,96.246709999999993,97.108059999999995,97.251649999999998,96.925659999999993,96.294169999999994,96.869907499999997,93.956320000000005,95.314499999999995,96.728170000000006,97.158670000000001,96.957819999999998,96.445009999999996,96.744574,93.147900000000007,94.589960000000005,96.389939999999996,96.979820000000004,96.859210000000004,96.373390000000001,96.542019800000006,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.28999999999999998,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7PLUS-72-x-US-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-5-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.28999999999999998,208,96.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7PLUS-72-x-US-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,94.911249999999995,96.246709999999993,97.108059999999995,97.251649999999998,96.925659999999993,96.294169999999994,96.869907499999997,93.956320000000005,95.314499999999995,96.728170000000006,97.158670000000001,96.957819999999998,96.445009999999996,96.744574,93.147900000000007,94.589960000000005,96.389939999999996,96.979820000000004,96.859210000000004,96.373390000000001,96.542019800000006,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-5-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.28999999999999998,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7PLUS-72-x-US-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 208 Vac Grid Support Utility Interactive microinverter",0.28999999999999998,208,96.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.8999999999999998E-2,5.7999999999999996E-2,8.6999999999999994E-2,0.14499999999999999,0.21749999999999997,0.28999999999999998,94.911249999999995,96.246709999999979,97.108059999999995,97.251649999999998,96.925660000000022,96.294169999999994,96.869907500000011,93.956320000000005,95.314499999999995,96.728169999999977,97.158670000000001,96.957820000000012,96.445009999999996,96.744574,93.147899999999993,94.589959999999991,96.389939999999996,96.979819999999989,96.859210000000004,96.373390000000001,96.542019799999991,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive microinverter",0.28999999999999998,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 208 Vac Grid Support Utility Interactive microinverter",0.28999999999999998,208,96.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.8999999999999998E-2,5.7999999999999996E-2,8.6999999999999994E-2,0.14499999999999999,0.21749999999999997,0.28999999999999998,94.911249999999995,96.246709999999979,97.108059999999995,97.251649999999998,96.925660000000022,96.294169999999994,96.869907500000011,93.956320000000005,95.314499999999995,96.728169999999977,97.158670000000001,96.957820000000012,96.445009999999996,96.744574,93.147899999999993,94.589959999999991,96.389939999999996,96.979819999999989,96.859210000000004,96.373390000000001,96.542019799999991,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive microinverter",0.28999999999999998,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-E-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 208 Vac Grid Support Utility Interactive microinverter",0.28999999999999998,208,96.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.8999999999999998E-2,5.7999999999999996E-2,8.6999999999999994E-2,0.14499999999999999,0.21749999999999997,0.28999999999999998,94.911249999999995,96.246709999999979,97.108059999999995,97.251649999999998,96.925660000000022,96.294169999999994,96.869907500000011,93.956320000000005,95.314499999999995,96.728169999999977,97.158670000000001,96.957820000000012,96.445009999999996,96.744574,93.147899999999993,94.589959999999991,96.389939999999996,96.979819999999989,96.859210000000004,96.373390000000001,96.542019799999991,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-E-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive microinverter",0.28999999999999998,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-E-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 208 Vac Grid Support Utility Interactive microinverter",0.28999999999999998,208,96.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.8999999999999998E-2,5.7999999999999996E-2,8.6999999999999994E-2,0.14499999999999999,0.21749999999999997,0.28999999999999998,94.911249999999995,96.246709999999979,97.108059999999995,97.251649999999998,96.925660000000022,96.294169999999994,96.869907500000011,93.956320000000005,95.314499999999995,96.728169999999977,97.158670000000001,96.957820000000012,96.445009999999996,96.744574,93.147899999999993,94.589959999999991,96.389939999999996,96.979819999999989,96.859210000000004,96.373390000000001,96.542019799999991,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-E-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive microinverter",0.28999999999999998,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-E-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.28999999999999998,208,96.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7PLUS-72-x-US-& [208V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,94.911249999999995,96.246709999999993,97.108059999999995,97.251649999999998,96.925659999999993,96.294169999999994,96.869907499999997,93.956320000000005,95.314499999999995,96.728170000000006,97.158670000000001,96.957819999999998,96.445009999999996,96.744574,93.147900000000007,94.589960000000005,96.389939999999996,96.979820000000004,96.859210000000004,96.373390000000001,96.542019800000006,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-E-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.28999999999999998,240,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7PLUS-72-x-US-& [240V].","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-M-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.28999999999999998,208,96.5,"UL","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2021-09-01","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","2021-09-01","UL","2021-08-04","2021-09-01",null,"N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,94.911249999999995,96.246709999999993,97.108059999999995,97.251649999999998,96.925659999999993,96.294169999999994,96.869907499999997,93.956320000000005,95.314499999999995,96.728170000000006,97.158670000000001,96.957819999999998,96.445009999999996,96.744574,93.147900000000007,94.589960000000005,96.389939999999996,96.979820000000004,96.859210000000004,96.373390000000001,96.542019800000006,"2021-09-01"]
["Enphase Energy Inc.","IQ7PLUS-72-M-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.28999999999999998,240,97,"UL","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2021-09-01","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","2021-09-01","UL","2021-08-04","2021-09-01",null,"N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2021-09-01"]
["Enphase Energy Inc.","IQ7A-66-x-US-& [208V]","N","Y","Y","Y","Y","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive Microinverter, where x = 2, 5, E, or blank, and & = any characters or blank",0.29290899999999997,208,96.5,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09]","2019-08-01","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290900000000002E-2,5.8581800000000003E-2,8.7872699999999998E-2,0.14645449999999999,0.21968175000000001,0.29290899999999997,94.504329999999996,95.617829999999998,96.379450000000006,96.998639999999995,96.843940000000003,96.310929999999999,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.3048,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921629999999993,96.800489999999996,96.29392,96.569612899999996,"2019-08-01","2020-11-12"]
["Enphase Energy Inc.","IQ7A-72-2-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive Microinverter",0.29290899999999997,208,96.5,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7A-72-x-US-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290900000000002E-2,5.8581800000000003E-2,8.7872699999999998E-2,0.14645449999999999,0.21968175000000001,0.29290899999999997,94.504329999999996,95.617829999999998,96.379450000000006,96.998639999999995,96.843940000000003,96.310929999999999,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.3048,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921629999999993,96.800489999999996,96.29392,96.569612899999996,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-5-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive Microinverter",0.29290899999999997,208,96.5,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7A-72-x-US-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290900000000002E-2,5.8581800000000003E-2,8.7872699999999998E-2,0.14645449999999999,0.21968175000000001,0.29290899999999997,94.504329999999996,95.617829999999998,96.379450000000006,96.998639999999995,96.843940000000003,96.310929999999999,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.3048,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921629999999993,96.800489999999996,96.29392,96.569612899999996,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-E-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive Microinverter",0.29290899999999997,208,96.5,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7A-72-x-US-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290900000000002E-2,5.8581800000000003E-2,8.7872699999999998E-2,0.14645449999999999,0.21968175000000001,0.29290899999999997,94.504329999999996,95.617829999999998,96.379450000000006,96.998639999999995,96.843940000000003,96.310929999999999,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.3048,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921629999999993,96.800489999999996,96.29392,96.569612899999996,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-M-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive Microinverter",0.29290899999999997,208,96.5,"UL","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2021-09-01","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","2021-09-01","UL","2021-08-04","2021-09-01",null,"N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290900000000002E-2,5.8581800000000003E-2,8.7872699999999998E-2,0.14645449999999999,0.21968175000000001,0.29290899999999997,94.504329999999996,95.617829999999998,96.379450000000006,96.998639999999995,96.843940000000003,96.310929999999999,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.3048,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921629999999993,96.800489999999996,96.29392,96.569612899999996,"2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-2-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive Microinverter",0.29290899999999997,208,96.5,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290900000000002E-2,5.8581800000000003E-2,8.7872699999999998E-2,0.14645449999999999,0.21968175000000001,0.29290899999999997,94.504329999999996,95.617829999999998,96.379450000000006,96.998639999999995,96.843940000000003,96.310929999999999,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.3048,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921629999999993,96.800489999999996,96.29392,96.569612899999996,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-5-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive Microinverter",0.29290899999999997,208,96.5,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290900000000002E-2,5.8581800000000003E-2,8.7872699999999998E-2,0.14645449999999999,0.21968175000000001,0.29290899999999997,94.504329999999996,95.617829999999998,96.379450000000006,96.998639999999995,96.843940000000003,96.310929999999999,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.3048,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921629999999993,96.800489999999996,96.29392,96.569612899999996,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-E-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive Microinverter",0.29290899999999997,208,96.5,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290900000000002E-2,5.8581800000000003E-2,8.7872699999999998E-2,0.14645449999999999,0.21968175000000001,0.29290899999999997,94.504329999999996,95.617829999999998,96.379450000000006,96.998639999999995,96.843940000000003,96.310929999999999,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.3048,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921629999999993,96.800489999999996,96.29392,96.569612899999996,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-66-x-ACM-US-y-z-& [208V]","N","Y","Y","Y","Y","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive microinverter, where x = 2, 5, E, or blank, y = NM or blank, z = RMA or blank, and & = any characters or blank",0.29291,208,96.5,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09]","2020-04-01","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290899999999998E-2,5.8581799999999996E-2,8.7872699999999984E-2,0.14645449999999999,0.21968174999999998,0.29290899999999997,94.504329999999982,95.617829999999998,96.379449999999991,96.998640000000009,96.843940000000003,96.310930000000013,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.304799999999986,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921630000000007,96.800489999999996,96.293919999999986,96.56961290000001,"2020-04-01","2020-11-12"]
["Enphase Energy Inc.","IQ7A-72-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive microinverter",0.29291,208,96.5,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290899999999998E-2,5.8581799999999996E-2,8.7872699999999984E-2,0.14645449999999999,0.21968174999999998,0.29290899999999997,94.504329999999982,95.617829999999998,96.379449999999991,96.998640000000009,96.843940000000003,96.310930000000013,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.304799999999986,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921630000000007,96.800489999999996,96.293919999999986,96.56961290000001,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-E-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive microinverter",0.29291,208,96.5,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290899999999998E-2,5.8581799999999996E-2,8.7872699999999984E-2,0.14645449999999999,0.21968174999999998,0.29290899999999997,94.504329999999982,95.617829999999998,96.379449999999991,96.998640000000009,96.843940000000003,96.310930000000013,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.304799999999986,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921630000000007,96.800489999999996,96.293919999999986,96.56961290000001,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-E-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive microinverter",0.29291,208,96.5,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290899999999998E-2,5.8581799999999996E-2,8.7872699999999984E-2,0.14645449999999999,0.21968174999999998,0.29290899999999997,94.504329999999982,95.617829999999998,96.379449999999991,96.998640000000009,96.843940000000003,96.310930000000013,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.304799999999986,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921630000000007,96.800489999999996,96.293919999999986,96.56961290000001,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive microinverter",0.29291,208,96.5,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290899999999998E-2,5.8581799999999996E-2,8.7872699999999984E-2,0.14645449999999999,0.21968174999999998,0.29290899999999997,94.504329999999982,95.617829999999998,96.379449999999991,96.998640000000009,96.843940000000003,96.310930000000013,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.304799999999986,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921630000000007,96.800489999999996,96.293919999999986,96.56961290000001,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive microinverter",0.29291,208,96.5,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290899999999998E-2,5.8581799999999996E-2,8.7872699999999984E-2,0.14645449999999999,0.21968174999999998,0.29290899999999997,94.504329999999982,95.617829999999998,96.379449999999991,96.998640000000009,96.843940000000003,96.310930000000013,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.304799999999986,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921630000000007,96.800489999999996,96.293919999999986,96.56961290000001,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-ACM-US-RMA [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive microinverter",0.29291,208,96.5,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290899999999998E-2,5.8581799999999996E-2,8.7872699999999984E-2,0.14645449999999999,0.21968174999999998,0.29290899999999997,94.504329999999982,95.617829999999998,96.379449999999991,96.998640000000009,96.843940000000003,96.310930000000013,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.304799999999986,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921630000000007,96.800489999999996,96.293919999999986,96.56961290000001,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-E-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive microinverter",0.29291,208,96.5,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290899999999998E-2,5.8581799999999996E-2,8.7872699999999984E-2,0.14645449999999999,0.21968174999999998,0.29290899999999997,94.504329999999982,95.617829999999998,96.379449999999991,96.998640000000009,96.843940000000003,96.310930000000013,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.304799999999986,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921630000000007,96.800489999999996,96.293919999999986,96.56961290000001,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-E-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","290 W, 208 Vac Grid Support Utility Interactive microinverter",0.29291,208,96.5,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [208V].","N","Y",4.4999999999999998E-2,null,null,38,40.5,43,2.9290899999999998E-2,5.8581799999999996E-2,8.7872699999999984E-2,0.14645449999999999,0.21968174999999998,0.29290899999999997,94.504329999999982,95.617829999999998,96.379449999999991,96.998640000000009,96.843940000000003,96.310930000000013,96.639147800000003,94.512270000000001,95.536490000000001,96.279600000000002,96.969759999999994,96.836519999999993,96.304799999999986,96.6131125,94.501469999999998,95.512410000000003,96.178629999999998,96.921630000000007,96.800489999999996,96.293919999999986,96.56961290000001,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7GPLUS-72-2-US [240V]","N","Y","Y","Y","Y","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.29799999999999999,240,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021]","[V2.19.01];[V2.22.02];[V2.23.01]","2021-05-03","[04/23/2021];[04/23/2021];[04/23/2021]","2021-05-03","UL","2021-03-17","2021-05-03",null,"N","Y",0.03,null,null,29,37,45,2.9767486572300002E-2,5.9534973144600004E-2,8.9302459716899998E-2,0.1488374328615,0.22325614929225002,0.297674865723,94.907478484199999,94.77802776019,96.62984693144999,97.177422980430009,96.730921760750022,96.309045211430004,96.620881778810826,95.493213193009993,96.84225568447998,96.412778585179993,97.551785922169984,97.496808291010012,97.212227443190002,97.251169552216496,95.82041759661999,96.873299227709992,96.976587903090007,97.515884529220003,97.655169490199995,97.453409158699998,97.421918252498301,"2021-05-03"]
["Enphase Energy Inc.","IQ8PLUS-72-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.29799999999999999,240,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-05-03","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-05-03","UL","2021-03-17","2021-05-03",null,"N","Y",0.03,null,null,29,37,45,2.9767486572300002E-2,5.9534973144600004E-2,8.9302459716899998E-2,0.1488374328615,0.22325614929225002,0.297674865723,94.907478484199999,94.77802776019,96.62984693144999,97.177422980430009,96.730921760750022,96.309045211430004,96.620881778810826,95.493213193009993,96.84225568447998,96.412778585179993,97.551785922169984,97.496808291010012,97.212227443190002,97.251169552216496,95.82041759661999,96.873299227709992,96.976587903090007,97.515884529220003,97.655169490199995,97.453409158699998,97.421918252498301,"2021-05-03","2021-10-21"]
["Enphase Energy Inc.","IQ8PLUS-72-M-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","290 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.29799999999999999,240,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-09-14","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-09-14","UL","2021-08-10","2021-09-13",null,"N","Y",0.03,null,null,29,37,45,2.9767486572300002E-2,5.9534973144600004E-2,8.9302459716899998E-2,0.1488374328615,0.22325614929225002,0.297674865723,94.907478484199999,94.77802776019,96.62984693144999,97.177422980430009,96.730921760750022,96.309045211430004,96.620881778810826,95.493213193009993,96.84225568447998,96.412778585179993,97.551785922169984,97.496808291010012,97.212227443190002,97.251169552216496,95.82041759661999,96.873299227709992,96.976587903090007,97.515884529220003,97.655169490199995,97.453409158699998,97.421918252498301,"2021-09-13","2021-10-21"]
["Enphase Energy Inc.","IQ7X-96-2-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.315,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7X-96-x-US-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,90.483609999999999,96.662760000000006,97.099879999999999,97.635729999999995,97.52422,97.103530000000006,97.150984399999999,95.414169999999999,96.465389999999999,96.900779999999997,97.542019999999994,97.461280000000002,97.049989999999994,97.258731999999995,95.270489999999995,96.333489999999998,96.813519999999997,97.502470000000002,97.42989,97.0197,97.209461899999994,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.315,240,97.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7X-96-x-US-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-5-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.315,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7X-96-x-US-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,90.483609999999999,96.662760000000006,97.099879999999999,97.635729999999995,97.52422,97.103530000000006,97.150984399999999,95.414169999999999,96.465389999999999,96.900779999999997,97.542019999999994,97.461280000000002,97.049989999999994,97.258731999999995,95.270489999999995,96.333489999999998,96.813519999999997,97.502470000000002,97.42989,97.0197,97.209461899999994,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-5-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.315,240,97.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7X-96-x-US-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive microinverter",0.315,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive microinverter",0.315,240,97.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive microinverter",0.315,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive microinverter",0.315,240,97.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-E-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive microinverter",0.315,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-E-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive microinverter",0.315,240,97.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-E-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive microinverter",0.315,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-E-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive microinverter",0.315,240,97.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-E-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.315,208,97,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7X-96-x-US-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,90.483609999999999,96.662760000000006,97.099879999999999,97.635729999999995,97.52422,97.103530000000006,97.150984399999999,95.414169999999999,96.465389999999999,96.900779999999997,97.542019999999994,97.461280000000002,97.049989999999994,97.258731999999995,95.270489999999995,96.333489999999998,96.813519999999997,97.502470000000002,97.42989,97.0197,97.209461899999994,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-E-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.315,240,97.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7X-96-x-US-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-M-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.315,208,97,"UL","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2021-09-01","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","2021-09-01","UL","2021-08-04","2021-09-01",null,"N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,90.483609999999999,96.662760000000006,97.099879999999999,97.635729999999995,97.52422,97.103530000000006,97.150984399999999,95.414169999999999,96.465389999999999,96.900779999999997,97.542019999999994,97.461280000000002,97.049989999999994,97.258731999999995,95.270489999999995,96.333489999999998,96.813519999999997,97.502470000000002,97.42989,97.0197,97.209461899999994,"2021-09-01"]
["Enphase Energy Inc.","IQ7X-96-M-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.315,240,97.5,"UL","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2021-09-01","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","2021-09-01","UL","2021-08-04","2021-09-01",null,"N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-2-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.315,208,97,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,90.483609999999999,96.662760000000006,97.099879999999999,97.635729999999995,97.52422,97.103530000000006,97.150984399999999,95.414169999999999,96.465389999999999,96.900779999999997,97.542019999999994,97.461280000000002,97.049989999999994,97.258731999999995,95.270489999999995,96.333489999999998,96.813519999999997,97.502470000000002,97.42989,97.0197,97.209461899999994,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.315,240,97.5,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-5-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.315,208,97,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,90.483609999999999,96.662760000000006,97.099879999999999,97.635729999999995,97.52422,97.103530000000006,97.150984399999999,95.414169999999999,96.465389999999999,96.900779999999997,97.542019999999994,97.461280000000002,97.049989999999994,97.258731999999995,95.270489999999995,96.333489999999998,96.813519999999997,97.502470000000002,97.42989,97.0197,97.209461899999994,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-5-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.315,240,97.5,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive microinverter",0.315,208,97,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive microinverter",0.315,240,97.5,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive microinverter",0.315,208,97,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive microinverter",0.315,240,97.5,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-ACM-US-RMA [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive microinverter",0.315,208,97,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-ACM-US-RMA [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive microinverter",0.315,240,97.5,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-E-ACM-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive microinverter",0.315,208,97,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-E-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive microinverter",0.315,240,97.5,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-E-ACM-US-NM [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive microinverter",0.315,208,97,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-E-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive microinverter",0.315,240,97.5,"UL","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2018-10-15","[08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-E-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.315,208,97,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& [208V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,90.483609999999999,96.662760000000006,97.099879999999999,97.635729999999995,97.52422,97.103530000000006,97.150984399999999,95.414169999999999,96.465389999999999,96.900779999999997,97.542019999999994,97.461280000000002,97.049989999999994,97.258731999999995,95.270489999999995,96.333489999999998,96.813519999999997,97.502470000000002,97.42989,97.0197,97.209461899999994,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7XS-96-E-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.315,240,97.5,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& [240V].","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ8M-72-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","325 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.32700000000000001,240,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-05-03","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-05-03","UL","2021-03-17","2021-05-03",null,"N","Y",2.8000000000000001E-2,null,null,33,39,45,3.2679910278300001E-2,6.5359820556600001E-2,9.8039730834900002E-2,0.1633995513915,0.24509932708725002,0.32679910278300001,95.869601762200006,96.789800990989988,96.806086059069983,97.502116132520001,97.228529865100001,96.730880365469986,97.134113681731606,96.137377721209987,96.788624507750001,96.732814003579989,97.584777893709983,97.446718881510009,97.12982884937,97.288919822013384,96.126259945300006,96.946346105149999,96.358287466630003,97.560123626580008,97.562355596879996,97.31132497434001,97.316602875710302,"2021-05-03","2021-10-21"]
["Enphase Energy Inc.","IQ8M-72-M-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","325 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.32700000000000001,240,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-09-15","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-09-15","UL","2021-08-10","2021-09-13",null,"N","Y",2.8000000000000001E-2,null,null,33,39,45,3.2679910278300001E-2,6.5359820556600001E-2,9.8039730834900002E-2,0.1633995513915,0.24509932708725002,0.32679910278300001,95.869601762200006,96.789800990989988,96.806086059069983,97.502116132520001,97.228529865100001,96.730880365469986,97.134113681731606,96.137377721209987,96.788624507750001,96.732814003579989,97.584777893709983,97.446718881510009,97.12982884937,97.288919822013384,96.126259945300006,96.946346105149999,96.358287466630003,97.560123626580008,97.562355596879996,97.31132497434001,97.316602875710302,"2021-09-13","2021-10-21"]
["Enphase Energy Inc.","IQ7A-66-x-US-& [240V]","N","Y","Y","Y","Y","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter, where x = 2, 5, E, or blank, and & = any characters or blank",0.34869800000000001,240,97,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09]","2019-08-01","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2019-08-01","2020-11-12"]
["Enphase Energy Inc.","IQ7A-72-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34869800000000001,240,97,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7A-72-x-US-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-5-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34869800000000001,240,97,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7A-72-x-US-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-E-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34869800000000001,240,97,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","Formerly IQ7A-72-x-US-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-M-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34869800000000001,240,97,"UL","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2021-09-01","[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021]","2021-09-01","UL","2021-08-04","2021-09-01",null,"N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34869800000000001,240,97,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-5-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34869800000000001,240,97,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-E-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34869800000000001,240,97,"UL","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-10-12","[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-10-12","UL","2020-01-24","2020-10-12","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-66-x-ACM-US-y-z-& [240V]","N","Y","Y","Y","Y","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive microinverter, where x = 2, 5, E, or blank, y = NM or blank, z = RMA or blank, and & = any characters or blank",0.34899999999999998,240,97,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09]","2020-04-01","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-04-01","2020-11-12"]
["Enphase Energy Inc.","IQ7A-72-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive microinverter",0.34899999999999998,240,97,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-E-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive microinverter",0.34899999999999998,240,97,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7A-72-E-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive microinverter",0.34899999999999998,240,97,"UL","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2020-04-01","[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive microinverter",0.34899999999999998,240,97,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive microinverter",0.34899999999999998,240,97,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-ACM-US-RMA [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive microinverter",0.34899999999999998,240,97,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-E-ACM-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive microinverter",0.34899999999999998,240,97,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ7AS-66-E-ACM-US-NM [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive microinverter",0.34899999999999998,240,97,"UL","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07]","2019-03-15","[01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& [240V].","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2021-06-01","2021-09-01"]
["Enphase Energy Inc.","IQ8A-72-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.35399999999999998,240,97.5,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-05-03","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-05-03","UL","2021-03-17","2021-05-03",null,"N","Y",2.8000000000000001E-2,null,null,36,40.5,45,3.5385592651400004E-2,7.0771185302800008E-2,0.10615677795419999,0.176927963257,0.2653919448855,0.353855926514,96.063266755809991,96.925780283229997,97.067474484149983,97.567750514639997,97.238146019210006,96.685407378089991,97.196631989652104,96.025364591800013,97.017674815250004,96.959337927479993,97.666624219520003,97.499817795009989,97.054964452969983,97.364661615835104,96.097661974330009,96.99392927305,97.259756635310012,97.650599078169989,97.57580721878,97.228946585879996,97.448024700526005,"2021-05-03","2021-10-21"]
["Enphase Energy Inc.","IQ8A-72-M-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","349 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.35399999999999998,240,97.5,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-09-16","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-09-16","UL","2021-08-10","2021-09-13",null,"N","Y",2.8000000000000001E-2,null,null,36,40.5,45,3.5385592651400004E-2,7.0771185302800008E-2,0.10615677795419999,0.176927963257,0.2653919448855,0.353855926514,96.063266755809991,96.925780283229997,97.067474484149983,97.567750514639997,97.238146019210006,96.685407378089991,97.196631989652104,96.025364591800013,97.017674815250004,96.959337927479993,97.666624219520003,97.499817795009989,97.054964452969983,97.364661615835104,96.097661974330009,96.99392927305,97.259756635310012,97.650599078169989,97.57580721878,97.228946585879996,97.448024700526005,"2021-09-13","2021-10-21"]
["Enphase Energy Inc.","IQ8H-208-72-2-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","360 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.36099999999999999,208,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-05-03","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-05-03","UL","2021-03-17","2021-05-03",null,"N","Y",0.02,null,null,38,41.5,45,3.6055560302700004E-2,7.2111120605400009E-2,0.1081666809081,0.18027780151350001,0.27041670227025,0.36055560302700002,96.166523236860002,96.940393288959996,97.194761455719998,97.438506091679997,96.978660920229999,96.385761271359996,97.037116599151503,96.198699885929997,96.877174821800011,97.083294078250006,97.428285787379977,97.054699669089999,96.489918847799999,97.065228808274696,96.093839568759989,96.710573570499989,96.964113315049985,97.379347448390007,97.041774968130014,96.510846212059988,97.02232186695521,"2021-05-03","2021-10-21"]
["Enphase Energy Inc.","IQ8H-208-72-M-US [208V]","N","Y","Y ","Y ","Y ","Y*","Y","360 VA, 208 Vac Grid Support Utility Interactive Microinverter",0.36099999999999999,208,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-09-18","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-09-18","UL","2021-08-10","2021-09-13",null,"N","Y",0.02,null,null,38,41.5,45,3.6055560302700004E-2,7.2111120605400009E-2,0.1081666809081,0.18027780151350001,0.27041670227025,0.36055560302700002,96.166523236860002,96.940393288959996,97.194761455719998,97.438506091679997,96.978660920229999,96.385761271359996,97.037116599151503,96.198699885929997,96.877174821800011,97.083294078250006,97.428285787379977,97.054699669089999,96.489918847799999,97.065228808274696,96.093839568759989,96.710573570499989,96.964113315049985,97.379347448390007,97.041774968130014,96.510846212059988,97.02232186695521,"2021-09-13","2021-10-21"]
["Enphase Energy Inc.","IQ7HS-66-ACM-US [208V]","N","Y ","Y ","Y ","Y ","Y*","Y","369 VA, 208 Vac Grid Support Utility Interactive microinverter",0.36699999999999999,208,97,"UL","[01/19/2021];[01/19/2021]","[V04.19.06];[V04.21.04]","2021-02-11","[01/19/2021];[01/19/2021]","2021-02-11","UL","2020-01-24","2021-02-11","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-07-12"]
["Enphase Energy Inc.","IQ7HS-66-ACM-US-NM [208V]","N","Y ","Y ","Y ","Y ","Y*","Y","369 VA, 208 Vac Grid Support Utility Interactive microinverter",0.36699999999999999,208,97,"UL","[01/19/2021];[01/19/2021]","[V04.19.06];[V04.21.04]","2021-02-11","[01/19/2021];[01/19/2021]","2021-02-11","UL","2020-01-24","2021-02-11","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-07-12"]
["Enphase Energy Inc.","IQ7HS-66-E-ACM-US [208V]","N","Y ","Y ","Y ","Y ","Y*","Y","369 VA, 208 Vac Grid Support Utility Interactive microinverter",0.36699999999999999,208,97,"UL","[01/19/2021];[01/19/2021]","[V04.19.06];[V04.21.04]","2021-02-11","[01/19/2021];[01/19/2021]","2021-02-11","UL","2020-01-24","2021-02-11","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-07-12"]
["Enphase Energy Inc.","IQ7HS-66-E-ACM-US-NM [208V]","N","Y ","Y ","Y ","Y ","Y*","Y","369 VA, 208 Vac Grid Support Utility Interactive microinverter",0.36699999999999999,208,97,"UL","[01/19/2021];[01/19/2021]","[V04.19.06];[V04.21.04]","2021-02-11","[01/19/2021];[01/19/2021]","2021-02-11","UL","2020-01-24","2021-02-11","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-07-12"]
["Enphase Energy Inc.","IQ8H-240-72-2-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","384 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.379,240,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-05-03","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-05-03","UL","2021-03-17","2021-05-03",null,"N","Y",2.8000000000000001E-2,null,null,38,41.5,45,3.7911108398400006E-2,7.5822216796800013E-2,0.11373332519519999,0.189555541992,0.28433331298800002,0.37911108398400001,96.244497696910003,96.997752130199984,97.179857283510003,97.509120321699982,97.059046314650004,96.57515509516999,97.108217957487597,96.211663637940006,96.995535365399988,97.130677326429989,97.599893470800012,97.279481282970011,96.911831304299994,97.253618867016314,96.292159424369999,96.908871291769998,97.001061403980003,97.569444778969995,97.352029924220005,96.974843386809994,97.272158742801693,"2021-05-03","2021-10-21"]
["Enphase Energy Inc.","IQ8H-240-72-M-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","384 VA, 240 Vac Grid Support Utility Interactive Microinverter",0.379,240,97,"UL","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","[V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02]","2021-09-17","[04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021]","2021-09-17","UL","2021-08-10","2021-09-13",null,"N","Y",2.8000000000000001E-2,null,null,38,41.5,45,3.7911108398400006E-2,7.5822216796800013E-2,0.11373332519519999,0.189555541992,0.28433331298800002,0.37911108398400001,96.244497696910003,96.997752130199984,97.179857283510003,97.509120321699982,97.059046314650004,96.57515509516999,97.108217957487597,96.211663637940006,96.995535365399988,97.130677326429989,97.599893470800012,97.279481282970011,96.911831304299994,97.253618867016314,96.292159424369999,96.908871291769998,97.001061403980003,97.569444778969995,97.352029924220005,96.974843386809994,97.272158742801693,"2021-09-13","2021-10-21"]
["Enphase Energy Inc.","IQ7HS-66-ACM-US [240V]","N","Y ","Y ","Y ","Y ","Y*","Y","384 VA, 240 Vac Grid Support Utility Interactive microinverter",0.38400000000000001,240,97,"UL","[01/19/2021];[01/19/2021]","[V04.19.06];[V04.21.04]","2021-02-11","[01/19/2021];[01/19/2021]","2021-02-11","UL","2020-01-24","2021-02-11","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [240V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-07-12"]
["Enphase Energy Inc.","IQ7HS-66-ACM-US-NM [240V]","N","Y ","Y ","Y ","Y ","Y*","Y","384 VA, 240 Vac Grid Support Utility Interactive microinverter",0.38400000000000001,240,97,"UL","[01/19/2021];[01/19/2021]","[V04.19.06];[V04.21.04]","2021-02-11","[01/19/2021];[01/19/2021]","2021-02-11","UL","2020-01-24","2021-02-11","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [240V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-07-12"]
["Enphase Energy Inc.","IQ7HS-66-E-ACM-US [240V]","N","Y ","Y ","Y ","Y ","Y*","Y","384 VA, 240 Vac Grid Support Utility Interactive microinverter",0.38400000000000001,240,97,"UL","[01/19/2021];[01/19/2021]","[V04.19.06];[V04.21.04]","2021-02-11","[01/19/2021];[01/19/2021]","2021-02-11","UL","2020-01-24","2021-02-11","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [240V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-07-12"]
["Enphase Energy Inc.","IQ7HS-66-E-ACM-US-NM [240V]","N","Y ","Y ","Y ","Y ","Y*","Y","384 VA, 240 Vac Grid Support Utility Interactive microinverter",0.38400000000000001,240,97,"UL","[01/19/2021];[01/19/2021]","[V04.19.06];[V04.21.04]","2021-02-11","[01/19/2021];[01/19/2021]","2021-02-11","UL","2020-01-24","2021-02-11","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [240V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-07-12"]
["EPC Power Corp.","HY LC12/6-7 [480V]","Y","Y","Y","Y","N","N","N","220 kVA, 480 Vac, 3 phase Grid Support Utility Interactive Hybrid Inverter with PV MPPT and DC input",220.03299999999999,480,96,"TUV Rheinland of North America","[09/25/2018]","[042C314]","2019-01-15","[09/25/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",19.2,null,null,455,475,600,22.003332999999998,44.006665999999996,66.009998999999993,110.01666499999999,165.02499749999998,220.03332999999998,95.015714285714282,96.159999999999982,96.411428571428573,96.357142857142861,96.094285714285732,95.765714285714282,96.131257142857166,93.96142857142857,95.395714285714263,95.672857142857154,95.734285714285718,95.52428571428571,95.179999999999993,95.500057142857145,94.338571428571427,95.8,96.09714285714287,96.165714285714259,96.01428571428572,95.718571428571437,95.963499999999996,"2019-01-15"]
["Fronius International GmbH","Fronius Primo 3.8-1 208-240 [208V]","N","Y","Y","Y","N","N","N","3.8 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter",3.8,208,96,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.41,null,null,100,650,800,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,87.3,92.4,93.9,95.2,95.6,95.7,94.8,90.7,95.2,96.4,97.2,97.5,97.6,96.9,85.7,93.4,95.2,96.6,97.1,97.3,96.1,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 3.8-1 208-240 [240V]","N","Y","Y","Y","N","N","N","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter",3.8,240,95.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.55000000000000004,null,null,100,650,800,0.38,0.76,1.1399999999999999,1.9,2.85,3.8,85.5,91.5,93.3,94.8,95.4,95.6,94.4,87.2,93.4,95,96.4,96.9,97.2,96,87,93.7,95.5,96.9,97.4,97.6,96.5,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 5.0-1 208-240 [208V]","N","Y","Y","Y","N","N","N","5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter",5,208,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.41,null,null,100,650,800,0.5,1,1.5,2.5,3.75,5,89.4,93.8,94.8,95.8,96,96,95.4,92.5,96,96.8,97.5,97.6,97.6,97.2,89.3,94.6,96,97,97.3,97.4,96.6,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 5.0-1 208-240 [240V]","N","Y","Y","Y","N","N","N","5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter",5,240,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.55000000000000004,null,null,100,660,800,0.5,1,1.5,2.5,3.75,5,89,93.2,94.6,95.6,95.9,96,95.3,91.6,95.4,96.4,97.1,97.4,97.4,96.9,92.3,96,97,97.7,97.9,97.9,97.4,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 6.0-1 208-240 [208V]","N","Y","Y","Y","N","N","N","6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter",6,208,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.41,null,null,100,660,800,0.6,1.2,1.8,3,4.5,6,90.7,94.4,95.2,95.9,96,95.9,95.6,93.5,96.5,97.1,97.6,97.6,97.6,97.3,91,95.4,96.4,97.2,97.3,97.4,96.8,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 6.0-1 208-240 [240V]","N","Y","Y","Y","N","N","N","6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter",6,240,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.55000000000000004,null,null,100,660,800,0.6,1.2,1.8,3,4.5,6,89.8,93.6,94.9,95.8,96,96,95.4,91.4,95.3,96.3,97,97.3,97.3,96.8,91.7,95.7,96.7,97.5,97.7,97.7,97.2,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 7.6-1 208-240 [208V]","N","Y","Y","Y","N","N","N","7.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter",7.6,208,97,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.41,null,null,100,660,800,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,92.7,95.1,95.8,96.1,96.1,95.8,95.8,96,97.4,97.7,97.8,97.7,97.6,97.7,94.1,96.7,97.3,97.6,97.5,97.4,97.3,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 7.6-1 208-240 [240V]","N","Y","Y","Y","N","N","N","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter",7.6,240,97,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.55000000000000004,null,null,100,660,800,0.76,1.52,2.2799999999999998,3.8,5.7,7.6,91.6,94.8,95.5,96,96.1,95.9,95.7,94,96.4,97,97.4,97.5,97.4,97.2,94.6,97,97.6,97.9,97.9,97.8,97.7,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 8.2-1 208-240 [208V]","N","Y","Y","Y","N","N","N","8.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter",7.9,208,97,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.41,null,null,100,660,800,0.79,1.58,2.37,3.95,5.93,7.9,93,95.3,95.9,96.2,96.2,95.9,96,95.8,97.3,97.7,97.8,97.8,97.5,97.7,94,96.7,97.3,97.6,97.6,97.4,97.3,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 8.2-1 208-240 [240V]","N","Y","Y","Y","N","N","N","8.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter",8.1999999999999993,240,97,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0]","2018-10-15","[7/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.55000000000000004,null,null,100,660,800,0.82,1.64,2.46,4.0999999999999996,6.15,8.1999999999999993,92.1,94.9,95.7,96.2,96.2,96.1,95.9,94.2,96.6,97.1,97.4,97.4,97.4,97.2,94.7,97.1,97.6,97.9,97.9,97.8,97.7,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 10.0-1 208-240 [208V]","N","Y","Y","Y","N","N","N","10 kW, 208 Vac, Grid Support Utility Interactive Inverter with arc detector and meter",9.9949999999999992,208,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.9.0]","2018-10-15","[9/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Model number formerly listed as Fronius Primo 1.-1 [28V]. ","Y","N",0.24,null,null,100,660,800,1,2,3,5,7.5,10,92,94.7,95.1,95.6,95.6,95.5,95.3,94.5,97.4,96.8,97.3,97.3,97.4,97.1,93.3,97.1,96.5,97,97.3,97.3,97,"2017-11-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 10.0-1 208-240 [240V]","N","Y","Y","Y","N","N","N","10 kW, 240 Vac, Grid Support Utility Interactive Inverter with arc detector and meter",9.9949999999999992,240,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.9.0]","2018-10-15","[9/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Model number formerly listed as Fronius Primo 1.-1 [24V]. ","Y","N",0.32,null,null,100,655,800,1,2,3,5,7.5,10,91.4,94.3,94.8,95.4,95.6,95.6,95.2,93.5,95.8,96.3,96.9,97.1,97,96.7,95.6,97,97.2,97.6,97.7,97.5,97.5,"2017-11-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo 10.0-3 208-240 [208V]","N","Y","Y","Y","N","N","N","10 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",9.9949999999999992,208,96.5,"CSA Group","[10/16/2017];[03/28/2018]","[ReCerbo V0.3.14.8\nRoach V0.26.18.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8,\nRoach V0.26.25.0\nGuard V0.10.9.0]","2018-10-15","[10/16/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.81,null,null,100,370,480,1,2,3,5,7.5,10,94,95.6,96.1,96.2,96.2,96,96.1,95.4,96.8,97,97.1,97.1,96.9,97,94.8,96.4,96.7,96.9,96.9,96.7,96.7,"2017-12-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo 10.0-3 208-240 [240V]","N","Y","Y","Y","N","N","N","10 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",9.9949999999999992,240,96.5,"CSA Group","[10/16/2017];[03/28/2018]","[ReCerbo V0.3.14.8\nRoach V0.26.18.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8,\nRoach V0.26.25.0\nGuard V0.10.9.0]","2018-10-15","[10/16/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.8,null,null,100,370,480,1,2,3,5,7.5,10,94,95.6,96.1,96.2,96.2,96,96.1,95.4,96.8,97,97.1,97.1,96.9,97,94.8,96.4,96.7,96.9,96.9,96.7,96.7,"2017-12-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo 10.0-3 480 [480V]","N","Y","Y","Y","N","N","N","10 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",9.9949999999999992,480,96.5,"CSA Group","[7/27/2017];[03/28/2018]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0]","2018-10-15","[7/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.86,null,null,100,670,800,1,2,3,5,7.5,10,89.6,93.7,94.8,95.3,96,96.2,95.3,91.8,95.2,96.1,96.7,97.2,97.3,96.6,92.9,96.1,96.9,97.3,97.7,97.8,97.2,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 10.0-3 208-240 [208V]","N","Y","Y","Y","N","N","N","10 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",10.010999999999999,208,96.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2019-02-15","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.6,null,null,300,355,480,1.0010600000000001,2.0021200000000001,3.00318,5.0053000000000001,7.5079500000000001,10.0106,94.519009568535679,95.899927353909121,96.162013751958028,96.198800130252479,96.032730306812141,95.714297404757531,96.000008360873181,95.414711455032631,96.574721944504731,96.781649546159471,96.800433167872072,96.660999056168905,96.399596007593573,96.637522766368022,94.36181904589003,95.971378365346439,96.324429710555705,96.444995456986462,96.091747578754877,96.177655301980025,96.122931273175851,"2019-02-15","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 10.0-3 208-240 Lite [208V]","N","Y","Y","Y","N","N","N","10 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",10.010999999999999,208,96.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2020-05-11","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.6,null,null,300,355,480,1.0010600000000001,2.0021200000000001,3.00318,5.0053000000000001,7.5079500000000001,10.0106,94.519009568535679,95.899927353909121,96.162013751958028,96.198800130252479,96.032730306812141,95.714297404757531,96.000008360873181,95.414711455032631,96.574721944504731,96.781649546159471,96.800433167872072,96.660999056168905,96.399596007593573,96.637522766368022,94.36181904589003,95.971378365346439,96.324429710555705,96.444995456986462,96.091747578754877,96.177655301980025,96.122931273175851,"2020-05-11"]
["Fronius International GmbH","Fronius Symo Advanced 10.0-3 208-240 [240V]","N","Y","Y","Y","N","N","N","10 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",10.061999999999999,240,96.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2019-02-15","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.8,null,null,300,370,480,1.0061600000000002,2.0123200000000003,3.0184799999999998,5.0308000000000002,7.5462000000000007,10.0616,94.009185795922122,95.629761429716126,96.080273901482812,96.248573788302309,96.213773809680077,96.033389279538127,96.078658450151465,95.404905519923133,96.763474828819668,97.049926747338972,97.12930370787997,97.078894920067015,96.947601819022367,96.996709349160014,94.775945022232762,96.362545696753386,96.719798702026267,96.860676846044242,96.877356545777872,96.729094148120311,96.737736744307725,"2019-02-15","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 10.0-3 208-240 Lite [240V]","N","Y","Y","Y","N","N","N","10 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",10.061999999999999,240,96.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2020-05-11","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.8,null,null,300,370,480,1.0061600000000002,2.0123200000000003,3.0184799999999998,5.0308000000000002,7.5462000000000007,10.0616,94.009185795922122,95.629761429716126,96.080273901482812,96.248573788302309,96.213773809680077,96.033389279538127,96.078658450151465,95.404905519923133,96.763474828819668,97.049926747338972,97.12930370787997,97.078894920067015,96.947601819022367,96.996709349160014,94.775945022232762,96.362545696753386,96.719798702026267,96.860676846044242,96.877356545777872,96.729094148120311,96.737736744307725,"2020-05-11"]
["Fronius International GmbH","Fronius Primo 11.4-1 208-240 [208V]","N","Y","Y","Y","N","N","N","11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter",11.4,208,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.9.0]","2018-10-15","[9/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Model number formerly listed as Fronius Primo 11.4-1 [28V]. ","Y","N",0.24,null,null,240,660,800,1.1399999999999999,2.2799999999999998,3.42,5.7,8.5500000000000007,11.4,93,94.9,95.4,95.8,95.8,95.7,95.6,95.4,97,97.3,97.4,97.4,97.4,97.3,94.5,96.4,96.9,97.2,97.2,97.3,97.1,"2017-11-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 11.4-1 208-240 [240V]","N","Y","Y","Y","N","N","N","11.4 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter",11.4,240,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.9.0]","2018-10-15","[9/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Model number formerly listed as Fronius Primo 11.4-1 [24V]. ","Y","N",0.32,null,null,240,660,800,1.1399999999999999,2.2799999999999998,3.42,5.7,8.5500000000000007,11.4,92.1,94.8,95.3,95.8,95.9,95.8,95.6,93.7,96.1,96.6,97,97.1,97.1,96.9,94.8,96.9,97.4,97.6,97.6,97.6,97.4,"2017-11-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo 12.0-3 208-240 [208V]","N","Y","Y","Y","N","N","N","12 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",12,208,96.5,"CSA Group","[10/16/2017];[03/28/2018]","[ReCerbo V0.3.14.8\nRoach V0.26.18.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8,\nRoach V0.26.25.0\nGuard V0.10.9.0]","2018-10-15","[10/16/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.61,null,null,300,350,480,1.2,2.4,3.6,6,9,12,95.4,96.2,96.3,96.2,95.9,95.4,95.9,96.3,96.9,96.9,96.8,96.5,96.2,96.6,94.7,96.1,96.4,96.4,96.3,96,96.2,"2017-12-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo 12.0-3 208-240 [240V]","N","Y","Y","Y","N","N","N","12 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",12,240,96.5,"CSA Group","[10/16/2017];[03/28/2018]","[ReCerbo V0.3.14.8\nRoach V0.26.18.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8,\nRoach V0.26.25.0\nGuard V0.10.9.0]","2018-10-15","[10/16/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.81,null,null,300,370,480,1.2,2.4,3.6,6,9,12,94.4,95.9,96.2,96.3,96.1,95.8,96.1,96,96.9,97.1,97.1,97,96.8,97,95.2,96.6,96.8,96.9,96.8,96.6,96.7,"2017-12-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 12.0-3 208-240 [240V]","N","Y","Y","Y","N","N","N","12 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",12.09,240,96.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2019-02-15","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.8,null,null,300,370,480,1.2090200000000002,2.4180400000000004,3.6270600000000002,6.0451000000000006,9.0676500000000004,12.090200000000001,94.368110232506652,95.892591116805448,96.183609957195344,96.259168851666118,96.112813309312941,95.818539515129942,96.056530648546214,95.96878852712085,96.944362434826957,97.096865939081653,97.112812968596486,97.001048386914235,96.818624545776956,96.982771171274635,95.235218242739734,96.577017146431658,96.799319868460742,96.87857337110789,96.788909553631157,96.596855655531229,96.726643225380201,"2019-02-15","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 12.0-3 208-240 Lite [240V]","N","Y","Y","Y","N","N","N","12 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",12.09,240,96.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2020-05-11","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.8,null,null,300,370,480,1.2090200000000002,2.4180400000000004,3.6270600000000002,6.0451000000000006,9.0676500000000004,12.090200000000001,94.368110232506652,95.892591116805448,96.183609957195344,96.259168851666118,96.112813309312941,95.818539515129942,96.056530648546214,95.96878852712085,96.944362434826957,97.096865939081653,97.112812968596486,97.001048386914235,96.818624545776956,96.982771171274635,95.235218242739734,96.577017146431658,96.799319868460742,96.87857337110789,96.788909553631157,96.596855655531229,96.726643225380201,"2020-05-11"]
["Fronius International GmbH","Fronius Symo Advanced 12.0-3 208-240 [208V]","N","Y","Y","Y","N","N","N","12 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",12.340999999999999,208,96.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2019-02-15","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.61,null,null,300,350,480,1.2340800000000001,2.4681600000000001,3.7022399999999998,6.1703999999999999,9.2555999999999994,12.3408,95.358678737621432,96.184848341697503,96.273927559322075,96.181378447078401,95.855468172966297,95.410697226904546,95.948483340612199,96.265787667643764,96.863886988610275,96.903704189756823,96.816181235310211,96.526151120335172,96.16472401789197,96.620764712994472,94.730185167876712,96.120808838845704,96.384756278113855,96.445891835655814,96.284563999089613,96.000896354491587,96.245919624760816,"2019-02-15","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 12.0-3 208-240 Lite [208V]","N","Y","Y","Y","N","N","N","12 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",12.340999999999999,208,96.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2020-05-11","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.61,null,null,300,350,480,1.2340800000000001,2.4681600000000001,3.7022399999999998,6.1703999999999999,9.2555999999999994,12.3408,95.358678737621432,96.184848341697503,96.273927559322075,96.181378447078401,95.855468172966297,95.410697226904546,95.948483340612199,96.265787667643764,96.863886988610275,96.903704189756823,96.816181235310211,96.526151120335172,96.16472401789197,96.620764712994472,94.730185167876712,96.120808838845704,96.384756278113855,96.445891835655814,96.284563999089613,96.000896354491587,96.245919624760816,"2020-05-11"]
["Fronius International GmbH","Fronius Primo 12.5-1 208-240 [208V]","N","Y","Y","Y","N","N","N","12.5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter",12.5,208,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.9.0]","2018-10-15","[9/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Model number formerly listed as Fronius Primo 12.5-1 [28V]. ","Y","N",0.24,null,null,260,665,800,1.25,2.5,3.75,6.25,9.3800000000000008,12.5,92.5,95.1,95.5,95.9,95.9,95.6,95.6,95.3,96.9,97.3,97.5,97.3,97.3,97.2,94.5,96.6,97,97.2,97.1,97.2,97,"2017-11-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 12.5-1 208-240 [240V]","N","Y","Y","Y","N","N","N","12.5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter",12.5,240,96.5,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.9.0]","2018-10-15","[9/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Model number formerly listed as Fronius Primo 12.5-1 [24V]. ","Y","N",0.32,null,null,260,660,800,1.25,2.5,3.75,6.25,9.3800000000000008,12.5,92.1,95,95.4,95.9,95.9,95.8,95.6,93.7,96.2,96.6,97,97.1,97.1,96.8,95.4,97.2,97.3,97.5,97.6,97.7,97.5,"2017-11-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo 12.5-3 480 [480V]","N","Y","Y","Y","N","N","N","12.5 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",12.5,480,97,"CSA Group","[7/27/2017];[03/28/2018]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0]","2018-10-15","[7/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.94,null,null,350,685,800,1.25,2.5,3.75,6.25,9.3699999999999992,12.5,92.5,94.9,95.6,96,96.4,96.5,96,94.4,96.5,97,97.3,97.5,97.5,97.2,95.6,97.3,97.7,97.9,98,98,97.8,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 15.0-1 208-240 [208V]","N","Y","Y","Y","N","N","N","15 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter",13.75,208,97,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.9.0]","2018-10-15","[9/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Model number formerly listed as Fronius Primo 15.-1 [28V]. ","Y","N",0.24,null,null,320,680,800,1.38,2.75,4.13,6.88,10.31,13.75,93.3,95.7,96,96.3,96.2,96,96,95.9,97.1,97.4,97.4,97.4,97.2,97.3,95.1,96.8,97.1,97.2,97.2,97.1,97.1,"2017-11-01","2019-03-01"]
["Fronius International GmbH","Fronius Primo 15.0-1 208-240 [240V]","N","Y","Y","Y","N","N","N","15 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter",15,240,97,"CSA Group","[7/7/2017];[12/21/2017]","[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.7.0];[ReCerbo V0.3.14.8\nRoach V0.26.16.0\nGuard V0.10.9.0]","2018-10-15","[9/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Model number formerly listed as Fronius Primo 15.-1 [24V]. ","Y","N",0.32,null,null,320,680,800,1.5,3,4.5,7.5,11.25,15,93.5,95.5,96,96.3,96.3,96.1,96.1,94.5,96.5,96.9,97.2,97.2,97,97,95.7,97.2,97.5,97.6,97.6,97.4,97.5,"2017-11-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo 15.0-3 208 [208V]","N","Y","Y","Y","N","N","N","15 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",15,208,96.5,"CSA Group","[9/27/2017]","[ReCerbo V0.3.14.8,\nRoach V0.26.14.0,\nGuard V0.10.9.0]","2018-10-15","[9/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Model number formerly listed as Fronius Symo 15.-3 [28V]. ","Y","N",0.43,null,null,325,445,800,1.5,3,4.5,7.5,11.25,15,96.1,97,97.1,97.1,96.9,96.7,96.9,95.3,96.4,96.6,96.7,96.5,96.2,96.5,92.7,94.9,95.4,95.6,95.5,95.3,95.4,"2017-11-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo 15.0-3 480 [480V]","N","Y","Y","Y","N","N","N","15 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",15,480,97,"CSA Group","[7/27/2017];[03/28/2018]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0]","2018-10-15","[7/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.03,null,null,350,685,800,1.5,3,4.5,7.5,11.25,15,92,94.9,95.6,96.2,96.5,96.4,96.1,93.5,96,96.7,97.2,97.4,97.4,97.1,94.6,96.8,97.4,97.8,97.9,97.9,97.6,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 15.0-3 480 [480V]","N","Y","Y","Y","N","N","N","15 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",15.196999999999999,480,97,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2019-02-15","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1,null,null,350,685,800,1.5196779999999999,3.0393559999999997,4.5590339999999996,7.5983899999999993,11.397584999999999,15.196779999999999,92.041589863870271,94.91964593162821,95.624455631735273,96.237422914377035,96.485431444459593,96.387099283281017,96.069073008691262,93.543995460840279,95.998378827776165,96.696348505894704,97.240325293365302,97.407654085354906,97.437857239067384,97.063658419327965,94.622972516951833,96.812694403298863,97.365647324576372,97.769337729645059,97.888645679374235,97.897281491093622,97.616838507640665,"2019-02-15","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 15.0-3 480 Lite [480V]","N","Y","Y","Y","N","N","N","15 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",15.196999999999999,480,97,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2020-05-11","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1,null,null,350,685,800,1.5196779999999999,3.0393559999999997,4.5590339999999996,7.5983899999999993,11.397584999999999,15.196779999999999,92.041589863870271,94.91964593162821,95.624455631735273,96.237422914377035,96.485431444459593,96.387099283281017,96.069073008691262,93.543995460840279,95.998378827776165,96.696348505894704,97.240325293365302,97.407654085354906,97.437857239067384,97.063658419327965,94.622972516951833,96.812694403298863,97.365647324576372,97.769337729645059,97.888645679374235,97.897281491093622,97.616838507640665,"2020-05-11"]
["Fronius International GmbH","Fronius Symo 17.5-3 480 [480V]","N","Y","Y","Y","N","N","N","17.5 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",17.5,480,97.5,"CSA Group","[7/27/2017];[03/28/2018]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0]","2018-10-15","[7/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.03,null,null,400,700,800,1.75,3.5,5.25,8.75,13.12,17.5,92.7,95.3,95.8,96.5,96.6,96.7,96.3,95.7,97.4,97.8,98.1,98.1,98.2,98,94.8,96.9,97.4,97.7,97.8,97.8,97.6,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo 20.0-3 480 [480V]","N","Y","Y","Y","N","N","N","20 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",20,480,97.5,"CSA Group","[7/27/2017];[03/28/2018]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0]","2018-10-15","[7/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.04,null,null,450,712,800,2,4,6,10,15,20,93.7,95.6,96.3,96.7,96.8,96.8,96.5,96,97.2,97.7,98,98,98,97.9,95.7,97,97.5,97.7,97.8,97.8,97.6,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 20.0-3 480 [480V]","N","Y","Y","Y","N","N","N","20 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",20.227,480,97,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2019-02-15","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1,null,null,450,710,800,2.0227139999999997,4.0454279999999994,6.0681419999999981,10.113569999999998,15.170354999999997,20.227139999999995,93.0612623209757,95.493857450995776,96.142166575436093,96.700901941853445,96.784885330722474,96.806465087192649,96.477705241872926,95.096166713692284,97.042083445707775,97.530716554074772,97.863489532455873,97.971466683243179,98.00444003699738,97.736068973106541,94.462463256041829,96.687133800520058,97.264502866483426,97.659357524786984,97.731839168170112,97.768076436494425,97.479339225405838,"2019-02-15","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 20.0-3 480 Lite [480V]","N","Y","Y","Y","N","N","N","20 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",20.227,480,97,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2020-05-11","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1,null,null,450,710,800,2.0227139999999997,4.0454279999999994,6.0681419999999981,10.113569999999998,15.170354999999997,20.227139999999995,93.0612623209757,95.493857450995776,96.142166575436093,96.700901941853445,96.784885330722474,96.806465087192649,96.477705241872926,95.096166713692284,97.042083445707775,97.530716554074772,97.863489532455873,97.971466683243179,98.00444003699738,97.736068973106541,94.462463256041829,96.687133800520058,97.264502866483426,97.659357524786984,97.731839168170112,97.768076436494425,97.479339225405838,"2020-05-11"]
["Fronius International GmbH","Fronius Symo 22.7-3 480 [480V]","N","Y","Y","Y","N","N","N","22.7 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",22.73,480,97.5,"CSA Group","[7/27/2017];[03/28/2018]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0]","2018-10-15","[7/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.03,null,null,500,720,800,2.27,4.55,6.82,11.36,17.05,22.73,94.3,96.2,96.7,97,97,96.9,96.8,96.4,97.6,97.8,98,98,98,97.9,95.9,97.3,97.7,97.8,97.9,97.8,97.7,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 22.7-3 480 [480V]","N","Y","Y","Y","N","N","N","22.7 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",22.876000000000001,480,97.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2019-02-15","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1,null,null,500,722,800,2.2875799999999997,4.5751599999999994,6.8627399999999996,11.437899999999999,17.156849999999999,22.875799999999998,94.319153396668113,96.163141608609081,96.661756345827499,96.951459054201692,96.990760221655123,96.948409380259022,96.792663765669005,96.38855934891761,97.551760411799364,97.806770088065903,97.999596093082118,98.020888700727554,97.981259840645649,97.899991988079719,95.944132313041493,97.337088217971754,97.666559168276663,97.839166197501726,97.862870517438836,97.806740534534583,97.728490106058118,"2019-02-15","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 22.7-3 480 Lite [480V]","N","Y","Y","Y","N","N","N","22.7 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",22.876000000000001,480,97.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2020-05-11","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1,null,null,500,722,800,2.2875799999999997,4.5751599999999994,6.8627399999999996,11.437899999999999,17.156849999999999,22.875799999999998,94.319153396668113,96.163141608609081,96.661756345827499,96.951459054201692,96.990760221655123,96.948409380259022,96.792663765669005,96.38855934891761,97.551760411799364,97.806770088065903,97.999596093082118,98.020888700727554,97.981259840645649,97.899991988079719,95.944132313041493,97.337088217971754,97.666559168276663,97.839166197501726,97.862870517438836,97.806740534534583,97.728490106058118,"2020-05-11"]
["Fronius International GmbH","Fronius Symo 24.0-3 480 [480V]","N","Y","Y","Y","N","N","N","24 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",24,480,97.5,"CSA Group","[7/27/2017];[03/28/2018]","[ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0]","2018-10-15","[7/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.03,null,null,500,725,800,2.4,4.8,7.2,12,18,24,94.3,96.1,96.6,97,97,97,96.8,96.2,97.5,97.8,98,98,97.9,97.9,95.8,97.2,97.6,97.8,97.8,97.7,97.7,"2017-08-01","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 24.0-3 480 [480V]","N","Y","Y","Y","N","N","N","24 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",24.141999999999999,480,97.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2019-02-15","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1,null,null,500,722,800,2.41418,4.82836,7.24254,12.0709,18.106349999999999,24.1418,94.298559581044074,96.138336449199727,96.588896784094771,96.951127656168396,96.952936768599201,96.954121357451385,96.76202618281863,96.244961016193955,97.476914573977169,97.790615499320054,97.957335491967925,97.982847302864613,97.922998991587718,97.856617502675903,95.769609949788745,97.234429015050907,97.616915845498539,97.821717266513275,97.813565824785215,97.724760972565377,97.676524311936149,"2019-02-15","2019-03-01"]
["Fronius International GmbH","Fronius Symo Advanced 24.0-3 480 Lite [480V]","N","Y","Y","Y","N","N","N","24 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter",24.141999999999999,480,97.5,"CSA Group","[11/22/2018]","[ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3]","2020-05-11","[11/22/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1,null,null,500,722,800,2.41418,4.82836,7.24254,12.0709,18.106349999999999,24.1418,94.298559581044074,96.138336449199727,96.588896784094771,96.951127656168396,96.952936768599201,96.954121357451385,96.76202618281863,96.244961016193955,97.476914573977169,97.790615499320054,97.957335491967925,97.982847302864613,97.922998991587718,97.856617502675903,95.769609949788745,97.234429015050907,97.616915845498539,97.821717266513275,97.813565824785215,97.724760972565377,97.676524311936149,"2020-05-11"]
["Gamesa Electric","PV3800 [600V]","N","Y","Y","Y","N","N","N","3800 kVA, 600 Vac Grid Support Utilitity Interactive Inverters",3418.3939999999998,600,98,"MET","[12/3/2020]","[FIP 1027 1.1.4]","2021-02-22","[12/3/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer.","N","N",267,null,null,835,1050,1300,341.83940000000001,683.67880000000002,1025.5182,1709.1969999999999,2563.7954999999997,3418.3939999999998,97.53680895795155,98.673551910767159,98.689600670460365,98.562326471824676,98.236119622493831,97.903545468924676,98.33631126676282,96.818804206494576,98.004672061306451,98.478025350539497,98.295122905165428,97.850015485350994,97.426472508594827,97.964156456140358,95.972049877811429,97.58054761595362,98.080764481063071,98.032800239639542,97.673259460351161,97.26139607844361,97.704386481870316,"2021-02-22"]
["Gamesa Electric","PV4000 [630V]","N","Y","Y","Y","N","N","N","4000 kVA, 630 Vac Grid Support Utilitity Interactive Inverters",3597.3319999999999,630,98,"MET","[12/3/2020]","[FIP 1027 1.1.4]","2021-02-22","[12/3/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer.","N","N",267,null,null,875,1050,1300,359.73320000000001,719.46640000000002,1079.1995999999999,1798.6659999999999,2697.9989999999998,3597.3319999999999,97.458081042294594,98.559460458294453,98.697209054491225,98.5796541510624,98.248242783056327,97.938685676226541,98.340191681699736,96.747744392695935,98.032947621087331,98.356001655747406,98.262482512575389,97.877056862190145,97.518741202157557,97.960175880161373,96.267094884408522,97.71296761050759,98.232645613570554,98.164521899400881,97.751344317923881,97.337332003889827,97.813878337098515,"2021-02-22"]
["Gamesa Electric","PV4100 [600V]","N","Y","Y","Y","N","N","N","4100 kVA, 600 Vac Grid Support Utilitity Interactive Inverters",3644.0659999999998,600,98,"MET","[12/3/2020]","[FIP 1027 1.1.4]","2021-02-22","[12/3/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer.","N","N",267,null,null,835,1050,1300,364.40660000000003,728.81320000000005,1093.2197999999999,1822.0329999999999,2733.0495000000001,3644.0659999999998,97.602448672073663,98.744466927336902,98.797422226591536,98.602782446011716,98.207652733335379,97.884280248263281,98.347866235184142,96.836193867573826,98.065154324663851,98.588029343630026,98.05923140681621,97.826005597670331,97.33410512116069,97.914195810426477,95.893700366249817,97.673011518243698,98.26939277046273,98.145959700805108,97.698689677705346,97.27564302732064,97.766464940736654,"2021-02-22"]
["Gamesa Electric","PV4200 [660V]","N","Y","Y","Y","N","N","N","4200 kVA, 660 Vac Grid Support Utilitity Interactive Inverters",3767.3519999999999,660,98,"MET","[12/3/2020]","[FIP 1027 1.1.4]","2021-02-22","[12/3/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer.","N","N",267,null,null,915,1050,1300,376.73520000000002,753.47040000000004,1130.2056,1883.6759999999999,2825.5140000000001,3767.3519999999999,97.48024077817044,98.714151003136024,98.827055652613197,98.695349017103837,98.375931807311886,98.019269500214563,98.460394486075032,96.976673489598838,98.540669739911209,98.709219227980441,98.529985486238544,98.136075940586323,97.701724876177707,98.239710178366906,96.471577685191264,97.780085018623254,98.288528485266454,98.221044168378668,97.900785064484182,97.486518644664272,97.930652068340152,"2021-02-22"]
["Gamesa Electric","PV4300 [630V]","N","Y","Y","Y","N","N","N"," 4300 kVA, 630 Vac Grid Support Utilitity Interactive Inverters",3826.652,630,98,"MET","[12/3/2020]","[FIP 1027 1.1.4]","2021-02-22","[12/3/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer.","N","N",267,null,null,875,1050,1300,382.66520000000003,765.33040000000005,1147.9956,1913.326,2869.989,3826.652,97.571976957048662,98.656455799018644,98.795317178349833,98.643813743689009,98.284310068405759,97.945651563950875,98.394307730262142,97.035771737766723,98.477273542696949,98.562081331757824,98.372459484633254,97.935607359276176,97.469574083098848,98.070311402800755,96.09400450733807,97.837427289302653,98.357404950373208,98.220315791235663,97.789230035004707,97.319157622032066,97.859036254617038,"2021-02-22"]
["Gamesa Electric","PV4400 [690V]","N","Y","Y","Y","N","N","N","4400 kVA, 690 Vac Grid Support Utilitity Interactive Inverters",3939.5740000000001,690,98,"MET","[12/3/2020]","[FIP 1027 1.1.4]","2021-02-22","[12/3/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer.","N","N",267,null,null,955,1050,1300,393.95740000000001,787.91480000000001,1181.8722,1969.787,2954.6804999999999,3939.5740000000001,97.42000894640023,98.35055324910509,98.612676002496812,98.601116463856329,98.307462699000268,98.050751362565009,98.359576396619104,96.930245359665591,98.012360379395105,98.350182325704665,98.318647521589369,97.986389194051483,97.62926499716761,98.041015214680371,96.081170087145637,97.662577728151433,97.919461328413902,97.984177032466292,97.676226256713093,97.274282645920209,97.685502274474942,"2021-02-22"]
["Gamesa Electric","PV4500 [660V]","N","Y","Y","Y","N","N","N","4500 kVA, 660 Vac Grid Support Utilitity Interactive Inverters",4006.9459999999999,660,98,"MET","[12/3/2020]","[FIP 1027 1.1.4]","2021-02-22","[12/3/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer.","N","N",267,null,null,915,1050,1300,400.69460000000004,801.38920000000007,1202.0837999999999,2003.473,3005.2094999999999,4006.9459999999999,97.509866049189199,98.749388386204231,98.828857603879655,98.684295775543049,98.318132069644832,98.010761279536595,98.430177147495968,96.998185461254891,98.523205646656422,98.573381090761302,98.432995506657775,98.039528095150416,97.620412946479703,98.147793025826218,96.48611120935584,97.821269944650254,98.477203804290781,98.307221108023327,97.841257579062315,97.425634068964229,97.939437055157782,"2021-02-22"]
["Gamesa Electric","PV4700 [690V]","N","Y","Y","Y","N","N","N","4700 kVA, 690 Vac Grid Support Utilitity Interactive Inverters",4190.43,690,98,"MET","[12/3/2020]","[FIP 1027 1.1.4]","2021-02-22","[12/3/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer.","N","N",267,null,null,955,1050,1300,419.04300000000006,838.08600000000013,1257.1290000000001,2095.2150000000001,3142.8225000000002,4190.43,97.491642531723642,98.799535197366453,98.888643261687008,98.732567463012188,98.348682139247799,98.050727060444331,98.467456706595812,97.156201251852679,98.476412821271026,98.582969643243757,98.434817805815342,98.074291450530325,97.686923622198279,98.175057437439122,96.524413778196006,97.973141619567599,98.507384998758681,98.420512199231709,97.938316413658526,97.504361924165153,98.031353189243205,"2021-02-22"]
["GE Renewable Energy","RIU-2500-U [550V]","Y","Y","Y","Y","N","N","N","2500 kVA, 550 Vac, Bi-directional, Grid Support Utility Interactive Hybrid Inverter",2507.194,550,97.5,"CSA Group","[11/01/2019]","[DSP_RIU-2500-U_V11_V1_A, LCD_RIU-2500-U_V1_A]   ","2020-03-23","[11/01/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 2500 kVA Medium-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",62.8,null,null,800,975,1500,250.71940000000001,501.43880000000001,752.15819999999997,1253.597,1880.3955000000001,2507.194,96.165587825617536,97.496024626913893,97.84611827224451,97.917731002770864,97.654712804724852,97.323989855524346,97.64887972690201,96.024564148543945,97.239077966047518,97.730826426636156,97.852050543793169,97.544402877512624,97.189977456983456,97.537598647567904,95.432639383368937,96.821878647291854,97.345753997551,97.466367294046691,97.19680752091476,96.942642988776186,97.169267254678914,"2021-03-01"]
["Generac Power Systems","X7602 [240V]","Y","Y","Y","Y","Y","Y","Y","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS Functionality",7.5860000000000003,240,96.5,"Intertek","[10/09/2020]","[13430];[13590]","2020-02-03","[10/09/2020]","2020-03-23","SunSpec Alliance","2019-11-26","2020-02-03","Model number formerly listed as Pika Energy","N","N",1.2917000000000001,null,null,390,400,420,0.75900000000000001,1.5169999999999999,2.2759999999999998,3.7930000000000001,5.6890000000000001,7.5860000000000003,91.67,95.89,96.62,97.26,97.24,97.04,96.87,91.01,95.4,96.52,97.26,97.15,97.01,96.75,90.48,95.21,96.33,96.86,97.02,96.91,96.55,"2020-02-03","2021-04-01"]
["Generac Power Systems","XVT076A03 [240V]","Y","Y","Y","Y","Y","Y","Y","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS Functionality\n",7.8390000000000004,240,97,"Intertek","[10/09/2020]","[13430];[13590]","2020-10-01","[10/09/2020]","2020-10-01","SunSpec Alliance","2019-11-26","2020-10-01",null,"N","N",1.29,null,null,390,400,420,0.78386000000000011,1.5677200000000002,2.3515800000000002,3.9193000000000002,5.8789500000000006,7.8386000000000005,93.677571661912438,95.998695918204376,96.532584169437186,97.203606428872618,97.160321284506622,97.104690959587344,96.893909941550305,92.823435812878273,95.608312530903618,96.668103505003316,97.212868781288137,97.223080010698936,97.133748280222818,96.893147743412783,92.288725595479406,95.332004693618927,96.190215837424773,96.986588538568142,97.129959421275132,97.018910806982078,96.69798278571534,"2020-10-01","2021-04-01"]
["Generac Power Systems","X11402 [208V]","Y","Y","Y","Y","Y","Y","Y","11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS Functionality",11.18,208,97.5,"Intertek","[10/09/2020]","[13430];[13590]","2020-02-03","[10/09/2020]","2020-03-23","SunSpec Alliance","2019-11-26","2020-02-03","Model number formerly listed as Pika Energy","N","N",0.125,null,null,390,400,420,1.1180000000000001,2.2360000000000002,3.3540000000000001,5.59,8.3849999999999998,11.18,97.25,97.35,97.58,97.65,97.44,97.06,97.47,97.03,97.35,97.67,97.54,97.25,96.93,97.34,95.83,97.24,97.27,97.39,97.08,96.89,97.12,"2020-02-03","2021-04-01"]
["Generac Power Systems","XVT114G03 [208V]","Y","Y","Y","Y","Y","Y","Y","11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS Functionality",11.747999999999999,208,97,"Intertek","[10/09/2020]","[13430];[13590]","2020-10-01","[10/09/2020]","2020-10-01","SunSpec Alliance","2019-11-26","2020-10-01",null,"N","N",0.13,null,null,390,400,420,1.1747799999999999,2.3495599999999999,3.52434,5.8738999999999999,8.8108500000000003,11.7478,94.395211446168631,96.361356960371879,96.984363713293462,97.348791855457421,97.391308612260303,97.322335432679594,97.158756577238563,93.83751781107668,96.115972231046584,96.813462247015622,97.3002678881099,97.255554722173059,97.114925605882902,97.011161333186209,92.903509361520491,95.765877282912555,96.540038288330763,97.077104337918129,97.168018148504345,97.065836329336818,96.827772179343086,"2020-10-01","2021-04-01"]
["Ginlong Technologies Co., Ltd.","Solis-1P2.5K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","2.5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",2.5,240,97,"Intertek","[8/14/2017]","[08_01]","2018-10-15","[8/14/2017]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,"N","N",3.2,null,null,120,330,500,0.25,0.5,0.75,1.25,1.875,2.5,93.64009089369759,94.645664421270453,95.691972893334565,96.836310056469273,96.713026788043152,96.48326444893533,96.378616135979769,93.91585626132742,95.504317848279925,96.592125759970912,97.689552553141795,97.43791276303179,97.114041199272336,97.135507094593848,93.7984174193098,95.168450902035602,96.329719819008758,97.426891666506009,96.998939128665057,96.804719815047363,96.77924659906634,"2017-10-16","2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-1P3K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","3 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",3,240,97,"Intertek","[8/14/2017]","[08_01]","2018-10-15","[8/14/2017]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,"N","N",3.3,null,null,140,330,500,0.30000000000000004,0.60000000000000009,0.89999999999999991,1.5,2.25,3,93.866362045573325,94.713615226317359,95.611436841133582,97.057414007214888,96.812186600936343,96.476965657638644,96.480071786968153,94.066710820970357,95.669654965023668,96.553873307195644,97.767540234850273,97.426406382654449,97.001242413635239,97.149856930760677,93.844991582308452,95.296862689394715,96.17578739336723,97.440775457825168,97.173306206173294,96.696956371666118,96.859000238964569,"2017-10-16","2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-1P3.6K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","3.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",3.6,240,97,"Intertek","[8/14/2017]","[08_01]","2018-10-15","[8/14/2017]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,"N","N",3.5,null,null,180,330,500,0.36000000000000004,0.72000000000000008,1.08,1.8,2.7,3.6,93.880410809405305,94.744608833229535,95.630247875517895,97.090449873016482,96.83855793667837,96.490700570558161,96.50604182740075,93.901739048725005,95.672168517006114,96.897284438541305,97.795929191459606,97.421390868668482,97.062195260477367,97.190944174048951,93.879160915135756,95.494696539050523,96.552192472215637,97.483113722441473,97.151107276255416,96.764456505784935,96.915927923641163,"2017-10-16","2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-1P4K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","4 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",4,240,97,"Intertek","[8/14/2017]","[08_01]","2018-10-15","[8/14/2017]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,"N","N",3.5,null,null,190,330,500,0.4,0.8,1.2,2,3,4,93.871501231104475,94.72553599271626,96.090842051821781,97.086947612260346,96.821654862153054,96.403999272846008,96.545973934256693,94.029282316330082,95.720601543272863,96.983668557667372,97.919211293239186,97.490918959368486,97.321626545023875,97.284544344033648,93.876077058123798,95.472535553669402,96.556757132693718,97.531072371253103,97.144393942024223,96.779604374883647,96.922514921911841,"2017-10-16","2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-1P4.6K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","4.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",4.5999999999999996,240,97,"Intertek","[8/14/2017]","[08_01]","2018-10-15","[8/14/2017]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,"N","N",3.6,null,null,200,360,500,0.45999999999999996,0.91999999999999993,1.38,2.2999999999999998,3.4499999999999997,4.5999999999999996,93.028195734313769,94.339053526325344,95.735856633384714,96.904337586749961,96.800085399999944,96.532524653481389,96.406965689586514,94.065488340627752,95.574073479004198,96.907410827882686,97.937545089780741,97.542723225222645,97.311778641122601,97.300329217199334,93.787640256380428,95.100883560474969,96.546118688323915,97.43737176295663,97.266633540859203,96.964009895307953,96.953448372519489,"2017-10-16","2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-1P5K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",5,240,97,"Intertek","[8/14/2017]","[08_01]","2018-10-15","[8/14/2017]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,"N","N",3.6,null,null,240,360,500,0.5,1,1.5,2.5,3.75,5,93.996706641031309,94.597949603710674,95.717205535843362,97.316091933001459,97.015499351932007,96.516651627649978,96.656256953964757,94.541781172499185,95.737381698898545,96.595282460935181,97.931932459613151,97.616770874423452,97.432986097884552,97.334217912014552,94.009381120970076,94.97515884697296,96.144960399912321,97.470538103970014,97.330846738964055,96.848085910197412,96.943094504171441,"2017-10-16","2020-09-11"]
["Ginlong Technologies Co., Ltd.","RHI-1P5K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",5.0030000000000001,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,115,330,450,0.5,1.0009999999999999,1.5009999999999999,2.5009999999999999,3.7519999999999998,5.0030000000000001,95.12,96.18,96.94,97.37,97.18,96.63,97.03,95.66,97.24,97.42,97.55,97.7,96.96,97.49,95.38,96.75,97.61,97.82,97.85,97.71,97.65,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-1P6K2-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, 1-phase Utility Interactive Inverter, 2 channel",6,240,97,"Intertek","[8/14/2017]","[08_01]","2018-10-15","[8/14/2017]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,"N","N",3.5,null,null,300,360,500,0.60000000000000009,1.2000000000000002,1.7999999999999998,3,4.5,6,94.197535726830296,94.803353761468742,95.916149598193371,97.43250288564505,97.212299328519038,96.712185326395939,96.836960585350198,94.433517737300264,95.64157274756991,96.52690498184333,97.830342345040066,97.713908618607121,97.336335950188385,97.342208202521306,94.212599552420215,95.176308210388456,96.348919315137366,97.666307646143125,97.526579814015747,97.042708604417626,97.140337047772007,"2017-10-16","2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-1P6K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, 3 channel",6,240,97.5,"Intertek","[06/30/2019]","[08_01]","2018-10-15","[06/30/2019]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"N","N",6,null,null,200,380,500,0.60000000000000009,1.2000000000000002,1.7999999999999998,3,4.5,6,94.899770164528803,96.120754598027418,96.764537644534499,97.304464686096452,97.323418673708375,96.476132204853485,97.052929145215032,95.548667212840428,96.981255211095871,97.396397632963414,97.422751793816218,97.371743747168495,97.952511725361148,97.322004813992791,95.308252818866848,96.91462083439346,97.479407193637854,97.587301167885428,97.579454798035869,97.582808566643422,97.445174734258018,"2017-10-16","2020-09-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P6K-HVES-5G [240V]    ","Y","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",6.0039999999999996,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,130,330,450,0.6,1.2010000000000001,1.8009999999999999,3.0019999999999998,4.5030000000000001,6.0039999999999996,94.9,96.12,96.76,97.3,97.32,96.48,97.05,95.55,96.98,97.4,97.42,97.37,97.95,97.32,95.31,96.91,97.48,97.59,97.58,97.58,97.45,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-1P7K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",7,240,97.5,"Intertek","[06/30/2019]","[08_01]","2018-10-15","[06/30/2019]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"Y","N",7,null,null,250,380,500,0.70000000000000007,1.4000000000000001,2.1,3.5,5.25,7,94.960672962684697,96.155042573333731,96.831370621296372,97.356481029596281,97.353815384428287,96.539846188084397,97.095319001096072,95.584550496798755,97.012296652157914,97.429006533355562,97.5,97.509041106010642,97.043716045573291,97.372455224946819,95.320789193775596,96.955133599404505,97.520125461640987,97.663923408425362,97.598820047351609,97.595908209399227,97.479597254453807,"2017-10-16","2020-09-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P7K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",7.0060000000000002,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,160,330,450,0.70099999999999996,1.401,2.1019999999999999,3.5030000000000001,5.2539999999999996,7.0060000000000002,94.96,96.16,96.83,97.36,97.35,96.54,97.1,95.58,97.01,97.43,97.5,97.51,97.04,97.37,95.32,96.96,97.52,97.66,97.6,97.6,97.48,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-1P7.6K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",7.6,240,97.5,"Intertek","[06/30/2019]","[08_01]","2018-10-15","[06/30/2019]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"N","N",7,null,null,200,380,500,0.76,1.52,2.2799999999999998,3.8,5.6999999999999993,7.6,95.054544778915016,96.16013372200068,96.88851941562136,97.343299079676314,97.146845964984067,96.576007736626707,96.995532362136117,95.630951815313068,97.183559291499847,97.475293348378585,97.779406666709733,97.346973662421036,97.896154149605167,97.403830387565392,95.358595879365339,96.753366238298483,97.605982628900193,97.82415064028558,97.854089025575689,97.709442999404004,97.655941030542849,"2017-10-16","2020-09-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P7.6K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",7.6029999999999998,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,175,330,450,0.76,1.5209999999999999,2.2810000000000001,3.8010000000000002,5.702,7.6029999999999998,95.05,96.16,96.89,97.34,97.15,96.58,97,95.63,97.18,97.48,97.78,97.35,97.9,97.4,95.36,96.75,97.61,97.82,97.85,97.71,97.66,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-1P8K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","8 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",8,240,97.5,"Intertek","[06/30/2019]","[08_01]","2018-10-15","[06/30/2019]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"N","N",6,null,null,250,380,500,0.8,1.6,2.4,4,6,8,95.115332913266315,96.175462439271996,96.938998105272361,97.369277320040268,97.182721638284903,96.631909451106281,97.0320523891817,95.656514167277948,97.239896453210392,97.421688340363517,97.547855541188852,97.702384479805346,96.955872352369511,97.493965045760234,95.375683381401501,96.746576974605176,97.610663471114009,97.817300881360168,97.852795609423126,97.705330884128529,97.654517202806332,"2017-10-16","2020-09-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P8K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","8 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",8.0060000000000002,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,185,330,450,0.80100000000000005,1.601,2.4020000000000001,4.0030000000000001,6.0039999999999996,8.0060000000000002,95.12,96.18,96.94,97.37,97.18,96.63,97.03,95.66,97.24,97.42,97.55,97.7,96.96,97.49,95.38,96.75,97.61,97.82,97.85,97.71,97.65,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-1P9K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","9 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",9,240,97.5,"Intertek","[06/30/2019]","[08_01]","2018-10-15","[06/30/2019]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"N","N",7,null,null,250,380,500,0.9,1.8,2.6999999999999997,4.5,6.75,9,95.141976475572321,96.753278905181432,96.999162712106937,97.486554101075555,97.37298741629192,96.995723796850655,97.212888411437916,95.717959215198519,97.274406726890376,97.447757410264941,97.608752800446155,97.75013123951851,97.106407965630538,97.546897637504287,95.577424654150192,96.739230404181313,97.661059952596048,97.821299906822475,97.821478007725091,97.707574028943398,97.652620726660786,"2017-10-16","2020-09-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P9K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",9.0060000000000002,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,210,330,450,0.90100000000000002,1.8009999999999999,2.702,4.5030000000000001,6.7539999999999996,9.0060000000000002,95.14,96.75,97,97.49,97.37,97,97.21,95.72,97.27,97.45,97.61,97.75,97.11,97.55,95.58,96.74,97.66,97.82,97.82,97.71,97.65,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-1P10K-4G-US [240V]","N","Y","Y","Y","Y","Y*","Y","10 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",10,240,97.5,"Intertek","[06/30/2019]","[08_01]","2018-10-15","[06/30/2019]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"N","N",7,null,null,250,380,500,1,2,3,5,7.5,10,95.2,96.8,97.1,97.5,97.6,97.1,97.4,95.3,96.3,97.6,97.7,97.7,97.2,97.5,95.6,96.8,97.7,97.8,97.8,97.7,97.6,"2017-10-16","2020-09-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P10K-HVES-5G [240V]    ","Y","Y","Y","Y","Y","Y*","Y","10 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",10.005000000000001,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,230,330,450,1,2.0009999999999999,3.0009999999999999,5.0019999999999998,7.5039999999999996,10.005000000000001,95.18,96.78,97.08,97.55,97.61,97.06,97.37,95.3,96.32,97.58,97.66,97.73,97.21,97.5,95.6,96.8,97.68,97.79,97.81,97.71,97.65,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-25K-US-LSW [480V]","N","Y","Y","Y","Y","Y*","Y","25 kW, 480 Vac Grid Support Utility Interactive Inverter",24.957999999999998,480,98.5,"Intertek","[10/30/2019]","[1D]","2020-09-11","[10/30/2019]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,null,null,1,null,null,347,470,800,2.4958062000000001,4.9916124000000002,7.4874185999999989,12.479030999999999,18.718546499999999,24.958061999999998,97.853771727652003,98.386845403985191,98.419952387549216,98.566500213491139,98.410525960115365,98.354027246196793,98.418132591815365,98.000100000000003,98.427499999999981,98.417400000000015,98.665900000000008,98.423000000000002,98.347599999999986,98.452876000000003,97.893000000000001,98.418700000000015,98.492999999999995,98.685000000000002,98.465900000000005,98.373000000000005,98.485242,"2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-25K-US [480V]","N","Y","Y","Y","N","N","N","25 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",25,480,98,"Intertek","[01/29/2018]","[1D]","2018-10-15","[01/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",14,null,null,580,650,780,2.5,5,7.5,12.5,18.75,25,97.1,97.4,97.6,97.9,98,97.8,97.9,97.1,97.3,97.6,97.8,98.3,97.6,98,97.2,97.4,97.7,97.8,98,97.5,97.9,"2018-02-15","2019-11-15"]
["Ginlong Technologies Co., Ltd.","Solis-25K-US-SW [480V]","N","Y","Y","Y","Y","Y*","Y","25 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box",25,480,98,"Intertek","[12/21/2018]","[1D]","2019-03-01","[12/21/2018]","2020-08-21","CSA Group","2020-07-20","2020-08-21",null,"N","N",14,null,null,580,650,770,2.5,5,7.5,12.5,18.75,25,97.142964722609719,97.310266944970607,97.558210787909843,97.902019188713425,98.186266472133454,97.785643565531629,97.945644668839236,97.136908002620146,97.294740203904553,97.401291401475831,97.883743867106773,98.295370114052176,97.750866187372679,97.978043980385848,97.236056040998633,97.395994266218807,97.543490263387042,97.692214831859445,98.001190746739226,97.48550403188284,97.794732198613758,"2019-03-01","2020-08-21"]
["Ginlong Technologies Co., Ltd.","Solis-30K-US-LSW [480V]","N","Y","Y","Y","Y","Y*","Y","30 kW, 480 Vac Grid Support Utility Interactive Inverter",29.948,480,98.5,"Intertek","[10/30/2019]","[1D]","2020-09-11","[10/30/2019]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,null,null,1,null,null,417,700,800,2.9947656600000001,5.9895313200000002,8.9842969799999999,14.973828299999999,22.460742449999998,29.947656599999998,97.768902305203113,98.391990453870477,98.434352470454385,98.566898759988248,98.412125272315521,98.316637698776148,98.415784930219743,97.813999999999993,98.424199999999999,98.504000000000005,98.650999999999996,98.419999999999987,98.356000000000023,98.451359999999994,97.890000000000015,98.427900000000022,98.516999999999996,98.6982,98.451000000000008,98.365000000000009,98.482937000000007,"2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-30K-US [480V]","N","Y","Y","Y","N","N","N","30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",30,480,98,"Intertek","[01/29/2018]","[1D]","2018-10-15","[01/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",15,null,null,580,650,780,3,6,9,15,22.5,30,97.1,97.9,97.9,98.3,97.5,97.9,97.8,97.4,98.1,98.1,98.4,98.1,97.9,98.1,97.1,97.9,98,98.3,98,97.8,98,"2018-02-15","2019-11-15"]
["Ginlong Technologies Co., Ltd.","Solis-30K-US-SW [480V]","N","Y","Y","Y","Y","Y*","Y","30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box",30,480,98,"Intertek","[12/21/2018]","[1D]","2019-03-02","[12/21/2018]","2020-08-21","CSA Group","2020-07-20","2020-08-21",null,"N","N",15,null,null,580,650,780,3,6,9,15,22.5,30,97.136729034962897,97.91235168892814,97.904963869081769,98.308894833573305,97.870536038966534,97.917405124902231,97.94180468208252,97.378314041689322,98.038837889530924,98.035886776299634,98.347723576110241,98.11389303563567,97.915010820497599,98.110516670195011,97.119954609958342,97.865597999954872,97.961685543933498,98.238894650235139,97.96866928700517,97.810325302197526,97.977559213440088,"2019-03-01","2020-08-21"]
["Ginlong Technologies Co., Ltd.","Solis-36K-US-LSW [480V]","N","Y","Y","Y","Y","Y*","Y","36 kW, 480 Vac Grid Support Utility Interactive Inverter",35.924999999999997,480,98.5,"Intertek","[10/30/2019]","[1D]","2020-09-11","[10/30/2019]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,null,null,1,null,null,500,700,800,3.592505800000001,7.1850116000000019,10.777517400000002,17.962529000000004,26.943793500000005,35.925058000000007,97.743542748672965,98.364995951458212,98.406126214457615,98.579027787829361,98.430897196517691,98.307273880710142,98.42206169688879,97.796000000000006,98.347400000000022,98.464999999999989,98.635999999999981,98.468000000000004,98.334000000000003,98.463310000000007,97.826000000000008,98.403800000000004,98.495999999999995,98.662100000000009,98.48299999999999,98.319000000000003,98.483730999999992,"2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-36K-US [480V]","N","Y","Y","Y","N","N","N","36 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",36,480,98,"Intertek","[01/29/2018]","[1D]","2018-10-15","[01/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",15,null,null,580,650,780,3.6,7.2,10.8,18,27,36,97.3,98.2,98.1,98.4,97.6,98.1,97.9,97.7,98.3,98.3,98.4,98.3,98.1,98.3,97.4,98.1,98.2,98.3,98.2,98.1,98.2,"2018-02-15","2019-11-15"]
["Ginlong Technologies Co., Ltd.","Solis-36K-US-F-SW [480V]","N","Y","Y","Y","Y","Y*","Y","36 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box and external Fan ",36,480,98,"Intertek","[12/21/2018]","[1D]","2019-03-01","[12/21/2018]","2020-08-21","CSA Group","2020-07-20","2020-08-21",null,"N","N",15,null,null,580,650,780,3.6,7.2,10.799999999999999,18,27,36,97.352610179015386,98.152707488253839,98.120660490393703,98.34565406369245,98.025094302751029,98.157804634629812,98.08999660598549,97.637315799515903,98.323917384796545,98.259065626094156,98.423751785147246,98.357299529090184,98.144570884666294,98.318361545883803,97.374218812243754,98.154013131424975,98.208865571837634,98.375693057759193,98.170440747004449,98.083298315932467,98.181127331519932,"2019-03-01","2020-08-21"]
["Ginlong Technologies Co., Ltd.","Solis-36K-US-SW [480V]","N","Y","Y","Y","Y","Y*","Y","36 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box",36,480,98,"Intertek","[12/21/2018]","[1D]","2019-03-01","[12/21/2018]","2020-08-21","CSA Group","2020-07-20","2020-08-21",null,"N","N",15,null,null,580,650,780,3.6,7.2,10.799999999999999,18,27,36,97.355578045132162,98.146917292221246,98.113242472029853,98.345701137831327,98.021452704297786,98.148305437610048,98.086540527162839,97.654488278356141,98.316398063259214,98.259121423086086,98.438016064841605,98.34302453004014,98.1379196196186,98.313776360586488,97.362390657069383,98.153961833334407,98.213796105992046,98.374901951968553,98.171535410091963,98.075769292291866,98.18128089254526,"2019-03-01","2020-08-21"]
["Ginlong Technologies Co., Ltd.","Solis-40K-US-LSW [480V]","N","Y","Y","Y","Y","Y*","Y","40 kW, 480 Vac Grid Support Utility Interactive Inverter",39.926000000000002,480,98.5,"Intertek","[10/30/2019]","[1D]","2020-09-11","[10/30/2019]","2020-09-11","CSA Group","2020-07-20","2020-09-11",null,null,null,1,null,null,556,700,800,3.9925869200000004,7.9851738400000007,11.977760760000001,19.962934600000001,29.944401900000003,39.925869200000001,97.756568472373232,98.349904317363411,98.430978331530511,98.565106380262918,98.43188587334069,98.327263423100959,98.423410378427576,97.786999999999992,98.366899999999987,98.458999999999989,98.628,98.441000000000003,98.347000000000008,98.447865000000007,97.832000000000008,98.414799999999985,98.466000000000008,98.635000000000005,98.515000000000001,98.335999999999999,98.493040000000008,"2020-09-11"]
["Ginlong Technologies Co., Ltd.","Solis-40K-US [480V]","N","Y","Y","Y","N","N","N","40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",40,480,98.5,"Intertek","[01/29/2018]","[1D]","2018-10-15","[01/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,780,4,8,12,20,30,40,97.5,98,98.1,98.2,98.1,98,98.1,97.9,98.3,98.4,98.7,98.6,98.3,98.5,97.6,98.2,98.2,98.4,98.3,98.2,98.3,"2018-02-15","2019-11-15"]
["Ginlong Technologies Co., Ltd.","Solis-40K-US-F [480V]","N","Y","Y","Y","N","N","N","40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter with external Fan",40,480,98.5,"Intertek","[01/29/2018]","[1D]","2018-10-15","[01/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,780,4,8,12,20,30,40,97.5,98,98.1,98.2,98.1,97.7,98.1,97.8,98.3,98.4,98.6,98.5,98.3,98.5,97.6,98.1,98.2,98.4,98.3,98,98.3,"2018-02-15","2019-11-15"]
["Ginlong Technologies Co., Ltd.","Solis-40K-US-F-SW [480V]","N","Y","Y","Y","Y","Y*","Y","40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box and external Fan   ",40,480,98.5,"Intertek","[12/21/2018]","[1D]","2019-03-02","[12/21/2018]","2020-08-21","CSA Group","2020-07-20","2020-08-21",null,"N","N",1,null,null,580,650,780,4,8,12,20,30,40,97.470025307598263,98.006823686121322,98.057428071819388,98.197211562051521,98.113980664562945,98.029180485035397,98.089316769729265,97.925867299237069,98.308888937177215,98.392001764941469,98.714528238058236,98.572481627994733,98.34230976222382,98.530101031561941,97.582250848768538,98.156490052565275,98.193182081593463,98.435303308923267,98.348895960607109,98.244441064517957,98.302846993591785,"2019-03-01","2020-08-21"]
["Ginlong Technologies Co., Ltd.","Solis-40K-US-SW [480V]","N","Y","Y","Y","Y","Y*","Y","40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box",40,480,98.5,"Intertek","[12/21/2018]","[1D]","2019-03-02","[12/21/2018]","2020-08-21","CSA Group","2020-07-20","2020-08-21",null,"N","N",1,null,null,580,650,780,4,8,12,20,30,40,97.47774059338056,98.003904274929724,98.056390714442401,98.19522213581763,98.12583970822547,98.027356845132402,98.095131259352613,97.924650523872657,98.310478358411089,98.400182583606565,98.72105900754346,98.578524443130533,98.342023806171653,98.535673385660147,97.576353190610263,98.150441636686395,98.179486696378575,98.433666102320259,98.342812395871789,98.244022499188716,98.297076189282905,"2019-03-01","2020-08-21"]
["Ginlong Technologies Co., Ltd.","Solis-50K-US-F-LSW [480V]","N","Y","Y","Y","Y","Y*","Y"," 50 kW, 480 Vac Grid Support Utility Interactive Inverter    ",49.915999999999997,480,98.5,"Intertek","[06/17/2020]","[1D]","2020-09-01","[06/17/2020]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"N","N",1,null,null,568,720,850,4.9916124000000002,9.9832248000000003,14.974837199999998,24.958061999999998,37.437092999999997,49.916123999999996,97.751999999999995,98.364199999999997,98.433999999999997,98.585000000000008,98.419999999999987,98.313000000000002,98.421469999999999,97.790999999999997,98.380900000000011,98.446999999999989,98.644999999999982,98.443000000000012,98.352000000000004,98.452165000000008,97.84,98.411000000000001,98.483000000000004,98.679999999999993,98.493000000000009,98.320099999999996,98.492204999999998,"2020-09-01"]
["Ginlong Technologies Co., Ltd.","Solis-50K-US-LSW [480V]","N","Y","Y","Y","Y","Y*","Y"," 50 kW, 480 Vac Grid Support Utility Interactive Inverter    ",49.984000000000002,480,98.5,"Intertek","[06/17/2020]","[1D]","2020-09-01","[06/17/2020]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"N","N",1,null,null,568,720,850,4.99836642,9.99673284,14.99509926,24.9918321,37.487748150000002,49.9836642,97.743000000000009,98.389799999999994,98.433000000000021,98.552999999999997,98.436000000000007,98.350000000000009,98.425880000000006,97.793999999999997,98.358000000000033,98.448999999999998,98.655000000000001,98.436999999999983,98.310000000000016,98.448200000000014,97.805700000000002,98.413499999999999,98.477999999999994,98.721000000000004,98.474000000000004,98.358999999999995,98.490842999999998,"2020-09-01"]
["Ginlong Technologies Co., Ltd.","Solis-50K-US [480V]","N","Y","Y","Y","N","N","N","50 kW, 480 Vac, Fanless, 3-phase Grid Support Utility Interactive Inverter",50,480,98.5,"Intertek","[12/23/2017]","[19/01]","2018-10-15","[12/23/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,720,5,10,15,25,37.5,50,97.5,98.5,98.4,98.6,98.3,98.5,98.4,97.8,98.6,98.5,98.7,98.4,98.5,98.5,98,98.7,98.8,98.8,98.6,98.5,98.6,"2018-02-01","2019-11-15"]
["Ginlong Technologies Co., Ltd.","Solis-50K-US-F [480V]","N","Y","Y","Y","N","N","N","50 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",50,480,98.5,"Intertek","[12/23/2017]","[19/01]","2018-10-15","[12/23/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,720,5,10,15,25,37.5,50,97.74,98.44,98.46,98.58,98.45,98.35,98.44,97.8,98.53,98.55,98.7,98.51,98.4,98.52,97.88,98.58,98.65,98.76,98.57,98.46,98.59,"2018-02-01","2019-11-15"]
["Ginlong Technologies Co., Ltd.","Solis-50K-US-F-SW [480V]","N","Y","Y","Y","Y","Y*","Y","50 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",50,480,98.5,"Intertek","[12/25/2017];[10/30/2019]","[19/01];[1D]","2018-10-15","[12/25/2017];[10/30/2019]","2020-09-01","CSA Group","2020-07-15","2020-09-01",null,"N","N",1,null,null,580,650,720,5,10,15,25,37.5,50,97.73621,98.444220000000001,98.455920000000006,98.582179999999994,98.449969999999993,98.347470000000001,98.444490000000002,97.798339999999996,98.53134,98.552109999999999,98.700419999999994,98.512280000000004,98.395949999999999,98.523150000000001,97.876750000000001,98.578149999999994,98.650589999999994,98.759609999999995,98.567750000000004,98.464439999999996,98.585700000000003,"2018-02-01","2020-09-01"]
["Ginlong Technologies Co., Ltd.","Solis-50K-US-SW [480V]","N","Y","Y","Y","Y","Y*","Y","50 kW, 480 Vac, Fanless, 3-phase Grid Support Utility Interactive Inverter",50,480,98.5,"Intertek","[12/25/2017];[10/30/2019]","[19/01];[1D]","2018-10-15","[12/25/2017];[10/30/2019]","2020-09-01","CSA Group","2020-07-15","2020-09-01",null,"N","N",1,null,null,580,650,720,5,10,15,25,37.5,50,97.516660000000002,98.527910000000006,98.440969999999993,98.556190000000001,98.322069999999997,98.44641,98.369799999999998,97.746949999999998,98.550470000000004,98.522189999999995,98.653930000000003,98.433809999999994,98.488839999999996,98.47175,97.980519999999999,98.699969999999993,98.804749999999999,98.791889999999995,98.567930000000004,98.500640000000004,98.62312,"2018-02-01","2020-09-01"]
["Ginlong Technologies Co., Ltd.","Solis-60K-US-F-LSW [480V]","N","Y","Y","Y","Y","Y*","Y"," 60 kW, 480 Vac Grid Support Utility Interactive Inverter    ",59.933,480,98.5,"Intertek","[06/17/2020]","[1D]","2020-09-01","[06/17/2020]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"N","N",1,null,null,526,720,850,5.993277120000001,11.986554240000002,17.979831360000002,29.966385600000002,44.949578400000007,59.932771200000005,97.739000000000004,98.411000000000016,98.443999999999988,98.579000000000008,98.411999999999992,98.280000000000015,98.41734000000001,97.786999999999992,98.4024,98.465000000000003,98.622,98.441000000000003,98.341999999999985,98.448850000000007,97.808999999999997,98.433999999999997,98.521999999999991,98.688999999999993,98.47999999999999,98.325999999999993,98.49208999999999,"2020-09-01"]
["Ginlong Technologies Co., Ltd.","Solis-60K-US-F [480V]","N","Y","Y","Y","N","N","N","60 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",60,480,98.5,"Intertek","[12/23/2017]","[19/01]","2018-10-15","[12/23/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,720,6,12,18,30,45,60,97.73,98.31,98.42,98.55,98.37,98.22,98.38,97.82,98.45,98.54,98.63,98.5,98.33,98.49,97.86,98.53,98.59,98.7,98.55,98.45,98.55,"2018-02-01","2019-11-15"]
["Ginlong Technologies Co., Ltd.","Solis-60K-US-F-SW [480V]","N","Y","Y","Y","Y","Y*","Y","60 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",60,480,98.5,"Intertek","[12/25/2017];[10/30/2019]","[19/01];[1D]","2018-10-15","[12/25/2017];[10/30/2019]","2020-09-01","CSA Group","2020-07-15","2020-09-01",null,"N","N",1,null,null,580,650,720,6,12,18,30,45,60,97.725110000000001,98.310810000000004,98.418899999999994,98.550129999999996,98.371089999999995,98.223780000000005,98.378209999999996,97.822659999999999,98.449550000000002,98.540400000000005,98.626189999999994,98.49897,98.329369999999997,98.492649999999998,97.862219999999994,98.525220000000004,98.586510000000004,98.699969999999993,98.55256,98.449910000000003,98.553479999999993,"2018-02-01","2020-09-01"]
["Ginlong Technologies Co., Ltd.","Solis-66K-US-F-LSW [480V]","N","Y","Y","Y","Y","Y*","Y"," 66 kW, 480 Vac Grid Support Utility Interactive Inverter    ",65.926000000000002,480,98.5,"Intertek","[06/17/2020]","[1D]","2020-09-01","[06/17/2020]","2020-09-01","CSA Group","2020-07-20","2020-09-01",null,"N","N",1,null,null,579,720,850,6.592550720000002,13.185101440000004,19.777652160000002,32.962753600000006,49.444130400000006,65.925507200000013,97.751999999999995,98.350999999999999,98.412999999999997,98.587999999999994,98.419999999999987,98.309999999999988,98.418769999999981,97.772999999999996,98.342999999999989,98.47999999999999,98.676999999999992,98.436000000000007,98.318999999999988,98.45487,97.806999999999988,98.368999999999986,98.501000000000005,98.657000000000011,98.487000000000009,98.320999999999998,98.482980000000012,"2020-09-01"]
["Ginlong Technologies Co., Ltd.","Solis-66K-US-F [480V]","N","Y","Y","Y","N","N","N","66 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",66,480,98.5,"Intertek","[12/23/2017]","[19/01]","2018-10-15","[12/23/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,580,650,720,6.6,13.2,19.8,33,49.5,66,97.57,98.38,98.48,98.56,98.42,98.31,98.42,97.74,98.5,98.55,98.7,98.5,98.39,98.51,97.77,98.67,98.65,98.77,98.56,98.49,98.58,"2018-02-01","2019-11-15"]
["Ginlong Technologies Co., Ltd.","Solis-66K-US-F-SW [480V]","N","Y","Y","Y","Y","Y*","Y","66 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter     ",66,480,98.5,"Intertek","[12/25/2017];[10/30/2019]","[19/01];[1D]","2018-10-15","[12/25/2017];[10/30/2019]","2020-09-01","CSA Group","2020-07-15","2020-09-01","No Information Submitted","N","N",1,null,null,580,650,720,6.6,13.2,19.8,33,49.5,66,97.571680000000001,98.376260000000002,98.476309999999998,98.563289999999995,98.421390000000002,98.311779999999999,98.416049999999998,97.744069999999994,98.500609999999995,98.553719999999998,98.7042,98.498869999999997,98.390150000000006,98.513030000000001,97.772109999999998,98.671279999999996,98.653779999999998,98.773750000000007,98.556129999999996,98.491799999999998,98.584729999999993,"2018-02-01","2020-09-01"]
["Ginlong Technologies Co., Ltd.","Solis-75K-5G-US [480V]","N","Y","Y","Y","Y","Y*","Y","75 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive Inverter ",75,480,98.5,"CSA Group","[09/03/2020]","[1C]","2020-10-01","[09/03/2020]","2020-10-01","CSA Group","2020-08-20","2020-10-01",null,"N","N",1,null,null,550,720,850,7.5002329129464727,15.000465825892945,22.500698738839418,37.501164564732363,56.251746847098545,75.002329129464727,98.147025032417488,98.538297364749269,98.524999107031618,98.623779108232739,98.379194007296135,98.216237003843389,98.438574049165965,98.17746730354655,98.521488547158611,98.543858150753337,98.666551658550517,98.444472139663873,98.238359986110964,98.485900179213203,98.244021361705535,98.573713583958948,99.014770545419339,98.621144781425926,98.5743288559581,98.294002446800633,98.609753819213765,"2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-80K-5G-US [480V]","N","Y","Y","Y","Y","Y*","Y","85 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter",80,480,98.5,"CSA Group","[09/03/2020]","[1C]","2020-10-01","[09/03/2020]","2020-10-01","CSA Group","2020-08-20","2020-10-01",null,"N","N",1,null,null,550,720,850,8.0003050776117188,16.000610155223438,24.000915232835151,40.001525388058589,60.002288082087887,80.003050776117178,98.144056766704836,98.536304442013858,98.524086928927204,98.626467261140164,98.379382268335164,98.212328397713335,98.438715071182898,98.176411874265156,98.523181299386493,98.543033514575981,98.665352417337218,98.444660833820109,98.242401261303542,98.4858938743197,98.245072716984239,98.577628018526184,99.014921894647586,98.627129098799657,98.575015590597445,98.289762113147972,98.611418416385362,"2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-90K-5G-US [480V]","N","Y","Y","Y","Y","Y*","Y","90 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter ",90,480,98.5,"CSA Group","[09/03/2020]","[1C]","2020-10-01","[09/03/2020]","2020-10-01","CSA Group","2020-08-20","2020-10-01",null,"N","N",1,null,null,550,720,850,9.0004863717252821,18.000972743450564,27.001459115175845,45.002431858626409,67.503647787939613,90.004863717252817,98.142462468207924,98.530089186513663,98.517514631575267,98.620241445136358,98.381968147783681,98.212915859518517,98.437644328622937,98.167699369061353,98.520772502298982,98.536703570264194,98.657051898547635,98.44293645368937,98.229611437880564,98.481368819353506,98.240022511847229,98.571329194013131,99.015803036201163,98.619661805706784,98.571478964294428,98.291391257797599,98.607646117683032,"2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-100K-5G-US [480V]","N","Y","Y","Y","Y","Y*","Y","100 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter ",100,480,98.5,"CSA Group","[09/03/2020]","[1C]","2020-10-01","[09/03/2020]","2020-10-01","CSA Group","2020-08-20","2020-10-01",null,"N","N",1,null,null,550,720,850,10.000404076371181,20.000808152742362,30.001212229113538,50.0020203818559,75.003030572783842,100.0040407637118,98.140564410825306,98.526079453185915,98.519674341535762,98.618874231032336,98.379626790887073,98.210929571364574,98.43599973633178,98.16926795541994,98.524401802932246,98.538788389017313,98.658248405104047,98.442025680353225,98.230123739739625,98.481657377691548,98.242034120221604,98.571351197024953,99.013935310145271,98.618839828970707,98.571012971722467,98.288911860939493,98.606959994021295,"2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-100K-EHV-5G [600V]","N","Y","Y","Y","Y","Y*","Y","100 kW, 600 Vac, 3-phase Grid Support Utility Interactive Inverter\n\n",100,600,98.5,"CSA Group","[06/06/2019]","[V08]","2019-08-15","[06/06/2019]","2020-10-01","CSA Group","2020-08-20","2020-10-01",null,"N","N",1,null,null,860,950,1250,10.008376872392056,20.016753744784111,30.025130617176167,50.041884361960278,75.062826542940414,100.08376872392056,98.966206181997933,99.044217530422429,98.885922188641686,98.972176695033994,98.899974942737515,98.647465567515411,98.910686890421829,98.598342692264168,98.791343607577886,98.872108977472607,98.800420700553374,98.612276160528239,98.635953773920761,98.692546366258384,98.276747082484334,98.628147930574329,98.640594611755773,98.629605304272232,98.467752882813357,98.264444444464772,98.512696997250274,"2019-08-15","2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-125K-EHV-5G [600V]","N","Y","Y","Y","Y","Y*","Y","125 kW, 600 Vac, 3-phase Grid Support Utility Interactive Inverter  \n",125,600,98.5,"CSA Group","[06/06/2019]","[V08]","2019-08-15","[06/06/2019]","2020-10-01","CSA Group","2020-08-20","2020-10-01",null,"N","N",1,null,null,860,950,1250,12.508265174439627,25.016530348879254,37.524795523318879,62.541325872198129,93.811988808297201,125.08265174439626,98.91665522812005,99.027907871118359,98.940968438394933,98.94618560587287,98.85207356138136,98.746414168721444,98.888596488489611,98.5469464246206,98.840474251603069,98.772193840490829,98.80392771433803,98.633809068909542,98.62883538295489,98.692750226104664,98.280518048463477,98.699974088322037,98.794745388070737,98.661885226486504,98.467930647761705,98.300639692202196,98.543619998409113,"2019-08-15","2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-125K1-EHV-5G [600V]","N","Y","Y","Y","Y","Y*","Y","125 kW, 600 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter, Single-Input ",125.083,600,98.5,"CSA Group","[08/21/2020]","[V08]","2020-10-01","[08/21/2020]","2020-10-01","CSA Group","2020-08-20","2020-10-01",null,"N","N",1,null,null,860,1080,1250,12.508265174439641,25.016530348879282,37.524795523318922,62.5413258721982,93.811988808297301,125.0826517443964,98.244150078788806,98.633881987410717,98.622049586795669,98.725008043697628,98.477330413578301,98.313568328361839,98.537021277728655,98.273504152953748,98.629869980182661,98.646207777090751,98.760872825293617,98.546891900995405,98.335963954530357,98.586412796943918,98.343571962692792,98.673361179391733,99.115933131286468,98.721105260927743,98.67586508935122,98.396605109774001,98.710793770871362,"2020-10-01"]
["Ginlong Technologies Co., Ltd.","Solis-185K-EHV-5G-US [600V]","N","Y","Y","Y","Y","Y*","Y","185 kW, 600 Vac Grid Support Utility Interactive Inverter",185.005,600,98.5,"CSA Group","[11/04/2020]","[V18]","2021-01-11","[11/04/2020]","2021-01-11","CSA Group","2020-11-04","2021-01-11",null,"N","N",1,null,null,850,1080,1300,18.500525910334222,37.001051820668444,55.501577731002662,92.502629551671106,138.75394432750664,185.00525910334221,97.817999999999984,98.477000000000018,98.621000000000009,98.626999999999995,98.457000000000022,98.25,98.477470000000011,97.932000000000016,98.565999999999988,98.653999999999982,98.581999999999994,98.403999999999996,98.181000000000012,98.449450000000013,97.649999999999991,98.488,98.579000000000008,98.893000000000001,98.698000000000022,98.444000000000031,98.659550000000024,"2021-01-11"]
["Ginlong Technologies Co., Ltd.","Solis-255K-EHV-5G-US [800V]","N","Y","Y","Y","Y","Y*","Y","255 kW, 800 Vac Grid Support Utility Interactive Inverter",255.01300000000001,800,98.5,"CSA Group","[11/04/2020]","[V18]","2021-01-11","[11/04/2020]","2021-01-11","CSA Group","2020-11-04","2021-01-11",null,"N","N",1,null,null,850,1080,1300,25.501261036265959,51.002522072531917,76.503783108797876,127.50630518132979,191.25945777199468,255.01261036265959,97.817999999999984,98.477000000000004,98.621000000000009,98.626999999999995,98.457000000000022,98.25,98.477470000000011,97.64500000000001,98.298999999999978,98.49499999999999,98.545999999999978,98.427000000000007,98.254999999999995,98.413869999999989,98.058999999999997,98.701000000000008,98.84,98.834999999999994,98.696000000000026,98.520999999999987,98.708490000000012,"2021-01-11"]
["Hanwha Q CELLS","Q.PEAK DUO BLK-G6+/AC 340 [240V]","N","Y","Y","Y","Y","Y*","Y","340 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Q.PEAK DUO BLK-G6+ 340. Microinverter: IQ7PLUS-72-x-ACM-US-y [240V]",0.28999999999999998,240,97,"TUV Rheinland of North America","[06/16/2020]","[V04.18.02]","2020-07-13","[06/16/2020]","2020-07-13","UL","2020-03-18","2020-07-13","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2020-07-13"]
["Hanwha Q CELLS","Q.PEAK DUO BLK-G6+/AC 345 [240V]","N","Y","Y","Y","Y","Y*","Y","345 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Q.PEAK DUO BLK-G6+ 345. Microinverter: IQ7PLUS-72-x-ACM-US-y [240V]",0.28999999999999998,240,97,"TUV Rheinland of North America","[06/16/2020]","[V04.18.02]","2020-07-13","[06/16/2020]","2020-07-13","UL","2020-03-18","2020-07-13","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.9000000000000001E-2,5.8000000000000003E-2,8.6999999999999994E-2,0.14499999999999999,0.2175,0.28999999999999998,95.003640000000004,96.245670000000004,97.1477,97.429069999999996,97.164060000000006,96.603870000000001,97.057403100000002,94.161959999999993,95.57517,96.780240000000006,97.495289999999997,97.442819999999998,97.156899999999993,97.135416199999995,93.32141,94.805890000000005,96.394019999999998,97.273160000000004,97.309510000000003,97.075739999999996,96.8956242,"2020-07-13"]
["Hanwha Q CELLS America Inc.","Q.HOME+ HYB-G1-6.0 [240V]","Y","Y","Y","Y","Y","Y*","Y","6.0 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",5.57,240,94,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2021-01-11","[10/23/2020]","2021-01-11","Intertek","2020-09-11","2021-01-11",null,"N","N",25,null,null,240,335,425,0.57500000000000007,1.1500000000000001,1.7249999999999999,2.875,4.3125,5.75,86.869682822533804,91.494323337741122,93.197507125817154,94.277347956539373,94.528577104512152,94.419480087783,93.852567275540324,86.534692544508331,91.719237390678572,93.532641876704261,94.760758659216464,95.116012615226765,95.142514472111017,94.339638324629973,85.944083659918661,91.055826867889806,93.119565276460762,94.55685225894733,95.055933937626449,95.188812247401856,94.160927096657588,"2021-01-11"]
["Hanwha Q CELLS America Inc.","Q.HOME+ HYB-G1-7.0 [240V]","Y","Y","Y","Y","Y","Y*","Y","7.0 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",6.6660000000000004,240,94.5,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2021-01-11","[10/23/2020]","2021-01-11","Intertek","2020-09-11","2021-01-11",null,"N","N",25,null,null,290,360,425,0.66660000000000008,1.3332000000000002,1.9998,3.3330000000000002,4.9995000000000003,6.6660000000000004,88.19254532766071,92.480024599906656,93.864222646892841,94.728177374748682,94.859277550957373,94.661603922022621,94.31682430753466,87.895016741997523,92.552209013216427,93.98568096527471,94.939255036123782,95.145985429310571,95.084346217536066,94.540525982171076,87.188290385772305,91.840278359010497,93.665346252959509,94.812415113107377,95.188151694943144,95.183576013873704,94.438893456502669,"2021-01-11"]
["Hanwha Q CELLS America Inc.","Q.HOME+ HYB-G1-7.6 [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",7.6420000000000003,240,95.5,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2020-04-13","[10/23/2020]","2020-12-11","Intertek","2020-09-25","2020-10-12",null,"N","N",44,null,null,304,402,500,0.76415320000000009,1.5283064000000002,2.2924595999999999,3.8207660000000003,5.7311490000000003,7.6415320000000007,91.707418177902383,94.572943893510569,95.343208396678733,95.732834528334209,95.650063634275952,95.385614239539109,95.40583861848647,90.557349146015056,94.483695582739486,95.237254457268747,95.752187855671906,95.755162516040727,95.573013398331213,95.411795532959076,93.454639453611506,95.564299299611108,96.165924657149233,96.488739138122966,96.365110394539414,96.144925249431296,96.199701492566206,"2020-04-13","2020-12-11"]
["Hanwha Q CELLS America Inc.","Q.HOME+ HYB-G1-8.6 [240V]","Y","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",8.6039999999999992,240,96,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2020-04-13","[10/23/2020]","2020-12-11","Intertek","2020-09-25","2020-10-12",null,"N","N",40,null,null,258,379,500,0.8604440000000001,1.7208880000000002,2.5813320000000002,4.3022200000000002,6.4533300000000002,8.6044400000000003,92.699334355597514,94.539928618718363,95.297824749048559,95.613611296666747,95.424147601271741,94.940413722572345,95.271386062148309,92.844051102514101,95.289415785898782,95.970144903059008,96.182450712551415,95.871598553910871,95.529337174346537,95.781378963688468,93.694083911121623,95.776806518196878,96.274499321609412,96.519408732377741,96.296844266964186,95.892164355116009,96.19055511399398,"2020-04-13","2020-12-11"]
["HiQ Solar","TSXL480-10k [480V]","N","Y","Y","Y","N","N","N","9.975 kW, 480 Vac Grid Support Utility Interactive Inverter    ",9.9749999999999996,480,97.5,"UL","[09/28/2018]","[0.28]","2019-02-01","[09/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",8.3000000000000007,null,null,450,750,850,0.99750000000000005,1.9950000000000001,2.9924999999999997,4.9874999999999998,7.4812499999999993,9.9749999999999996,94.115714285714276,96.777142857142849,97.342857142857142,97.727142857142866,97.695714285714303,97.517142857142858,97.4619142857143,94.11,96.84571428571428,97.644285714285701,98.161428571428573,98.220000000000013,98.139999999999986,97.901500000000013,93.187142857142859,96.460000000000008,97.455714285714294,98.102857142857147,98.238571428571433,98.200000000000017,97.823214285714286,"2018-11-01","2019-02-15"]
["Hoymiles Power Electronics Inc.","HM-300N [240V]","N","Y","Y","Y","Y","Y*","Y","295 W, 240 Vac Grid Support Utility Interactive Microinverter",0.29542000000000002,240,96.5,"CSA Group","[06/12/2020]","[V01.01.00]","2020-08-03","[06/12/2020]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.108,null,null,29,40,48,2.9541800000000003E-2,5.9083600000000007E-2,8.8625400000000007E-2,0.14770900000000001,0.22156350000000002,0.29541800000000001,95.712142857142879,96.128238095238103,96.196380952380963,96.433047619047642,96.606476190476201,96.105476190476196,96.436109523809534,95.908952380952385,95.984619047619049,96.358952380952374,96.318095238095239,96.625666666666675,96.449047619047619,96.459519047619054,95.373714285714286,95.830904761904762,96.412857142857135,96.185047619047623,96.699285714285708,96.541000000000011,96.452568095238092,"2020-08-03","2021-03-11"]
["Hoymiles Power Electronics Inc.","HM-300NA [240V]","N","Y","Y","Y","Y","Y*","Y","295 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.29542000000000002,240,96.5,"CSA Group","[06/12/2020]","[V01.01.00]","2020-08-03","[06/12/2020]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.108,null,null,29,40,48,2.9541800000000003E-2,5.9083600000000007E-2,8.8625400000000007E-2,0.14770900000000001,0.22156350000000002,0.29541800000000001,95.712142857142879,96.128238095238103,96.196380952380963,96.433047619047642,96.606476190476201,96.105476190476196,96.436109523809534,95.908952380952385,95.984619047619049,96.358952380952374,96.318095238095239,96.625666666666675,96.449047619047619,96.459519047619054,95.373714285714286,95.830904761904762,96.412857142857135,96.185047619047623,96.699285714285708,96.541000000000011,96.452568095238092,"2020-08-03","2021-03-11"]
["Hoymiles Power Electronics Inc.","HM-300NT [240V]","N","Y","Y","Y","Y","Y*","Y","295 W, 240 Vac Grid Support Utility Interactive Microinverter",0.29542000000000002,240,96.5,"CSA Group","[06/12/2020]","[V01.01.00]","2020-08-03","[06/12/2020]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.108,null,null,29,40,48,2.9541800000000003E-2,5.9083600000000007E-2,8.8625400000000007E-2,0.14770900000000001,0.22156350000000002,0.29541800000000001,95.712142857142879,96.128238095238103,96.196380952380963,96.433047619047642,96.606476190476201,96.105476190476196,96.436109523809534,95.908952380952385,95.984619047619049,96.358952380952374,96.318095238095239,96.625666666666675,96.449047619047619,96.459519047619054,95.373714285714286,95.830904761904762,96.412857142857135,96.185047619047623,96.699285714285708,96.541000000000011,96.452568095238092,"2020-08-03","2021-03-11"]
["Hoymiles Power Electronics Inc.","HMS-300-1A-NA [240V]","N","Y","Y","Y","Y","Y*","Y","295 W, 240 Vac Grid Support Utility Interactive Microinverter",0.29542000000000002,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-11","[01/29/2021]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.108,null,null,29,40,48,2.9541800000000003E-2,5.9083600000000007E-2,8.8625400000000007E-2,0.14770900000000001,0.22156350000000002,0.29541800000000001,95.712142857142879,96.128238095238103,96.196380952380963,96.433047619047642,96.606476190476201,96.105476190476196,96.436109523809534,95.908952380952385,95.984619047619049,96.358952380952374,96.318095238095239,96.625666666666675,96.449047619047619,96.459519047619054,95.373714285714286,95.830904761904762,96.412857142857135,96.185047619047623,96.699285714285708,96.541000000000011,96.452568095238092,"2021-03-11"]
["Hoymiles Power Electronics Inc.","HMS-300-1D-NA [240V]","N","Y","Y","Y","Y","Y*","Y","295 W, 240 Vac Grid Support Utility Interactive Microinverter",0.29542000000000002,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-11","[01/29/2021]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.108,null,null,29,40,48,2.9541800000000003E-2,5.9083600000000007E-2,8.8625400000000007E-2,0.14770900000000001,0.22156350000000002,0.29541800000000001,95.712142857142879,96.128238095238103,96.196380952380963,96.433047619047642,96.606476190476201,96.105476190476196,96.436109523809534,95.908952380952385,95.984619047619049,96.358952380952374,96.318095238095239,96.625666666666675,96.449047619047619,96.459519047619054,95.373714285714286,95.830904761904762,96.412857142857135,96.185047619047623,96.699285714285708,96.541000000000011,96.452568095238092,"2021-03-11"]
["Hoymiles Power Electronics Inc.","HMS-300-1T-NA [240V]","N","Y","Y","Y","Y","Y*","Y","295 W, 240 Vac Grid Support Utility Interactive Microinverter ",0.29542000000000002,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-11","[01/29/2021]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.108,null,null,29,40,48,2.9541800000000003E-2,5.9083600000000007E-2,8.8625400000000007E-2,0.14770900000000001,0.22156350000000002,0.29541800000000001,95.712142857142879,96.128238095238103,96.196380952380963,96.433047619047642,96.606476190476201,96.105476190476196,96.436109523809534,95.908952380952385,95.984619047619049,96.358952380952374,96.318095238095239,96.625666666666675,96.449047619047619,96.459519047619054,95.373714285714286,95.830904761904762,96.412857142857135,96.185047619047623,96.699285714285708,96.541000000000011,96.452568095238092,"2021-03-11"]
["Hoymiles Power Electronics Inc.","HM-350N [240V]","N","Y","Y","Y","Y","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.34949999999999998,240,96.5,"CSA Group","[06/12/2020]","[V01.01.00]","2020-08-03","[06/12/2020]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,33,40,48,3.4949599999999997E-2,6.9899199999999995E-2,0.10484879999999999,0.17474799999999999,0.26212199999999997,0.34949599999999997,95.711714285714294,96.128380952380937,96.196476190476204,96.432904761904766,96.606428571428552,96.105285714285714,96.436046190476191,95.908714285714282,95.984714285714276,96.35866666666665,96.319190476190485,96.625047619047606,96.449047619047619,96.459381904761912,95.373523809523817,95.831047619047609,96.41290476190477,96.184380952380948,96.699904761904762,96.541190476190494,96.452770952380945,"2020-08-03","2021-03-11"]
["Hoymiles Power Electronics Inc.","HM-350NA [240V]","N","Y","Y","Y","Y","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.34949999999999998,240,96.5,"CSA Group","[06/12/2020]","[V01.01.00]","2020-08-03","[06/12/2020]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,33,40,48,3.4949599999999997E-2,6.9899199999999995E-2,0.10484879999999999,0.17474799999999999,0.26212199999999997,0.34949599999999997,95.711714285714294,96.128380952380937,96.196476190476204,96.432904761904766,96.606428571428552,96.105285714285714,96.436046190476191,95.908714285714282,95.984714285714276,96.35866666666665,96.319190476190485,96.625047619047606,96.449047619047619,96.459381904761912,95.373523809523817,95.831047619047609,96.41290476190477,96.184380952380948,96.699904761904762,96.541190476190494,96.452770952380945,"2020-08-03","2021-03-11"]
["Hoymiles Power Electronics Inc.","HM-350NT [240V]","N","Y","Y","Y","Y","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34949999999999998,240,96.5,"CSA Group","[06/12/2020]","[V01.01.00]","2020-08-03","[06/12/2020]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,33,40,48,3.4949599999999997E-2,6.9899199999999995E-2,0.10484879999999999,0.17474799999999999,0.26212199999999997,0.34949599999999997,95.711714285714294,96.128380952380937,96.196476190476204,96.432904761904766,96.606428571428552,96.105285714285714,96.436046190476191,95.908714285714282,95.984714285714276,96.35866666666665,96.319190476190485,96.625047619047606,96.449047619047619,96.459381904761912,95.373523809523817,95.831047619047609,96.41290476190477,96.184380952380948,96.699904761904762,96.541190476190494,96.452770952380945,"2020-08-03","2021-03-11"]
["Hoymiles Power Electronics Inc.","HMS-350-1A-NA [240V]","N","Y","Y","Y","Y","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34949999999999998,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-11","[01/29/2021]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,33,40,48,3.4949599999999997E-2,6.9899199999999995E-2,0.10484879999999999,0.17474799999999999,0.26212199999999997,0.34949599999999997,95.711714285714294,96.128380952380937,96.196476190476204,96.432904761904766,96.606428571428552,96.105285714285714,96.436046190476191,95.908714285714282,95.984714285714276,96.35866666666665,96.319190476190485,96.625047619047606,96.449047619047619,96.459381904761912,95.373523809523817,95.831047619047609,96.41290476190477,96.184380952380948,96.699904761904762,96.541190476190494,96.452770952380945,"2021-03-11"]
["Hoymiles Power Electronics Inc.","HMS-350-1D-NA [240V]","N","Y","Y","Y","Y","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34949999999999998,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-11","[01/29/2021]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,33,40,48,3.4949599999999997E-2,6.9899199999999995E-2,0.10484879999999999,0.17474799999999999,0.26212199999999997,0.34949599999999997,95.711714285714294,96.128380952380937,96.196476190476204,96.432904761904766,96.606428571428552,96.105285714285714,96.436046190476191,95.908714285714282,95.984714285714276,96.35866666666665,96.319190476190485,96.625047619047606,96.449047619047619,96.459381904761912,95.373523809523817,95.831047619047609,96.41290476190477,96.184380952380948,96.699904761904762,96.541190476190494,96.452770952380945,"2021-03-11"]
["Hoymiles Power Electronics Inc.","HMS-350-1T-NA [240V]","N","Y","Y","Y","Y","Y*","Y","349 W, 240 Vac Grid Support Utility Interactive Microinverter",0.34949999999999998,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-11","[01/29/2021]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,33,40,48,3.4949599999999997E-2,6.9899199999999995E-2,0.10484879999999999,0.17474799999999999,0.26212199999999997,0.34949599999999997,95.711714285714294,96.128380952380937,96.196476190476204,96.432904761904766,96.606428571428552,96.105285714285714,96.436046190476191,95.908714285714282,95.984714285714276,96.35866666666665,96.319190476190485,96.625047619047606,96.449047619047619,96.459381904761912,95.373523809523817,95.831047619047609,96.41290476190477,96.184380952380948,96.699904761904762,96.541190476190494,96.452770952380945,"2021-03-11"]
["Hoymiles Power Electronics Inc.","HM-400N [240V]","N","Y","Y","Y","Y","Y*","Y","382 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.38253999999999999,240,96.5,"CSA Group","[06/12/2020]","[V01.01.00]","2020-08-03","[06/12/2020]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,34,42,48,3.8254200000000002E-2,7.6508400000000004E-2,0.11476259999999999,0.191271,0.28690650000000001,0.38254199999999999,95.22842857142858,96.218428571428589,96.257238095238108,96.545714285714283,96.783523809523814,96.193761904761899,96.550482857142867,95.679523809523815,96.12704761904763,96.407190476190493,96.343142857142865,96.775857142857134,96.531571428571425,96.552239047619054,96.036380952380952,95.973476190476177,96.408523809523814,96.204571428571427,96.698857142857165,96.608857142857147,96.492949047619049,"2020-08-03","2021-03-11"]
["Hoymiles Power Electronics Inc.","HM-400NA [240V]","N","Y","Y","Y","Y","Y*","Y","382 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.38253999999999999,240,96.5,"CSA Group","[06/12/2020]","[V01.01.00]","2020-08-03","[06/12/2020]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,34,42,48,3.8254200000000002E-2,7.6508400000000004E-2,0.11476259999999999,0.191271,0.28690650000000001,0.38254199999999999,95.22842857142858,96.218428571428589,96.257238095238108,96.545714285714283,96.783523809523814,96.193761904761899,96.550482857142867,95.679523809523815,96.12704761904763,96.407190476190493,96.343142857142865,96.775857142857134,96.531571428571425,96.552239047619054,96.036380952380952,95.973476190476177,96.408523809523814,96.204571428571427,96.698857142857165,96.608857142857147,96.492949047619049,"2020-08-03","2021-03-11"]
["Hoymiles Power Electronics Inc.","HM-400NT [240V]","N","Y","Y","Y","Y","Y*","Y"," 382 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.38253999999999999,240,96.5,"CSA Group","[06/12/2020]","[V01.01.00]","2020-08-03","[06/12/2020]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,34,42,48,3.8254200000000002E-2,7.6508400000000004E-2,0.11476259999999999,0.191271,0.28690650000000001,0.38254199999999999,95.22842857142858,96.218428571428589,96.257238095238108,96.545714285714283,96.783523809523814,96.193761904761899,96.550482857142867,95.679523809523815,96.12704761904763,96.407190476190493,96.343142857142865,96.775857142857134,96.531571428571425,96.552239047619054,96.036380952380952,95.973476190476177,96.408523809523814,96.204571428571427,96.698857142857165,96.608857142857147,96.492949047619049,"2020-08-03","2021-03-11"]
["Hoymiles Power Electronics Inc.","HMS-400-1A-NA [240V]","N","Y","Y","Y","Y","Y*","Y","382 W, 240 Vac Grid Support Utility Interactive Microinverter",0.38253999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-11","[01/29/2021]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,34,42,48,3.7999999999999999E-2,7.6999999999999999E-2,0.115,0.191,0.28699999999999998,0.38300000000000001,95.23,96.22,96.26,96.55,96.78,96.19,96.55,95.68,96.13,96.41,96.34,96.78,96.53,96.55,96.04,95.97,96.41,96.2,96.7,96.61,96.49,"2021-03-11"]
["Hoymiles Power Electronics Inc.","HMS-400-1D-NA [240V]","N","Y","Y","Y","Y","Y*","Y","382 W, 240 Vac Grid Support Utility Interactive Microinverter",0.38253999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-11","[01/29/2021]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,34,42,48,3.7999999999999999E-2,7.6999999999999999E-2,0.115,0.191,0.28699999999999998,0.38300000000000001,95.23,96.22,96.26,96.55,96.78,96.19,96.55,95.68,96.13,96.41,96.34,96.78,96.53,96.55,96.04,95.97,96.41,96.2,96.7,96.61,96.49,"2021-03-11"]
["Hoymiles Power Electronics Inc.","HMS-400-1T-NA [240V]","N","Y","Y","Y","Y","Y*","Y","382 W, 240 Vac Grid Support Utility Interactive Microinverter",0.38253999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-11","[01/29/2021]","2021-03-11","CSA Group","2021-01-26","2021-03-11",null,"N","Y",0.105,null,null,34,42,48,3.7999999999999999E-2,7.6999999999999999E-2,0.115,0.191,0.28699999999999998,0.38300000000000001,95.23,96.22,96.26,96.55,96.78,96.19,96.55,95.68,96.13,96.41,96.34,96.78,96.53,96.55,96.04,95.97,96.41,96.2,96.7,96.61,96.49,"2021-03-11"]
["Hoymiles Power Electronics Inc.","HM-600N [240V]","N","Y","Y","Y","Y","Y","Y","590 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.59099999999999997,240,96.5,"CSA Group","[04/03/2020]","[V01.01.00]","2020-05-11","[04/03/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,29,37,48,5.9144600000000019E-2,0.11828920000000004,0.17743380000000003,0.29572300000000007,0.4435845000000001,0.59144600000000014,95.46676190476191,96.175619047619051,96.22780952380954,96.490095238095236,96.529809523809519,96.150190476190488,96.406017142857152,95.793095238095248,96.055714285714288,96.385380952380956,96.331333333333319,96.632047619047626,96.489238095238093,96.469782380952381,95.702380952380949,95.901142857142858,96.389190476190478,96.195428571428565,96.593333333333334,96.575619047619043,96.414142857142863,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-600NT [240V]","N","Y","Y","Y","Y","Y*","Y","590 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.59099999999999997,240,96.5,"CSA Group","[04/03/2020]","[V01.01.00]","2020-05-11","[04/03/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,29,37,48,5.9144600000000019E-2,0.11828920000000004,0.17743380000000003,0.29572300000000007,0.4435845000000001,0.59144600000000014,95.46676190476191,96.175619047619051,96.22780952380954,96.490095238095236,96.529809523809519,96.150190476190488,96.406017142857152,95.793095238095248,96.055714285714288,96.385380952380956,96.331333333333319,96.632047619047626,96.489238095238093,96.469782380952381,95.702380952380949,95.901142857142858,96.389190476190478,96.195428571428565,96.593333333333334,96.575619047619043,96.414142857142863,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-600-2D-NA [240V]","N","Y","Y","Y","Y","Y*","Y","590W, 240 Vac Grid Support Utility Interactive Microinverter",0.59099999999999997,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,29,37,48,5.9144600000000019E-2,0.11828920000000004,0.17743380000000003,0.29572300000000007,0.4435845000000001,0.59144600000000014,95.46676190476191,96.175619047619051,96.22780952380954,96.490095238095236,96.529809523809519,96.150190476190488,96.406017142857152,95.793095238095248,96.055714285714288,96.385380952380956,96.331333333333319,96.632047619047626,96.489238095238093,96.469782380952381,95.702380952380949,95.901142857142858,96.389190476190478,96.195428571428565,96.593333333333334,96.575619047619043,96.414142857142863,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-600-2T-NA [240V]","N","Y","Y","Y","Y","Y*","Y","590W, 240 Vac Grid Support Utility Interactive Microinverter",0.59099999999999997,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,29,37,48,5.9144600000000019E-2,0.11828920000000004,0.17743380000000003,0.29572300000000007,0.4435845000000001,0.59144600000000014,95.46676190476191,96.175619047619051,96.22780952380954,96.490095238095236,96.529809523809519,96.150190476190488,96.406017142857152,95.793095238095248,96.055714285714288,96.385380952380956,96.331333333333319,96.632047619047626,96.489238095238093,96.469782380952381,95.702380952380949,95.901142857142858,96.389190476190478,96.195428571428565,96.593333333333334,96.575619047619043,96.414142857142863,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-700N [240V]","N","Y","Y","Y","Y","Y","Y","696 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.69699999999999995,240,96.5,"CSA Group","[04/03/2020]","[V01.01.00]","2020-05-11","[04/03/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,33,42,48,6.9749800000000001E-2,0.1394996,0.20924939999999997,0.34874899999999998,0.52312349999999996,0.69749799999999995,95.466571428571442,96.175095238095238,96.227428571428547,96.489619047619044,96.530047619047622,96.150523809523818,96.405980476190493,95.79285714285713,96.05585714285715,96.385904761904754,96.332190476190476,96.631952380952384,96.48961904761903,96.469991428571433,95.702380952380949,95.900952380952376,96.389714285714277,96.332190476190476,96.593476190476181,96.575285714285698,96.442975238095229,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-700NT [240V]","N","Y","Y","Y","Y","Y*","Y","696 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.69699999999999995,240,96.5,"CSA Group","[04/03/2020]","[V01.01.00]","2020-05-11","[04/03/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,33,42,48,6.9749800000000001E-2,0.1394996,0.20924939999999997,0.34874899999999998,0.52312349999999996,0.69749799999999995,95.466571428571442,96.175095238095238,96.227428571428547,96.489619047619044,96.530047619047622,96.150523809523818,96.405980476190493,95.79285714285713,96.05585714285715,96.385904761904754,96.332190476190476,96.631952380952384,96.48961904761903,96.469991428571433,95.702380952380949,95.900952380952376,96.389714285714277,96.332190476190476,96.593476190476181,96.575285714285698,96.442975238095229,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-700-2D-NA [240V]","N","Y","Y","Y","Y","Y*","Y","696W, 240 Vac Grid Support Utility Interactive Microinverter",0.69699999999999995,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,33,42,48,6.9749800000000001E-2,0.1394996,0.20924939999999997,0.34874899999999998,0.52312349999999996,0.69749799999999995,95.466571428571442,96.175095238095238,96.227428571428547,96.489619047619044,96.530047619047622,96.150523809523818,96.405980476190493,95.79285714285713,96.05585714285715,96.385904761904754,96.332190476190476,96.631952380952384,96.48961904761903,96.469991428571433,95.702380952380949,95.900952380952376,96.389714285714277,96.332190476190476,96.593476190476181,96.575285714285698,96.442975238095229,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-700-2T-NA [240V]","N","Y","Y","Y","Y","Y*","Y","696W, 240 Vac Grid Support Utility Interactive Microinverter",0.69699999999999995,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,33,42,48,6.9749800000000001E-2,0.1394996,0.20924939999999997,0.34874899999999998,0.52312349999999996,0.69749799999999995,95.466571428571442,96.175095238095238,96.227428571428547,96.489619047619044,96.530047619047622,96.150523809523818,96.405980476190493,95.79285714285713,96.05585714285715,96.385904761904754,96.332190476190476,96.631952380952384,96.48961904761903,96.469991428571433,95.702380952380949,95.900952380952376,96.389714285714277,96.332190476190476,96.593476190476181,96.575285714285698,96.442975238095229,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-800N [240V]","N","Y","Y","Y","Y","Y","Y","766 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.76700000000000002,240,96.5,"CSA Group","[04/03/2020]","[V01.01.00]","2020-05-11","[04/03/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,34,42,48,7.6708800000000008E-2,0.15341760000000002,0.23012639999999998,0.383544,0.57531599999999994,0.76708799999999999,95.466952380952392,96.173380952380967,96.22742857142859,96.490142857142885,96.694571428571422,96.149809523809523,96.493181904761911,95.793190476190475,96.05585714285715,96.384380952380951,96.331904761904767,96.700714285714298,96.490285714285719,96.506239047619061,95.702809523809506,95.90157142857143,96.412190476190474,96.194571428571436,96.70052380952383,96.574952380952382,96.473539047619056,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-800NT [240V]","N","Y","Y","Y","Y","Y*","Y","766 W, 240 Vac Grid Support Utility Interactive Microinverter\n",0.76700000000000002,240,96.5,"CSA Group","[04/03/2020]","[V01.01.00]","2020-05-11","[04/03/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,34,42,48,7.6708800000000008E-2,0.15341760000000002,0.23012639999999998,0.383544,0.57531599999999994,0.76708799999999999,95.466952380952392,96.173380952380967,96.22742857142859,96.490142857142885,96.694571428571422,96.149809523809523,96.493181904761911,95.793190476190475,96.05585714285715,96.384380952380951,96.331904761904767,96.700714285714298,96.490285714285719,96.506239047619061,95.702809523809506,95.90157142857143,96.412190476190474,96.194571428571436,96.70052380952383,96.574952380952382,96.473539047619056,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-800-2D-NA [240V]","N","Y","Y","Y","Y","Y*","Y","766W, 240 Vac Grid Support Utility Interactive Microinverter",0.76700000000000002,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,34,42,48,7.6708800000000008E-2,0.15341760000000002,0.23012639999999998,0.383544,0.57531599999999994,0.76708799999999999,95.466952380952392,96.173380952380967,96.22742857142859,96.490142857142885,96.694571428571422,96.149809523809523,96.493181904761911,95.793190476190475,96.05585714285715,96.384380952380951,96.331904761904767,96.700714285714298,96.490285714285719,96.506239047619061,95.702809523809506,95.90157142857143,96.412190476190474,96.194571428571436,96.70052380952383,96.574952380952382,96.473539047619056,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-800-2T-NA [240V]","N","Y","Y","Y","Y","Y*","Y","766W, 240 Vac Grid Support Utility Interactive Microinverter",0.76700000000000002,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,34,42,48,7.6708800000000008E-2,0.15341760000000002,0.23012639999999998,0.383544,0.57531599999999994,0.76708799999999999,95.466952380952392,96.173380952380967,96.22742857142859,96.490142857142885,96.694571428571422,96.149809523809523,96.493181904761911,95.793190476190475,96.05585714285715,96.384380952380951,96.331904761904767,96.700714285714298,96.490285714285719,96.506239047619061,95.702809523809506,95.90157142857143,96.412190476190474,96.194571428571436,96.70052380952383,96.574952380952382,96.473539047619056,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1000N [240V]","N","Y","Y","Y","Y","Y*","Y","1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter",0.98499999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,32,40,48,9.5805599999999991E-2,0.19161119999999998,0.28741679999999997,0.47902799999999995,0.7185419999999999,0.95805599999999991,95.814952380952377,96.185095238095229,96.267238095238099,96.619428571428571,96.5502380952381,96.150714285714272,96.463163333333355,95.936523809523806,96.155904761904779,96.395761904761912,96.552000000000007,96.625380952380951,96.189380952380944,96.509588571428566,95.783000000000015,96.005571428571429,96.429571428571421,96.354190476190496,96.65061904761906,96.545523809523829,96.489631428571442,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1000NT [240V]","N","Y","Y","Y","Y","Y*","Y","1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter",0.98499999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,32,40,48,9.5805599999999991E-2,0.19161119999999998,0.28741679999999997,0.47902799999999995,0.7185419999999999,0.95805599999999991,95.814952380952377,96.185095238095229,96.267238095238099,96.619428571428571,96.5502380952381,96.150714285714272,96.463163333333355,95.936523809523806,96.155904761904779,96.395761904761912,96.552000000000007,96.625380952380951,96.189380952380944,96.509588571428566,95.783000000000015,96.005571428571429,96.429571428571421,96.354190476190496,96.65061904761906,96.545523809523829,96.489631428571442,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1000-4D-NA [240V]","N","Y","Y","Y","Y","Y*","Y","985 W, 240 Vac Grid Support Utility Interactive Microinverter",0.98499999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,32,40,48,9.5805599999999991E-2,0.19161119999999998,0.28741679999999997,0.47902799999999995,0.7185419999999999,0.95805599999999991,95.814952380952377,96.185095238095229,96.267238095238099,96.619428571428571,96.5502380952381,96.150714285714272,96.463163333333355,95.936523809523806,96.155904761904779,96.395761904761912,96.552000000000007,96.625380952380951,96.189380952380944,96.509588571428566,95.783000000000015,96.005571428571429,96.429571428571421,96.354190476190496,96.65061904761906,96.545523809523829,96.489631428571442,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1000-4T-NA [240V]","N","Y","Y","Y","Y","Y*","Y","1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter",0.98499999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,32,40,48,9.5805599999999991E-2,0.19161119999999998,0.28741679999999997,0.47902799999999995,0.7185419999999999,0.95805599999999991,95.814952380952377,96.185095238095229,96.267238095238099,96.619428571428571,96.5502380952381,96.150714285714272,96.463163333333355,95.936523809523806,96.155904761904779,96.395761904761912,96.552000000000007,96.625380952380951,96.189380952380944,96.509588571428566,95.783000000000015,96.005571428571429,96.429571428571421,96.354190476190496,96.65061904761906,96.545523809523829,96.489631428571442,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1000 [240V]","N","Y","Y","Y","Y","Y*","Y","1.0 kW, 240 Vac Grid Support Utility Interactive Microinverters",1.032,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2019-10-15","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.03,null,null,27,37,48,0.103244,0.206488,0.30973200000000001,0.51622000000000001,0.77432999999999996,1.03244,95.608095238095231,96.415238095238081,96.536238095238105,96.450476190476181,96.716142857142856,96.396285714285696,96.563404285714284,96.004619047619045,96.282333333333341,96.573047619047628,96.648666666666671,96.715285714285713,96.604952380952369,96.628636190476186,95.83942857142857,96.088285714285703,96.339571428571432,96.679904761904751,96.714190476190453,96.612523809523822,96.590667142857129,"2019-10-15","2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1000T [240V]","N","Y","Y","Y","Y","Y*","Y","1.0 kW, 240 Vac Grid Support Utility Interactive Microinverters",1.032,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2019-10-15","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.03,null,null,27,37,48,0.103244,0.206488,0.30973200000000001,0.51622000000000001,0.77432999999999996,1.03244,95.608095238095231,96.415238095238081,96.536238095238105,96.450476190476181,96.716142857142856,96.396285714285696,96.563404285714284,96.004619047619045,96.282333333333341,96.573047619047628,96.648666666666671,96.715285714285713,96.604952380952369,96.628636190476186,95.83942857142857,96.088285714285703,96.339571428571432,96.679904761904751,96.714190476190453,96.612523809523822,96.590667142857129,"2019-10-15","2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1000-4D [240V]","N","Y","Y","Y","Y","Y*","Y","1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.032,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.03,null,null,27,37,48,0.103244,0.206488,0.30973200000000001,0.51622000000000001,0.77432999999999996,1.03244,95.608095238095231,96.415238095238081,96.536238095238105,96.450476190476181,96.716142857142856,96.396285714285696,96.563404285714284,96.004619047619045,96.282333333333341,96.573047619047628,96.648666666666671,96.715285714285713,96.604952380952369,96.628636190476186,95.83942857142857,96.088285714285703,96.339571428571432,96.679904761904751,96.714190476190453,96.612523809523822,96.590667142857129,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1000-4T [240V]","N","Y","Y","Y","Y","Y*","Y","1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.032,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.03,null,null,27,37,48,0.103244,0.206488,0.30973200000000001,0.51622000000000001,0.77432999999999996,1.03244,95.608095238095231,96.415238095238081,96.536238095238105,96.450476190476181,96.716142857142856,96.396285714285696,96.563404285714284,96.004619047619045,96.282333333333341,96.573047619047628,96.648666666666671,96.715285714285713,96.604952380952369,96.628636190476186,95.83942857142857,96.088285714285703,96.339571428571432,96.679904761904751,96.714190476190453,96.612523809523822,96.590667142857129,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1200 [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverters",1.2130000000000001,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2019-10-15","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",1.461E-2,null,null,32,40,48,0.12131800000000002,0.24263600000000005,0.36395400000000006,0.60659000000000007,0.90988500000000005,1.2131800000000001,95.813036805416814,96.110484343317935,96.254409212530888,96.609551617293192,96.279694756286986,95.420300881289762,96.275833899414437,95.849341151120569,96.167992170177513,96.284334446261013,96.54213984840419,96.533102007673079,96.043660043725737,96.435069822522919,95.386916107846801,95.959788067095715,96.205849806025668,96.32102651281582,96.552969145473867,96.301315715561984,96.373723024962317,"2019-10-15","2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1200N [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.2130000000000001,240,96.5,"CSA Group","[03/12/2020]","[V01.01.00]","2020-05-11","[03/12/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",1.461E-2,null,null,32,40,48,0.12131800000000002,0.24263600000000005,0.36395400000000006,0.60659000000000007,0.90988500000000005,1.2131800000000001,95.813036805416814,96.110484343317935,96.254409212530888,96.609551617293192,96.279694756286986,95.420300881289762,96.275833899414437,95.849341151120569,96.167992170177513,96.284334446261013,96.54213984840419,96.533102007673079,96.043660043725737,96.435069822522919,95.386916107846801,95.959788067095715,96.205849806025668,96.32102651281582,96.552969145473867,96.301315715561984,96.373723024962317,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1200NT [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.2130000000000001,240,96.5,"CSA Group","[03/12/2020]","[V01.01.00]","2020-05-11","[03/12/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",1.461E-2,null,null,32,40,48,0.12131800000000002,0.24263600000000005,0.36395400000000006,0.60659000000000007,0.90988500000000005,1.2131800000000001,95.813036805416814,96.110484343317935,96.254409212530888,96.609551617293192,96.279694756286986,95.420300881289762,96.275833899414437,95.849341151120569,96.167992170177513,96.284334446261013,96.54213984840419,96.533102007673079,96.043660043725737,96.435069822522919,95.386916107846801,95.959788067095715,96.205849806025668,96.32102651281582,96.552969145473867,96.301315715561984,96.373723024962317,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1200T [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverters",1.2130000000000001,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2019-10-15","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",1.461E-2,null,null,32,40,48,0.12131800000000002,0.24263600000000005,0.36395400000000006,0.60659000000000007,0.90988500000000005,1.2131800000000001,95.813036805416814,96.110484343317935,96.254409212530888,96.609551617293192,96.279694756286986,95.420300881289762,96.275833899414437,95.849341151120569,96.167992170177513,96.284334446261013,96.54213984840419,96.533102007673079,96.043660043725737,96.435069822522919,95.386916107846801,95.959788067095715,96.205849806025668,96.32102651281582,96.552969145473867,96.301315715561984,96.373723024962317,"2019-10-15","2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1200-4D [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.2130000000000001,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",1.461E-2,null,null,32,40,48,0.12131800000000002,0.24263600000000005,0.36395400000000006,0.60659000000000007,0.90988500000000005,1.2131800000000001,95.813036805416814,96.110484343317935,96.254409212530888,96.609551617293192,96.279694756286986,95.420300881289762,96.275833899414437,95.849341151120569,96.167992170177513,96.284334446261013,96.54213984840419,96.533102007673079,96.043660043725737,96.435069822522919,95.386916107846801,95.959788067095715,96.205849806025668,96.32102651281582,96.552969145473867,96.301315715561984,96.373723024962317,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1200-4D-NA [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.2130000000000001,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",1.461E-2,null,null,32,40,48,0.12131800000000002,0.24263600000000005,0.36395400000000006,0.60659000000000007,0.90988500000000005,1.2131800000000001,95.813036805416814,96.110484343317935,96.254409212530888,96.609551617293192,96.279694756286986,95.420300881289762,96.275833899414437,95.849341151120569,96.167992170177513,96.284334446261013,96.54213984840419,96.533102007673079,96.043660043725737,96.435069822522919,95.386916107846801,95.959788067095715,96.205849806025668,96.32102651281582,96.552969145473867,96.301315715561984,96.373723024962317,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1200-4T [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.2130000000000001,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",1.461E-2,null,null,32,40,48,0.12131800000000002,0.24263600000000005,0.36395400000000006,0.60659000000000007,0.90988500000000005,1.2131800000000001,95.813036805416814,96.110484343317935,96.254409212530888,96.609551617293192,96.279694756286986,95.420300881289762,96.275833899414437,95.849341151120569,96.167992170177513,96.284334446261013,96.54213984840419,96.533102007673079,96.043660043725737,96.435069822522919,95.386916107846801,95.959788067095715,96.205849806025668,96.32102651281582,96.552969145473867,96.301315715561984,96.373723024962317,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1200-4T-NA [240V]","N","Y","Y","Y","Y","Y*","Y","1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.2130000000000001,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",1.461E-2,null,null,32,40,48,0.12131800000000002,0.24263600000000005,0.36395400000000006,0.60659000000000007,0.90988500000000005,1.2131800000000001,95.813036805416814,96.110484343317935,96.254409212530888,96.609551617293192,96.279694756286986,95.420300881289762,96.275833899414437,95.849341151120569,96.167992170177513,96.284334446261013,96.54213984840419,96.533102007673079,96.043660043725737,96.435069822522919,95.386916107846801,95.959788067095715,96.205849806025668,96.32102651281582,96.552969145473867,96.301315715561984,96.373723024962317,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1500N [240V]","N","Y","Y","Y","Y","Y*","Y","1.438 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.4390000000000001,240,96.5,"CSA Group","[03/12/2020]","[V01.01.00]","2020-05-11","[03/12/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,36,42,48,0.1439,0.2878,0.43170000000000003,0.71950000000000003,1.07925,1.4390000000000001,95.474952380952374,96.175095238095238,96.227238095238093,96.489428571428562,96.530238095238104,96.150714285714272,96.406363333333346,95.786523809523814,96.05590476190477,96.385761904761921,96.332000000000008,96.631857142857129,96.489380952380969,96.469620952380964,95.702999999999989,95.900523809523818,96.390857142857143,96.194190476190457,96.593666666666664,96.575523809523816,96.414248571428573,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1500NT [240V]","N","Y","Y","Y","Y","Y*","Y","1.438 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.4390000000000001,240,96.5,"CSA Group","[03/12/2020]","[V01.01.00]","2020-05-11","[03/12/2020]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,36,42,48,0.1439,0.2878,0.43170000000000003,0.71950000000000003,1.07925,1.4390000000000001,95.474952380952374,96.175095238095238,96.227238095238093,96.489428571428562,96.530238095238104,96.150714285714272,96.406363333333346,95.786523809523814,96.05590476190477,96.385761904761921,96.332000000000008,96.631857142857129,96.489380952380969,96.469620952380964,95.702999999999989,95.900523809523818,96.390857142857143,96.194190476190457,96.593666666666664,96.575523809523816,96.414248571428573,"2020-05-11","2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1500-4D-NA [240V]","N","Y","Y","Y","Y","Y*","Y","1.438 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.4390000000000001,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,36,42,48,0.1439,0.2878,0.43170000000000003,0.71950000000000003,1.07925,1.4390000000000001,95.474952380952374,96.175095238095238,96.227238095238093,96.489428571428562,96.530238095238104,96.150714285714272,96.406363333333346,95.786523809523814,96.05590476190477,96.385761904761921,96.332000000000008,96.631857142857129,96.489380952380969,96.469620952380964,95.702999999999989,95.900523809523818,96.390857142857143,96.194190476190457,96.593666666666664,96.575523809523816,96.414248571428573,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1500-4T-NA [240V]","N","Y","Y","Y","Y","Y*","Y","1.5 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.4390000000000001,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.11,null,null,36,42,48,0.1439,0.2878,0.43170000000000003,0.71950000000000003,1.07925,1.4390000000000001,95.474952380952374,96.175095238095238,96.227238095238093,96.489428571428562,96.530238095238104,96.150714285714272,96.406363333333346,95.786523809523814,96.05590476190477,96.385761904761921,96.332000000000008,96.631857142857129,96.489380952380969,96.469620952380964,95.702999999999989,95.900523809523818,96.390857142857143,96.194190476190457,96.593666666666664,96.575523809523816,96.414248571428573,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1500 [240V]","N","Y","Y","Y","Y","Y*","Y","1.5 kW, 240 Vac Grid Support Utility Interactive Microinverters",1.5509999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2019-10-15","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.03,null,null,36,42,48,0.15507199999999999,0.31014399999999998,0.46521599999999996,0.77535999999999994,1.1630399999999999,1.5507199999999999,95.952784292610119,96.053996345130741,96.305971657660578,96.640993431781467,96.740058950478769,95.897398164544825,96.559237560535308,95.944835396658632,95.651087066541763,96.355402623873346,96.304572283692309,96.719099675255805,96.426669691153535,96.489412576076859,95.141461663395688,95.867453724799361,96.451621446755908,96.166729343123976,96.673241596986159,96.590981226785217,96.434605996184473,"2019-10-15","2021-03-01"]
["Hoymiles Power Electronics Inc.","HM-1500T [240V]","N","Y","Y","Y","Y","Y*","Y","1.5 kW, 240 Vac Grid Support Utility Interactive Microinverters",1.5509999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2019-10-15","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.03,null,null,36,42,48,0.15507199999999999,0.31014399999999998,0.46521599999999996,0.77535999999999994,1.1630399999999999,1.5507199999999999,95.952784292610119,96.053996345130741,96.305971657660578,96.640993431781467,96.740058950478769,95.897398164544825,96.559237560535308,95.944835396658632,95.651087066541763,96.355402623873346,96.304572283692309,96.719099675255805,96.426669691153535,96.489412576076859,95.141461663395688,95.867453724799361,96.451621446755908,96.166729343123976,96.673241596986159,96.590981226785217,96.434605996184473,"2019-10-15","2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1500-4D [240V]","N","Y","Y","Y","Y","Y*","Y","1.5 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.5509999999999999,240,95.6,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.03,null,null,36,42,48,0.15507199999999999,0.31014399999999998,0.46521599999999996,0.77535999999999994,1.1630399999999999,1.5507199999999999,95.952784292610119,96.053996345130741,96.305971657660578,96.640993431781467,96.740058950478769,95.897398164544825,96.559237560535308,95.944835396658632,95.651087066541763,96.355402623873346,96.304572283692309,96.719099675255805,96.426669691153535,96.489412576076859,95.141461663395688,95.867453724799361,96.451621446755908,96.166729343123976,96.673241596986159,96.590981226785217,96.434605996184473,"2021-03-01"]
["Hoymiles Power Electronics Inc.","HMS-1500-4T [240V]","N","Y","Y","Y","Y","Y*","Y","1.5 kW, 240 Vac Grid Support Utility Interactive Microinverter",1.5509999999999999,240,96.5,"CSA Group","[01/29/2021]","[V01.01.00]","2021-03-01","[01/29/2021]","2021-03-01","CSA Group","2021-01-26","2021-03-01",null,"N","Y",0.03,null,null,36,42,48,0.15507199999999999,0.31014399999999998,0.46521599999999996,0.77535999999999994,1.1630399999999999,1.5507199999999999,95.952784292610119,96.053996345130741,96.305971657660578,96.640993431781467,96.740058950478769,95.897398164544825,96.559237560535308,95.944835396658632,95.651087066541763,96.355402623873346,96.304572283692309,96.719099675255805,96.426669691153535,96.489412576076859,95.141461663395688,95.867453724799361,96.451621446755908,96.166729343123976,96.673241596986159,96.590981226785217,96.434605996184473,"2021-03-01"]
["Hoymiles Power Electronics Inc.","THM-1500 [240V]","N","Y","Y","Y","N","N","N","1.5 kW, 240 Vac Grid Support Utility Interactive Microinverters",1.5509999999999999,240,96.5,"CSA Group","[03/12/2020]","[V01.01.00]","2020-05-21","[03/12/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",0.03,null,null,36,42,48,0.15507199999999999,0.31014399999999998,0.46521599999999996,0.77535999999999994,1.1630399999999999,1.5507199999999999,95.952784292610119,96.053996345130741,96.305971657660578,96.640993431781467,96.740058950478769,95.897398164544825,96.559237560535308,95.944835396658632,95.651087066541763,96.355402623873346,96.304572283692309,96.719099675255805,96.426669691153535,96.489412576076859,95.141461663395688,95.867453724799361,96.451621446755908,96.166729343123976,96.673241596986159,96.590981226785217,96.434605996184473,"2020-05-21","2021-01-11"]
["Huawei Technologies Co., Ltd.","SUN2000-3.8KTL-USL0 [240V]","N","Y","Y","Y","N","N","N","3.8 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter",3.8,240,99,"UL","[06/14/2018]","[V100R001D00]","2019-01-15","[06/14/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",2.1800000000000002,null,null,370,395,420,0.38,0.76,1.1399999999999999,1.9,2.8499999999999996,3.8,96.375031617998374,98.233215547703168,98.664083176913977,99.00284900284899,99.057221096739127,99.077590884427551,98.851157039426184,96.163682864450138,98.117647058823522,98.478783026421155,98.94691988895012,99.023064856235919,99.036499547460252,98.782786158547296,96.070229333969607,97.994516255385832,98.45627359030081,98.864074301006298,98.992315168426373,98.996704465070792,98.734505682695016,"2018-07-16","2019-01-15"]
["Huawei Technologies Co., Ltd.","SUN2000-5KTL-USL0 [240V]","N","Y","Y","Y","N","N","N","5 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter",5,240,99,"UL","[06/14/2018]","[V100R001D00]","2019-01-15","[06/14/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",2.0699999999999998,null,null,370,395,420,0.5,1,1.5,2.5,3.75,5,97.0703125,98.385577252483728,98.721071863580988,99.023904040143663,99.019874761775114,98.870253237065455,98.867686120278165,96.881091617933734,98.381364219367683,98.660986001217296,98.931877114350954,98.965986394557831,98.820257904100984,98.802310074166215,96.692607003891069,98.29290206648696,98.592410407244145,98.882480173035319,98.88622708105666,98.774165460528749,98.727168094673175,"2018-07-16","2019-01-15"]
["Huawei Technologies Co., Ltd.","SUN2000-7.6KTL-USL0 [240V]","N","Y","Y","Y","N","N","N","7.6 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter",7.6,240,99,"UL","[06/14/2018]","[V100R001D00]","2019-01-15","[06/14/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",2.06,null,null,370,395,420,0.76,1.52,2.2799999999999998,3.8,5.6999999999999993,7.6,98.024645488884758,98.810939357907259,98.958553015114916,98.997288918291375,98.918168971428102,98.748951404805581,98.890066947202897,97.825310999296548,98.718718755046822,98.916988187844737,98.938211420706281,98.867424073203637,98.716381417007497,98.831565188262189,97.692522840201306,98.626617125196802,98.879194198791538,98.911282479655938,98.847323368473226,98.676581636712726,98.798814861577071,"2018-07-16","2019-01-15"]
["Huawei Technologies Co., Ltd.","SUN2000-9KTL-USL0 [240V]","N","Y","Y","Y","N","N","N","9 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter",9,240,99,"UL","[06/14/2018]","[V100R001D00]","2018-10-15","[06/14/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.97,null,null,370,395,420,0.9,1.8,2.6999999999999997,4.5,6.75,9,97.68465700573195,98.645469628308931,98.919896388250805,99.061754601828056,99.0358612580835,98.973774230330648,98.950710972919509,97.533802045824686,98.595943837753495,98.905234348272316,99.040534134493342,99.015955221976697,98.932032552204689,98.923347459014835,97.577316834020593,98.598420127281287,98.858271916679868,99.024050844816443,99.009115259059541,98.918270032621734,98.911801576070559,"2018-07-16","2018-10-15"]
["Huawei Technologies Co., Ltd.","SUN2000-10KTL-USL0 [240V]","N","Y","Y","Y","N","N","N","10 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter",10,240,99,"UL","[06/14/2018]","[V100R001D00]","2018-10-15","[06/14/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.98,null,null,370,395,420,1,2,3,5,7.5,10,97.640117994100279,98.65604000625099,98.936592333474479,99.048316251830173,99.012992322810646,98.903321870737884,98.932996237604385,97.448478900883245,98.548009367681502,98.859432799013561,99.004051757940147,98.977306347948414,98.879178720503461,98.881253729906291,97.185084705665261,98.420657665824891,98.767714109673435,98.933048437210559,98.937777723995637,98.845012252136229,98.815774942817384,"2018-07-16","2018-10-15"]
["Huawei Technologies Co., Ltd.","SUN2000-11.4KTL-USL0 [240V]","N","Y","Y","Y","N","N","N","11.4 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter",11.4,240,99,"UL","[06/14/2018]","[V100R001D00]","2018-10-15","[06/14/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.97,null,null,370,395,420,1.1400000000000001,2.2800000000000002,3.42,5.7,8.5500000000000007,11.4,97.88546255506607,98.785528197292905,98.973546739857198,99.0470873767634,98.983558158460895,98.837481621322169,98.93456877502085,97.715367092422369,98.65386046399577,98.917325381817932,98.988111710077632,98.940718004312004,98.801375159949785,98.877539512113998,97.539543057996497,98.582157096361243,98.83945344931621,98.943617483464806,98.912403488229415,98.774883947720909,98.83190170873111,"2018-07-16","2018-10-15"]
["Huawei Technologies Co., Ltd.","SUN2000-25KTL-US [480V]","N","Y","Y","Y","N","N","N","25kW, 480Vac, 3-phase transformerless Grid Support Utility Interactive Inverter",25,480,98,"CSA Group","[12/29/2018]","[SUN2000 V200 R001]","2019-05-01","[12/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,560,730,800,2.5,5,7.5,12.5,18.75,25,95.7,97.1,97.6,97.9,97.9,97.9,97.7,96.3,97.7,98.2,98.4,98.4,98.4,98.3,95.9,97.5,98,98.3,98.3,98.3,98.1,"2019-05-01"]
["Huawei Technologies Co., Ltd.","SUN2000-30KTL-US [480V]","N","Y","Y","Y","N","N","N","30kW, 480Vac, 3-phase transformerless Grid Support Utility Interactive Inverter ",30,480,98,"CSA Group","[12/29/2018]","[SUN2000 V200 R001]","2019-05-01","[12/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1,null,null,560,730,800,3,6,9,15,22.5,30,96.1,97.4,97.7,97.9,97.9,97.8,97.8,96.6,97.9,98.3,98.4,98.4,98.3,98.3,96.4,97.8,98.2,98.3,98.3,98.2,98.2,"2019-05-01"]
["Huawei Technologies Co., Ltd.","SUN2000-33KTL-US [480V]","N","Y","Y","Y","N","N","N","33 kW, 480 Vac, transformerless Grid Support Utility Interactive Inverter",33,480,98.5,"CSA Group","[3/22/2017]","[SUN2000 V200 R002C20]","2018-10-15","[3/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.8,null,null,460,720,850,3.3000000000000003,6.6000000000000005,9.9,16.5,24.75,33,95.630469927276991,97.310036505268826,97.623901610438097,97.83334333356153,97.888870456254139,97.788128321993113,97.721098673569372,97.516871811078531,98.67409277667268,98.8513071683726,98.88408683335021,98.874097898809069,98.789398500966755,98.804936417902184,96.914454581398289,98.109446935368311,98.37996746207223,98.457607412231482,98.46224478261388,98.383768023280254,98.367922317990988,"2017-11-01","2018-10-15"]
["Huawei Technologies Co., Ltd.","SUN2000-36KTL-US [480V]","N","Y","Y","Y","N","N","N","36 kW, 480 Vac, Transformerlss Grid Support Utility Interactive Inverter",36,480,98.5,"CSA Group","[3/22/2017]","[SUN2000 V200 R002C20]","2018-10-15","[3/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.8,null,null,490,720,850,3.6,7.2,10.799999999999999,18,27,36,96.4077311912922,97.545820870882707,97.813675383505782,97.991157284213202,97.987845609331899,97.877476167255708,97.876816348209985,97.973892096751015,98.741338944593736,98.87343126218461,98.895496173760151,98.857816097688669,98.762019609059948,98.821632091279511,97.110091536795707,98.215610614555217,98.41581608389275,98.471283525682495,98.444292259053896,98.352426532017674,98.377147886559484,"2017-11-01","2018-10-15"]
["Huawei Technologies Co., Ltd.","SUN2000-40KTL-US [480V]","N","Y","Y","Y","N","N","N","40 kW, 480 Vac, transformerless Grid Support Utility Interactive Inverter",40,480,98.5,"CSA Group","[3/22/2017]","[SUN2000 V200 R002C20]","2018-10-15","[3/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.8,null,null,530,720,850,4,8,12,20,30,40,96.748549773647738,97.728864384062192,97.946597114044309,98.102029888936798,98.049016661168523,97.908674394318737,97.972815690646314,98.053754251274981,98.727271037736912,98.778088260806854,98.8628416309691,98.790704433083846,98.805253458820715,98.77241707821365,97.266210056885868,98.215502763671708,98.363828147895191,98.457088705010364,98.376392189893494,98.416867734446882,98.341402793624511,"2017-11-01","2018-10-15"]
["Huawei Technologies Co., Ltd.","SUN2000-45KTL-US-HV-D0 [600V]","N","Y","Y","Y","N","N","N","45kW, 600 Vac, Transformerlss Grid Support Utility Interactive Inverter",45.207000000000001,600,98.5,"CSA Group","[9/29/2017]","[SUN2000HA\nV100R001]","2018-10-15","[9/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.1100000000000001,null,null,800,1000,1200,97.5,98.1,98.2,98.2,98.1,97.9,98.2,98.6,98.7,98.6,98.5,98.4,98.5,98.2,98.6,98.7,98.6,98.5,98.4,98.5,98.1,98.5,98.5,98.5,98.4,98.2,98.4,"2017-11-15","2018-10-15"]
["Huawei Technologies Co., Ltd.","SUN2000-100KTL-USH0 [800V]","N","Y","Y","Y","N","N","N","100 kW, 800 Vac, 3-phase transformerless Grid Support Utility Interactive Inverter ",100,800,98.5,"CSA Group","[10/16/2018]","[SUN2000HA V200 R001]","2019-01-15","[10/16/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.61,null,null,880,1120,1200,10,20,30,50,75,100,97.297060000000002,98.049090000000007,98.304159999999996,98.447010000000006,98.410420000000002,98.31644,98.338049999999996,97.691339999999997,98.412009999999995,98.599450000000004,98.692269999999994,98.659400000000005,98.573899999999995,98.603740000000002,98.224800000000002,98.790670000000006,98.936269999999993,98.987870000000001,98.981089999999995,98.631020000000007,98.91986,"2019-01-15"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 610TL U B220 [220V]","Y","Y","Y","Y","N","N","N","610 kW, 220 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",610,220,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,440,590,740,61,122,183,305,457.5,610,97.11,98.06,98.25,98.17,97.74,97.1,97.85,96.37,97.64,98.01,97.9,97.48,96.73,97.56,95.53,97.29,97.68,97.72,97.45,96.53,97.41,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 830TL U B300 [300V]","Y","Y","Y","Y","N","N","N","830 kW, 300 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",830,300,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,440,590,740,83,166,249,415,622.5,830,97.21,98.13,98.27,98.16,97.74,97.18,97.86,96.5,97.77,97.96,97.92,97.55,97.06,97.62,95.7,97.41,97.7,97.66,97.36,96.88,97.38,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 915TL U B330 [330V]","Y","Y","Y","Y","N","N","N","915 kW, 330 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",915,330,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,485,613,740,91.5,183,274.5,457.5,686.25,915,97.17,98.13,98.33,98.22,97.86,97.27,97.95,96.5,97.84,98.09,98.05,97.69,97.15,97.75,95.82,97.49,97.82,97.81,97.51,97.17,97.53,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1000TL U B360 [360V]","Y","Y","Y","Y","N","N","N","1000 kW, 360 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1000,360,98,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,524,632,740,100,200,300,500,750,1000,97.34,98.14,98.33,98.21,97.83,97.31,97.94,96.84,97.92,98.13,98.08,97.7,97.09,97.78,96.36,97.64,97.97,97.94,97.55,96.97,97.61,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1140TL U B410 [410V]","Y","Y","Y","Y","N","N","N","1136 kVA, 410 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1027.752,410,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,595,668,800,102.7752,205.5504,308.32559999999995,513.87599999999998,770.81399999999996,1027.752,95.862485381251901,97.441697492401133,97.811332352904088,97.891168179619768,97.74411648135623,97.382896895342981,97.674616069824722,95.673585519005911,97.378077219658323,97.755703475534403,97.860554231371538,97.719335061881765,97.378124414474883,97.637401890916379,95.140003898891223,97.080090167707112,97.524003696301421,97.689736564126648,97.556122921873055,97.213022129275785,97.442726041420286,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1245TL U B480 [480V]","Y","Y","Y","Y","N","N","N","1247 kVA, 480 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1042.22,480,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,697,949,1200,104.22200000000001,208.44400000000002,312.666,521.11,781.66499999999996,1042.22,96.903698050438123,97.618814750297517,97.802986930357335,97.739491462227122,97.501507681732335,97.117409292811473,97.550409834201687,96.404674685259025,97.431021008596332,97.599251152283387,97.471936920226455,97.282213741029167,96.858978778224767,97.31127715101843,96.025957796716156,97.074663463996743,97.397898680593329,97.226770294224494,96.990291244472502,96.513792986680627,97.030685097431302,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1190TL U B430 [430V]","Y","Y","Y","Y","N","N","N","1192 kVA, 430 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1048.5940000000001,430,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,624,682,800,104.85940000000001,209.71880000000002,314.57819999999998,524.29700000000003,786.44550000000004,1048.5940000000001,96.004131167883529,97.481140832780383,97.837312964836116,97.923089297190614,97.789347637594915,97.413812385648953,97.717593463752465,95.869210079707514,97.430341823072879,97.796576602197305,97.903911963788389,97.781005512397059,97.450615230613408,97.698159882102303,95.382516161655985,97.183226707302126,97.593498616554569,97.741068874937696,97.649566841568571,97.317414469035342,97.531447429037911,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1220TL U B440 [440V]","Y","Y","Y","Y","N","N","N","1217 kVA, 440 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1099.306,440,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,638,689,800,109.93060000000001,219.86120000000003,329.79180000000002,549.65300000000002,824.47950000000003,1099.306,95.932010276324007,97.49265051753207,97.867964868192075,97.948666576433268,97.8105002896787,97.453652066344446,97.737536459010528,95.83631075130819,97.465193905098587,97.850931329649029,97.944192380988355,97.803900269609201,97.467666751246611,97.726554765327904,95.426130372969482,97.239481090374937,97.647783531418611,97.803695764929572,97.683236673332686,97.351408834240246,97.575215282421311,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1110TL U B400 [400V]","Y","Y","Y","Y","N","N","N","1110 kW, 400 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1110,400,98,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,580,660,740,111,222,333,555,832.5,1110,97.16,98.08,98.29,98.27,97.94,97.39,98,96.8,97.93,98.19,98.25,97.8,97.32,97.89,96.54,97.71,98.06,98.12,97.67,97.35,97.75,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1250TL U B450 [450V]","Y","Y","Y","Y","N","N","N","1247 kVA, 450 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1114.104,450,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,652,696,800,111.41040000000001,222.82080000000002,334.2312,557.05200000000002,835.57799999999997,1114.104,95.970642143925957,97.501616847126058,97.868762712731552,97.936366948280323,97.810266840204704,97.496823165386601,97.739077696357825,95.900121191315378,97.483655278990469,97.854994237938826,97.974343165614329,97.831573475816199,97.520426325602784,97.754154243396542,95.507328978243521,97.260350661207383,97.698182169906815,97.844321173743367,97.717172632052652,97.413248464368081,97.615163917271346,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1275TL U B460 [460V]","Y","Y","Y","Y","N","N","N","1275 kVA, 460 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1128.4760000000001,460,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,666,703,800,112.84760000000001,225.69520000000003,338.5428,564.23800000000006,846.35700000000008,1128.4760000000001,95.99382220256561,97.507971055551451,97.861674580167048,97.970563015992951,97.844152982532691,97.627833420787141,97.771163375640441,95.888817550203342,97.482348805456581,97.870894574140294,97.991603253818624,97.86706263712847,97.559672152450915,97.779940979780349,95.542870550986734,97.320155042788016,97.733441007951882,97.912252424669219,97.763481981035881,97.490549414914128,97.666481425008357,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1165TL U B420 [420V]","Y","Y","Y","Y","N","N","N","1165 kW, 420 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1165,420,98,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,610,675,740,116.5,233,349.5,582.5,873.75,1165,97.28,98.08,98.28,98.26,98.01,97.47,98.04,96.99,97.92,98.18,98.24,97.91,97.53,97.95,96.74,97.75,98.03,98.15,97.85,97.42,97.87,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1740TL U B670 [670V]","Y","Y","Y","Y","N","N","N","1741 kVA, 670 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1272.412,670,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,962,1081,1200,127.24120000000001,254.48240000000001,381.72359999999998,636.20600000000002,954.30899999999997,1272.412,95.964557738299547,97.374808884374247,97.690183597413451,97.760353023553648,97.628674276890095,97.348016627916479,97.570417118534152,95.731305317544397,97.287881016192969,97.557286456785931,97.696974511284054,97.544160408187125,97.222955419255484,97.47643807299734,95.377827614865865,97.136475191779098,97.419043572372345,97.50595040476847,97.402036743097852,97.143998142972393,97.318751058860144,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1800TL U B690 [690V]","Y","Y","Y","Y","N","N","N","1793 kVA, 690 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1300.644,690,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,962,1081,1200,130.06440000000001,260.12880000000001,390.19319999999999,650.322,975.48299999999995,1300.644,96.671689964420295,97.66516992006899,97.878799533636567,97.902063780379663,97.7538343845995,97.399010071196059,97.734498159893917,96.472240657415441,97.596088832359982,97.804012362449711,97.827986624285316,97.677848526433479,97.335621108278545,97.655093516932169,96.333523362786579,97.514469835502524,97.708216936425416,97.734575890986818,97.562504003544106,97.257914519181156,97.549334243602317,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1665TL U B640 [640V]","Y","Y","Y","Y","N","N","N","1663 kVA, 640 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1367.076,640,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,919,1060,1200,136.70760000000001,273.41520000000003,410.12279999999998,683.53800000000001,1025.307,1367.076,96.249477763929832,97.442263685687166,97.720428241358945,97.755000523746432,97.618394959633193,97.312262443393948,97.580456244566648,95.97723736896917,97.314091902113276,97.590648097722578,97.669729930664502,97.506129753944407,97.192912859076884,97.464209559575082,95.515538943736459,97.14010892160556,97.406387717096251,97.452868370901456,97.342606406702743,97.037111326595536,97.274932849652814,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1690TL U B650 [650V]","Y","Y","Y","Y","N","N","N","1689 kVA, 650 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1375.2819999999999,650,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,933,1067,1200,137.5282,275.0564,412.58459999999997,687.64099999999996,1031.4614999999999,1375.2819999999999,96.288130060211245,97.505114184155389,97.775673492269448,97.818326185609266,97.661944150947051,97.358128241493759,97.630447041743125,96.000786646427244,97.401582473417079,97.663816807220741,97.740457877121727,97.573571682822731,97.250069712731133,97.531761238122598,95.667576566877756,97.262672977755344,97.541939152838466,97.557458698480445,97.423828212721602,97.085137641245751,97.370821571389115,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1715TL U B660 [660V]","Y","Y","Y","Y","N","N","N","1715 kVA, 660 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1390.614,660,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,948,1074,1200,139.06140000000002,278.12280000000004,417.18419999999998,695.30700000000002,1042.9605000000001,1390.614,96.062235468670153,97.403376404219202,97.686348745965319,97.753615279858352,97.622034950443336,97.339232986027454,97.569919470280212,95.841890787129174,97.270665199007212,97.550170030702319,97.700887549968797,97.538433991441593,97.230456630980342,97.47730852762632,95.364706922046778,97.109170250043064,97.400495619794086,97.525329846750523,97.403401392754972,97.086498890356509,97.316553214254895,"2019-05-01"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW5000H-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, Bi-directional Grid Support Utility Interactive PV and Battery Inverter\n",4.9889999999999999,240,95.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21","Efficiency data includes external Isolation transformer GW5000G-TF effect.","N","N",47.36,null,null,300,400,480,0.499,0.998,1.4970000000000001,2.4950000000000001,3.742,4.9889999999999999,87.29,92.59,94.36,95.51,95.76,95.68,95.04,88.08,93.35,94.82,95.82,96.09,96.05,95.42,87.62,93.17,94.65,95.74,96.09,96.02,95.36,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW5000A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",5.0674999999999999,240,97.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",11.24,null,null,300,400,480,0.50675000000000003,1.0135000000000001,1.5202499999999999,2.5337499999999999,3.8006250000000001,5.0674999999999999,93.992476056920239,96.231582104991659,96.87969976945854,97.251681481939372,97.264304783943217,97.148369422310324,97.027195237674107,94.930731020114379,96.945902871292461,97.409766453632315,97.610278961161072,97.595850265342534,97.502117238035311,97.432761443182216,94.878227293429546,96.521480497356563,97.218071317052377,97.726646497952842,97.660705236860736,97.550888024748616,97.447685615995027,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW5000A-MS [240V]","N","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter\n",5.0674999999999999,240,97.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",11.24,null,null,300,400,480,0.50675000000000003,1.0135000000000001,1.5202499999999999,2.5337499999999999,3.8006250000000001,5.0674999999999999,93.992476056920239,96.231582104991659,96.87969976945854,97.251681481939372,97.264304783943217,97.148369422310324,97.027195237674107,94.930731020114379,96.945902871292461,97.409766453632315,97.610278961161072,97.595850265342534,97.502117238035311,97.432761443182216,94.878227293429546,96.521480497356563,97.218071317052377,97.726646497952842,97.660705236860736,97.550888024748616,97.447685615995027,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW5000A-MS [208V]","N","Y","Y","Y","Y","Y*","Y","5 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter\n",5.133,208,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.31,null,null,300,400,480,0.51329999999999998,1.0266,1.5399,2.5665,3.8497500000000002,5.133,94.1097700389317,96.073431491627588,96.735273428730096,97.014680509894788,96.93276247585797,96.73084300928268,96.760284357333035,95.083820527343406,96.711220630919669,97.177158030466657,97.337621358506723,97.217596021303322,97.066831061113319,97.119740745928567,94.220930686668112,96.375249616781616,96.985616755877729,97.229105198534313,97.135278558531581,96.985202074712674,96.974943550460708,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW6000A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",6.109,240,97.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.3000000000000007,null,null,360,400,480,0.6109,1.2218,1.8327,3.0545,4.5817499999999995,6.109,95.14283831972466,96.913830426935164,97.275137375470692,97.447186137333162,97.362356981640659,97.164551444090662,97.248607400506273,95.691697753666503,97.203139768646707,97.571283957447903,97.670891443681271,97.558718660861786,97.375615123802234,97.482167823092681,95.30478006405103,96.964657812904804,97.384951167238,97.593041379831604,97.486119591339204,97.319569027926988,97.374778757846599,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW6000A-MS [240V]","N","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter\n",6.109,240,97.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.3000000000000007,null,null,360,400,480,0.6109,1.2218,1.8327,3.0545,4.5817499999999995,6.109,95.14283831972466,96.913830426935164,97.275137375470692,97.447186137333162,97.362356981640659,97.164551444090662,97.248607400506273,95.691697753666503,97.203139768646707,97.571283957447903,97.670891443681271,97.558718660861786,97.375615123802234,97.482167823092681,95.30478006405103,96.964657812904804,97.384951167238,97.593041379831604,97.486119591339204,97.319569027926988,97.374778757846599,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW6000A-MS [208V]","N","Y","Y","Y","Y","Y*","Y","6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter\n",6.1379999999999999,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",11.5,null,null,360,400,480,0.61380000000000001,1.2276,1.8413999999999999,3.069,4.6035000000000004,6.1379999999999999,95.124308324456322,96.747517536821405,97.077752549770779,97.185853861910957,96.951780313147879,96.65847138177638,96.918074961850323,95.49256073161321,96.980459474911058,97.283165566892791,97.314660734068042,97.089542323515886,96.78624311774503,97.075553612542194,95.130811922763897,96.771122709723869,97.140467155893731,97.300351183278181,97.038331292602621,96.7392484942376,97.00099642938369,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7000A-MS [208V]","N","Y","Y","Y","Y","Y*","Y","7 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter\n",7.0069999999999997,208,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.34,null,null,210,400,480,0.70069999999999999,1.4014,2.1020999999999996,3.5034999999999998,5.2552500000000002,7.0069999999999997,94.218717248699633,95.707930078947228,96.108377823406997,96.23148344993966,95.941666707427927,95.657791768336409,95.927735000545141,95.759577173423054,96.995869489140702,97.272783959230296,97.312539496998866,97.122327315149974,96.819345539049792,97.104344684853345,95.150779159015201,96.669082497896724,97.049554599618077,97.149710651824762,96.974551206132901,96.682319010444061,96.917499169865465,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7000A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",7.0570000000000004,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.48,null,null,210,400,480,0.7057000000000001,1.4114000000000002,2.1171000000000002,3.5285000000000002,5.2927499999999998,7.0570000000000004,94.369339307317915,95.914408634886016,96.382125133264552,96.542539075369675,96.39475419219211,96.151942144376292,96.307099054937026,95.938380207142345,97.269437644857931,97.593466606285915,97.666041279987084,97.565094786802163,97.323216956127936,97.497752836891735,95.300635007015146,96.875512620957878,97.322855627787092,97.703348944915916,97.571113274784722,97.331880004510595,97.431531020956726,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7000A-MS [240V]","N","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter\n",7.0570000000000004,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.48,null,null,210,400,480,0.7057000000000001,1.4114000000000002,2.1171000000000002,3.5285000000000002,5.2927499999999998,7.0570000000000004,94.369339307317915,95.914408634886016,96.382125133264552,96.542539075369675,96.39475419219211,96.151942144376292,96.307099054937026,95.938380207142345,97.269437644857931,97.593466606285915,97.666041279987084,97.565094786802163,97.323216956127936,97.497752836891735,95.300635007015146,96.875512620957878,97.322855627787092,97.703348944915916,97.571113274784722,97.331880004510595,97.431531020956726,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7600A-MS [208V]","N","Y","Y","Y","Y","Y*","Y","7.6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter\n",7.61,208,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.58,null,null,230,400,480,0.76100000000000012,1.5220000000000002,2.2829999999999999,3.8050000000000002,5.7075000000000005,7.61,94.546642969393105,95.928060406882054,96.264785954571352,96.350825379088775,96.04231713433127,95.654503988325288,96.048869663888865,95.942836248759633,97.093320187094363,97.330408463026089,97.300707426387035,97.04664930417276,96.699406290236354,97.074871480132899,95.387321106484663,96.779458172512491,97.098689729902574,97.113560567024123,96.886279969607102,96.543175301533751,96.877043388516839,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7600A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",7.6440000000000001,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.44,null,null,230,400,480,0.76440000000000008,1.5288000000000002,2.2932000000000001,3.8220000000000001,5.7330000000000005,7.6440000000000001,94.86432445244229,96.149953043032909,96.525494022056179,96.684135072866653,96.444263220270798,96.198052414201712,96.4141604056517,96.219687597285059,97.362307295085614,97.653240048668309,97.681109246548189,97.529716382330108,97.260675494149226,97.502108073603424,95.620155916733026,97.011248908407268,97.397681606715153,97.588095450939136,97.44733372738483,97.197992135042753,97.363577001858815,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7600A-MS [240V]","N","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter\n",7.6440000000000001,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.44,null,null,230,400,480,0.76440000000000008,1.5288000000000002,2.2932000000000001,3.8220000000000001,5.7330000000000005,7.6440000000000001,94.86432445244229,96.149953043032909,96.525494022056179,96.684135072866653,96.444263220270798,96.198052414201712,96.4141604056517,96.219687597285059,97.362307295085614,97.653240048668309,97.681109246548189,97.529716382330108,97.260675494149226,97.502108073603424,95.620155916733026,97.011248908407268,97.397681606715153,97.588095450939136,97.44733372738483,97.197992135042753,97.363577001858815,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW8600A-MS [208V]","N","Y","Y","Y","Y","Y*","Y","8.6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter\n",8.6120000000000001,208,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.8699999999999992,null,null,260,400,480,0.86120000000000008,1.7224000000000002,2.5836000000000001,4.306,6.4589999999999996,8.6120000000000001,95.168327322448548,96.232575401796353,96.481027673447073,96.487261274049303,96.090140159134336,95.680076183664141,96.170188144876164,96.257415825848355,97.197759011932717,97.319607948960154,97.188533598905607,96.834839004000315,96.394365991905957,96.94031256499143,95.737843421238523,96.916178803618109,97.134539980575028,97.156697887027661,96.79202453462139,96.347145245152547,96.851504296582235,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW8600A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",8.6140000000000008,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.5399999999999991,null,null,260,400,480,0.86140000000000017,1.7228000000000003,2.5842000000000001,4.3070000000000004,6.4605000000000006,8.6140000000000008,95.373677152466954,96.487433823638668,96.788717049302946,96.874277196177204,96.597576834616589,96.306825604697224,96.609620036975826,96.49368114310478,97.470760932714583,97.660291531549063,97.644735792343837,97.423977151261667,97.105828723427095,97.447914118878046,95.859259081243209,97.154374622494856,97.450637203619138,97.500862861920851,97.320978717989959,97.012514180093632,97.29209118935151,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW8600A-MS [240V]","N","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter\n",8.6140000000000008,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.5399999999999991,null,null,260,400,480,0.86140000000000017,1.7228000000000003,2.5842000000000001,4.3070000000000004,6.4605000000000006,8.6140000000000008,95.373677152466954,96.487433823638668,96.788717049302946,96.874277196177204,96.597576834616589,96.306825604697224,96.609620036975826,96.49368114310478,97.470760932714583,97.660291531549063,97.644735792343837,97.423977151261667,97.105828723427095,97.447914118878046,95.859259081243209,97.154374622494856,97.450637203619138,97.500862861920851,97.320978717989959,97.012514180093632,97.29209118935151,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW9600H-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","9.6 kW, 240 Vac, Bi-directional Grid Support Utility Interactive PV and Battery Inverter\n",9.5190000000000001,240,95.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21","Efficiency data includes external Isolation transformer GW9600G-TF effect.","N","N",45.22,null,null,300,400,480,0.95190000000000008,1.9038000000000002,2.8557000000000001,4.7595000000000001,7.1392500000000005,9.5190000000000001,92.207175576489959,94.739802327575902,95.389898486524004,95.547136746174431,95.155745089088882,94.555175546089188,95.09726734903947,93.028476133424888,95.45290688904683,96.02106522502892,96.106223821347072,95.738404590589667,95.173183443465732,95.698632824461498,92.605062814602377,95.182922737469738,95.72324617626407,95.955750140480845,95.64133762082929,94.991757779862965,95.540342548142917,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW9600A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",9.6280000000000001,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.4,null,null,300,400,480,0.9628000000000001,1.9256000000000002,2.8883999999999999,4.8140000000000001,7.2210000000000001,9.6280000000000001,95.836106427217857,96.812128332124203,97.058225171112923,97.004010072682675,96.702213766782762,96.332883575991772,96.760697284686287,96.713422078214379,97.537176705477236,97.658937512311681,97.575299819457413,97.311454063738651,96.952366395631614,97.377970155528971,96.153120452251898,97.274799052286099,97.521554719784405,97.445565134331602,97.19826040742511,96.836918305803579,97.232943946513643,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW9600A-MS [208V]","N","Y","Y","Y","Y","Y*","Y","9.6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter\n",9.6280000000000001,208,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.67,null,null,300,400,480,0.9628000000000001,1.9256000000000002,2.8883999999999999,4.8140000000000001,7.2210000000000001,9.6280000000000001,95.688011070559924,96.540221874908084,96.744115405185582,96.580714913277987,96.15246454004172,95.687435838375038,96.290953515119327,96.47404010929246,97.227054152973437,97.2978488330034,97.092779464857344,96.637483607883595,96.125381482618522,96.809675245910043,95.999017505575722,96.990635701003143,97.1322430071328,96.938902162465141,96.682012979796596,96.131034661546849,96.750549712616348,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW9600A-MS [240V]","N","Y","Y","Y","Y","Y*","Y","9.6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter\n",9.6280000000000001,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.4,null,null,300,400,480,0.9628000000000001,1.9256000000000002,2.8883999999999999,4.8140000000000001,7.2210000000000001,9.6280000000000001,95.836106427217857,96.812128332124203,97.058225171112923,97.004010072682675,96.702213766782762,96.332883575991772,96.760697284686287,96.713422078214379,97.537176705477236,97.658937512311681,97.575299819457413,97.311454063738651,96.952366395631614,97.377970155528971,96.153120452251898,97.274799052286099,97.521554719784405,97.445565134331602,97.19826040742511,96.836918305803579,97.232943946513643,"2021-01-21"]
["Jinko Solar Co., Ltd","JKMS260M-60B-EP [240V]","N","Y","Y","Y","N","N","N","260 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS265M-60B-EP [240V]","N","Y","Y","Y","N","N","N","265 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS270M-60B-EP [240V]","N","Y","Y","Y","N","N","N","270 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS275M-60B-EP [240V]","N","Y","Y","Y","N","N","N","275 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS275M-60-EP [240V]","N","Y","Y","Y","N","N","N","275 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS280M-60B-EP [240V]","N","Y","Y","Y","N","N","N","280 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS280M-60-EP [240V]","N","Y","Y","Y","N","N","N","280 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS285M-60B-EP [240V]","N","Y","Y","Y","N","N","N","285 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS285M-60-EP [240V]","N","Y","Y","Y","N","N","N","285 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS290M-60B-EP [240V]","N","Y","Y","Y","N","N","N","290 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS290M-60-EP [240V]","N","Y","Y","Y","N","N","N","290 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS295M-60B-EP [240V]","N","Y","Y","Y","N","N","N","295 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS295M-60-EP [240V]","N","Y","Y","Y","N","N","N","295 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS300M-60-EP [240V]","N","Y","Y","Y","N","N","N","300 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter",0.23,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This microinverter is sold as an individual unit but is only for ACPV modules","N","Y",0.03,null,null,27,32,37,2.3E-2,4.5999999999999999E-2,6.9000000000000006E-2,0.115,0.17249999999999999,0.23,94.655230000000003,96.037739999999999,96.665639999999996,97.423699999999997,97.484939999999995,97.25591,97.176760000000002,95.060559999999995,96.356809999999996,96.706540000000004,97.392669999999995,97.586340000000007,97.529629999999997,97.274749999999997,94.744969999999995,96.105410000000006,96.43141,97.196730000000002,97.469279999999998,97.483500000000006,97.111050000000006,"2017-11-01","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS300M-60BL-EP [208V]","N","Y","Y","Y","N","N","N","300 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM300M-60BL. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS300M-60BL-EP [240V]","N","Y","Y","Y","N","N","N","300 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM300M-60BL. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS300M-60BL-EP-Q [208V]","N","Y","Y","Y","N","N","N","300 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM300M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS300M-60BL-EP-Q [240V]","N","Y","Y","Y","N","N","N","300 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM300M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS305M-60BL-EP [208V]","N","Y","Y","Y","N","N","N","305 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM305M-60BL. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS305M-60BL-EP [240V]","N","Y","Y","Y","N","N","N","305 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM305M-60BL. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS305M-60BL-EP-Q [208V]","N","Y","Y","Y","N","N","N","305 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM305M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS305M-60BL-EP-Q [240V]","N","Y","Y","Y","N","N","N","305 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM305M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS305M-60L-EP [208V]","N","Y","Y","Y","N","N","N","305 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM305M-60L. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS305M-60L-EP [240V]","N","Y","Y","Y","N","N","N","305 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM305M-60L. Microinverter: IQ7-60-ACM-US [208V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS305M-60L-EP-Q [208V]","N","Y","Y","Y","N","N","N","305 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM305M-60L-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS305M-60L-EP-Q [240V]","N","Y","Y","Y","N","N","N","305 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM305M-60L-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS310M-60BL-EP [208V]","N","Y","Y","Y","N","N","N","310 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM310M-60BL. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS310M-60BL-EP [240V]","N","Y","Y","Y","N","N","N","310 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM310M-60BL. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS310M-60BL-EP-Q [208V]","N","Y","Y","Y","N","N","N","310 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM310M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS310M-60BL-EP-Q [240V]","N","Y","Y","Y","N","N","N","310 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM310M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS310M-60L-EP [208V]","N","Y","Y","Y","N","N","N","310 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM310M-60L. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS310M-60L-EP [240V]","N","Y","Y","Y","N","N","N","310 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM310M-60L. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS310M-60L-EP-Q [208V]","N","Y","Y","Y","N","N","N","310 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM310M-60L-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS310M-60L-EP-Q [240V]","N","Y","Y","Y","N","N","N","310 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM310M-60L-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS315M-60BL-EP [208V]","N","Y","Y","Y","N","N","N","315 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM315M-60BL. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS315M-60BL-EP [240V]","N","Y","Y","Y","N","N","N","315 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM315M-60BL. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS315M-60BL-EP-Q [208V]","N","Y","Y","Y","N","N","N","315 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM315M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS315M-60BL-EP-Q [240V]","N","Y","Y","Y","N","N","N","315 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM315M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS315M-60L-EP [208V]","N","Y","Y","Y","N","N","N","315 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM315M-60L. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS315M-60L-EP [240V]","N","Y","Y","Y","N","N","N","315 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM315M-60L. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS315M-60L-EP-Q [208V]","N","Y","Y","Y","N","N","N","315 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM315M-60L-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS315M-60L-EP-Q [240V]","N","Y","Y","Y","N","N","N","315 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM315M-60L-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS320M-60BL-EP [208V]","N","Y","Y","Y","N","N","N","320 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM320M-60BL. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS320M-60BL-EP [240V]","N","Y","Y","Y","N","N","N","320 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM320M-60BL. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS320M-60BL-EP-Q [208V]","N","Y","Y","Y","N","N","N","320 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM320M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS320M-60BL-EP-Q [240V]","N","Y","Y","Y","N","N","N","320 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM320M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS320M-60L-EP [208V]","N","Y","Y","Y","N","N","N","320 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM320M-60L. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS320M-60L-EP [240V]","N","Y","Y","Y","N","N","N","320 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM320M-60L. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS320M-60L-EP-Q [208V]","N","Y","Y","Y","N","N","N","320 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM320M-60L-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS320M-60L-EP-Q [240V]","N","Y","Y","Y","N","N","N","320 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM320M-60L-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS325M-60BL-EP [208V]","N","Y","Y","Y","N","N","N","325 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM325M-60BL. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS325M-60BL-EP [240V]","N","Y","Y","Y","N","N","N","325 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM325M-60BL. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS325M-60BL-EP-Q [208V]","N","Y","Y","Y","N","N","N","325 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM325M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS325M-60BL-EP-Q [240V]","N","Y","Y","Y","N","N","N","325 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black substrate. DC Module: JKM325M-60BL-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS325M-60L-EP [208V]","N","Y","Y","Y","N","N","N","325 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM325M-60L. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS325M-60L-EP [240V]","N","Y","Y","Y","N","N","N","325 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM325M-60L. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS325M-60L-EP-Q [208V]","N","Y","Y","Y","N","N","N","325 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM325M-60L-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS325M-60L-EP-Q [240V]","N","Y","Y","Y","N","N","N","325 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM325M-60L-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS330M-60L-EP [208V]","N","Y","Y","Y","N","N","N","330 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM330M-60L. Microinverter: IQ7-60-ACM-US [208V].",0.24,208,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS330M-60L-EP [240V]","N","Y","Y","Y","N","N","N","330 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM330M-60L. Microinverter: IQ7-60-ACM-US [240V].",0.24,240,97,"UL","[04/18/2019]","[V02.14.02]","2019-07-15","[04/18/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2019-07-15","2020-02-11"]
["Jinko Solar Co., Ltd","JKMS330M-60L-EP-Q [208V]","N","Y","Y","Y","N","N","N","330 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM330M-60L-Q. Microinverter: IQ7-60-x-ACM-US [208V].",0.24,208,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,94.204329999999999,96.226399999999984,97.02145999999999,97.553879999999992,97.414230000000003,96.959759999999989,97.185913100000008,93.324760000000012,95.734390000000005,96.756340000000009,97.463930000000005,97.41528000000001,97.056359999999998,97.080812400000013,92.419209999999993,95.095890000000026,96.538389999999993,97.353760000000008,97.337369999999993,97.025310000000019,96.920530900000003,"2020-02-11"]
["Jinko Solar Co., Ltd","JKMS330M-60L-EP-Q [240V]","N","Y","Y","Y","N","N","N","330 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white substrate. DC Module: JKM330M-60L-Q. Microinverter: IQ7-60-x-ACM-US [240V].",0.24,240,97,"UL","[01/17/2020]","[V02.14.02]","2020-02-11","[01/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,32,37,2.4E-2,4.8000000000000001E-2,7.1999999999999995E-2,0.12,0.18,0.24,93.945300000000003,96.08005,96.814459999999983,97.474629999999991,97.419160000000005,97.02876999999998,97.132815300000004,92.990709999999993,95.658750000000012,96.504930000000002,97.55228000000001,97.614990000000006,97.408739999999995,97.175517999999997,92.006249999999994,95.026440000000008,96.230880000000013,97.381270000000001,97.543800000000005,97.410729999999987,96.998094800000004,"2020-02-11"]
["KACO new energy GmbH","KACO blueplanet 110 TL3 M1 WM OD IIK0 [480V]","N","Y","Y","Y","N","N","N","110 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter   ",109.765,480,98.5,"Intertek","[12/19/2019]","[V 1.07, V 1.09, V 1.11, V 1.13]","2020-02-11","[12/19/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5,null,null,705,854,1300,10.976531999999999,21.953063999999998,32.929595999999997,54.882659999999994,82.323989999999995,109.76531999999999,98.928483999999997,99.071429999999992,99.063512000000017,98.971981999999997,98.818867999999995,98.633778000000007,98.888137459999996,98.584294,98.856462000000008,98.883022000000011,98.796959999999984,98.60845599999999,98.35793000000001,98.679897279999992,97.536302000000006,98.113026000000005,98.289299999999997,98.343285999999992,98.237343999999993,98.019301999999996,98.220666859999994,"2020-02-11"]
["KACO new energy GmbH","KACO blueplanet 110 TL3 M1 WM OD IIKX [480V]","N","Y","Y","Y","N","N","N","110 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter   ",109.765,480,98.5,"Intertek","[12/19/2019]","[V 1.07, V 1.09, V 1.11, V 1.13]","2020-02-11","[12/19/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5,null,null,705,854,1300,10.976531999999999,21.953063999999998,32.929595999999997,54.882659999999994,82.323989999999995,109.76531999999999,98.928483999999997,99.071429999999992,99.063512000000017,98.971981999999997,98.818867999999995,98.633778000000007,98.888137459999996,98.584294,98.856462000000008,98.883022000000011,98.796959999999984,98.60845599999999,98.35793000000001,98.679897279999992,97.536302000000006,98.113026000000005,98.289299999999997,98.343285999999992,98.237343999999993,98.019301999999996,98.220666859999994,"2020-02-11"]
["KACO new energy GmbH","KACO blueplanet 125 TL3 M1 WM OD IIP0 [600V]","N","Y","Y","Y","N","N","N","125 kVA Nominal Power, 137 kVA Max Power, 600Vac, 1500Vdc Grid Support Utility Interactive Inverter",138.66300000000001,600,99,"Intertek","[12/19/2019]","[V 1.07, V 1.09, V 1.11, V 1.13]","2020-02-11","[12/19/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5.57,null,null,875,981,1300,13.866348,27.732696000000001,41.599043999999999,69.331739999999996,103.99760999999999,138.66347999999999,98.896833999999998,99.121973999999994,99.143168000000017,99.081521999999993,98.966363999999999,98.833606000000003,99.010125060000007,98.655450000000002,98.951779999999999,99.00003199999999,98.962208000000004,98.806222000000005,98.623017999999988,98.854323080000015,97.995435999999998,98.454754000000008,98.611918000000003,98.667811999999998,98.557732000000001,98.393072000000004,98.551477380000009,"2020-02-11"]
["KACO new energy GmbH","KACO blueplanet 125 TL3 M1 WM OD IIPX [600V]","N","Y","Y","Y","N","N","N","125 kVA Nominal Power, 137 kVA Max Power, 600Vac, 1500Vdc Grid Support Utility Interactive Inverter",138.66300000000001,600,99,"Intertek","[12/19/2019]","[V 1.07, V 1.09, V 1.11, V 1.13]","2020-02-11","[12/19/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5.57,null,null,875,981,1300,13.866348,27.732696000000001,41.599043999999999,69.331739999999996,103.99760999999999,138.66347999999999,98.896833999999998,99.121973999999994,99.143168000000017,99.081521999999993,98.966363999999999,98.833606000000003,99.010125060000007,98.655450000000002,98.951779999999999,99.00003199999999,98.962208000000004,98.806222000000005,98.623017999999988,98.854323080000015,97.995435999999998,98.454754000000008,98.611918000000003,98.667811999999998,98.557732000000001,98.393072000000004,98.551477380000009,"2020-02-11"]
["KACO new energy GmbH","KACO blueplanet 137 TL3 M1 WM OD IIP0 [600V]","N","Y","Y","Y","N","N","N","137 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter   ",138.66300000000001,600,99,"Intertek","[12/19/2019]","[V 1.07, V 1.09, V 1.11, V 1.13]","2020-02-11","[12/19/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5.57,null,null,875,981,1300,13.866348,27.732696000000001,41.599043999999999,69.331739999999996,103.99760999999999,138.66347999999999,98.896833999999998,99.121973999999994,99.143168000000017,99.081521999999993,98.966363999999999,98.833606000000003,99.010125060000007,98.655450000000002,98.951779999999999,99.00003199999999,98.962208000000004,98.806222000000005,98.623017999999988,98.854323080000015,97.995435999999998,98.454754000000008,98.611918000000003,98.667811999999998,98.557732000000001,98.393072000000004,98.551477380000009,"2020-02-11"]
["KACO new energy GmbH","KACO blueplanet 137 TL3 M1 WM OD IIPX [600V]","N","Y","Y","Y","N","N","N","137 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter   ",138.66300000000001,600,99,"Intertek","[12/19/2019]","[V 1.07, V 1.09, V 1.11, V 1.13]","2020-02-11","[12/19/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5.57,null,null,875,981,1300,13.866348,27.732696000000001,41.599043999999999,69.331739999999996,103.99760999999999,138.66347999999999,98.896833999999998,99.121973999999994,99.143168000000017,99.081521999999993,98.966363999999999,98.833606000000003,99.010125060000007,98.655450000000002,98.951779999999999,99.00003199999999,98.962208000000004,98.806222000000005,98.623017999999988,98.854323080000015,97.995435999999998,98.454754000000008,98.611918000000003,98.667811999999998,98.557732000000001,98.393072000000004,98.551477380000009,"2020-02-11"]
["KACO new energy GmbH","KACO blueplanet 150 TL3 M1 WM OD IIQ0 [660V]","N","Y","Y","Y","N","N","N","150 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter   ",151.22800000000001,660,99,"Intertek","[12/19/2019]","[V 1.07, V 1.09, V 1.11, V 1.13]","2020-02-11","[12/19/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5.25,null,null,960,1045,1300,15.122756000000003,30.245512000000005,45.368268,75.613780000000006,113.42067,151.22756000000001,98.833631999999994,99.109975999999989,99.148942000000005,99.103821999999994,99.010261999999983,98.895336,99.03872539999999,98.698094000000012,99.001002,99.049338000000006,99.013633999999996,98.892204000000007,98.722651999999997,98.925758280000025,98.110169999999997,98.592300000000009,98.741780000000006,98.786256000000009,98.698000000000008,98.552198000000004,98.685699060000019,"2020-02-11"]
["KACO new energy GmbH","KACO blueplanet 150 TL3 M1 WM OD IIQX [660V]","N","Y","Y","Y","N","N","N","150 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter   ",151.22800000000001,660,99,"Intertek","[12/19/2019]","[V 1.07, V 1.09, V 1.11, V 1.13]","2020-02-11","[12/19/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5.25,null,null,960,1045,1300,15.122756000000003,30.245512000000005,45.368268,75.613780000000006,113.42067,151.22756000000001,98.833631999999994,99.109975999999989,99.148942000000005,99.103821999999994,99.010261999999983,98.895336,99.03872539999999,98.698094000000012,99.001002,99.049338000000006,99.013633999999996,98.892204000000007,98.722651999999997,98.925758280000025,98.110169999999997,98.592300000000009,98.741780000000006,98.786256000000009,98.698000000000008,98.552198000000004,98.685699060000019,"2020-02-11"]
["LeadSolar Energy Co., Ltd","LS600 [240V]","N","Y","Y","Y","N","N","N","500 W, 240 Vac Grid Support Utility Interactive Micro-Inverter",0.5,240,95.5,"CSA Group","[4/26/2019]","[V105]","2018-10-15","[4/26/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",0.09,null,null,27,36,45,0.05,0.1,0.15,0.25,0.375,0.5,94.6,95.4,95.6,95.6,95.4,94.9,95.4,94.2,95.6,95.2,95.9,95.7,95.3,95.6,93.7,93.8,94.8,95.9,95.7,95.5,95.5,"2017-10-13","2019-05-01"]
["LeadSolar Energy Co., Ltd","LS700S [208V]","N","Y","Y","Y","N","N","N","600W, 208 Vac Grid Support Utility Interactive Inverter ",0.60599999999999998,208,95.5,"CSA Group","[04/04/2019]","[V105LS700G2]","2019-05-01","[04/04/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",0.21,null,null,52,54,56,6.0579500000000001E-2,0.121159,0.1817385,0.30289749999999999,0.45434624999999995,0.60579499999999997,91.21780860622242,94.31654967853693,94.948172498943123,95.464798860854245,95.566229494460131,95.320894262595061,95.222074634021936,90.055667787780479,93.69487980213664,94.953189354905689,95.701420812888998,95.815995623963047,95.513256022815526,95.336792276754622,90.156890747381297,93.941379845136723,95.007336179834439,95.355803066462244,95.814728731442003,95.555000526460759,95.288499861676584,"2019-05-01"]
["LeadSolar Energy Co., Ltd","LS600X [240V]","N","Y","Y","N","N","N","N","700 W, 240 Vac Grid Support Utility Interactive Microinverter",0.70799999999999996,240,96,"CSA Group","[03/19/2018]","[V105LS700G2HV1.1_789Boot]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",0.16,null,null,50,57,64,7.0800000000000002E-2,0.1416,0.21240000000000001,0.35399999999999998,0.53100000000000003,0.70799999999999996,89.386799999999994,93.546449999999993,95.133979999999994,96.262680000000003,96.577579999999998,96.382440000000003,95.889269999999996,90.188069999999996,93.853949999999998,95.269369999999995,96.306049999999999,96.594769999999997,96.545280000000005,95.979309999999998,87.473979999999997,92.894419999999997,95.062100000000001,96.067639999999997,96.486090000000004,96.485820000000004,95.687250000000006,"2018-04-16","2018-10-15"]
["LG Electronics Inc.","LG315E1K-A5 [208V]","N","Y","Y","Y","N","N","N","315 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,208,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.636139999999997,96.340069999999997,96.930219999999991,97.37612,97.14246,96.57859999999998,96.997494500000002,94.562870000000004,95.684449999999998,96.451030000000003,97.149680000000018,97.092019999999991,96.683809999999994,96.835254800000001,93.928889999999996,95.02709999999999,95.970729999999989,96.918510000000012,96.913079999999994,96.59496,96.571565699999994,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG315E1K-A5 [240V]","N","Y","Y","Y","N","N","N","315 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.253059999999991,96.163120000000006,96.817109999999985,97.302610000000016,97.145589999999984,96.716480000000004,96.952866400000005,94.554840000000013,95.744399999999999,96.281419999999983,97.254899999999992,97.333410000000001,97.170069999999996,96.991923799999995,93.905879999999996,95.090100000000007,95.744929999999997,96.971979999999988,97.148679999999985,97.038429999999991,96.704969500000004,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG320E1K-A5 [208V]","N","Y","Y","Y","N","N","N","320 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,208,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.636139999999997,96.340069999999997,96.930219999999991,97.37612,97.14246,96.57859999999998,96.997494500000002,94.562870000000004,95.684449999999998,96.451030000000003,97.149680000000018,97.092019999999991,96.683809999999994,96.835254800000001,93.928889999999996,95.02709999999999,95.970729999999989,96.918510000000012,96.913079999999994,96.59496,96.571565699999994,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG320E1K-A5 [240V]","N","Y","Y","Y","N","N","N","320 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.253059999999991,96.163120000000006,96.817109999999985,97.302610000000016,97.145589999999984,96.716480000000004,96.952866400000005,94.554840000000013,95.744399999999999,96.281419999999983,97.254899999999992,97.333410000000001,97.170069999999996,96.991923799999995,93.905879999999996,95.090100000000007,95.744929999999997,96.971979999999988,97.148679999999985,97.038429999999991,96.704969500000004,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG325E1C-A5 [208V]","N","Y","Y","Y","N","N","N","325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,208,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.636139999999997,96.340069999999997,96.930219999999991,97.37612,97.14246,96.57859999999998,96.997494500000002,94.562870000000004,95.684449999999998,96.451030000000003,97.149680000000018,97.092019999999991,96.683809999999994,96.835254800000001,93.928889999999996,95.02709999999999,95.970729999999989,96.918510000000012,96.913079999999994,96.59496,96.571565699999994,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG325E1C-A5 [240V]","N","Y","Y","Y","N","N","N","325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.253059999999991,96.163120000000006,96.817109999999985,97.302610000000016,97.145589999999984,96.716480000000004,96.952866400000005,94.554840000000013,95.744399999999999,96.281419999999983,97.254899999999992,97.333410000000001,97.170069999999996,96.991923799999995,93.905879999999996,95.090100000000007,95.744929999999997,96.971979999999988,97.148679999999985,97.038429999999991,96.704969500000004,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG325E1K-A5 [208V]","N","Y","Y","Y","N","N","N","325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,208,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.636139999999997,96.340069999999997,96.930219999999991,97.37612,97.14246,96.57859999999998,96.997494500000002,94.562870000000004,95.684449999999998,96.451030000000003,97.149680000000018,97.092019999999991,96.683809999999994,96.835254800000001,93.928889999999996,95.02709999999999,95.970729999999989,96.918510000000012,96.913079999999994,96.59496,96.571565699999994,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG325E1K-A5 [240V]","N","Y","Y","Y","N","N","N","325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.253059999999991,96.163120000000006,96.817109999999985,97.302610000000016,97.145589999999984,96.716480000000004,96.952866400000005,94.554840000000013,95.744399999999999,96.281419999999983,97.254899999999992,97.333410000000001,97.170069999999996,96.991923799999995,93.905879999999996,95.090100000000007,95.744929999999997,96.971979999999988,97.148679999999985,97.038429999999991,96.704969500000004,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG330E1C-A5 [208V]","N","Y","Y","Y","N","N","N","330 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,208,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.636139999999997,96.340069999999997,96.930219999999991,97.37612,97.14246,96.57859999999998,96.997494500000002,94.562870000000004,95.684449999999998,96.451030000000003,97.149680000000018,97.092019999999991,96.683809999999994,96.835254800000001,93.928889999999996,95.02709999999999,95.970729999999989,96.918510000000012,96.913079999999994,96.59496,96.571565699999994,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG330E1C-A5 [240V]","N","Y","Y","Y","N","N","N","330 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.3,96.2,96.8,97.3,97.1,96.7,97,94.6,95.7,96.3,97.3,97.3,97.2,97,93.9,95.1,95.7,97,97.1,97,96.7,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG335E1C-A5 [208V]","N","Y","Y","Y","N","N","N","335 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,208,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.6,96.3,96.9,97.4,97.1,96.6,97,94.6,95.7,96.5,97.1,97.1,96.7,96.8,93.9,95,96,96.9,96.9,96.6,96.6,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG335E1C-A5 [240V]","N","Y","Y","Y","N","N","N","335 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter",0.28000000000000003,240,97,"UL","[6/29/2017]","[01.06.03]","2018-10-15","[6/29/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.02,null,null,27,36,45,28,56,84,140,210,280,94.3,96.2,96.8,97.3,97.1,96.7,97,94.6,95.7,96.3,97.3,97.3,97.2,97,93.9,95.1,95.7,97,97.1,97,96.7,"2017-08-01","2018-10-15"]
["LG Electronics Inc.","LG355A1C-A5 [208V]","N","Y","N","Y","N","N","N","355 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG355Q1C-A5. Microinverter: LM320UE-A2.",0.32,208,96,"UL","[12/15/2017]","[A320UD260C]","No Information Submitted","[12/15/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.85,null,null,32,35,42,3.2000000000000001E-2,6.4000000000000001E-2,9.6000000000000002E-2,0.16,0.24,0.32,91.3,94.9,95.8,96.5,96.4,95.3,96,90.8,94.9,95.4,96.4,96.3,95.6,95.9,90.2,94.5,95.3,96.2,96.2,95.8,95.7,"2018-02-15"]
["LG Electronics Inc.","LG355A1C-A5 [240V]","N","Y","N","Y","N","N","N","355 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG355Q1C-A5. Microinverter: LM320UE-A2.",0.32,240,97,"UL","[12/15/2017]","[A320UD260C]","No Information Submitted","[12/15/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.16,null,null,32,35,42,3.2000000000000001E-2,6.4000000000000001E-2,9.6000000000000002E-2,0.16,0.24,0.32,92.6,95.9,96.6,97.2,97.2,96.8,96.9,92.6,95.9,96.6,97.1,97.2,96.8,96.8,92.1,95.6,96.4,96.9,97,96.8,96.6,"2018-02-15"]
["LG Electronics Inc.","LG360A1C-A5 [208V]","N","Y","N","Y","N","N","N","360 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG360Q1C-A5. Microinverter: LM320UE-A2.",0.32,208,96,"UL","[12/15/2017]","[A320UD260C]","No Information Submitted","[12/15/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.85,null,null,32,35,42,3.2000000000000001E-2,6.4000000000000001E-2,9.6000000000000002E-2,0.16,0.24,0.32,91.3,94.9,95.8,96.5,96.4,95.3,96,90.8,94.9,95.4,96.4,96.3,95.6,95.9,90.2,94.5,95.3,96.2,96.2,95.8,95.7,"2018-02-15"]
["LG Electronics Inc.","LG360A1C-A5 [240V]","N","Y","N","Y","N","N","N","360 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG360Q1C-A5. Microinverter: LM320UE-A2.",0.32,240,97,"UL","[12/15/2017]","[A320UD260C]","No Information Submitted","[12/15/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.16,null,null,32,35,42,3.2000000000000001E-2,6.4000000000000001E-2,9.6000000000000002E-2,0.16,0.24,0.32,92.6,95.9,96.6,97.2,97.2,96.8,96.9,92.6,95.9,96.6,97.1,97.2,96.8,96.8,92.1,95.6,96.4,96.9,97,96.8,96.6,"2018-02-15"]
["LG Electronics Inc.","LG365A1C-A5 [208V]","N","Y","N","Y","N","N","N","365 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG365Q1C-A5. Microinverter: LM320UE-A2.",0.32,208,96,"UL","[12/15/2017]","[A320UD260C]","No Information Submitted","[12/15/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.85,null,null,32,35,42,3.2000000000000001E-2,6.4000000000000001E-2,9.6000000000000002E-2,0.16,0.24,0.32,91.3,94.9,95.8,96.5,96.4,95.3,96,90.8,94.9,95.4,96.4,96.3,95.6,95.9,90.2,94.5,95.3,96.2,96.2,95.8,95.7,"2018-02-15"]
["LG Electronics Inc.","LG365A1C-A5 [240V]","N","Y","N","Y","N","N","N","365 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG365Q1C-A5. Microinverter: LM320UE-A2.",0.32,240,97,"UL","[12/15/2017]","[A320UD260C]","No Information Submitted","[12/15/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.16,null,null,32,35,42,3.2000000000000001E-2,6.4000000000000001E-2,9.6000000000000002E-2,0.16,0.24,0.32,92.6,95.9,96.6,97.2,97.2,96.8,96.9,92.6,95.9,96.6,97.1,97.2,96.8,96.8,92.1,95.6,96.4,96.9,97,96.8,96.6,"2018-02-15"]
["LG Electronics Inc.","LG370A1C-A5 [208V]","N","Y","N","Y","N","N","N","370 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG370Q1C-A5. Microinverter: LM320UE-A2.",0.32,208,96,"UL","[12/15/2017]","[A320UD260C]","No Information Submitted","[12/15/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.85,null,null,32,35,42,3.2000000000000001E-2,6.4000000000000001E-2,9.6000000000000002E-2,0.16,0.24,0.32,91.3,94.9,95.8,96.5,96.4,95.3,96,90.8,94.9,95.4,96.4,96.3,95.6,95.9,90.2,94.5,95.3,96.2,96.2,95.8,95.7,"2018-02-15"]
["LG Electronics Inc.","LG370A1C-A5 [240V]","N","Y","N","Y","N","N","N","370 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG370Q1C-A5. Microinverter: LM320UE-A2.",0.32,240,97,"UL","[12/15/2017]","[A320UD260C]","No Information Submitted","[12/15/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.16,null,null,32,35,42,3.2000000000000001E-2,6.4000000000000001E-2,9.6000000000000002E-2,0.16,0.24,0.32,92.6,95.9,96.6,97.2,97.2,96.8,96.9,92.6,95.9,96.6,97.1,97.2,96.8,96.8,92.1,95.6,96.4,96.9,97,96.8,96.6,"2018-02-15"]
["LG Electronics Inc.","LG340M1K-L5 [240V]","N","Y","Y","Y","Y","Y*","Y","340 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG340N1K-L5. Microinverter: LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-24","[07/22/2020]","2020-08-24","UL","2020-01-31","2020-08-24","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2020-08-21"]
["LG Electronics Inc.","LG345M1K-L5 [240V]","N","Y","Y","Y","Y","Y*","Y","345 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG345N1K-L5. Microinverter: LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-25","[07/22/2020]","2020-08-25","UL","2020-01-31","2020-08-25","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2020-08-21"]
["LG Electronics Inc.","LG350M1K-L5 [240V]","N","Y","Y","Y","Y","Y*","Y","350 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG350N1K-L5. Microinverter: LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-26","[07/22/2020]","2020-08-26","UL","2020-01-31","2020-08-26","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2020-08-21"]
["LG Electronics Inc.","LG355M1C-N5 [240V]","N","Y","Y","Y","Y","Y*","Y","355 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG355N1C-N5. Microinverter: LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-21","[07/22/2020]","2020-08-21","UL","2020-01-31","2020-08-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2020-08-21"]
["LG Electronics Inc.","LG355M1K-A6 [240V]","N","Y ","Y ","Y ","Y","Y*","Y","355 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG355N1K-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LG360A1K-V5 [240V]","N","Y","Y","Y","Y","Y*","Y","360 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG360Q1K-V5. Microinverter : LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[03/12/2020]","[A320UD3005]","2020-05-01","[03/12/2020]","2020-05-01","UL","2020-01-31","2020-05-01",null,"N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2020-05-01"]
["LG Electronics Inc.","LG360M1C-N5 [240V]","N","Y","Y","Y","Y","Y*","Y","360 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG360N1C-N5. Microinverter: LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-21","[07/22/2020]","2020-08-21","UL","2020-01-31","2020-08-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2020-08-21"]
["LG Electronics Inc.","LG360M1K-A6 [240V]","N","Y ","Y ","Y ","Y","Y*","Y","360 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG360N1K-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LG365A1C-V5 [240V]","N","Y","Y","Y","Y","Y*","Y","365 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1C-V5. Microinverter : LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[09/04/2019]","[A320UD3005]","2019-10-15","[09/04/2019]","2020-05-01","UL","2020-01-31","2020-05-01","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2019-10-15","2020-05-01"]
["LG Electronics Inc.","LG365A1K-V5 [240V]","N","Y","Y","Y","Y","Y*","Y","365 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1K-V5. Microinverter : LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[03/12/2020]","[A320UD3005]","2020-05-01","[03/12/2020]","2020-05-01","UL","2020-01-31","2020-05-01",null,"N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2020-05-01"]
["LG Electronics Inc.","LG365M1C-N5 [240V]","N","Y","Y","Y","Y","Y*","Y","365 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365N1C-N5. Microinverter: LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-21","[07/22/2020]","2020-08-21","UL","2020-01-31","2020-08-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2020-08-21"]
["LG Electronics Inc.","LG365M1K-A6 [240V]","N","Y ","Y ","Y ","Y","Y*","Y","365 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG365N1K-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LG370A1C-V5 [240V]","N","Y","Y","Y","Y","Y*","Y","370 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG370Q1C-V5. Microinverter : LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[09/04/2019]","[A320UD3005]","2019-10-15","[09/04/2019]","2020-05-01","UL","2020-01-31","2020-05-01","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2019-10-15","2020-05-01"]
["LG Electronics Inc.","LG370M1C-N5 [240V]","N","Y","Y","Y","Y","Y*","Y","370 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG370N1C-N5. Microinverter: LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-21","[07/22/2020]","2020-08-21","UL","2020-01-31","2020-08-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2020-08-21"]
["LG Electronics Inc.","LG370M1K-A6 [240V]","N","Y ","Y ","Y ","Y","Y*","Y","370 W, 240Vac, Grid Support Utility Interactive, Monocrystalline ACPV module, black backsheet. DC Module:  LG370N1K-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LG375A1C-V5 [240V]","N","Y","Y","Y","Y","Y*","Y","375 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG375Q1C-V5. Microinverter : LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[09/04/2019]","[A320UD3005]","2019-10-15","[09/04/2019]","2020-05-01","UL","2020-01-31","2020-05-01","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2019-10-15","2020-05-01"]
["LG Electronics Inc.","LG375M1C-A6 [240V]","N","Y","Y","Y","Y","Y*","Y","375 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG375N1C-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LG375M1K-A6 [240V]","N","Y","Y ","Y ","Y ","Y*","Y","375 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module : LG375N1K-A6, Microinverter : LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[08/03/2021]","[A320UD260C]; [A320UD3005]","2021-09-13","[08/03/2021]","2021-09-13","UL","2020-01-31","2021-09-13","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-09-13"]
["LG Electronics Inc.","LG380A1C-V5 [240V]","N","Y","Y","Y","Y","Y*","Y","380 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG380Q1C-V5. Microinverter : LM320UE-A2 [240V].",0.32100000000000001,240,97,"UL","[09/04/2019]","[A320UD3005]","2019-10-15","[09/04/2019]","2020-05-01","UL","2020-01-31","2020-05-01","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2019-10-15","2020-05-01"]
["LG Electronics Inc.","LG380M1C-A6 [240V]","N","Y","Y","Y","Y","Y*","Y","380 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG380N1C-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LG380M1K-A6 [240V]","N","Y","Y ","Y ","Y ","Y*","Y","380 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module : LG380N1K-A6, Microinverter : LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[08/03/2021]","[A320UD260C]; [A320UD3005]","2021-09-13","[08/03/2021]","2021-09-13","UL","2020-01-31","2021-09-13","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-09-13"]
["LG Electronics Inc.","LG385M1C-A6 [240V]","N","Y","Y","Y","Y","Y*","Y","385 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG385N1C-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LG395A1C-A6 [240V]","N","Y ","Y ","Y ","Y","Y*","Y","395 W, 240Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG395Q1C-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LG400A1C-A6 [240V]","N","Y ","Y ","Y ","Y","Y*","Y","400 W, 240Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG400Q1C-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LG405A1C-A6 [240V]","N","Y ","Y ","Y ","Y","Y*","Y","405 W, 240Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG405Q1C-A6, Microinverter: LM320UE-A2 [240V]",0.32100000000000001,240,97,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2021-05-11"]
["LG Electronics Inc.","LM320UE-A2 [240V]","N","Y","Y","Y","Y","Y*","Y","320 W, 240 Vac Grid Support Utility Interactive Microinverter ",0.32100000000000001,240,97,"UL","[01/04/2018]; [08/23/2019]","[A320UD260C]; [A320UD3005]","2019-10-01","[01/04/2018]","2020-05-01","UL","2020-01-31","2020-05-01",null,"N","Y",0.15,null,null,32,35,42,3.2101461295681102E-2,6.4202922591362205E-2,9.6304383887043293E-2,0.1605073064784055,0.24076095971760825,0.321014612956811,92.781996685082845,96.016577900552448,96.712061325966872,97.206571823204499,97.206013812154794,96.785938015947153,96.889420425659296,92.780040331491676,95.940045856353578,96.643065745856305,97.121097790055131,97.151420441989018,96.856468508287477,96.833878591160243,92.188028176795584,95.705816022099413,96.460323756906035,96.832819337016616,96.973497237569191,96.799745215102377,96.618883636445801,"2018-02-15","2020-05-01"]
["LG Electronics Inc.","LG340M1K-L5 [208V]","N","Y","Y","Y","Y","Y*","Y","340 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG340N1K-L5. Microinverter: LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-21","[07/22/2020]","2020-08-21","UL","2020-01-31","2020-08-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2020-08-21"]
["LG Electronics Inc.","LG345M1K-L5 [208V]","N","Y","Y","Y","Y","Y*","Y","345 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG345N1K-L5. Microinverter: LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-22","[07/22/2020]","2020-08-22","UL","2020-01-31","2020-08-22","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2020-08-21"]
["LG Electronics Inc.","LG350M1K-L5 [208V]","N","Y","Y","Y","Y","Y*","Y","350 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG350N1K-L5. Microinverter: LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-23","[07/22/2020]","2020-08-23","UL","2020-01-31","2020-08-23","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2020-08-21"]
["LG Electronics Inc.","LG355M1C-N5 [208V]","N","Y","Y","Y","Y","Y*","Y","355 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG355N1C-N5. Microinverter: LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-21","[07/22/2020]","2020-08-21","UL","2020-01-31","2020-08-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2020-08-21"]
["LG Electronics Inc.","LG355M1K-A6 [208V]","N","Y ","Y ","Y ","Y","Y*","Y","355 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG355N1K-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LG360A1K-V5 [208V]","N","Y","Y","Y","Y","Y*","Y","360 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG360Q1K-V5. Microinverter : LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[03/12/2020]","[A320UD3005]","2020-05-01","[03/12/2020]","2020-05-01","UL","2020-01-31","2020-05-01",null,"N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2020-05-01"]
["LG Electronics Inc.","LG360M1C-N5 [208V]","N","Y","Y","Y","Y","Y*","Y","360 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG360N1C-N5. Microinverter: LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-21","[07/22/2020]","2020-08-21","UL","2020-01-31","2020-08-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2020-08-21"]
["LG Electronics Inc.","LG360M1K-A6 [208V]","N","Y ","Y ","Y ","Y","Y*","Y","360 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG360N1K-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LG365A1C-V5 [208V]","N","Y","Y","Y","Y","Y*","Y","365 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1C-V5. Microinverter : LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[09/04/2019]","[A320UD3005]","2019-10-15","[09/04/2019]","2020-05-01","UL","2020-01-31","2020-05-01","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2019-10-15","2020-05-01"]
["LG Electronics Inc.","LG365A1K-V5 [208V]","N","Y","Y","Y","Y","Y*","Y","365 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1K-V5. Microinverter : LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[03/12/2020]","[A320UD3005]","2020-05-01","[03/12/2020]","2020-05-01","UL","2020-01-31","2020-05-01",null,"N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2020-05-01"]
["LG Electronics Inc.","LG365M1C-N5 [208V]","N","Y","Y","Y","Y","Y*","Y","365 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365N1C-N5. Microinverter: LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-21","[07/22/2020]","2020-08-21","UL","2020-01-31","2020-08-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2020-08-21"]
["LG Electronics Inc.","LG365M1K-A6 [208V]","N","Y ","Y ","Y ","Y","Y*","Y","365 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG365N1K-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LG370A1C-V5 [208V]","N","Y","Y","Y","Y","Y*","Y","370 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG370Q1C-V5. Microinverter : LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[09/04/2019]","[A320UD3005]","2019-10-15","[09/04/2019]","2020-05-01","UL","2020-01-31","2020-05-01","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2019-10-15","2020-05-01"]
["LG Electronics Inc.","LG370M1C-N5 [208V]","N","Y","Y","Y","Y","Y*","Y","370 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG370N1C-N5. Microinverter: LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[07/22/2020]","[A320UD260C, A320UD3005]","2020-08-21","[07/22/2020]","2020-08-21","UL","2020-01-31","2020-08-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2020-08-21"]
["LG Electronics Inc.","LG370M1K-A6 [208V]","N","Y ","Y ","Y ","Y","Y*","Y","370 W, 208Vac, Grid Support Utility Interactive, Monocrystalline ACPV module, black backsheet. DC Module:  LG370N1K-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LG375A1C-V5 [208V]","N","Y","Y","Y","Y","Y*","Y","375 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG375Q1C-V5. Microinverter : LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[09/04/2019]","[A320UD3005]","2019-10-15","[09/04/2019]","2020-05-01","UL","2020-01-31","2020-05-01","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2019-10-15","2020-05-01"]
["LG Electronics Inc.","LG375M1C-A6 [208V]","N","Y","Y","Y","Y","Y*","Y","375 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG375N1C-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LG375M1K-A6 [208V]","N","Y","Y ","Y ","Y ","Y*","Y","375 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module : LG375N1K-A6, Microinverter : LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[08/03/2021]","[A320UD260C]; [A320UD3005]","2021-09-13","[08/03/2021]","2021-09-13","UL","2020-01-31","2021-09-13","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-09-13"]
["LG Electronics Inc.","LG380A1C-V5 [208V]","N","Y","Y","Y","Y","Y*","Y","380 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG380Q1C-V5. Microinverter : LM320UE-A2 [208V].",0.32200000000000001,208,96.5,"UL","[09/04/2019]","[A320UD3005]","2019-10-15","[09/04/2019]","2020-05-01","UL","2020-01-31","2020-05-01","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2019-10-15","2020-05-01"]
["LG Electronics Inc.","LG380M1C-A6 [208V]","N","Y","Y","Y","Y","Y*","Y","380 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG380N1C-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LG380M1K-A6 [208V]","N","Y","Y ","Y ","Y ","Y*","Y","380 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module : LG380N1K-A6, Microinverter : LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[08/03/2021]","[A320UD260C]; [A320UD3005]","2021-09-13","[08/03/2021]","2021-09-13","UL","2020-01-31","2021-09-13","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-09-13"]
["LG Electronics Inc.","LG385M1C-A6 [208V]","N","Y","Y","Y","Y","Y*","Y","385 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG385N1C-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LG395A1C-A6 [208V]","N","Y ","Y ","Y ","Y","Y*","Y","395 W, 208Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG395Q1C-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LG400A1C-A6 [208V]","N","Y ","Y ","Y ","Y","Y*","Y","400 W, 208Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG400Q1C-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LG405A1C-A6 [208V]","N","Y ","Y ","Y ","Y","Y*","Y","405 W, 208Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG405Q1C-A6, Microinverter: LM320UE-A2 [208V]",0.32200000000000001,208,96.5,"UL","[04/10/2021]","[A320UD3005]","2021-05-11","[04/10/2021]","2021-05-11","UL","2020-01-31","2021-05-11","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2021-05-11"]
["LG Electronics Inc.","LM320UE-A2 [208V]","N","Y","Y","Y","Y","Y*","Y","320 W, 208 Vac Grid Support Utility Interactive Microinverter",0.32200000000000001,208,96.5,"UL","[01/04/2018]; [08/23/2019]","[A320UD260C]; [A320UD3005]","2019-10-01","[01/04/2018]","2020-05-01","UL","2020-01-31","2020-05-01",null,"N","Y",0.11,null,null,32,35,42,3.2245584333333376E-2,6.4491168666666751E-2,9.6736753000000106E-2,0.16122792166666686,0.24184188250000027,0.32245584333333371,93.501750276243101,96.119155590916733,96.21239116022106,96.933422099447512,96.761991160220816,95.823264640884048,96.5225519176673,93.31171160220994,95.996981552164812,95.993242541436459,96.829142019643868,96.710827071823189,96.017313259668299,96.443230481843926,92.760658011049742,95.72480220994477,95.529522651933647,96.597681215469635,96.567816022099379,96.093392265193287,96.231334309392224,"2018-02-15","2020-05-01"]
["LG Electronics Inc.","D007KEEN261 [208V]","Y","Y","Y","Y","Y","Y*","Y","6656W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter\n",6.6559999999999997,208,97.5,"CSA Group","[08/30/2018]","[1.4.1]","2018-10-15","[08/30/2018]","2020-05-11","CSA Group","2020-03-26","2020-05-11",null,"Y","N",1.1499999999999999,null,null,270,380,450,0.66559999999999997,1.3311999999999999,1.9967999999999999,3.3279999999999998,4.992,6.6559999999999997,94.577142857142846,96.30147619047618,96.99633333333334,97.387761904761902,97.294809523809505,96.929047619047623,97.101850952380943,95.905285714285696,97.331380952380954,97.763285714285729,97.861904761904768,97.586190476190467,97.213761904761895,97.566743809523814,95.039238095238076,96.954095238095235,97.465952380952373,97.73076190476192,97.510285714285715,97.146190476190469,97.406409523809529,"2018-10-01","2020-05-11"]
["LG Electronics Inc.","D007KEEN261 [240V]","Y","Y","Y","Y","Y","Y*","Y","7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",7.68,240,97.5,"CSA Group","[08/30/2018]","[1.4.1]","2018-10-15","[08/30/2018]","2020-05-11","CSA Group","2020-03-26","2020-05-11",null,"Y","N",1.19,null,null,270,380,450,0.76800000000000002,1.536,2.3039999999999998,3.84,5.76,7.68,95.141761904761907,96.556571428571417,97.332523809523806,97.597190476190477,97.510428571428591,97.13038095238096,97.345858095238114,96.495714285714271,97.678238095238086,98.032761904761898,98.064428571428579,97.776238095238099,97.431095238095239,97.794162857142865,95.768333333333331,97.321714285714293,97.81547619047619,97.95814285714286,97.747952380952384,97.447142857142879,97.684658095238092,"2018-10-01","2020-05-11"]
["NeoVolta Inc.","NV7600 [208V]","Y","Y ","Y ","Y ","Y ","Y*","Y ","7680 W, 208 Vac, 1-phase hybrid Grid Support Utility Interactive Inverter that works with PV and energy storage. Inverter is capable of PCS functionality.",7.4473000000000003,208,96.5,"SGS","[02/18/2019]","[Ver1585]","2019-03-15","[02/18/2019]","2020-08-11","CSA Group","2020-06-22","2020-08-11","The NV7600 inverter and batteries are components of the NV14 Energy Storage System.","N","N",13.4,null,null,240,370,425,0.74473167219999992,1.4894633443999998,2.2341950165999998,3.7236583609999996,5.5854875414999992,7.4473167219999992,91.486264550039337,94.760248969262392,95.352663162123591,97.296267712149941,97.185123619139432,96.859870192303077,96.623107857230082,91.699965357816623,94.963850615122325,95.495711668085661,97.428829723597843,97.231635305996946,96.929680695919046,96.714981534168942,91.907256517136105,94.928995056460167,95.369819427808693,97.318654328391062,96.925617369279323,97.063119550059341,96.527768937028625,"2019-03-15","2021-08-11"]
["NeoVolta Inc.","NV7600 [240V]","Y","Y ","Y ","Y ","Y ","Y*","Y ","7680W, 240 Vac, 1-phase hybrid Grid Support Utility Interactive Inverter that works with PV and energy storage. Inverter is capable of PCS functionality.",7.657,240,96.5,"SGS","[02/18/2019]","[Ver1585]","2019-03-15","[02/18/2019]","2020-08-11","CSA Group","2020-06-22","2020-08-11","The NV7600 inverter and batteries are components of the NV14 Energy Storage System.","N","N",13.4,null,null,240,370,425,0.76571188991999994,1.5314237798399999,2.2971356697599994,3.8285594495999993,5.7428391743999985,7.6571188991999986,91.819615795312856,94.910997776364283,95.520513772204296,97.079550873826477,96.988012087484861,97.130498991107089,96.527673212721126,91.670908997205146,95.000841359179049,95.707732171504404,97.546548492774008,97.445862228404309,97.08346102095264,96.887061504012152,91.551333333333318,95.071706716631525,95.858438563503356,97.600636400067273,97.273962762904389,97.086789328574284,96.824324671567467,"2019-03-15","2021-08-11"]
["Northern Electric & Power Co. Ltd","BDM-800-208A [208V]","N","Y ","Y ","Y ","Y ","Y*","Y ","700 VA, 208 Vac Grid Support Utility Interactive Inverter",0.70699999999999996,208,96.5,"Intertek","[06/17/2021]","[9200]","2021-08-11","[06/17/2021]","2021-08-11","Intertek","2021-06-01","2021-08-11",null,"N","Y",0.1,null,null,22,35,55,7.0699999999999999E-2,0.1414,0.21209999999999998,0.35349999999999998,0.53025,0.70699999999999996,93.659878341771133,95.598959379312547,96.960958378720647,96.829648417129164,96.623660794086305,96.490448879537468,96.530946940522696,92.605999393776671,96.169212831435587,96.849634421520349,96.868930206849456,96.682388461752936,96.121686804343497,96.524882316289904,93.466609266215912,94.887549200983528,97.06118213346906,96.875624634958072,96.695540555900891,96.437884064723391,96.544795557918931,"2021-08-11"]
["Northern Electric & Power Co. Ltd","BDM-800-240A [240V]","N","Y ","Y ","Y ","Y ","Y*","Y ","768 VA, 240 Vac Grid Support Utility Interactive Inverter",0.77200000000000002,240,96.5,"Intertek","[06/17/2021]","[9200]","2021-08-11","[06/17/2021]","2021-08-11","Intertek","2021-06-01","2021-08-11",null,"N","Y",0.1,null,null,22,35,55,7.7200000000000005E-2,0.15440000000000001,0.2316,0.38600000000000001,0.57899999999999996,0.77200000000000002,94.208856266297204,95.833517912512164,96.865359581511385,97.073150158389652,96.589181487711045,96.090212419485781,96.566011638781831,93.953509038405826,96.862836506766399,96.648396516048521,97.078066199439448,96.979016356936057,96.429140353378415,96.805819357527696,93.466609266215912,95.983726516776017,96.774230402684864,96.757834719905929,96.654785511358767,96.415963905928336,96.517738152306435,"2021-08-11"]
["ONE SUN, MEXICO S.A. DE C.V.","1S480-10k [480V]","N","Y","Y","Y","N","N","N","10 kW, 480 Vac, Grid Support Utility Interactive Inverter",9.9749999999999996,480,97.5,"UL","[10/26/2018]","[0.28]","2018-11-15","[10/26/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",8.3000000000000007,null,null,450,750,850,0.99750000000000005,1.9950000000000001,2.9924999999999997,4.9874999999999998,7.4812499999999993,9.9749999999999996,94.115714285714276,96.777142857142849,97.342857142857142,97.727142857142866,97.695714285714303,97.517142857142858,97.4619142857143,94.11,96.84571428571428,97.644285714285701,98.161428571428573,98.220000000000013,98.139999999999986,97.901500000000013,93.187142857142859,96.460000000000008,97.455714285714294,98.102857142857147,98.238571428571433,98.200000000000017,97.823214285714286,"2018-11-15"]
["OutBack Power Technologies, Inc.","SBX5048-120/240 [240V]","Y","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac, Multimode Grid Support Utility Interactive PV and Battery Inverter with PCS Functionality",4.9850000000000003,240,94,"UL","[08/08/2018];[08/08/2018];[01/28/2021]","[NPC:0.0.0.2.2.0.9352,PBM:0.3.1.0.0.0.9359];[NPC:0.0.0.3.0.2.10015,PBM:0.3.1.0.0.6.10006];[NPC:0.0.0.3.0.2.10164,PMB:0.3.1.0.0.6.10482]","2019-04-02","[08/08/2018];[08/08/2018];[01/28/2021]","2021-03-11","SunSpec Alliance","2020-01-28","2020-03-23",null,"Y","N",24.85,null,null,250,420,550,0.5,1,1.5,2.5,3.75,5,85.911187999999996,91.878574,93.403974000000005,94.205962,94.083302000000003,93.775123999999991,93.575011380000007,87.041831999999999,92.430833999999976,94.191839999999999,94.897618000000008,95.095255999999992,94.894152000000005,94.479928839999985,85.362352000000001,91.925973999999997,93.509060000000005,94.477918000000003,94.741786000000005,94.617313999999993,94.016255040000004,"2018-09-17","2021-03-11"]
["OutBack Power Technologies, Inc.","PHXL480-10k [480V]","N","Y","Y","Y","N","N","N","10 kW, 480 Vac, 3 phase Grid Support Utility Interactive Inverter    ",9.9749999999999996,480,97.5,"UL","[11/27/2018]","[0.28]","2019-02-15","[11/27/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",8.3000000000000007,null,null,450,750,850,0.99750000000000005,1.9950000000000001,2.9924999999999997,4.9874999999999998,7.4812499999999993,9.9749999999999996,94.115714285714276,96.777142857142849,97.342857142857142,97.727142857142866,97.695714285714303,97.517142857142858,97.4619142857143,94.11,96.84571428571428,97.644285714285701,98.161428571428573,98.220000000000013,98.139999999999986,97.901500000000013,93.187142857142859,96.460000000000008,97.455714285714294,98.102857142857147,98.238571428571433,98.200000000000017,97.823214285714286,"2019-02-15"]
["Pika Energy","X7603 [240V]","N","Y","Y","Y","N","N","N","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter",7.585,240,96.5,"Intertek","[11/22/2017]","[11430]","2018-10-15","[11/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.29,null,null,390,400,420,0.76,1.52,2.2799999999999998,3.79,5.69,7.59,91.7,95.9,96.6,97.3,97.2,97,96.9,91,95.4,96.5,97.3,97.1,97,96.8,90.5,95.2,96.3,96.9,97,96.9,96.5,"2018-04-02","2018-10-15"]
["Pika Energy","X7601 [240V]","N","Y","Y","Y","N","N","N","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter",7.5869999999999997,240,96.5,"Intertek","[11/22/2017]","[11430]","2018-10-15","[11/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.29,null,null,390,400,420,0.76,1.52,2.2799999999999998,3.79,5.69,7.59,91.7,95.9,96.6,97.3,97.2,97,96.9,91,95.4,96.5,97.3,97.1,97,96.8,90.5,95.2,96.3,96.9,97,96.9,96.5,"2017-12-15","2018-10-15"]
["Pika Energy","X7602 [240V]","Y","Y","Y","Y","Y","Y","Y","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter",7.5869999999999997,240,96.5,"Intertek","[11/11/2019]","[12982]","2018-10-15","[11/11/2019]","2020-03-23","SunSpec Alliance","2019-11-26","2020-03-23",null,"N","N",1.29,null,null,390,400,420,0.75900000000000001,1.5169999999999999,2.2759999999999998,3.7930000000000001,5.6890000000000001,7.5860000000000003,91.67,95.89,96.62,97.26,97.24,97.04,96.87,91.01,95.4,96.52,97.26,97.15,97.01,96.75,90.48,95.21,96.33,96.86,97.02,96.91,96.55,"2017-12-15","2020-03-23"]
["Pika Energy","X11403 [208V]","N","Y","Y","Y","N","N","N","11.4 kW, 208 Vac Grid Support Utility Interactive Inverter",11.18,208,97.5,"Intertek","[11/22/2017]","[11430]","2018-10-15","[11/22/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",0.13,null,null,390,400,420,1.1200000000000001,2.2400000000000002,3.35,5.59,8.39,11.18,97.2,97.4,97.6,97.6,97.4,97.1,97.5,97,97.3,97.7,97.5,97.3,96.9,97.3,95.8,97.2,97.3,97.4,97.1,96.9,97.1,"2018-04-02","2018-10-15"]
["Pika Energy","X11402 [208V]","Y","Y","Y","Y","Y","Y","Y","11.4 kW, 208 Vac Grid Support Utility Interactive Inverter",11.186999999999999,208,97.5,"Intertek","[11/11/2019]","[12982]","2018-10-15","[11/11/2019]","2020-03-23","SunSpec Alliance","2019-11-26","2020-03-23",null,"N","N",0.13,null,null,390,400,420,1.1200000000000001,2.2400000000000002,3.36,5.59,8.39,11.19,97.2,97.4,97.6,97.6,97.4,97.1,97.5,97,97.3,97.7,97.5,97.3,96.9,97.3,95.8,97.2,97.3,97.4,97.1,96.9,97.1,"2017-12-15","2020-03-23"]
["POMCube Inc.","PNZ-10K1N2-NA0 [240V]","Y","Y","Y","Y","Y","Y","Y","10kW, 240 Vac Split Phase, Transformerless Grid Support Utility Interactive Hybrid Inverter for PV and Energy Storage Application   ",9.923,240,94,"Intertek","[04/14/2021]","[UPCS-PV/V10039, UPCS-DCAC/V32011, UPCS-ARM/V32030]","2021-03-22","[04/14/2021]","2021-05-21","SunSpec Alliance","2021-03-23","2021-05-21",null,"N","N",21.92,null,null,250,360,530,0.99226600000000009,1.9845320000000002,2.9767980000000001,4.9613300000000002,7.4419950000000004,9.9226600000000005,91.272774666419039,93.866547913879771,92.84659327012335,93.981799893497353,94.188233466226848,93.891807441863762,93.836361661593429,94.433006068625858,94.228691789218004,93.578985142743548,93.090516726080907,94.039130481670156,94.297421038478006,93.822851769021241,93.369742705303821,95.176365403486585,93.792771682156086,94.576490734167592,94.884428609312039,95.158111517001529,94.656456373205856,"2021-03-22","2021-05-21"]
["Power Electronics","FS1050CU15 [565V]","N","Y","y","N","N","N","N","1050 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box",1163.5,565,97,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 15 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",338.51,null,null,800,900,1200,116,233,349,582,873,1164,93,96.2,96.7,97.5,97.6,97.5,97.2,93,96.1,96.7,97.4,97.5,97.3,97.1,93.2,96.2,96.6,97.4,97.6,97.3,97.2,"2018-05-15","2018-10-15"]
["Power Electronics","FS1100CU15O3 [600V]","N","Y","y","N","N","N","N","1100 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant",1176.44,600,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 11 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",358.91,null,null,849,940,1200,118,235,353,588,882,1176,95.9,97.5,97.7,98,98,98,97.9,95.8,97.4,97.7,98,97.9,97.9,97.8,95.8,97.4,97.7,98,97.9,97.9,97.8,"2018-05-15","2018-10-15"]
["Power Electronics","FS1100CU15 [600V]","N","Y","y","N","N","N","N","1100 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box",1209.25,600,97,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 11 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",347.22,null,null,849,940,1200,121,242,363,605,907,1209,93.1,96.2,96.8,97.5,97.8,97.7,97.3,93.1,96.1,96.8,97.5,97.6,97.6,97.2,93.2,96.2,96.7,97.5,97.7,97.5,97.2,"2018-05-15","2018-10-15"]
["Power Electronics","FS1200CU15 [645V]","N","Y","y","N","N","N","N","1200 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box",1300.9000000000001,645,97.5,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 12 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",348.45,null,null,913,980,1200,130,260,390,650,976,1301,93.5,96.5,97,97.7,97.8,97.7,97.5,93.5,96.5,96.9,97.6,97.7,97.6,97.4,93.5,96.5,96.9,97.6,97.8,97.6,97.4,"2018-05-15","2018-10-15"]
["Power Electronics","FS1275CU15 [690V]","N","Y","y","N","N","N","N","1275 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box",1389.08,690,97,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 1275 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",353.05,null,null,976,1030,1200,139,278,417,695,1042,1389,91.8,95.5,96.2,97.7,97.9,97.8,97.3,91.7,95.5,96.3,97.6,97.8,97.6,97.2,91.9,95.6,96.3,97.6,97.8,97.6,97.2,"2018-05-15","2018-10-15"]
["Power Electronics","FS1400CU15 [565V]","N","Y","y","N","N","N","N","1400 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box",1517.09,565,97.5,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 14 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",359.56,null,null,800,900,1200,152,303,455,759,1138,1517,94.3,96.5,97.3,97.7,97.8,97.6,97.5,94.3,96.4,97.2,97.7,97.7,97.5,97.4,94.4,96.5,97.2,97.6,97.7,97.5,97.5,"2018-05-15","2018-10-15"]
["Power Electronics","FS1500CU15O3 [600V]","N","Y","Y","N","N","N","N","1500 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant",1594.72,600,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 15 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",379.71,null,null,849,940,1200,159,319,478,797,1196,1595,96.9,97.6,97.9,98.1,98,97.9,97.9,96.6,97.5,97.8,98,98,97.8,97.9,96.7,97.5,97.8,98,98,97.8,97.9,"2018-05-15","2018-10-15"]
["Power Electronics","FS1475CU15 [600V]","N","Y","Y","N","N","N","N","1475 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box",1610.37,600,97.5,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 1475 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",368.71,null,null,849,940,1200,161,322,483,805,1208,1610,94.5,96.7,97.5,97.8,97.9,97.6,97.6,94.5,96.6,97.4,97.8,97.8,97.6,97.5,94.6,96.6,97.4,97.7,97.8,97.5,97.5,"2018-05-15","2018-10-15"]
["Power Electronics","FS1600CU15 [645V]","N","Y","Y","N","N","N","N","1600 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box",1734.81,645,97.5,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 16 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",373.96,null,null,913,980,1200,173,347,520,867,1301,1735,94.7,96.8,97.5,98,98,97.8,97.7,94.7,96.8,97.5,97.9,97.9,97.7,97.6,94.7,96.8,97.5,97.8,97.9,97.7,97.6,"2018-05-15","2018-10-15"]
["Power Electronics","FS1700CU15 [690V]","N","Y","Y","N","N","N","N","1700 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box",1850.63,690,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 17 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",368.51,null,null,976,1030,1200,185,370,555,925,1388,1851,95,97,97.7,98.1,98.2,97.9,97.9,94.9,97,97.6,98.1,98,97.9,97.8,94.9,96.9,97.6,98,98.1,97.8,97.8,"2018-05-15","2018-10-15"]
["Power Electronics","FS1750CU15 [565V]","N","Y","Y","N","N","N","N","1750 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box",1896.53,565,97.5,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 175 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",378.47,null,null,800,900,1200,190,379,569,948,1422,1897,94.8,96.6,97.4,98,97.9,97.7,97.6,94.8,96.5,97.3,97.8,97.8,97.6,97.5,94.7,96.4,97.3,97.8,97.8,97.5,97.5,"2018-05-15","2018-10-15"]
["Power Electronics","FS1850CU15O3 [600V]","N","Y","Y","N","N","N","N","1850 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant",1974.29,600,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 185 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",397.3,null,null,849,940,1200,197,395,592,987,1481,1974,96.9,97.7,97.9,98.1,98.1,97.9,98,96.7,97.5,97.8,98,98,97.8,97.9,96.8,97.6,97.9,98,98,97.8,97.9,"2018-05-15","2018-10-15"]
["Power Electronics","FS1850CU15 [600V]","N","Y","Y","N","N","N","N","1850 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box",2020.96,600,97.5,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 185 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",388.77,null,null,849,940,1200,202,404,606,1010,1516,2021,95.1,96.7,97.5,98,98,97.8,97.8,95,96.6,97.5,97.9,97.9,97.7,97.7,95,96.6,97.4,97.9,97.9,97.6,97.7,"2018-05-15","2018-10-15"]
["Power Electronics","FS2000K [600V]","N","Y","Y","Y","N","N","N","2100 kW, 600 Vac Grid Support Utility Interactive Inverter",2103.4160000000002,600,98,"MET","[05/23/2018]","[1.0.0.]","2019-04-02","[05/23/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 21 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.\nThe inverter is central control composed by 4 modules.","N","N",442.59,null,null,849,940,1200,210.34160000000003,420.68320000000006,631.02480000000003,1051.7080000000001,1577.5620000000001,2103.4160000000002,96.091948793980521,97.52381719894349,97.970395382082458,98.380642306225923,98.207786735688586,97.913401339706525,98.082048178764026,96.123454539756565,97.504043463054401,97.943753029184052,98.208480867701212,98.130647039387711,97.727925324679489,97.992810897571786,96.196419543681841,97.45353356447589,97.985933301735514,98.35572202092888,98.140968256141562,97.747682372282853,98.035644374943558,"2019-04-02"]
["Power Electronics","FS2000CU15 [645V]","N","Y","Y","N","N","N","N","2000 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box",2162.42,645,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 2 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",388.97,null,null,913,980,1200,216,432,649,1081,1622,2162,95.2,96.9,97.6,98.1,98.1,97.9,97.9,95.2,96.8,97.5,98,98,97.8,97.8,95.2,96.8,97.5,98,98,97.8,97.7,"2018-05-15","2018-10-15"]
["Power Electronics","FS2000M [34000V]","N","Y","Y","Y","N","N","N","2000 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer",2178.0680000000002,34500,97,"MET","[05/23/2018]","[1.0.0.]","2019-03-15","[05/23/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%).","N","N",5970,null,null,849,940,1200,217.80680000000004,435.61360000000008,653.42040000000009,1089.0340000000001,1633.5510000000002,2178.0680000000002,93.498291666666674,95.993500000000012,96.801083333333324,97.45808333333332,97.657208333333344,97.554791666666659,97.257994166666677,93.349208333333337,95.898333333333326,96.826083333333344,97.39595833333334,97.562875000000005,97.422291666666666,97.180604583333349,93.411374999999992,95.928666666666672,96.709041666666678,97.39233333333334,97.618083333333331,97.483541666666682,97.202124583333344,"2019-03-15"]
["Power Electronics","FS2125K [600V]","N","Y","Y","Y","N","N","N","2200 kW, 600 Vac Grid Support Utility Interactive  Inverter",2201.52,600,98,"SGS North America","[03/10/2020]","[1.9.1]","2020-05-21","[03/10/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","The inverter is central control composed by 4 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 2225 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",302.3,null,null,849,940,1200,220.15200000000002,440.30400000000003,660.45600000000002,1100.76,1651.1399999999999,2201.52,95.804907414924713,97.356315698858239,97.972252575706491,98.307120739567267,98.257973998141765,98.057912971322196,98.080799613515055,95.711942485309351,97.252883277553337,97.869176987320316,98.215343983428355,98.126801300706035,97.901609475561344,97.962930501440695,95.672305048269706,97.238380055006417,97.842843520666392,98.218047945153614,98.124844769961385,97.882464731122624,97.956033460278988,"2020-05-21"]
["Power Electronics","FS2180K [615V]","N","Y","Y","Y","N","N","N","2255 kW, 615 Vac Grid Support Utility Interactive  Inverter",2259.5,615,98,"SGS North America","[03/10/2020]","[1.9.1]","2020-05-21","[03/10/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","The inverter is central control composed by 4 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on PROLEC GE PAD-MOUNTED KNAN - 2255KVA - 12.47kV.","N","N",302.3,null,null,870,950,1200,225.95000000000002,451.90000000000003,677.85,1129.75,1694.625,2259.5,95.822769527578586,97.337628134936764,97.990203876365328,98.314335644844846,98.278510733061083,98.098935889359296,98.097184621421576,95.735520650635664,97.269323280646191,97.889357971320266,98.260010785119448,98.217758687389335,97.998278395854285,98.029538235600313,95.702054418754855,97.250709241671188,97.877462057957985,98.234263884282484,98.205604823030185,97.991287285791216,98.013643421983588,"2020-05-21"]
["Power Electronics","FS2100CU15 [565V]","N","Y","Y","N","N","N","N","2100 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box",2275.89,565,97.5,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 21 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",398.85,null,null,800,900,1200,228,455,683,1138,1707,2276,95.4,97.2,97.6,98,98,97.7,97.8,95.2,97.1,97.6,97.9,97.8,97.6,97.7,95.3,97,97.5,97.9,97.8,97.6,97.7,"2018-05-15","2018-10-15"]
["Power Electronics","FS2125CU15 [690V]","N","Y","Y","N","N","N","N","2125 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box",2306.41,690,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 2125 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",390.63,null,null,976,1030,1200,231,461,692,1153,1730,2306,95.6,97.1,97.8,98.2,98.2,98,98,95.6,97.1,97.7,98.1,98.1,97.9,97.9,95.5,97,97.6,98.1,98.1,97.8,97.9,"2018-05-15","2018-10-15"]
["Power Electronics","FS2225CU15 [600V]","N","Y","Y","N","N","N","N","2225 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box",2417.08,600,97.5,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 2225 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",403.32,null,null,849,940,1200,242,483,725,1209,1813,2417,95.5,97.2,97.7,98.1,98.1,97.8,97.9,95.5,97.2,97.7,98,98,97.7,97.8,95.4,97.1,97.6,98,98,97.7,97.8,"2018-05-15","2018-10-15"]
["Power Electronics","FS2250CU15O3 [600V]","N","Y","Y","N","N","N","N","2250 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant",2420.37,600,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 225 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",416.47,null,null,849,940,1200,242,484,726,1210,1815,2420,97.2,97.8,98,98.2,98.1,97.9,98,96.9,97.8,98,98,98,97.7,97.9,96.9,97.7,97.9,98.1,98,97.8,97.9,"2018-05-15","2018-10-15"]
["Power Electronics","FS2150CU15 [645V]","N","Y","Y","N","N","N","N","2150 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box",2558.48,645,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 215 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",409.99,null,null,913,980,1200,256,512,768,1279,1919,2558,95.7,97.4,97.8,98.1,98.1,97.9,97.9,95.6,97.3,97.8,98.1,98.1,97.8,97.9,95.6,97.3,97.7,98.1,98.1,97.8,97.9,"2018-05-15","2018-10-15"]
["Power Electronics","FS2400CU15 [645V]","N","Y","Y","N","N","N","N","2400 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box",2583.7600000000002,645,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 24 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",407.44,null,null,913,980,1200,258,517,775,1292,1938,2584,95.8,97.4,97.9,98.1,98.1,97.9,98,95.8,97.4,97.7,98.1,98.1,97.8,97.9,95.7,97.3,97.7,98.1,98,97.8,97.9,"2018-05-15","2018-10-15"]
["Power Electronics","FS2450CU15 [565V]","N","Y","Y","N","N","N","N","2450 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box",2664.07,565,97.5,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 245 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",417.35,null,null,800,900,1200,266,533,799,1332,1998,2664,95.7,97.3,97.6,98,98,97.7,97.8,95.6,97.2,97.6,97.9,97.9,97.6,97.7,95.6,97.2,97.5,97.9,97.9,97.6,97.7,"2018-05-15","2018-10-15"]
["Power Electronics","FS2550CU15 [690V]","N","Y","Y","N","N","N","N","2250 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box",2759.39,690,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 255 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",408.29,null,null,976,1030,1200,276,552,828,1380,2070,2759,96,97.5,97.9,98.2,98.2,97.9,98,95.9,97.4,97.8,98.2,98.1,97.8,97.9,95.9,97.4,97.8,98.1,98.1,97.9,98,"2018-05-15","2018-10-15"]
["Power Electronics","FS2300CU15 [690V]","N","Y","Y","N","N","N","N","2300 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box",2759.49,690,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 23 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",408.67,null,null,976,1030,1200,276,552,828,1380,2070,2759,95.9,97.5,97.9,98.2,98.2,98,98,95.8,97.4,97.8,98.1,98.2,97.9,98,95.8,97.4,97.8,98.2,98.1,97.9,98,"2018-05-15","2018-10-15"]
["Power Electronics","FS2600CU15O3 [600V]","N","Y","Y","N","N","N","N","2600 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant",2770.2,600,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 26 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",433.54,null,null,849,940,1200,277,554,831,1385,2078,2770,97.2,97.9,98.1,98.2,98.1,97.9,98,97.1,97.8,98,98,98,97.8,98,97.1,97.8,98,98.1,98,97.8,98,"2018-05-15","2018-10-15"]
["Power Electronics","FS2600CU15 [600V]","N","Y","Y","N","N","N","N","2600 kW, 600 Vac  Grid SupportUtility Interactive Inverter with combiner box",2821.84,600,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 26 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",423.67,null,null,849,940,1200,282,564,847,1411,2116,2822,95.7,97.4,97.9,98.1,98,97.8,97.9,95.7,97.3,97.8,98.1,98,97.7,97.8,95.7,97.2,97.7,98,98,97.7,97.8,"2018-05-15","2018-10-15"]
["Power Electronics","FS2840M [34000V]","N","Y","Y","Y","N","N","N","2840 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer",2844.7,34500,97.5,"MET","[05/23/2018]","[1.0.0.]","2019-03-15","[05/23/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%).","N","N",5970,null,null,849,940,1200,284.46999999999997,568.93999999999994,853.41,1422.35,2133.5249999999996,2844.7,94.441291666666672,96.56016666666666,97.223291666666668,97.627916666666664,97.750749999999996,97.65162500000001,97.464796249999992,94.353458333333322,96.453291666666672,97.123458333333332,97.530124999999998,97.634833333333347,97.529166666666669,97.355864166666677,94.309624999999997,96.512749999999997,97.135541666666668,97.596791666666661,97.707041666666655,97.548541666666665,97.411772916666663,"2019-03-15"]
["Power Electronics","FS3001M [34000V]","N","Y","Y","Y","N","N","N","3000 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer",3017.848,34500,97.5,"MET","[05/23/2018]","[1.0.0.]","2019-03-15","[05/23/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%).","N","N",6084,null,null,849,940,1200,301.78480000000002,603.56960000000004,905.35439999999994,1508.924,2263.386,3017.848,94.625250000000008,96.64620833333332,97.274666666666661,97.67649999999999,97.711333333333329,97.562458333333339,97.467475000000007,94.555166666666665,96.590499999999992,97.182041666666663,97.57641666666666,97.667249999999996,97.444833333333335,97.400508333333335,94.518374999999992,96.583750000000009,97.188416666666669,97.614750000000001,97.703708333333338,97.486250000000013,97.428907916666674,"2019-03-15"]
["Power Electronics","FS2800CU15 [645V]","N","Y","Y","N","N","N","N","2800 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box",3024.91,645,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 28 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",427.54,null,null,913,940,1200,302,605,907,1512,2269,3025,96,97.4,97.9,98.1,98.1,97.9,98,95.9,97.4,97.8,98.1,98.1,97.8,97.9,95.9,97.3,97.7,98.1,98,97.8,97.9,"2018-05-15","2018-10-15"]
["Power Electronics","FS3000M [34000V]","N","Y","Y","Y","N","N","N","3000 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer",3109.2660000000001,34500,97.5,"MET","[05/23/2018]","[1.0.0.]","2019-03-15","[05/23/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%).","N","N",6056,null,null,849,940,1200,310.92660000000001,621.85320000000002,932.77980000000002,1554.633,2331.9495000000002,3109.2660000000001,94.974916666666672,96.84708333333333,97.372333333333344,97.67754166666667,97.66020833333333,97.339875000000006,97.46521875000002,94.942750000000004,96.773583333333335,97.32374999999999,97.618083333333331,97.528041666666667,97.202666666666673,97.365032083333332,94.91225,96.819416666666683,97.353875000000002,97.638541666666683,97.591666666666669,97.275541666666655,97.411380000000008,"2019-03-15"]
["Power Electronics","FS3000K [600V]","N","Y","Y","Y","N","N","N","3300 kW, 600 Vac, Grid Support Utility Interactive Inverter",3121.31,600,98,"MET","[6/25/2019]","[1.0.0]","2020-05-21","[6/25/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","The inverter is central control composed by 6 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 2550 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",324.8,null,null,849,940,1200,312.13099999999997,624.26199999999994,936.39300000000003,1560.655,2340.9830000000002,3121.31,96.562600000000003,97.824250000000006,98.14367,98.371200000000002,98.246870000000001,97.926940000000002,98.156099999999995,96.454350000000005,97.706620000000001,98.063919999999996,98.268950000000004,98.128469999999993,97.835160000000002,98.047499999999999,96.438149999999993,97.713530000000006,98.046980000000005,98.277519999999996,98.126769999999993,97.851900000000001,98.046899999999994,"2020-05-21"]
["Power Electronics","FS3000CU15 [690V]","N","Y","Y","N","N","N","N","3000 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box",3201.17,690,98,"SGS North America","[02/15/2018]","[HEP2G_2.0.0]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 3 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",426.4,null,null,976,1030,1200,320,640,960,1601,2401,3201,96.1,97.5,97.9,98.2,98.3,98.1,98.1,96,97.5,97.9,98.1,98.2,98,98,95.9,97.5,97.9,98.2,98.2,97.9,98,"2018-05-15","2018-10-15"]
["Power Electronics","FS3150K [630V]","N","Y","Y","Y","N","N","N","3465 kW, 630 Vac, Grid Support Utility Interactive Inverter",3279.87,630,98,"MET","[6/25/2019]","[1.0.0]","2020-05-21","[6/25/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","The inverter is central control composed by 6 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on PROLEC GE PAD-MOUNTED KNAN - 3094KVA - 34500V.","N","N",324.8,null,null,891,970,1200,327.98700000000002,655.97400000000005,983.96100000000001,1639.9349999999999,2459.9029999999998,3279.87,96.772589999999994,97.570849999999993,97.888689999999997,98.128439999999998,97.807370000000006,97.672669999999997,97.824600000000004,96.692139999999995,97.486800000000002,97.810599999999994,98.040329999999997,97.723690000000005,97.59836,97.741240000000005,96.643039999999999,97.458939999999998,97.796139999999994,98.056820000000002,97.873959999999997,97.590299999999999,97.818849999999998,"2020-05-21"]
["Power Electronics","FS3190K [600V]","N","Y","Y","Y","N","N","N","3300 kW, 630 Vac Grid Support Utility Interactive  Inverter",3303.82,630,98,"SGS North America","[03/10/2020]","[1.9.1]","2020-05-21","[03/10/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","The inverter is central control composed by 6 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 3000 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",324.8,null,null,849,940,1200,330.38200000000006,660.76400000000012,991.14599999999996,1651.91,2477.8650000000002,3303.82,96.420790588252316,97.761612144282154,98.133611255185201,98.38629985122526,98.24163797904059,97.979314583825101,98.149102408206502,96.300826581320138,97.652663317134298,98.035785187009736,98.275267769388378,98.160031395313339,97.887895480862824,98.055978096681457,96.335027589343554,97.675909184194794,98.045744786838384,98.288710164194015,98.163390202875306,97.912428621820965,98.065533310299784,"2020-05-21"]
["Power Electronics","FS3150M [34000V]","N","Y","Y","Y","N","N","N","3150 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer",3307.98,34500,97.5,"MET","[05/23/2018]","[1.0.0.]","2019-03-15","[05/23/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%).","N","N",6880,null,null,891,970,1200,330.798,661.596,992.39400000000001,1653.99,2480.9850000000001,3307.98,95.021083333333337,96.902666666666661,97.43416666666667,97.751458333333346,97.642166666666682,97.366208333333333,97.484541666666672,94.957916666666677,96.780166666666659,97.356208333333342,97.670791666666659,97.588416666666674,97.23479166666668,97.414536666666663,94.974208333333337,96.782833333333343,97.347458333333321,97.693916666666667,97.59999999999998,97.308999999999997,97.428977499999988,"2019-03-15"]
["Power Electronics","FS3225M [34000V]","N","Y","Y","Y","N","N","N","3225 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer",3367.326,34500,97.5,"MET","[05/23/2018]","[1.0.0.]","2019-03-15","[05/23/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%).","N","N",7640,null,null,913,980,1200,336.73260000000005,673.4652000000001,1010.1977999999999,1683.663,2525.4944999999998,3367.326,95.018333333333345,96.892750000000007,97.397916666666688,97.763374999999996,97.723124999999996,96.925458333333353,97.502958750000005,94.970375000000018,96.822125,97.331000000000017,97.639291666666665,97.631833333333333,96.840541666666653,97.410791250000003,94.960374999999999,96.769166666666663,97.327624999999998,97.680666666666667,97.632750000000001,97.003047619047621,97.424638214285721,"2019-03-15"]
["Princeton Power Systems, Inc.","GTIB-480-30-WZZZZZZ-G1.3 [480V]","Y","Y","Y","Y","N","N","N","30 kVA, 480 Vac, 830Vdc, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank.\nCannot accept PV and Battery DC input simultaneously.",29.443999999999999,480,93.5,"TUV Rheinland of North America","[05/09/2019]","[V2.4.2]","2019-06-17","[05/09/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",35.14,null,null,540,750,830,2.9444320000000004,5.8888640000000008,8.8332960000000007,14.722160000000001,22.08324,29.444320000000001,86.763266666666667,92.620999999999995,93.103199999999987,93.816300000000012,93.242133333333328,92.085366666666658,92.997986666666677,87.648466666666664,93.265666666666675,93.530033333333321,94.116299999999995,93.404066666666665,92.92046666666667,93.307427666666669,88.606333333333325,92.492433333333324,94.669099999999986,94.546866666666659,93.654933333333332,93.047166666666669,93.673481999999993,"2019-06-17"]
["Princeton Power Systems, Inc.","GTIB-480-30-ZZZZZZ-G1.3 [480V]","Y","Y","Y","Y","N","N","N","30 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank (Z≠-W).\nCannot accept PV and Battery DC input simultaneously.",29.956,480,97,"TUV Rheinland of North America","[05/09/2019]","[V2.4.2]","2019-06-17","[05/09/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",46.3,null,null,540,750,830,2.9955659999999997,5.9911319999999995,8.9866979999999987,14.977829999999997,22.466744999999996,29.955659999999995,92.6541,95.119433333333333,96.076666666666668,96.846399999999988,96.976966666666669,96.853766666666658,96.569560333333314,93.775933333333342,95.241533333333322,96.501333333333349,97.176799999999986,97.375799999999998,97.398533333333333,96.979502666666676,92.794166666666655,94.885466666666673,96.3887,97.057933333333338,97.19076666666669,97.425100000000015,96.787211333333346,"2019-06-17"]
["Princeton Power Systems, Inc.","GTIB-480-125XXXXXX-G1.5 [480V]","Y","Y","Y","Y","N","N","N","125 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank.\nCannot accept PV and Battery DC input simultaneously.",124.964,480,96,"TUV Rheinland of North America","[05/07/2019]","[V2.72]","2019-06-17","[05/07/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",68,null,null,350,710,830,12.496400000000001,24.992800000000003,37.489199999999997,62.481999999999999,93.722999999999999,124.964,87.119633333333326,92.941333333333333,94.972333333333353,95.217933333333335,95.659266666666667,95.211466666666666,94.984282666666672,91.918933333333342,95.376133333333343,95.897933333333327,96.625766666666664,96.886533333333333,96.648966666666652,96.427037999999996,91.559566666666655,95.713033333333343,96.424533333333343,96.968400000000003,96.936033333333313,96.892933333333332,96.60308666666667,"2019-06-17"]
["Princeton Power Systems, Inc.","GTIB-480-125XXXXXX-W-G1.5 [480V]","Y","Y","Y","Y","N","N","N","125 kVA, 480 Vac, 830Vdc, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank.\nCannot accept PV and Battery DC input simultaneously.",124.964,480,94.5,"TUV Rheinland of North America","[05/07/2019]","[V2.7.2]","2019-06-17","[05/07/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 125 kVA Jefferson Electric 423-D7-13 distribution transformer.","N","N",68,null,null,350,710,830,12.496400000000001,24.992800000000003,37.489199999999997,62.481999999999999,93.722999999999999,124.964,84.93873851222223,91.649448799999988,93.842162566666687,94.017129396296298,94.157416179999998,93.224720728888883,93.549345273555573,89.617896035555574,94.050405080000004,94.756747926666662,95.407208387037045,95.365414760000007,94.632224895555538,94.968840675477765,89.267525514444444,94.382622170000019,95.27708138666668,95.745520733333336,95.414137609999983,94.871100791111118,95.142689222333331,"2019-06-17"]
["Rhombus Energy Solutions","RES-BESS60DP-480 [480V]","Y","Y","Y","Y","N","N","N","60 kW, 480 Vac Grid Support Utility Interactive PV and Battery Inverter",59.789000000000001,480,91.5,"UL","[09/03/2020]","[00020520]","2020-12-11","[09/03/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",92,null,null,270,441,870,5.9789000000000003,11.957800000000001,17.936699999999998,29.894500000000001,44.841750000000005,59.789000000000001,82.328000000000003,88.789999999999992,91.343999999999994,93.2,93.729000000000013,93.631999999999991,92.623870000000011,81.460000000000008,87.411999999999992,90.408000000000001,92.421999999999997,93.1,93,91.879580000000004,79.440000000000012,86.038000000000011,88.893999999999977,91.278000000000006,92.025999999999996,92.06,90.691940000000002,"2020-12-11"]
["SANYO ELECTRIC CO LTD OF PANASONIC GROUP","VBHN325KA03E [240V]","N","Y","Y","Y","Y","Y*","Y","325 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Model: VBHN325KA03. Microinverter: IQ7X-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[1/2/2020]","[V04.18.02]","2020-04-01","[1/2/2020]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2020-04-01"]
["SANYO ELECTRIC CO LTD OF PANASONIC GROUP","VBHN325SA17E [240V]","N","Y","Y","Y","Y","Y*","Y","325 W, 96 cell heterojunction monocrystalline ACPV module, white backsheet. DC Module: VBHN325SA17. Micro-inverter: IQ7X-96-x-ACM-US-y-z-& [240V].",0.315,240,97.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[01/02/2020];[01/02/2020];[01/02/2020]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[01/02/2020]","2020-12-01","UL","2020-03-18","2020-12-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2019-04-02","2020-12-01"]
["SANYO ELECTRIC CO LTD OF PANASONIC GROUP","VBHN330KA03E [240V]","N","Y","Y","Y","Y","Y*","Y","330 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Model: VBHN330KA03. Microinverter: IQ7X-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[1/2/2020]","[V04.18.02]","2020-04-01","[1/2/2020]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23624999999999999,0.315,95.734780000000001,96.840239999999994,96.996160000000003,97.762709999999998,97.755849999999995,97.468630000000005,97.525143499999999,95.610320000000002,96.678240000000002,96.75488,97.666659999999993,97.739180000000005,97.513729999999995,97.456360900000007,95.436539999999994,96.497950000000003,96.657110000000003,97.603840000000005,97.700140000000005,97.48254,97.393219900000005,"2020-04-01"]
["SANYO ELECTRIC CO LTD OF PANASONIC GROUP","VBHN330SA17E [240V]","N","Y","Y","Y","Y","Y*","Y","330 W, 96 cell heterojunction monocrystalline ACPV module, white backsheet. DC Module: VBHN330SA17. Micro-inverter: IQ7X-96-x-ACM-US-y-z-& [240V].",0.315,240,97.5,"UL","[10/30/2017];[05/25/2018];[06/26/2018];[01/02/2020];[01/02/2020];[01/02/2020]","[V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09]","2018-10-15","[10/30/2017];[05/25/2018];[06/26/2018];[01/02/2020]","2020-12-01","UL","2020-03-18","2020-12-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2019-04-02","2020-12-01"]
["Schneider Electric Solar Inverters USA, Inc.","Conext CL125 [600V]","N","Y","Y","N","N","N","N","125 kW, 600Vac, 3-phase Gird Support Utility Interactive Inverter with the advanced power conversion technology IGBT to convert the DC power normally from the photovoltaic array to stable three-phase AC power and then feed the power to the utility grid.",125,600,98.5,"CSA Group","[05/31/2018]","[MDSP_CL125_V11_V01_A_05]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5.59,null,null,860,945,1200,12.5,25,37.5,62.5,93.75,125,98.586801019777141,98.82652309567699,98.88387814308247,98.682135105177181,98.446000650548712,98.25533618070061,98.563259098657895,98.289357567940598,98.584163778937167,98.588946856747839,98.493126437907804,98.359351768917335,98.106737109659321,98.410805959444019,98.084097523523852,98.425857217687977,98.477267999265308,98.384840475419338,98.097001197396807,97.625954277206347,98.195453770055877,"2018-08-01","2018-10-15"]
["Schneider Electric Solar Inverters USA, Inc.","CS1666-1-NA [575V]","N","Y","Y","N","N","N","N","1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter with 1666 kVA Maximum Output Continuous Apparent Power",1666,575,98,"SGS North America","[07/01/2018]","[SG_ICB_MCU_R10.6-7]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 2. MVA Square D 3PH distribution transformer, liquid-filled type.","N","N",295,null,null,856,1024,1200,167,333,500,833,1250,1666,96.79,97.94,98.09,98.15,97.94,97.66,97.9,96.33,97.56,97.92,98.08,97.88,97.52,97.8,95.68,97.45,97.7,97.9,97.74,97.44,97.7,"2018-08-15","2018-10-15"]
["Schneider Electric Solar Inverters USA, Inc.","CS1666-2-NA [575V]","N","Y","Y","N","N","N","N","1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter with 1831 kVA Maximum Output Continuous Apparent Power",1666,575,98,"SGS North America","[07/01/2018]","[SG_ICB_MCU_R10.6-7]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 2. MVA Square D 3PH distribution transformer, liquid-filled type.","N","N",295,null,null,856,1024,1200,167,333,500,833,1250,1666,96.79,97.94,98.09,98.15,97.94,97.66,97.9,96.33,97.56,97.92,98.08,97.88,97.52,97.8,95.68,97.45,97.7,97.9,97.74,97.44,97.7,"2018-08-15","2018-10-15"]
["Schneider Electric Solar Inverters USA, Inc.","CS1666-3-NA [575V]","N","Y","Y","N","N","N","N","1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter with 1851 kVA Maximum Output Continuous Apparent Power",1666,575,98,"SGS North America","[07/01/2018]","[SG_ICB_MCU_R10.6-7]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 2. MVA Square D 3PH distribution transformer, liquid-filled type.","N","N",295,null,null,856,1024,1200,167,333,500,833,1250,1666,96.79,97.94,98.09,98.15,97.94,97.66,97.9,96.33,97.56,97.92,98.08,97.88,97.52,97.8,95.68,97.45,97.7,97.9,97.74,97.44,97.7,"2018-08-15","2018-10-15"]
["Schneider Electric Solar Inverters USA, Inc.","CS1800-NA [575V]","N","Y","Y","N","N","N","N","1.8 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter",1800,575,98,"SGS North America","[07/01/2018]","[SG_ICB_MCU_R10.6-7]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 2. MVA Square D 3PH distribution transformer, liquid-filled type.","N","N",295,null,null,856,1024,1200,180,360,540,900,1350,1800,96.89,97.93,98.08,98.11,97.92,97.47,97.9,96.67,97.74,98,97.99,97.8,97.45,97.8,95.89,97.43,97.67,97.87,97.7,97.34,97.6,"2018-08-15","2018-10-15"]
["Schneider Electric Solar Inverters USA, Inc.","CS2000-NA [575V]","N","Y","Y","N","N","N","N","2 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter",2000,575,97.5,"SGS North America","[07/01/2018]","[SG_ICB_MCU_R10.6-7]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Formerly Schneider Electric Solar Inverters USA, Inc. Conext SmartGen CS2-NA. Weighted Efficiency includes efficiency of 2 KVA Square D 3PH distribution transformer, liquid-filled type (4425642-6-S9-1).","N","N",295,null,null,865,1042,1195,200,400,600,1000,1500,2000,96.76,97.71,97.98,97.96,97.66,97.21,97.71,96.32,97.58,97.87,97.83,97.56,97.15,97.58,95.92,97.38,97.69,97.72,97.5,97.06,97.48,"2018-08-15","2018-10-15"]
["Schneider Electric Solar Inverters USA, Inc.","CS2200-NA [600V]","N","Y","Y","N","N","N","N","2.2 MW, 1500 Vdc, 600 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter",2200,600,98,"SGS North America","[07/01/2018]","[SG_ICB_MCU_R10.6-7]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 2.5 MVA Square D 3PH distribution transformer, liquid-filled type.","N","N",295,null,null,905,1054,1200,220,440,660,1100,1650,2200,97.9,98.28,98.33,98.2,97.82,97.24,98,97.6,98.1,98.19,98.09,97.72,97.17,97.8,97.21,97.9,98.05,97.99,97.65,97.1,97.7,"2018-08-15","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 3000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","2.626 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",2.6259999999999999,208,96.5,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,125,380,480,0.26258900000000002,0.52517800000000003,0.787767,1.312945,1.9694175,2.6258900000000001,91.293362527464552,93.708658559402892,95.218322148376544,95.899659413730078,95.835549926366809,95.664474879366807,95.47835976869996,93.582341629764059,95.347659750064892,96.904180719033917,97.228300990567604,97.399142736962418,97.087584880562389,97.033046441615284,92.503804000061209,95.685759532945383,96.430082390113469,96.877896438894567,96.849878019802546,96.962369311400792,96.578962091696582,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 3000TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","2.93 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",2.9340000000000002,240,93.5,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.29343648072000006,0.58687296144000012,0.88030944216000018,1.4671824036000003,2.2007736054000002,2.9343648072000006,83.549447597810484,88.741950658627019,91.518725765277352,93.46602653202423,94.377813212031768,94.573535741134791,93.138105889835714,82.953075358727844,88.977420340672026,91.283975058713153,94.78210464330374,95.760908276236748,95.949289159354137,94.176058857895256,81.248869880822056,86.999197545521113,91.728314598977363,93.615573761261004,94.948738388584474,95.588909967888654,93.368859758595249,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 3000TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","3.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",2.9990000000000001,208,93.5,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.29986100000000004,0.59972200000000009,0.89958300000000002,1.4993050000000001,2.2489575000000004,2.9986100000000002,83.293362527464552,88.708658559402892,91.218322148376544,93.399659413730078,94.335549926366809,94.664474879366807,93.058359768699987,83.582341629764059,88.347659750064892,91.904180719033917,94.228300990567604,95.399142736962418,95.887584880562358,93.933046441615275,82.503804000061209,87.685759532945383,91.430082390113469,93.877896438894567,94.849878019802546,95.762369311400803,93.42896209169659,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 3000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3.095 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",3.0950000000000002,240,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,125,380,480,0.30950900000000003,0.61901800000000007,0.9285270000000001,1.5475450000000002,2.3213175000000001,3.0950900000000003,92.549447597810484,94.741950658627019,95.518725765277352,96.46602653202423,96.377813212031768,96.173535741134771,96.048105889835725,94.953075358727858,96.977420340672026,97.283975058713153,97.78210464330374,97.760908276236748,97.449289159354137,97.541058857895266,93.248869880822056,95.999197545521113,96.728314598977363,97.215573761261027,97.348738388584479,97.388909967888651,97.016859758595231,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 3800TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","3.324 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",3.3239999999999998,208,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,160,380,480,0.33238499999999999,0.66476999999999997,0.9971549999999999,1.6619249999999999,2.4928874999999997,3.3238499999999997,91.755180590217549,94.427054546325252,95.624985137332857,96.396791893422602,96.371596058447253,96.236486896009197,95.998654720801156,92.840136706007556,95.733247132067817,97.329294782796779,97.290815806914082,97.774711172919311,97.472718032005659,97.305087341478782,92.871659181712658,95.766799085310566,96.778444876002226,97.495296333055563,97.588435399550463,97.467180675267372,97.185861732121083,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 3600TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","3.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",3.581,208,94,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.35810000000000003,0.71620000000000006,1.0743,1.7905,2.6857500000000001,3.581,84.955180590217552,90.427054546325252,92.82498513733286,93.796791893422608,94.571596058447255,94.4364868960092,93.600654720801174,85.040136706007544,90.733247132067817,93.429294782796759,94.4908158069141,95.774711172919311,96.272718032005656,94.567087341478782,82.371659181712658,88.966799085310569,92.978444876002229,94.295296333055546,95.78843539955048,95.66718067526736,94.253861732121095,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 3600TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","3.61 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",3.6080000000000001,240,94,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.36083600000000005,0.72167200000000009,1.082508,1.8041800000000001,2.70627,3.6083600000000002,84.922591470532467,90.049537139188644,92.907915460636232,93.787520478526631,94.431767346826717,94.456005695413168,93.515346650136493,84.868082954696078,90.930025652086897,93.856690289605723,94.561956933570571,95.558319826046343,95.97270963170358,94.506583380984452,82.497692670536821,88.98865673613679,92.293512624245835,94.468661270738565,94.738149356716107,95.614391367395442,93.654919652822215,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 4000MTLP-US [208V]","N","Y","Y","Y","N","N","N","4 kW, 208 Vac Grid Support Utility Interactive Inverter",3.62,208,95.5,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,100,482,550,0.36,0.72,1.08,1.81,2.71,3.62,88.8,91.7,93.1,94.6,95.2,95.2,94.4,92.2,95.7,95.7,96.5,96.7,96.7,96.3,91.4,94.3,95.3,96.2,96.5,96.6,96,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 3800TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3.888 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",3.8879999999999999,240,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,160,380,480,0.38882100000000003,0.77764200000000006,1.166463,1.944105,2.9161574999999997,3.8882099999999999,92.922591470532453,95.049537139188644,95.907915460636232,96.587520478526628,96.731767346826715,96.456005695413168,96.352346650136496,95.868082954696078,97.430025652086897,97.856690289605723,98.061956933570571,98.058319826046343,97.97270963170358,97.911583380984425,93.497692670536821,96.48865673613679,97.193512624245841,97.668661270738568,97.738149356716107,97.614391367395442,97.41991965282223,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 4000TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","3.99 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",3.988,240,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,180,380,480,0.39883600000000002,0.79767200000000005,1.1965079999999999,1.9941800000000001,2.9912700000000001,3.9883600000000001,86.922591470532453,91.049537139188644,92.907915460636232,94.587520478526628,95.131767346826706,95.156005695413171,94.219346650136472,86.568082954696095,92.230025652086908,94.356690289605723,95.661956933570565,96.258319826046346,96.172709631703597,95.311583380984445,84.497692670536821,91.088656736136798,93.393512624245858,95.168661270738568,96.138149356716127,96.014391367395433,94.880919652822229,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 4000TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",4.0039999999999996,208,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.40039999999999998,0.80079999999999996,1.2011999999999998,2.0019999999999998,3.0029999999999997,4.0039999999999996,86.755180590217549,91.427054546325252,93.124985137332857,94.396791893422602,94.971596058447261,95.236486896009197,94.136654720801147,86.840136706007556,92.133247132067822,94.329294782796779,95.690815806914117,96.174711172919316,96.172718032005662,95.276087341478785,84.871659181712658,91.266799085310566,93.578444876002223,95.195296333055552,96.088435399550463,96.067180675267352,94.908861732121082,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 4000MTLP-US [240V]","N","Y","Y","Y","N","N","N","4 kW, 240 Vac Grid Support Utility Interactive Inverter",4.05,240,96,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,100,482,550,0.4,0.81,1.21,2.02,3.04,4.05,89.5,92.1,93.7,95,95.5,95.6,94.8,93.1,95.4,96.2,96.9,97.1,97.1,96.7,92.3,94.8,95.9,96.6,96.9,97,96.4,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 4000MTLP-US [277V]","N","Y","Y","Y","N","N","N","4 kW, 277 Vac Grid Support Utility Interactive Inverter",4.0599999999999996,277,96,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,100,482,550,0.41,0.81,1.22,2.0299999999999998,3.04,4.0599999999999996,88.3,91.5,93.1,94.6,95.3,95.5,94.4,93.6,95.7,96.6,95.3,97.4,97.4,96.6,92.7,95.1,96.3,96.9,97.2,97.3,96.8,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 5000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","4.28 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",4.28,208,97.5,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,210,380,480,0.42804700000000007,0.85609400000000013,1.284141,2.1402350000000001,3.2103524999999999,4.2804700000000002,93.996851147427378,95.629087640627944,96.529188756944251,97.277007418730477,96.868530791047505,96.496785004728451,96.718163206186802,95.641514244657174,97.355583883477067,97.754499714035177,97.953556646908979,97.798943927134161,97.587203384819631,97.707027076117328,95.01366047546945,96.803364464641348,97.343448588191023,97.662867921364452,97.692424675265713,97.398466432447975,97.478039135833527,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 5000MTLP-US [208V]","N","Y","Y","Y","N","N","N","5 kW, 208 Vac Grid Support Utility Interactive Inverter",4.59,208,95.5,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,100,482,550,0.46,0.92,1.38,2.2999999999999998,3.44,4.59,89.9,92.5,93.8,94.9,95.1,95.1,94.6,93.2,95.3,96,96.6,96.7,96.6,96.4,92.5,94.8,95.7,96.4,96.6,96.5,96.2,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 4600TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.6 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",4.5979999999999999,240,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,180,380,480,0.45977250000000008,0.91954500000000017,1.3793175000000002,2.2988625000000003,3.4482937500000004,4.5977250000000005,86.922591470532453,92.049537139188644,93.307915460636224,94.90952047852663,95.25376734682672,95.188005695413182,94.451226650136505,86.868082954696078,92.430025652086897,94.556690289605712,95.896956933570578,96.23231982604635,96.207709631703565,95.394903380984431,85.497692670536821,91.48865673613679,93.603512624245838,95.432661270738564,96.28214935671609,96.116391367395423,95.102979652822199,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 4600TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.6 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",4.6040000000000001,208,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,180,380,480,0.46040000000000003,0.92080000000000006,1.3812,2.302,3.4530000000000003,4.6040000000000001,86.755180590217549,91.62705454632524,93.42498513733284,94.796791893422608,95.171596058447264,95.236486896009197,94.372654720801165,87.840136706007556,92.833247132067811,94.729294782796771,95.790815806914082,96.274711172919311,96.272718032005656,95.478087341478769,85.871659181712658,92.566799085310564,94.078444876002223,95.295296333055546,96.388435399550474,96.267180675267355,95.263861732121086,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 5000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","4.943 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",4.9429999999999996,240,97.5,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,210,380,480,0.49432200000000004,0.98864400000000008,1.482966,2.4716100000000001,3.7074150000000001,4.9432200000000002,94.267366712449771,96.027866498551376,96.617657713229335,96.968808318480185,96.797623042865695,96.462603080710252,96.655527032648251,95.82744666782294,97.647557997532857,97.992889962034198,98.197719306174335,98.026200918261708,97.775702757962975,97.938815240907147,95.15481202687161,97.215513493715306,97.700506408141493,97.980163351059588,97.817020842814571,97.608867979129769,97.690327674108346,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 5000TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.95 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",4.9539999999999997,240,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,230,380,480,0.495367,0.990734,1.4861009999999999,2.4768349999999999,3.7152525000000001,4.9536699999999998,88.267366712449771,92.027866498551376,93.917657713229346,95.168808318480188,95.597623042865678,95.462603080710252,94.827527032648248,88.82744666782294,93.647557997532857,94.592889962034178,96.197719306174335,96.526200918261708,95.975702757962978,95.745815240907135,86.65481202687161,92.415513493715309,93.700506408141493,95.580163351059582,96.117020842814568,96.108867979129769,95.150327674108325,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 5000TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.97 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",4.9690000000000003,208,95.5,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,230,380,480,0.49687900000000007,0.99375800000000014,1.490637,2.4843950000000001,3.7265925000000002,4.9687900000000003,87.996851147427378,91.829087640627947,94.029188756944251,95.277007418730477,95.668530791047502,95.496785004728451,94.882163206186817,88.641514244657174,93.555583883477055,94.754499714035177,95.953556646908979,96.598943927134158,96.087203384819631,95.746027076117329,87.01366047546945,92.803364464641348,93.543448588191026,96.162867921364452,96.092424675265733,96.198466432447987,95.279039135833557,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 5000MTLP-US [277V]","N","Y","Y","Y","N","N","N","5 kW, 277 Vac Grid Support Utility Interactive Inverter",5.0599999999999996,277,96.5,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,100,482,550,0.51,1.01,1.52,2.5299999999999998,3.8,5.0599999999999996,89.5,92.3,93.8,95,95.5,95.5,94.8,94.3,96.1,96.8,97.3,97.4,97.3,97.1,93.5,95.6,96.4,97,97.2,97.2,96.9,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 5000MTLP-US [240V]","N","Y","Y","Y","N","N","N","5 kW, 240 Vac Grid Support Utility Interactive Inverter",5.07,240,96,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,100,482,550,0.51,1.01,1.52,2.5299999999999998,3.8,5.07,90.5,93,94.3,95.2,95.4,95.3,94.9,93.9,95.8,96.5,97,97.1,96.9,96.8,93.1,95.3,96.1,96.8,96.9,96.9,96.6,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 6000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","5.143 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",5.1429999999999998,208,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,170,380,480,0.51425799999999999,1.028516,1.5427739999999999,2.5712899999999999,3.856935,5.1425799999999997,93.481204082097847,95.143621894033842,95.921639978922201,96.414307307624739,96.408584395065049,96.201559738902532,96.160658306387077,95.740431907203799,97.20226392049122,97.675309910643875,97.727611859614214,97.705868499477219,97.20034672805248,97.577693793234516,94.530997034371978,96.528735819174116,97.183911209691985,97.484093465582191,97.499956580169822,97.125463339241861,97.27265579972098,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 6000TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","5.23 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",5.2320000000000002,208,96,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,230,380,480,0.52322481004999999,1.0464496201,1.5696744301499999,2.6161240502499998,3.9241860753749997,5.2322481004999997,91.621602813152066,94.380390480666662,95.003957489078005,95.641543682886891,95.647954359667054,95.64975677121727,95.344986357839431,94.005771170000003,96.332077925666653,96.65995075056712,96.844207319172924,96.805818328239184,96.521558970093878,96.646474032649166,93.966622391069833,96.000071433485644,96.412837938980843,96.864324446543876,96.731434588977862,96.495662704401141,96.562160621147314,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 6000MTLP-US [208V]","N","Y","Y","Y","N","N","N","6 kW, 208 Vac Grid Support Utility Interactive Inverter",5.34,208,96,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,100,482,550,0.53,1.07,1.6,2.67,4.01,5.34,90.7,93.2,94.3,95,95,94.9,94.7,93.9,95.7,96.3,96.7,96.6,96.4,96.4,93.3,95.3,95.9,96.5,96.5,96.3,96.2,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 6000TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","5.86 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",5.8639999999999999,240,96,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,230,380,480,0.58643299999999998,1.172866,1.7592989999999999,2.9321649999999999,4.3982475000000001,5.8643299999999998,91.58160281315206,94.360390480666666,94.953957489078022,95.591543682886879,95.627954359667058,95.639756771217264,95.314786357839438,93.965771170000011,96.30207792566668,96.579950750567122,96.814207319172922,96.755818328239172,96.521558970093878,96.600974032649162,93.926622391069841,95.970071433485643,96.382837938980842,96.834324446543889,96.71143458897788,96.475662704401145,96.537560621147321,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 6000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","5.918 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",5.9180000000000001,240,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,170,380,480,0.59177500000000005,1.1835500000000001,1.7753249999999998,2.9588749999999999,4.4383125000000003,5.9177499999999998,93.49312456280208,95.071290997799792,96.009128356856777,96.506775898448311,96.537491526800594,96.276974884360101,96.259527127321348,96.283551128782477,97.623502381955774,97.995012321707193,98.032333863869923,97.740454263659132,97.640683129965907,97.763183670504276,95.282875546127613,97.093459861238671,97.489948272311352,97.82790394763353,97.699789002409091,97.433325500633003,97.561196082895918,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 6000MTLP-US [240V]","N","Y","Y","Y","N","N","N","6 kW, 240 Vac Grid Support Utility Interactive Inverter",6.08,240,96,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,100,482,550,0.61,1.22,1.82,3.04,4.5599999999999996,6.08,91.3,93.6,94.7,95.4,95.5,95.6,95.1,94.6,96.1,96.7,97,97,96.8,96.8,93.9,95.6,96.3,96.8,96.8,96.7,96.6,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 6000MTLP-US [277V]","N","Y","Y","Y","N","N","N","6 kW, 277 Vac Grid Support Utility Interactive Inverter",6.08,277,96.5,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,100,482,550,0.61,1.22,1.82,3.04,4.5599999999999996,6.08,90.4,93,94.4,95.3,95.4,95.3,94.9,94.9,96.4,96.9,97.3,97.4,97.2,97.2,94.1,95.9,96.6,97.1,97.2,97.1,96.9,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 7000MTLP-US [208V]","N","Y","Y","Y","N","N","N","7 kW, 208 Vac Grid Support Utility Interactive Inverter",6.093,208,96,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,280,385,485,609.29999999999995,1218.5999999999999,1827.9,3046.5,4569.75,6093,93.9,95.4,95.8,95.9,95.5,95.3,95.6,95.4,96.6,96.8,96.6,96.1,95.9,96.3,94.3,95.9,96.4,96.5,96.2,96,96.2,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 7600TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","6.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",6.58,208,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,212,380,480,0.65803500000000004,1.3160700000000001,1.974105,3.2901750000000001,4.9352625000000003,6.5803500000000001,93.7825737552172,95.54207098779338,96.606044154379617,96.83236417215366,96.8224267390096,96.441473859841409,96.593888138943328,95.614398932245905,97.20795693450485,97.628278749390489,97.712867337028214,97.808319239909849,97.38950013957637,97.62795359884889,94.065878474823975,96.343473361528524,97.314711226736364,97.379254821920298,97.445094589024549,97.221458351837427,97.214190716655892,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 7600MTLP-US [208V]","N","Y","Y","Y","N","N","N","7.6 kW, 208 Vac Grid Support Utility Interactive Inverter",6.7410100000000002,208,96,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0.05,null,null,270,380,480,674.1,1348.2,2022.3,3370.51,5055.76,6741.01,94.1,95.5,95.7,95.7,95.2,95,95.3,95.7,96.7,96.8,96.6,96.1,95.9,96.3,94.7,96.2,96.5,96.5,96.1,95.8,96.2,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 7000MTLP-US [240V]","N","Y","Y","Y","N","N","N","7 kW, 240 Vac Grid Support Utility Interactive Inverter",7.0110000000000001,240,96.5,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0999999999999997E-2,null,null,270,385,485,701.11,1402.22,2103.33,3505.55,5258.33,7011.1,94,95.7,95.9,96,95.8,95.5,95.8,95.7,96.8,97,96.9,96.7,96.4,96.7,94.6,96.4,96.8,96.9,96.7,96.3,96.6,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 7000MTLP-US [277V]","N","Y","Y","Y","N","N","N","7 kW, 277 Vac Grid Support Utility Interactive Inverter",7.01607,277,96.5,"Intertek","[10/13/2017]","[KA 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0999999999999997E-2,null,null,275,385,480,701.61,1403.21,2104.8200000000002,3508.04,5262.05,7016.07,92.8,95.2,95.4,95.9,96.1,95.9,95.8,93.6,96.3,96.7,96.9,96.8,96.5,96.6,95,96.6,97.1,97.3,97.2,97,97.1,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 8000MTLP-US [208V]","N","Y","Y","Y","N","N","N","8 kW, 208 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit",7.1070000000000002,208,97,"Intertek","[10/13/2017]","[KC 1.0]","2018-10-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",3.3,null,null,330,480,550,0.7107,1.4214,2.1320999999999999,3.5535000000000001,5.3302500000000004,7.1070000000000002,95.231939999999994,96.898070000000004,97.166759999999996,97.215220000000002,96.94059,96.732650000000007,96.944540000000003,95.324839999999995,96.898070000000004,97.353549999999998,97.525599999999997,97.365679999999998,97.204369999999997,97.284729999999996,94.567530000000005,96.538659999999993,97.078320000000005,97.371020000000001,97.291730000000001,97.130870000000002,97.128110000000007,"2017-10-16","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 8200TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","8.2 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",7.1660000000000004,208,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.71659000000000006,1.4331800000000001,2.1497699999999997,3.5829499999999999,5.3744249999999996,7.1658999999999997,93.818033333333332,95.946699999999993,96.5916,96.939433333333326,96.892099999999999,96.798100000000005,96.691047333333344,95.225833333333327,97.223066666666654,97.743199999999987,97.92383333333332,97.82286666666667,97.741233333333327,97.696556666666666,93.714700000000008,96.521599999999992,97.29516666666666,97.704099999999997,97.722104333333334,97.637333333333345,97.44253096333334,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 7600TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.524 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",7.524,240,97.5,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,212,380,480,0.75241900000000006,1.5048380000000001,2.2572570000000001,3.762095,5.6431424999999997,7.5241899999999999,94.832082543720276,96.244283779082338,96.937158930899699,97.135867226709507,97.054923358633204,96.468059416272766,96.899001030909147,96.103067497597607,97.819996666854209,98.010339138278908,98.187485590498028,98.030191099852217,97.408123146556775,97.94214264409419,95.219109592524489,97.203381594479268,97.683785313190782,97.874941033588698,97.792657448404924,97.378203889786818,97.643743960205413,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 7600MTLP-US [240V]","N","Y","Y","Y","N","N","N","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter",7.6040000000000001,240,96.5,"Intertek","[10/13/2017]","[KC 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0999999999999997E-2,null,null,270,380,480,760.4,1520.8,2281.19,3801.99,5702.99,7603.98,94.3,95.8,96.2,96.1,95.8,95.3,95.8,96.1,97,97.2,97.1,96.8,96.3,96.9,94.9,96.5,96.9,96.9,96.7,96.3,96.7,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 7600MTLP-US [277V]","N","Y","Y","Y","N","N","N","7.6 kW, 277 Vac Grid Support Utility Interactive Inverter",7.6520000000000001,277,96.5,"Intertek","[10/13/2017]","[KC 1.0]","2019-01-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0999999999999997E-2,null,null,270,380,480,765.15,1530.3,2295.4499999999998,3825.75,5738.63,7651.5,94.3,95.8,96.2,96.1,95.8,95.3,95.8,96.1,97,97.2,97.1,96.8,96.3,96.9,94.9,96.5,96.9,96.9,96.7,96.3,96.7,"2017-10-16","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 9000MTLP-US [208V]","N","Y","Y","Y","N","N","N","9 kW, 208 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit",7.8639999999999999,208,97,"Intertek","[10/13/2017]","[KC 1.0]","2018-10-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",3.3,null,null,330,480,550,0.78639999999999999,1.5728,2.3592,3.9319999999999999,5.8979999999999997,7.8639999999999999,95.43432,96.863429999999994,97.122839999999997,97.083680000000001,96.760149999999996,96.539320000000004,96.812700000000007,95.518439999999998,96.989900000000006,97.353149999999999,97.446280000000002,97.178740000000005,97.000060000000005,97.171059999999997,94.826999999999998,96.616910000000004,97.056359999999998,97.24727,97.081869999999995,96.893640000000005,96.990690000000001,"2017-10-16","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 9000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",7.8739999999999997,208,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.78742000000000001,1.57484,2.36226,3.9371,5.9056499999999996,7.8742000000000001,93.982933333333335,96.079733333333337,96.698633333333333,97.030366666666666,96.912666666666667,96.784599999999998,96.746460333333332,95.587166666666661,97.35263333333333,97.782000000000011,97.92376666666668,97.770499999999998,97.671266666666668,97.690877666666665,94.584666666666664,96.692033333333342,97.396033333333335,97.712033333333324,97.66746666666667,97.580600000000004,97.467826666666667,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 8000MTLP-US [240V]","N","Y","Y","Y","N","N","N","8 kW, 240 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit",8.0609999999999999,240,97.5,"Intertek","[10/13/2017]","[KC 1.0]","2018-10-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",3.5,null,null,330,480,550,0.80610000000000004,1.6122000000000001,2.4182999999999999,4.0305,6.04575,8.0609999999999999,95.4816,96.806020000000004,97.298220000000001,97.457989999999995,97.318010000000001,97.01661,97.230900000000005,95.793940000000006,97.091250000000002,97.595429999999993,97.858990000000006,97.792810000000003,97.576599999999999,97.657179999999997,95.263710000000003,96.757559999999998,97.312370000000001,97.63409,97.694239999999994,97.527929999999998,97.483410000000006,"2017-10-16","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 8000MTLP-US [277V]","N","Y","Y","Y","N","N","N","8 kW, 277 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit",8.1370000000000005,277,97.5,"Intertek","[10/13/2017]","[KC 1.0]","2018-10-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",3.7,null,null,330,480,550,0.81369999999999998,1.6274,2.4411,4.0685000000000002,6.1027500000000003,8.1370000000000005,95.442130000000006,96.610879999999995,97.182379999999995,97.519840000000002,97.492549999999994,97.242800000000003,97.322469999999996,96.269720000000007,97.204390000000004,97.776979999999995,98.099580000000003,98.098389999999995,97.949449999999999,97.934780000000003,95.863069999999993,96.889769999999999,97.487949999999998,97.839110000000005,97.964219999999997,97.894599999999997,97.739540000000005,"2017-10-16","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 8200TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","8.2 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",8.2509999999999994,240,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.8251400000000001,1.6502800000000002,2.4754200000000002,4.1257000000000001,6.1885500000000002,8.2514000000000003,93.925766666666661,96.12466666666667,96.814266666666668,97.266599999999997,97.26166666666667,97.072066666666657,97.009248666666664,95.572199999999995,97.486333333333334,97.99163333333334,98.239066666666659,98.184200000000004,98.016600000000011,98.024860666666669,93.774266666666662,96.673366666666666,97.486766666666668,97.960933333333315,97.966002777777788,97.922899999999998,97.672973472222225,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 10000MTLP-US [208V]","N","Y","Y","Y","N","N","N","10 kW, 208 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit",8.6300000000000008,208,97,"Intertek","[10/13/2017]","[KC 1.0]","2018-10-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",3.3,null,null,330,480,550,0.86299999999999999,1.726,2.589,4.3150000000000004,6.4725000000000001,8.6300000000000008,95.560919999999996,96.370199999999997,96.519289999999998,97.053700000000006,96.608760000000004,96.429270000000002,96.628640000000004,95.622730000000004,96.768129999999999,96.790099999999995,97.453130000000002,97.126859999999994,96.958539999999999,97.068449999999999,95.032640000000001,96.781210000000002,97.151790000000005,97.339939999999999,96.997479999999996,96.880499999999998,96.992649999999998,"2017-10-16","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 10000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","10 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",8.76,208,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.87595000000000001,1.7519,2.6278499999999996,4.3797499999999996,6.5696249999999994,8.7594999999999992,94.714666666666659,96.187166666666656,96.764099999999999,96.945633333333348,96.722566666666665,96.626966666666675,96.662528666666674,96.189833333333326,97.494733333333329,97.833133333333336,97.854666666666674,97.653033333333326,97.544166666666669,97.645101999999994,94.884033333333335,96.995766666666682,97.535266666666658,97.725966666666665,97.613433333333333,97.51509999999999,97.482709333333332,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 9000MTLP-US [240V]","N","Y","Y","Y","N","N","N","9 kW, 240 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit",9.0609999999999999,240,97.5,"Intertek","[10/13/2017]","[KC 1.0]","2018-10-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",3.5,null,null,330,480,550,0.90610000000000002,1.8122,2.7183000000000002,4.5305,6.79575,9.0609999999999999,95.93065,97.035060000000001,97.362440000000007,97.405529999999999,97.158659999999998,96.78322,97.160880000000006,96.126360000000005,97.330820000000003,97.709829999999997,97.856560000000002,97.706140000000005,97.435649999999995,97.642690000000002,95.536010000000005,96.982789999999994,97.334860000000006,97.587569999999999,97.556820000000002,97.313829999999996,97.414959999999994,"2017-10-16","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 9000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",9.0630000000000006,240,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.90625,1.8125,2.71875,4.53125,6.796875,9.0625,94.238433333333347,96.270200000000003,96.907966666666667,97.323466666666675,97.200033333333351,97.040300000000002,97.017964000000006,95.948166666666665,97.602599999999995,98.070666666666668,98.251533333333342,98.142799999999994,97.991399999999985,98.034612666666661,94.371600000000001,96.898499999999999,97.634733333333344,98.022900000000021,98.040899999999993,97.941199999999995,97.779502999999991,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 9000MTLP-US [277V]","N","Y","Y","Y","N","N","N","9 kW, 277 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit",9.1690000000000005,277,97.5,"Intertek","[10/13/2017]","[KC 1.0]","2018-10-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",3.7,null,null,330,480,550,0.91690000000000005,1.8338000000000001,2.7507000000000001,4.5845000000000002,6.8767500000000004,9.1690000000000005,95.687690000000003,96.865970000000004,97.33663,97.541709999999995,97.445030000000003,97.157430000000005,97.338700000000003,96.344859999999997,97.280630000000002,97.773439999999994,98.113960000000006,98.064689999999999,97.891440000000003,97.923429999999996,95.934560000000005,97.087289999999996,97.619349999999997,97.924369999999996,98.000309999999999,97.894289999999998,97.805059999999997,"2017-10-16","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 11400TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",10.039999999999999,208,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,1.0039800000000001,2.0079600000000002,3.0119399999999996,5.0198999999999998,7.5298499999999997,10.0398,95.028400000000005,96.561569440212068,97.015406666666678,97.18135333333332,96.902286666666654,96.856743333333327,96.880196572010604,95.703000000000003,97.529443333333347,97.858743333333337,97.873270000000005,97.760676666666669,97.717863333333327,97.700079866666655,95.102010000000007,97.007023333333336,97.502409999999998,97.687100000000015,97.627340000000004,97.601256666666671,97.49156480000002,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 10000MTLP-US [240V]","N","Y","Y","Y","N","N","N","10 kW, 240 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit",10.058,240,97,"Intertek","[10/13/2017]","[KC 1.0]","2018-10-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",3.5,null,null,330,480,550,1.0058,2.0116000000000001,3.0173999999999999,5.0289999999999999,7.5434999999999999,10.058,95.749579999999995,96.575100000000006,96.691590000000005,96.532259999999994,96.916989999999998,96.60866,96.729939999999999,95.860209999999995,96.901910000000001,97.033869999999993,97.052809999999994,97.614750000000001,97.300539999999998,97.305509999999998,95.375290000000007,96.937259999999995,97.397279999999995,97.640140000000002,97.536789999999996,97.234260000000006,97.41019,"2017-10-16","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 10000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","10 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",10.082000000000001,240,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,1.0082000000000002,2.0164000000000004,3.0246,5.0410000000000004,7.5615000000000006,10.082000000000001,95.127566666666667,96.497600000000006,97.06753333333333,97.329633333333334,97.198499999999996,96.922933333333333,97.078661333333343,96.325299999999999,97.761799999999994,98.138366666666656,98.291933333333333,98.146199999999993,97.931600000000003,98.073077999999995,95.013433333333325,97.198399999999992,97.780266666666677,98.051733333333331,98.009233333333327,97.871933333333331,97.823443666666662,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 10000MTLP-US [277V]","N","Y","Y","Y","N","N","N","10 kW, 277 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit",10.164999999999999,277,97.5,"Intertek","[10/13/2017]","[KC 1.0]","2018-10-15","[10/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",3.7,null,null,330,480,550,1.0165,2.0329999999999999,3.0495000000000001,5.0824999999999996,7.6237500000000002,10.164999999999999,95.579530000000005,96.429109999999994,96.930059999999997,97.516750000000002,97.317729999999997,97.051460000000006,97.185730000000007,96.069519999999997,97.219009999999997,97.392870000000002,98.122780000000006,97.960220000000007,97.731359999999995,97.802149999999997,95.873689999999996,97.160489999999996,97.925309999999996,97.953310000000002,97.950850000000003,97.763180000000006,97.816320000000005,"2017-10-16","2018-10-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 11400TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",11.52,240,98,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,1.1519999999999999,2.3039999999999998,3.456,5.76,8.64,11.52,95.362579999999994,96.957206666666679,97.477490000000003,97.684960000000004,97.543343333333354,97.353883333333343,97.439170066666676,96.581923333333322,98.027549999999991,98.399886666666674,98.527416666666653,98.435103333333331,98.253936666666661,98.346699933333326,95.457046666666685,97.191386666666659,97.74481333333334,97.97084666666666,97.831793333333337,97.658173333333337,97.71486573333334,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 33000TL3-US [480V]","N","Y","Y","Y","N","N","N","33 kW, 480 Vac, three phases, 3/N/PE, Transformerless Grid Support Utility Interactive Inverter",32.270000000000003,480,98.5,"Intertek","[09/05/2018]","[teba0101]","2019-01-15","[09/05/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.0920000000000001,null,null,480,700,800,3.23,6.45,9.68,16.14,24.2,32.270000000000003,97.3,97.8,98.1,98.1,97.8,97.5,97.9,97.8,98.6,98.8,98.9,98.7,98.5,98.7,97.5,98,98.3,98.5,98.3,98.1,98.3,"2018-11-15","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 36000TL3-US [480V]","N","Y","Y","Y","N","N","N","36 kW, 480 Vac, three phases, 3/N/PE, Transformerless Grid Support Utility Interactive Inverter",35.71,480,98.5,"Intertek","[09/05/2018]","[teba0101]","2019-01-15","[09/05/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.0510000000000002,null,null,520,700,800,3.57,7.14,10.71,17.86,26.78,35.71,97.5,98.1,98.2,98.3,97.9,97.6,98,98,98.6,98.6,98.6,98.6,98.4,98.6,97.4,98.1,98.2,98.2,98.3,98.1,98.2,"2018-11-15","2019-01-15"]
["Shenzhen Growatt New Energy Technology Co., Ltd","GROWATT 40000TL3-US [480V]","N","Y","Y","Y","N","N","N","40 kW, 480Vac, three phases, 3/N/PE, Transformerless Grid Support Utility Interactive Inverter",39.85,480,98.5,"Intertek","[09/05/2018]","[teba0101]","2019-01-15","[09/05/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.0510000000000002,null,null,570,700,800,3.98,7.97,11.95,19.920000000000002,29.89,39.85,97.5,98,98,98.2,98,97.6,98,98.2,98.6,98.6,98.4,98.7,98.5,98.6,97.5,98.1,98.1,98,98.3,98.1,98.2,"2018-11-15","2019-01-15"]
["SMA America","SB3.0-1SP-US-40 [208V]","N","Y","Y","Y","N","N","N","3.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter",3,208,96,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.36,null,null,155,365,480,0.30320000000000003,0.60640000000000005,0.90959999999999996,1.516,2.274,3.032,92.082847310823283,94.907812539893044,95.629452499667281,95.991624416925447,95.996645587599161,95.731527423095798,95.727278479524358,92.071008131935372,95.659723853330703,96.458307803469552,97.043468119824496,97.202121349789977,97.084010489748991,96.791276599399595,88.515418011062167,94.502976183803142,95.722745381337489,96.424646022747879,96.772413583948293,96.64426016014221,96.123262847669906,"2018-08-01","2019-02-15"]
["SMA America","SB3.0-1SP-US-40 [240V]","N","Y","Y","Y","N","N","N","3.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter",3,240,96.5,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.39,null,null,155,365,480,0.30402668918918918,0.60805337837837836,0.91208006756756754,1.5201334459459459,2.2802001689189186,3.0402668918918918,90.951224418581774,94.441972778565543,95.383118364394548,95.941753675717251,96.037813109429734,95.94092229249739,95.650977153922128,92.03553711429818,95.784786159583902,96.641076797758544,97.163663961863477,97.516387567042486,97.582074705372591,97.034748586074627,88.509780526514959,94.438549047417638,95.736397687134939,96.677883011273849,97.024958205206346,97.000804957798053,96.326309924904464,"2018-08-01","2019-02-15"]
["SMA America","SB3.0-1TP-US-40 [208V]","N","Y","Y","Y","N","N","N","3.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",3,208,96,"UL","[06/28/2018]","[02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.36,null,null,155,365,480,0.30320000000000003,0.60640000000000005,0.90959999999999996,1.516,2.274,3.032,92.082847310823283,94.907812539893044,95.629452499667281,95.991624416925447,95.996645587599161,95.731527423095798,95.727278479524358,92.071008131935372,95.659723853330703,96.458307803469552,97.043468119824496,97.202121349789977,97.084010489748991,96.791276599399595,88.515418011062167,94.502976183803142,95.722745381337489,96.424646022747879,96.772413583948293,96.64426016014221,96.123262847669906,"2018-08-01","2019-02-15"]
["SMA America","SB3.0-1TP-US-40 [240V]","N","Y","Y","Y","N","N","N","3.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",3,240,96.5,"UL","[06/28/2018]","[02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.39,null,null,155,365,480,0.30402668918918918,0.60805337837837836,0.91208006756756754,1.5201334459459459,2.2802001689189186,3.0402668918918918,90.951224418581774,94.441972778565543,95.383118364394548,95.941753675717251,96.037813109429734,95.94092229249739,95.650977153922128,92.03553711429818,95.784786159583902,96.641076797758544,97.163663961863477,97.516387567042486,97.582074705372591,97.034748586074627,88.509780526514959,94.438549047417638,95.736397687134939,96.677883011273849,97.024958205206346,97.000804957798053,96.326309924904464,"2018-08-01","2019-02-15"]
["SMA America","SB3.0-1SP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","3.0 kW, 208 Vac Grid Support Utility Interactive Inverter",3.0276000000000001,208,96,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.36,null,null,155,365,480,0.30276000000000003,0.60552000000000006,0.90827999999999998,1.5138,2.2707000000000002,3.0276000000000001,92.082847310823283,94.907812539893044,95.629452499667281,95.991624416925447,95.996645587599161,95.731527423095798,95.727278479524358,92.071008131935372,95.659723853330703,96.458307803469552,97.043468119824496,97.202121349789977,97.084010489748991,96.791276599399595,88.515418011062167,94.502976183803142,95.722745381337489,96.424646022747879,96.772413583948293,96.64426016014221,96.123262847669906,"2019-05-01","2020-01-21"]
["SMA America","SB3.0-1TP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","3.0 kW, 208 Vac Grid Support Utility Interactive Inverter ",3.028,208,96,"UL","[03/13/2019]","[V2.04.15.R]","2019-11-15","[03/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.36,null,null,155,365,480,0.30299999999999999,0.60599999999999998,0.90800000000000003,1.514,2.2709999999999999,3.028,92.08,94.91,95.63,95.99,96,95.73,95.73,92.07,95.66,96.46,97.04,97.2,97.08,96.79,88.52,94.5,95.72,96.42,96.77,96.64,96.12,"2019-11-15","2020-01-13"]
["SMA America","SB3.0-1SP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","3.0 kW, 240 Vac Grid Support Utility Interactive Inverter",3.036,240,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.39,null,null,155,365,480,0.30362,0.60724,0.91086,1.5181,2.2771499999999998,3.0362,90.951999999999998,94.441999999999993,95.379999999999981,95.94,96.037999999999997,95.940000000000012,95.650319999999994,92.035999999999987,95.787999999999997,96.641999999999996,97.166000000000011,97.515999999999991,97.580000000000013,97.035219999999995,88.51,94.438000000000002,95.738000000000014,96.677999999999997,97.024000000000001,97,96.325960000000009,"2019-05-01","2020-01-21"]
["SMA America","SB3.0-1TP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","3.0 kW, 240 Vac Grid Support Utility Interactive Inverter ",3.036,240,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-11-15","[03/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.39,null,null,155,365,480,0.30399999999999999,0.60699999999999998,0.91100000000000003,1.518,2.2770000000000001,3.036,90.95,94.44,95.38,95.94,96.04,95.94,95.65,92.04,95.79,96.64,97.17,97.52,97.58,97.04,88.51,94.44,95.74,96.68,97.02,97,96.33,"2019-11-15","2020-01-13"]
["SMA America","SB3.8-1SP-US-40 [208V]","N","Y","Y","Y","N","N","N","3.8 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter",3.6,208,96.5,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.36,null,null,195,365,480,0.36045400000000005,0.7209080000000001,1.0813619999999999,1.80227,2.7034050000000001,3.6045400000000001,92.9307882700177,95.476148178928241,96.029992473112927,96.472910461543449,96.37876487615506,96.152677617325793,96.162328498673276,92.531495773128313,95.951025180138728,96.621311597273717,97.059603157019836,97.224711983689119,96.978656177455747,96.853915304807103,89.80793356250021,94.91925956195459,95.99712875139376,96.576860828695345,96.770045807349476,96.849589768746824,96.269680311123579,"2018-08-01","2019-02-15"]
["SMA America","SB3.8-1TP-US-40 [208V]","N","Y","Y","Y","N","N","N","3.8 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",3.6,208,96.5,"UL","[06/28/2018]","[02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.36,null,null,195,365,480,0.36045400000000005,0.7209080000000001,1.0813619999999999,1.80227,2.7034050000000001,3.6045400000000001,92.9307882700177,95.476148178928241,96.029992473112927,96.472910461543449,96.37876487615506,96.152677617325793,96.162328498673276,92.531495773128313,95.951025180138728,96.621311597273717,97.059603157019836,97.224711983689119,96.978656177455747,96.853915304807103,89.80793356250021,94.91925956195459,95.99712875139376,96.576860828695345,96.770045807349476,96.849589768746824,96.269680311123579,"2018-08-01","2019-02-15"]
["SMA America","SB3.8-1SP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 208 Vac Grid Support Utility Interactive Inverter",3.6040000000000001,208,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.36,null,null,195,365,480,0.36039299999999996,0.72078599999999993,1.0811789999999999,1.8019649999999998,2.7029474999999996,3.6039299999999996,92.930788270017686,95.476148178928256,96.029992473112912,96.472910461543435,96.378764876155046,96.152677617325779,96.162328498673247,92.531495773128313,95.951025180138743,96.621311597273689,97.059603157019836,97.224711983689104,96.978656177455747,96.853915304807103,89.807933562500182,94.91925956195459,95.997128751393774,96.576860828695317,96.770045807349476,96.849589768746839,96.269680311123579,"2019-05-01","2020-01-21"]
["SMA America","SB3.8-1TP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 208 Vac Grid Support Utility Interactive Inverter  ",3.6040000000000001,208,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-11-15","[03/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.36,null,null,195,365,480,0.36,0.72099999999999997,1.081,1.802,2.7029999999999998,3.6040000000000001,92.93,95.48,96.03,96.47,96.38,96.15,96.16,92.53,95.95,96.62,97.06,97.22,96.98,96.85,89.81,96.92,96,96.58,96.77,96.85,96.27,"2019-11-15","2020-01-13"]
["SMA America","SB3.8-1SP-US-40 [240V]","N","Y","Y","Y","N","N","N","3.8 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter",3.8,240,96.5,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.39,null,null,195,365,480,0.38542700000000002,0.77085400000000004,1.1562809999999999,1.927135,2.8907025000000002,3.8542700000000001,92.681418318038126,95.370109391033424,96.070222112677214,96.455330264892524,96.443882991198933,96.232778992810211,96.186705146397841,93.680244478450931,96.435440070880389,96.895311691249105,97.434600781845177,97.587655846920612,97.46796631140225,97.252541264257474,90.805647134134389,95.309565566853777,96.404880449161809,96.909933627135729,97.155681948405487,97.307422483982663,96.675258436160021,"2018-08-01","2019-02-15"]
["SMA America","SB3.8-1TP-US-40 [240V]","N","Y","Y","Y","N","N","N","3.8 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",3.8,240,96.5,"UL","[06/28/2018]","[V02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.39,null,null,195,365,480,0.38542700000000002,0.77085400000000004,1.1562809999999999,1.927135,2.8907025000000002,3.8542700000000001,92.681418318038126,95.370109391033424,96.070222112677214,96.455330264892524,96.443882991198933,96.232778992810211,96.186705146397841,93.680244478450931,96.435440070880389,96.895311691249105,97.434600781845177,97.587655846920612,97.46796631140225,97.252541264257474,90.805647134134389,95.309565566853777,96.404880449161809,96.909933627135729,97.155681948405487,97.307422483982663,96.675258436160021,"2018-08-01","2019-02-15"]
["SMA America","SB3.8-1SP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter",3.8530000000000002,240,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.39,null,null,195,365,480,0.38532,0.77063999999999999,1.1559599999999999,1.9265999999999999,2.8898999999999999,3.8531999999999997,92.681418318038126,95.370109391033424,96.070222112677229,96.45533026489251,96.443882991198933,96.232778992810196,96.186705146397841,93.680244478450931,96.435440070880389,96.895311691249105,97.434600781845162,97.587655846920626,97.467966311402236,97.252541264257474,90.805647134134404,95.309565566853792,96.404880449161794,96.909933627135729,97.155681948405459,97.307422483982677,96.675258436160007,"2019-05-01","2020-01-21"]
["SMA America","SB3.8-1TP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter  ",3.8530000000000002,240,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-11-15","[03/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.39,null,null,195,365,480,0.38500000000000001,0.77100000000000002,1.1559999999999999,1.927,2.89,3.8530000000000002,92.68,95.37,96.07,96.46,96.44,96.23,96.19,93.68,96.44,96.9,97.43,97.59,97.47,97.25,90.81,95.31,96.4,96.91,97.16,97.31,96.68,"2019-11-15","2020-01-13"]
["SMA America","SB5.0-1SP-US-40 [208V]","N","Y","Y","Y","N","N","N","5.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter",5,208,96.5,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0599999999999996,null,null,220,365,480,0.51,1.01,1.52,2.5299999999999998,3.8,5.0599999999999996,94.7,96.3,96.6,96.6,96.4,96,96.4,94.7,96.7,97.1,97.2,97.1,96.8,97,91.1,96.1,96.7,96.9,97,96.8,96.6,"2018-08-01","2019-02-15"]
["SMA America","SB5.0-1SP-US-40 [240V]","N","Y","Y","Y","N","N","N","5.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter",5,240,97,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.21,null,null,220,365,480,0.51,1.01,1.52,2.5299999999999998,3.79,5.05,93.3,96,96.5,96.7,96.6,96.4,96.4,93.4,96.9,97.2,97.5,97.4,97.2,97.2,91.2,96.2,96.8,97.2,97.4,97.3,97,"2018-08-01","2019-02-15"]
["SMA America","SB5.0-1TP-US-40 [208V]","N","Y","Y","Y","N","N","N","5.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",5,208,96.5,"UL","[06/28/2018]","[V02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0599999999999996,null,null,220,365,480,0.51,1.01,1.52,2.5299999999999998,3.8,5.0599999999999996,94.7,96.3,96.6,96.6,96.4,96,96.4,94.7,96.7,97.1,97.2,97.1,96.8,97,91.1,96.1,96.7,96.9,97,96.8,96.6,"2018-08-01","2019-02-15"]
["SMA America","SB5.0-1TP-US-40 [240V]","N","Y","Y","Y","N","N","N","5.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",5,240,97,"UL","[06/28/2018]","[V02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.21,null,null,220,365,480,0.51,1.01,1.52,2.5299999999999998,3.79,5.05,93.3,96,96.5,96.7,96.6,96.4,96.4,93.4,96.9,97.2,97.5,97.4,97.2,97.2,91.2,96.2,96.8,97.2,97.4,97.3,97,"2018-08-01","2019-02-15"]
["SMA America","SB5.0-1SP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 208 Vac Grid Support Utility Interactive Inverter",5.05,208,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.0599999999999996,null,null,220,365,480,0.50498600000000005,1.0099720000000001,1.5149579999999998,2.5249299999999999,3.7873950000000001,5.0498599999999998,94.694272992012344,96.306403894962799,96.556182180436878,96.629139843854105,96.44590174223292,96.027414369447271,96.399650985146238,94.725365105158701,96.717172960691215,97.077107314242554,97.228895227184736,97.08430393019087,96.774699425955944,96.985610181957767,91.103239690370032,96.149008524443119,96.662506014160243,96.911977315709606,96.961821692191009,96.796678429119126,96.632195390152404,"2019-05-01","2020-01-21"]
["SMA America","SB5.0-1TP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 208 Vac Grid Support Utility Interactive Inverter ",5.05,208,96.5,"UL","[3/13/2019]","[V2.04.15.R]","2019-12-02","[3/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.0599999999999996,null,null,220,365,480,0.50498600000000005,1.0099720000000001,1.5149579999999998,2.5249299999999999,3.7873950000000001,5.0498599999999998,94.694272992012344,96.306403894962799,96.556182180436878,96.629139843854105,96.44590174223292,96.027414369447271,96.399650985146238,94.725365105158701,96.717172960691215,97.077107314242554,97.228895227184736,97.08430393019087,96.774699425955944,96.985610181957767,91.103239690370032,96.149008524443119,96.662506014160243,96.911977315709606,96.961821692191009,96.796678429119126,96.632195390152404,"2019-12-02","2020-01-13"]
["SMA America","SB5.0-1SP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac Grid Support Utility Interactive Inverter",5.0590000000000002,240,97,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.21,null,null,220,365,480,0.50586199999999992,1.0117239999999998,1.5175859999999999,2.5293099999999997,3.7939649999999996,5.0586199999999995,93.349375774640279,96.030817694837552,96.455855161268317,96.661398786463593,96.609935752767456,96.367771492351665,96.430766803821371,93.440541083059287,96.858532303920839,97.231850325066787,97.509783560576238,97.412867067403496,97.223708474662473,97.215429814704422,91.209970914504268,96.180352319821424,96.805422495274655,97.206750237719334,97.372804907658036,97.269999282994903,96.958571267133777,"2019-05-01","2020-01-21"]
["SMA America","SB5.0-1TP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac Grid Support Utility Interactive Inverter ",5.0590000000000002,240,97,"UL","[3/13/2019]","[V2.04.15.R]","2019-12-02","[3/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.21,null,null,220,365,480,0.50586199999999992,1.0117239999999998,1.5175859999999999,2.5293099999999997,3.7939649999999996,5.0586199999999995,93.349375774640279,96.030817694837552,96.455855161268317,96.661398786463593,96.609935752767456,96.367771492351665,96.430766803821371,93.440541083059287,96.858532303920839,97.231850325066787,97.509783560576238,97.412867067403496,97.223708474662473,97.215429814704422,91.209970914504268,96.180352319821424,96.805422495274655,97.206750237719334,97.372804907658036,97.269999282994903,96.958571267133777,"2019-12-02","2020-01-13"]
["SMA America","SB6.0-1SP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW, 208 Vac Grid Support Utility Interactive Inverter",5.4180000000000001,208,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.0599999999999996,null,null,220,365,480,0.54176800000000014,1.0835360000000003,1.6253040000000001,2.7088400000000004,4.0632600000000005,5.4176800000000007,94.809785653264569,96.322258336085312,96.566858060182724,96.626969769322528,96.429938786409096,95.983671323823444,96.395242084702517,94.849899506675314,96.738054188958984,97.078146760479299,97.231394965494019,97.069841848811478,96.774699425955944,96.984620394894094,91.746339082208735,96.180602697708323,96.677547108416007,96.845313882502666,96.961821692191009,96.786025600250284,96.646772043382995,"2019-05-01","2020-01-21"]
["SMA America","SB6.0-1TP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW, 208 Vac Grid Support Utility Interactive Inverter ",5.4180000000000001,208,96.5,"UL","[3/13/2019]","[V2.04.15.R]","2019-12-02","[3/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.0599999999999996,null,null,220,365,480,0.54176800000000014,1.0835360000000003,1.6253040000000001,2.7088400000000004,4.0632600000000005,5.4176800000000007,94.809785653264569,96.322258336085312,96.566858060182724,96.626969769322528,96.429938786409096,95.983671323823444,96.395242084702517,94.849899506675314,96.738054188958984,97.078146760479299,97.231394965494019,97.069841848811478,96.774699425955944,96.984620394894094,91.746339082208735,96.180602697708323,96.677547108416007,96.845313882502666,96.961821692191009,96.786025600250284,96.646772043382995,"2019-12-02","2020-01-13"]
["SMA America","SB6.0-1SP-US-40 [208V]","N","Y","Y","Y","N","N","N","6.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter",5.49,208,96.5,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0599999999999996,null,null,220,365,480,0.55000000000000004,1.1000000000000001,1.65,2.75,4.12,5.49,94.8,96.3,96.6,96.6,96.4,96,96.4,94.8,96.7,97.1,97.2,97.1,96.8,97,91.7,96.2,96.7,96.8,97,96.8,96.6,"2018-08-01","2019-02-15"]
["SMA America","SB6.0-1TP-US-40 [208V]","N","Y","Y","Y","N","N","N","6.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",5.49,208,96.5,"UL","[06/28/2018]","[V02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0599999999999996,null,null,220,365,480,0.55000000000000004,1.1000000000000001,1.65,2.75,4.12,5.49,94.8,96.3,96.6,96.6,96.4,96,96.4,94.8,96.7,97.1,97.2,97.1,96.8,97,91.7,96.2,96.7,96.8,97,96.8,96.6,"2018-08-01","2019-02-15"]
["SMA America","SB6.0-1SP-US-40 [240V]","N","Y","Y","Y","N","N","N","6.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter",6,240,97,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.21,null,null,220,365,480,0.61,1.21,1.82,3.03,4.54,6.05,94.7,96.3,96.6,96.6,96.5,96.1,96.4,95.4,97.1,97.4,97.6,97.3,97,97.3,93.4,96.5,97,97.3,97.3,97,97.1,"2018-08-01","2019-02-15"]
["SMA America","SB6.0-1TP-US-40 [240V]","N","Y","Y","Y","N","N","N","6.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",6,240,97,"UL","[06/28/2018]","[V02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.21,null,null,220,365,480,0.61,1.21,1.82,3.03,4.54,6.05,94.7,96.3,96.6,96.6,96.5,96.1,96.4,95.4,97.1,97.4,97.6,97.3,97,97.3,93.4,96.5,97,97.3,97.3,97,97.1,"2018-08-01","2019-02-15"]
["SMA America","SB6.0-1SP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW, 240 Vac Grid Support Utility Interactive Inverter",6.0519999999999996,240,97,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.21,null,null,220,365,480,0.605182,1.210364,1.8155459999999997,3.0259099999999997,4.5388649999999995,6.0518199999999993,94.6791908353769,96.306516766455701,96.615724425449216,96.64893623477505,96.481015988001374,96.136953754864592,96.434443173478485,95.437370066511718,97.102062854061003,97.373562246268847,97.564254334671404,97.312392575465111,97.013503803749401,97.272162080380753,93.374252341727399,96.545059881476405,97.014720357719824,97.323605866096713,97.282084860615043,97.012916898036025,97.052097583577392,"2019-05-01","2020-01-21"]
["SMA America","SB6.0-1TP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW, 240 Vac Grid Support Utility Interactive Inverter ",6.0519999999999996,240,97,"UL","[3/13/2019]","[V2.04.15.R]","2019-12-02","[3/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.21,null,null,220,365,480,0.605182,1.210364,1.8155459999999997,3.0259099999999997,4.5388649999999995,6.0518199999999993,94.6791908353769,96.306516766455701,96.615724425449216,96.64893623477505,96.481015988001374,96.136953754864592,96.434443173478485,95.437370066511718,97.102062854061003,97.373562246268847,97.564254334671404,97.312392575465111,97.013503803749401,97.272162080380753,93.374252341727399,96.545059881476405,97.014720357719824,97.323605866096713,97.282084860615043,97.012916898036025,97.052097583577392,"2019-12-02","2020-01-13"]
["SMA America","SB7.0-1SP-US-40 [208V]","N","Y","Y","Y","N","N","N","7.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter",6.92,208,96.5,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.37,null,null,245,365,480,0.69229200000000013,1.3845840000000003,2.0768759999999999,3.4614600000000002,5.1921900000000001,6.9229200000000004,95.419061703064287,96.499658027102697,96.88045791135923,96.393086769309974,96.129474857598581,95.592242556865628,96.238182342766436,95.353213586067,96.662819533921152,97.141218412093252,97.042413391199077,96.664770711519509,96.234566715506347,96.727179354622393,94.136333765369216,96.347477157208587,96.676448901531828,96.683895373382299,96.35230391567147,96.304758321348373,96.369578096442609,"2018-08-01","2019-02-15"]
["SMA America","SB7.0-1TP-US-40 [208V]","N","Y","Y","Y","N","N","N","7.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",6.92,208,96.5,"UL","[06/28/2018]","[V02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.37,null,null,245,365,480,0.69229200000000013,1.3845840000000003,2.0768759999999999,3.4614600000000002,5.1921900000000001,6.9229200000000004,95.419061703064287,96.499658027102697,96.88045791135923,96.393086769309974,96.129474857598581,95.592242556865628,96.238182342766436,95.353213586067,96.662819533921152,97.141218412093252,97.042413391199077,96.664770711519509,96.234566715506347,96.727179354622393,94.136333765369216,96.347477157208587,96.676448901531828,96.683895373382299,96.35230391567147,96.304758321348373,96.369578096442609,"2018-08-01","2019-02-15"]
["SMA America","SB7.7-1SP-US-40 [208V]","N","Y","Y","Y","N","N","N","7.7 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter",6.92,208,96.5,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.37,null,null,270,365,480,0.69229200000000013,1.3845840000000003,2.0768759999999999,3.4614600000000002,5.1921900000000001,6.9229200000000004,95.688053123906386,96.710543077634085,96.729020288510867,96.53964427594083,96.050655840705787,95.694674168608302,96.235438315411315,95.353213586067,96.662819533921152,97.141218412093252,97.042413391199077,96.664770711519509,96.234566715506347,96.727179354622393,94.136333765369216,96.347477157208587,96.676448901531828,96.683895373382299,96.35230391567147,96.304758321348373,96.369578096442609,"2018-08-01","2019-02-15"]
["SMA America","SB7.7-1TP-US-40 [208V]","N","Y","Y","Y","N","N","N","7.7 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",6.92,208,96.5,"UL","[06/28/2018]","[V02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.37,null,null,270,365,480,0.69229200000000013,1.3845840000000003,2.0768759999999999,3.4614600000000002,5.1921900000000001,6.9229200000000004,95.688053123906386,96.710543077634085,96.729020288510867,96.53964427594083,96.050655840705787,95.694674168608302,96.235438315411315,95.353213586067,96.662819533921152,97.141218412093252,97.042413391199077,96.664770711519509,96.234566715506347,96.727179354622393,94.136333765369216,96.347477157208587,96.676448901531828,96.683895373382299,96.35230391567147,96.304758321348373,96.369578096442609,"2018-08-01","2019-02-15"]
["SMA America","SB7.0-1SP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","7.0 kW, 208 Vac Grid Support Utility Interactive Inverter  ",6.923,208,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.37,null,null,245,365,480,0.69229200000000013,1.3845840000000003,2.0768759999999999,3.4614600000000002,5.1921900000000001,6.9229200000000004,95.419061703064301,96.499658027102683,96.88045791135923,96.393086769309974,96.129474857598595,95.592242556865642,96.23818234276645,95.353213586067,96.662819533921137,97.141218412093266,97.042413391199119,96.664770711519495,96.234566715506375,96.727179354622393,94.136333765369216,96.347477157208587,96.676448901531813,96.683895373382299,96.352303915671456,96.304758321348359,96.369578096442581,"2019-05-01","2020-01-21"]
["SMA America","SB7.0-1TP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","7.0 kW, 208 Vac Grid Support Utility Interactive Inverter ",6.923,208,96.5,"UL","[3/13/2019]","[V2.04.15.R]","2019-12-02","[3/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.37,null,null,245,365,480,0.69229200000000013,1.3845840000000003,2.0768759999999999,3.4614600000000002,5.1921900000000001,6.9229200000000004,95.419061703064301,96.499658027102683,96.88045791135923,96.393086769309974,96.129474857598595,95.592242556865642,96.23818234276645,95.353213586067,96.662819533921137,97.141218412093266,97.042413391199119,96.664770711519495,96.234566715506375,96.727179354622393,94.136333765369216,96.347477157208587,96.676448901531813,96.683895373382299,96.352303915671456,96.304758321348359,96.369578096442581,"2019-12-11","2020-01-13"]
["SMA America","SB7.7-1SP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","7.7 kW, 208 Vac Grid Support Utility Interactive Inverter  ",6.923,208,96.5,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.37,null,null,270,365,480,0.69229200000000013,1.3845840000000003,2.0768759999999999,3.4614600000000002,5.1921900000000001,6.9229200000000004,95.688053123906386,96.710543077634085,96.729020288510881,96.53964427594083,96.050655840705787,95.69467416860833,96.235438315411329,95.353213586067,96.662819533921137,97.141218412093266,97.042413391199119,96.664770711519495,96.234566715506375,96.727179354622393,94.136333765369216,96.347477157208587,96.676448901531813,96.683895373382299,96.352303915671456,96.304758321348359,96.369578096442581,"2019-05-01","2020-01-21"]
["SMA America","SB7.7-1TP-US-41 [208V]","N","Y","Y","Y","Y","Y*","Y","7.7 kW, 208 Vac Grid Support Utility Interactive Inverter ",6.923,208,96.54,"UL","[3/13/2019]","[V2.04.15.R]","2019-12-02","[3/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.37,null,null,270,365,480,0.69229200000000013,1.3845840000000003,2.0768759999999999,3.4614600000000002,5.1921900000000001,6.9229200000000004,95.688053123906386,96.710543077634085,96.729020288510881,96.53964427594083,96.050655840705787,95.69467416860833,96.235438315411329,95.353213586067,96.662819533921137,97.141218412093266,97.042413391199119,96.664770711519495,96.234566715506375,96.727179354622393,94.136333765369216,96.347477157208587,96.676448901531813,96.683895373382299,96.352303915671456,96.304758321348359,96.369578096442581,"2019-12-11","2020-01-13"]
["SMA America","SB7.0-1SP-US-40 [240V]","N","Y","Y","Y","N","N","N","7.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter",7,240,97,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0999999999999996,null,null,245,365,480,0.70972800000000003,1.4194560000000001,2.129184,3.5486399999999998,5.3229600000000001,7.0972799999999996,95.102458703405631,96.528916978526041,96.628576656752571,96.745284419395801,96.520188282400156,96.06756094030321,96.501560960633199,95.720680528733837,97.412913400576855,97.49429474759863,97.399367740480358,96.979143362181489,96.517274883002116,97.077465212497202,93.761096157212492,96.549548112626141,96.90964628936652,97.192345206813769,96.999613688267388,96.667718847050196,96.860652497208903,"2018-08-01","2019-02-15"]
["SMA America","SB7.0-1TP-US-40 [240V]","N","Y","Y","Y","N","N","N","7.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",7,240,97,"UL","[06/28/2018]","[V02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0999999999999996,null,null,245,365,480,0.70972800000000003,1.4194560000000001,2.129184,3.5486399999999998,5.3229600000000001,7.0972799999999996,95.102458703405631,96.528916978526041,96.628576656752571,96.745284419395801,96.520188282400156,96.06756094030321,96.501560960633199,95.720680528733837,97.412913400576855,97.49429474759863,97.399367740480358,96.979143362181489,96.517274883002116,97.077465212497202,93.761096157212492,96.549548112626141,96.90964628936652,97.192345206813769,96.999613688267388,96.667718847050196,96.860652497208903,"2018-08-01","2019-02-15"]
["SMA America","SB7.0-1SP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","7.0 kW, 240 Vac Grid Support Utility Interactive Inverter  ",7.0090000000000003,240,97,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.0999999999999996,null,null,245,365,480,0.70094000000000001,1.40188,2.1028199999999999,3.5046999999999997,5.2570499999999996,7.0093999999999994,95.102458703405631,96.528916978526027,96.628576656752557,96.745284419395816,96.520188282400184,96.067560940303224,96.501560960633213,95.720680528733823,97.412913400576869,97.494294747598659,97.399367740480344,96.979143362181503,96.517274883002145,97.077465212497216,93.761096157212449,96.549548112626141,96.90964628936652,97.192345206813783,96.999613688267388,96.667718847050224,96.860652497208903,"2019-05-01","2020-01-21"]
["SMA America","SB7.0-1TP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","7.0 kW, 240 Vac Grid Support Utility Interactive Inverter ",7.0090000000000003,240,97,"UL","[3/13/2019]","[V2.04.15.R]","2019-12-02","[3/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.0999999999999996,null,null,245,365,480,0.70094000000000001,1.40188,2.1028199999999999,3.5046999999999997,5.2570499999999996,7.0093999999999994,95.102458703405631,96.528916978526027,96.628576656752557,96.745284419395816,96.520188282400184,96.067560940303224,96.501560960633213,95.720680528733823,97.412913400576869,97.494294747598659,97.399367740480344,96.979143362181503,96.517274883002145,97.077465212497216,93.761096157212449,96.549548112626141,96.90964628936652,97.192345206813783,96.999613688267388,96.667718847050224,96.860652497208903,"2019-12-11","2020-01-13"]
["SMA America","SB7.7-1SP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","7.7 kW, 240 Vac Grid Support Utility Interactive Inverter  ",7.7560000000000002,240,97,"UL","[03/13/2019]","[V2.04.15.R]","2019-05-01","[03/13/2019]","2020-01-21","UL","2019-12-16","2020-01-21",null,"Y","N",5.0999999999999996,null,null,270,365,480,0.77564,1.55128,2.3269199999999999,3.8781999999999996,5.8172999999999995,7.7563999999999993,95.659488070726923,96.757391309155793,97.078301472709839,96.947842323174768,96.535665461330581,96.0094843886083,96.637069066814377,96.032054518718354,97.522955729246149,97.442724867789295,97.314559365868064,96.787686223418859,96.345625620524885,96.961369397616281,94.682466000905563,96.825185000365039,97.023585332140442,97.192345206813783,96.875075175305284,96.728412801633709,96.861991106335708,"2019-05-01","2020-01-21"]
["SMA America","SB7.7-1TP-US-41 [240V]","N","Y","Y","Y","Y","Y*","Y","7.7 kW, 240 Vac Grid Support Utility Interactive Inverter ",7.7560000000000002,240,97,"UL","[3/13/2019]","[V2.04.15.R]","2019-12-02","[3/13/2019]","2020-01-13","UL","2019-12-16","2020-01-13",null,"Y","N",5.0999999999999996,null,null,270,365,480,0.77564,1.55128,2.3269199999999999,3.8781999999999996,5.8172999999999995,7.7563999999999993,95.659488070726923,96.757391309155793,97.078301472709839,96.947842323174768,96.535665461330581,96.0094843886083,96.637069066814377,96.032054518718354,97.522955729246149,97.442724867789295,97.314559365868064,96.787686223418859,96.345625620524885,96.961369397616281,94.682466000905563,96.825185000365039,97.023585332140442,97.192345206813783,96.875075175305284,96.728412801633709,96.861991106335708,"2019-12-11","2020-01-13"]
["SMA America","SB7.7-1SP-US-40 [240V]","N","Y","Y","Y","N","N","N","7.7 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter",7.76,240,97,"UL","[2/21/2017]","[02.03.00.R]","2018-10-15","[2/21/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0999999999999996,null,null,270,365,480,0.77580000000000005,1.5516000000000001,2.3273999999999999,3.879,5.8185000000000002,7.758,95.659488070726908,96.757391309155807,97.078301472709839,96.947842323174768,96.535665461330566,96.009484388608314,96.637069066814362,96.032054518718382,97.522955729246149,97.442724867789281,97.314559365868078,96.787686223418859,96.345625620524885,96.961369397616281,94.682466000905563,96.825185000365011,97.02358533214047,97.192345206813769,96.875075175305284,96.728412801633681,96.861991106335708,"2018-08-01","2019-02-15"]
["SMA America","SB7.7-1TP-US-40 [240V]","N","Y","Y","Y","N","N","N","7.7 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter",7.76,240,97,"UL","[06/28/2018]","[V02.03.00.R]","2018-10-15","[06/28/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.0999999999999996,null,null,270,365,480,0.77580000000000005,1.5516000000000001,2.3273999999999999,3.879,5.8185000000000002,7.758,95.659488070726908,96.757391309155807,97.078301472709839,96.947842323174768,96.535665461330566,96.009484388608314,96.637069066814362,96.032054518718382,97.522955729246149,97.442724867789281,97.314559365868078,96.787686223418859,96.345625620524885,96.961369397616281,94.682466000905563,96.825185000365011,97.02358533214047,97.192345206813769,96.875075175305284,96.728412801633681,96.861991106335708,"2018-08-01","2019-02-15"]
["SMA America","STP12000TL-US-10 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 12 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter",12,480,97.5,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,300,675,800,1.2000000000000002,2.4000000000000004,3.5999999999999996,6,9,12,92.894674644817883,95.825371847114951,96.49457533743761,96.690700406340042,96.627312947730815,96.507013910909436,96.429278261815185,94.885736215076193,96.883040483522223,97.494372087983805,97.777000604401067,97.832115333209018,97.811357024005105,97.613665228062487,94.154840052277819,97.204030409030267,97.700750214004856,98.014008962786292,98.183788377033963,98.189784411397596,97.880324090806212,"2018-08-01","2019-02-15"]
["SMA America","STP15000TL-US-10 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 15 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter",15,480,97.5,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,300,675,800,1.5,3,4.5,7.5,11.25,15,93.855655768325036,96.220132968022185,96.731415475995405,96.662686184447367,96.525350018358225,96.347074199043405,96.447956054669547,95.495928692020158,97.192892755040859,97.796289926240703,97.802899005800356,97.832975895750408,97.777428409336565,97.693994013014347,95.552946082935037,97.515080368134008,97.923591757588014,98.172996722782088,98.214818639191321,98.157219501191648,98.02674703824988,"2018-08-01","2019-02-15"]
["SMA America","STP20000TL-US-10 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 20 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter",20,480,97.5,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,380,695,800,2,4,6,10,15,20,95.166002573680657,96.960461207919593,97.206210307973649,97.083526385263212,96.934118174722499,96.705141513761617,96.917288649496328,97.228849010193727,98.289481853362432,98.509907734190421,98.548489172388329,97.836810327646688,97.705085096687185,98.058763435867391,96.492868266958425,97.86877684687623,98.130627177880115,98.219804322689427,98.174642673551418,98.04215458277919,98.089656088253761,"2018-08-01","2019-02-15"]
["SMA America","STP24000TL-US-10 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 24 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter",24,480,98,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,450,712,800,2.4060000000000001,4.8120000000000003,7.2179999999999991,12.03,18.044999999999998,24.06,96.082505616067209,97.424181190564596,97.444656931781154,97.315063669223932,97.122156907959265,96.865885453167053,97.162068920398454,97.45990452259629,98.348028973855392,98.503124414275888,98.531362070230031,98.435119435359169,98.266514886637623,98.411697639130281,96.909942056488973,98.004925627161398,98.188558637442924,98.204070345596193,98.076628570877034,97.882251177120239,98.056851474106807,"2018-08-01","2019-02-15"]
["SMA America","STP30000TL-US-10 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 30 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter",30,480,98,"UL","[7/6/2017]","[2.03.04.R]","2018-10-15","[7/6/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.22,null,null,500,720,800,3.0010000000000003,6.0020000000000007,9.0030000000000001,15.005000000000001,22.5075,30.01,96.587999999999994,97.715999999999994,97.926000000000016,97.97999999999999,97.838000000000008,97.622,97.811480000000017,97.588000000000008,98.448000000000008,98.690000000000012,98.602000000000004,98.537999999999982,98.328000000000003,98.516679999999994,97.025999999999996,98.059999999999988,98.451999999999998,98.385999999999996,98.281999999999996,98.08,98.252799999999993,"2018-08-01","2019-02-15"]
["SMA America","STP 33-US-41 [480V]","N","Y","Y","Y","Y","Y*","Y","33.3 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter",33.299999999999997,480,97.5,"UL","[11/08/2018]","[01.09.03.R]","2018-12-17","[11/08/2018]","2020-01-13","UL","2019-12-16","2020-01-13",null,"N","N",5.43,null,null,330,683,800,3.33,6.66,9.9899999999999984,16.649999999999999,24.974999999999998,33.299999999999997,94.259,96.337000000000018,96.705000000000013,96.64400000000002,96.46,96.002999999999986,96.411000000000016,94.707000000000022,96.754999999999995,97.302999999999983,97.646999999999991,97.694000000000003,97.719000000000008,97.47202999999999,95.731000000000009,97.626000000000005,98.043999999999983,98.228999999999999,98.119,97.988000000000014,98.006379999999993,"2018-12-17","2020-01-13"]
["SMA America","STP 50-US-41 [480V]","N","Y","Y","Y","Y","Y*","Y","50 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter",50,480,97.5,"UL","[11/08/2018]","[01.09.03.R]","2018-12-17","[11/08/2018]","2020-01-13","UL","2019-12-16","2020-01-13",null,"N","N",5.43,null,null,500,725,800,5.0006000000000004,10.001200000000001,15.001799999999999,25.003,37.5045,50.006,95.551999999999992,97.12299999999999,97.41,97.362000000000009,97.004999999999995,96.688000000000017,97.060500000000005,96.195000000000007,97.446000000000026,97.741,97.833000000000013,97.603999999999999,97.356999999999999,97.591920000000002,97.061999999999998,98.073999999999998,98.228999999999999,98.119,97.965000000000003,97.765000000000015,97.988350000000011,"2018-12-17","2020-01-13"]
["SMA America","STP50-US-40 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower CORE1 50 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter",50,480,98,"UL","[8/14/2017]","[V1.01.19.R]","2018-10-15","[8/14/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5.0999999999999996,null,null,500,725,800,5.007200000000001,10.014400000000002,15.021599999999999,25.036000000000001,37.554000000000002,50.072000000000003,94.977052210975756,97.194100192003802,97.715813731459207,97.83176636038047,97.579339858053501,97.290231385965427,97.510917375560851,96.461798895561259,97.750782823830761,98.13005082647274,98.217536428930913,98.075696105718862,97.864463445029159,98.020641954548665,97.214025618024976,97.858978751253218,98.0247513670773,97.786820902736025,98.184619531557445,97.862828393640228,98.01070228731497,"2017-09-01","2019-02-15"]
["SMA America","STP 62-US-41 [480V]","N","Y","Y","Y","Y","Y*","Y","62.5 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter",62.5,480,97.5,"UL","[11/08/2018]","[01.09.03.R]","2018-12-17","[11/08/2018]","2020-01-13","UL","2019-12-16","2020-01-13",null,"N","N",5.43,null,null,500,725,800,6.25,12.5,18.75,31.25,46.875,62.5,96.186000000000007,97.248999999999995,97.41,97.376000000000005,97.170999999999992,96.537999999999997,97.175579999999997,96.698999999999998,97.649999999999991,97.804000000000002,97.787999999999982,97.419999999999987,97.048000000000002,97.507419999999996,97.37700000000001,98.172000000000011,98.225000000000009,98.063000000000002,97.819000000000017,97.456999999999994,97.900830000000013,"2018-12-17","2020-01-13"]
["SMA America","SHP 125-US-20 [480V]","N","Y","Y","Y","Y","Y*","Y","Sunny Highpower PEAK3, 125 kW, 1500 VDC, 480 VAC, 3-phase, transformerless, Grid Support Utility Interactive Inverter",125,480,98.5,"UL","[04/04/2019]","[V02.02.29.R]","2019-07-01","[04/04/2019]","2020-02-03","UL","2019-12-16","2020-02-03",null,"N","N",5.37,null,null,705,830,1200,12.500700000000002,25.001400000000004,37.502099999999999,62.503500000000003,93.755250000000004,125.00700000000001,98.755599999999987,98.997600000000006,98.883799999999994,98.82759999999999,98.606200000000015,98.284400000000005,98.695462000000006,98.440199999999976,98.823599999999985,98.695200000000014,98.627400000000009,98.404799999999994,98.053799999999995,98.491199999999992,97.470200000000006,98.042400000000001,98.234999999999999,98.284199999999984,98.147599999999983,97.811599999999999,98.137617999999989,"2019-07-01","2020-02-03"]
["SMA America","SHP 150-US-20 [600V]","N","Y","Y","Y","Y","Y*","Y","Sunny Highpower PEAK3, 150 kW, 1500 VDC, 600 VAC, 3-phase, transformerless, Grid Support Utility Interactive Inverter",150,600,99,"UL","[04/04/2019]","[V02.02.29.R]","2019-07-01","[04/04/2019]","2020-02-03","UL","2019-12-16","2020-02-03",null,"N","N",6.63,null,null,880,960,1200,15.007867000000003,30.015734000000005,45.023601000000006,75.039335000000008,112.55900250000002,150.07867000000002,98.7136,99.051999999999992,98.978999999999999,98.954999999999998,98.81519999999999,98.582000000000008,98.860330000000005,98.722000000000008,99.032200000000003,99.016199999999998,98.96220000000001,98.761799999999994,98.523200000000003,98.834410000000005,98.083799999999997,98.629400000000004,98.703999999999994,98.705600000000004,98.5702,98.319400000000002,98.585654000000005,"2019-07-01","2020-02-03"]
["SMA America","SC-1850-US [385V]","N","Y","Y","N","N","N","N","Sunny Central 1850 kW, 385 Vac Grid Support Utility Interactive Inverter",1661,385,97,"UL","[10/16/2017]","[04.00.25.R]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted efficiency includes transformer efficiency of Eaton 34.5kV.","Y","N",294,null,null,570,665,950,166.1,332.2,498.3,830.5,1245.75,1661,96.09,97.54,97.81,97.789999999999992,97.59,97.25,97.58,95.5,97.22,97.55,97.61999999999999,97.45,97.13000000000001,97.39,93.24,96.22,96.740000000000009,97.070000000000007,96.98,96.67,96.77,"2018-04-16","2019-02-15"]
["SMA America","SC-2200-US [385V]","N","Y","Y","N","N","N","N","Sunny Central 2200 kW, 385 Vac Grid Support Utility Interactive Inverter",2079,385,97,"UL","[10/16/2017]","[04.00.25.R]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted efficiency includes transformer efficiency of Eaton 34.5kV.","Y","N",297,null,null,570,665,950,207.9,415.8,623.70000000000005,1039.5,1559.25,2079,96.63000000000001,97.68,97.8,97.69,97.330000000000013,96.679999999999993,97.42,96.07,97.38,97.58,97.53,97.21,96.57,97.25,94.45,96.53,96.960000000000008,97.05,96.73,96.179999999999993,96.69,"2018-04-16","2019-02-15"]
["SMA America","SC 2500-EV-US [550V]","N","Y","Y","N","N","N","N","Sunny Central 2500 kW, 550 Vac Grid Support Utility Interactive Inverter",2353.87,550,97,"UL","[08/30/2017]","[04.00.25.R]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted efficiency includes transformer efficiency of Eaton 34.5 kV.","Y","N",370,null,null,850,994,1425,235.39,470.77,706.16,1176.94,1765.4,2353.87,96.42,97.63,97.83,97.79,97.42,96.82,97.49,95.86,97.35,97.63,97.65,97.28,96.74,97.32,94.25,96.58,97.07,97.2,96.81,96.42,96.79,"2018-05-01","2019-02-15"]
["SMA America","SC 2750-EV-US [600V]","N","Y","Y","N","N","N","N","Sunny Central 2750 kW, 600Vac, multi-mode, 3-phase Grid Support Utility Interactive Inverter",2600,600,97.5,"UL","[08/30/2017]","[04.00.25.R]","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted efficiency includes transformer efficiency of Eaton 34.5kV.","Y","N",379.32,null,null,875,957,1200,260,520,780,1300,1950,2600,95.654267999999988,97.278513000000018,97.676036400000015,97.833769199999992,97.64240199999999,97.218773599999977,97.567724010000006,95.393141999999983,97.142182800000029,97.56110360000001,97.745445599999996,97.548142999999982,97.071069899999983,97.460780112999998,94.470888000000031,96.735168000000002,97.058768000000001,97.489406399999993,97.359624999999994,96.888670700000006,97.180456208999999,"2018-08-15","2019-02-15"]
["SMA America","SC 4000 UP-US 600V 3850A [600V]","Y","Y","Y","Y","N","N","N","4000 kVA, 600 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter   ",3650.134,600,98.5,"UL","[09/06/2019]","[06.00.33.R]","2020-04-21","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",453.5,null,null,880,970,1200,365.01340000000005,730.02680000000009,1095.0401999999999,1825.067,2737.6005,3650.134,98.280699999999996,98.700099999999992,98.720499999999987,98.624899999999997,98.491099999999989,98.160600000000002,98.532235,98.052499999999995,98.589100000000002,98.62730000000002,98.555199999999985,98.395299999999992,98.022900000000007,98.434076999999988,97.322699999999998,98.2881,98.412900000000008,98.417600000000007,98.220200000000006,97.843699999999984,98.233447999999996,"2020-04-21"]
["SMA America","SC 4200 UP-US 630V 3850A [630V]","Y","Y","Y","Y","N","N","N","4200 kVA, 630 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter   ",3832.828,630,98.5,"UL","[09/06/2019]","[06.00.33.R]","2020-04-21","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",451.8,null,null,921,1001,1200,383.28280000000001,766.56560000000002,1149.8483999999999,1916.414,2874.6210000000001,3832.828,98.269400000000005,98.702100000000002,98.667400000000001,98.646600000000007,98.528700000000015,98.211899999999986,98.552561000000026,97.990299999999991,98.599700000000013,98.662200000000013,98.593899999999991,98.454599999999985,98.08720000000001,98.479077999999987,97.503999999999991,98.365799999999993,98.394700000000014,98.400899999999993,98.308099999999996,97.951899999999995,98.290890999999988,"2020-04-21"]
["SMA America","SC 4400 UP-US 660V 3850A [660V]","Y","Y","Y","Y","N","N","N","4400 kVA, 660 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter   ",4017.1129999999998,660,98.5,"UL","[09/06/2019]","[06.00.33.R]","2020-04-21","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",465.17,null,null,962,1032,1200,401.71129999999999,803.42259999999999,1205.1338999999998,2008.5564999999999,3012.83475,4017.1129999999998,98.287000000000006,98.733699999999999,98.710499999999996,98.707799999999992,98.6023,98.295000000000002,98.61603199999999,98.103800000000007,98.637100000000004,98.629199999999997,98.640600000000006,98.502400000000009,98.149000000000001,98.519759000000008,97.598199999999991,98.44959999999999,98.588400000000007,98.487300000000005,98.388600000000011,98.04010000000001,98.387312000000009,"2020-04-21"]
["SMA America","SC 4600 UP-US 690V 3850A [690V]","Y","Y","Y","Y","N","N","N","4600 kVA, 690 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter   ",4198.2349999999997,690,98.5,"UL","[09/06/2019]","[06.00.33.R]","2020-04-21","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",471.07,null,null,1003,1062,1200,419.82349999999997,839.64699999999993,1259.4704999999999,2099.1174999999998,3148.6762499999995,4198.2349999999997,98.272799999999989,98.742100000000008,98.724299999999985,98.735199999999992,98.647099999999995,98.347699999999989,98.649672999999993,98.149900000000017,98.674700000000001,98.686299999999989,98.691100000000006,98.565300000000008,98.214699999999993,98.577562000000015,97.740700000000004,98.529799999999994,98.643999999999991,98.595500000000001,98.455099999999987,98.12639999999999,98.465975999999984,"2020-04-21"]
["SolarEdge Technologies Ltd.","SE3000H-US [240V]","Y","Y ","Y ","Y ","Y ","Y*","Y ","3.0 kW, 240 Vac HD-Wave technology hybrid Grid Support Utility Interactive Inverter",2.9620000000000002,240,99,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",0,null,null,360,395,480,0.3,0.6,0.9,1.6,2.1,2.8,95.67,98.01,98.63,99.01,99.19,99.19,98.89,95.39,97.88,98.54,98.96,99.16,99.16,98.83,95.93,98.04,98.57,99,99.08,99.17,98.83,"2017-07-01","2021-08-02"]
["SolarEdge Technologies Ltd.","SE3000x [240V]","N","Y","Y","Y","N","N","N","3 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US.",3.01,240,97.5,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",3.39,null,null,100,388,480,0.3,0.6,0.9,1.51,2.2599999999999998,3.01,95.1,97.1,97.5,97.8,97.8,97.7,97.6,94.8,96.8,97.4,97.7,97.7,97.6,97.5,93.4,96.4,97,97.4,97.5,97.5,97.2,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE3000x [208V]","N","Y","Y","Y","N","N","N","3 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US.",3.02,208,97.5,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",3.71,null,null,305,350,480,0.3,0.6,0.91,1.51,2.27,3.02,96,97.4,97.6,97.7,97.6,97.4,97.5,95.6,97.1,97.5,97.6,97.5,97.3,97.4,93.6,96.3,96.9,97.2,97.2,97.1,97,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE3300x [240V]","N","Y","Y","Y","N","N","N","3.3 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US.",3.2509999999999999,240,97.5,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.46,null,null,370,435,500,0.33,0.65,0.98,1.63,2.44,3.25,95.3,97.1,97.5,97.6,97.6,97.5,97.5,94.9,96.8,97.3,97.5,97.5,97.3,97.3,94.2,96.5,96.9,97.3,97.4,97.2,97.1,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE3800H-US [208V]","N","Y","Y","Y","Y","Y*","Y","3.3 kW, 208 Vac HD-Wave technology Grid Support Utility Interactive Inverter",3.2549999999999999,208,99,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"N","N",4.12,null,null,360,395,480,0.32550000000000001,0.65100000000000002,0.97649999999999992,1.6274999999999999,2.4412500000000001,3.2549999999999999,89.794951399999988,99.390665599999991,99.381222399999999,99.276854799999995,99.002583599999994,98.779119199999997,98.745542799999996,92.106059000000002,99.351759600000008,99.3770016,99.245419999999996,98.986043600000002,98.754181799999998,98.81892092999999,95.580213600000008,99.428654200000011,99.392419000000004,99.252379999999988,98.997597999999996,98.729736999999986,98.969945123999992,"2018-06-01","2020-01-21"]
["SolarEdge Technologies Ltd.","SE3300x [208V]","N","Y","Y","Y","N","N","N","3.3 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US.",3.2879999999999998,208,97,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.55,null,null,320,410,500,0.33,0.66,0.99,1.64,2.4700000000000002,3.29,95.5,97.2,97.3,97.4,97.2,97.4,97.2,94.8,96.7,97,97.2,97,96.8,96.9,93.5,96.3,96.6,96.9,96.9,96.8,96.7,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE3800H-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter",3.7469999999999999,240,99,"Intertek","[04/02/2020]","[2.0.820]","2018-10-15","[04/02/2020]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",0,null,null,360,395,480,0.3,0.8,1.2,2,2.8,3.6,96.56,98.4,98.82,99.18,99.19,99.2,99,96.34,98.3,98.75,99.14,99.16,99.12,98.95,96.72,98.57,98.82,99.07,99.17,99.08,98.97,"2017-07-01","2020-11-23"]
["SolarEdge Technologies Ltd.","SE3800A-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter",3.79,240,98,"Intertek","[6/7/2017]","[2.52.507]","2018-10-15","[6/7/2017]","2020-01-21","Intertek","2019-12-16","2020-01-21","Formerly SolarEdge Technologies Ltd. SE3800x [240V]","Y","N",2.2400000000000002,null,null,360,400,480,0.38,0.76,1.1399999999999999,1.9,2.84,3.79,96.1,97.6,98,98.1,98.1,98.2,98,95.7,97.3,97.8,98.1,98,98.2,97.9,94.6,96.8,97.5,97.9,97.9,97.8,97.6,"2017-07-01","2020-01-21"]
["SolarEdge Technologies Ltd.","SE3800A-US [208V]","N","Y","Y","Y","N","N","N","3.8 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter",3.99,208,97,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Formerly SolarEdge Technologies Ltd. SE3800x [208V]","Y","N",5.0999999999999996,null,null,320,410,500,0.4,0.8,1.2,2,2.99,3.99,95.5,97.2,97.3,97.3,97.4,97.1,97.3,94.8,96.7,97.1,97.2,96.8,97,96.9,93.5,96.3,96.8,96.9,96.8,96.4,96.6,"2017-07-01","2020-01-21"]
["SolarEdge Technologies Ltd.","SE5000H-US [208V]","N","Y","Y","Y","Y","Y*","Y","5 kW, 208 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter",4.9790000000000001,208,98.5,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",4.51,null,null,360,395,480,0.4,1,1.6,2.7,3.6,4.9000000000000004,96.58,98.34,98.72,98.82,98.82,98.91,98.7,96.34,98.22,98.64,98.76,98.77,98.64,98.62,95.89,97.99,98.46,98.68,98.7,98.57,98.51,"2017-07-01","2020-01-21"]
["SolarEdge Technologies Ltd.","SE5000x [208V]","N","Y","Y","Y","N","N","N","5 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US.",4.9800000000000004,208,97,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.46,null,null,320,410,500,0.5,1,1.49,2.4900000000000002,3.73,4.9800000000000004,96.6,97.3,97.4,97.2,97.1,96.6,97.1,95.9,97,97.2,97,97,96.6,97,96.2,96.6,96.9,96.9,96.4,96.5,96.5,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE5000x [240V]","N","Y","Y","Y","N","N","N","5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US.",4.99,240,98,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",2.2400000000000002,null,null,370,400,480,0.5,1,1.5,2.5,3.74,4.99,96.7,97.9,98.1,98.1,98.3,98.1,98.1,96.4,97.7,98,98,98.2,98,98,95.7,97.4,97.7,97.8,97.8,97.9,97.7,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE5000H-US [240V]","N","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter",5.0519999999999996,240,99,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",4.5199999999999996,null,null,360,395,480,0.4,1,1.6,2.7,3.6,4.9000000000000004,96.65,98.42,98.79,99,98.97,99.11,98.84,96.38,98.28,98.7,98.94,98.92,98.86,98.76,96.03,98.07,98.57,98.87,98.87,98.81,98.68,"2017-07-01","2020-01-21"]
["SolarEdge Technologies Ltd.","SE6000H-US [208V]","N","Y","Y","Y","Y","Y*","Y","5 kW, 208 Vac HD-Wave technology Grid Support Utility Interactive Inverter",5.0540000000000003,208,99,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"N","N",4.5199999999999996,null,null,360,395,480,0.50540000000000007,1.0108000000000001,1.5162,2.5270000000000001,3.7905000000000002,5.0540000000000003,96.654559199999994,98.420969200000002,98.787293800000015,99.000340600000001,98.967589000000004,99.110835400000013,98.840141549999998,96.37568619999999,98.283448399999997,98.700434599999994,98.938382000000004,98.920587600000005,98.860395799999992,98.761243457999996,96.028461199999995,98.068861199999986,98.565832799999995,98.868919599999998,98.870164399999993,98.805445199999994,98.67641395199999,"2018-06-01","2020-01-21"]
["SolarEdge Technologies Ltd.","SE6000x [208V]","N","Y","Y","Y","N","N","N","6 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US.",5.33,208,97,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.22,null,null,320,410,500,0.53,1.07,1.6,2.66,3.99,5.33,96.6,97.3,97.4,97.2,97.1,96.4,97.1,95.9,97,97.2,97,97,96.4,97,96.2,96.6,96.9,96.9,96.4,96.3,96.5,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE6000x [240V]","N","Y","Y","Y","N","N","N","6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US.",5.99,240,97.5,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",3.52,null,null,370,435,500,0.6,1.2,1.8,3,4.5,5.99,96.5,97.6,97.7,97.5,97.3,97,97.4,96,97.4,97.5,97.3,97.3,97,97.3,95.7,97.1,97.3,97.2,97.3,96.9,97.2,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE6000H-US [240V]","Y","Y ","Y ","Y ","Y ","Y*","Y ","6 kW, 240 Vac, 1-phase, HD-Wave technology hybrid Grid Support Utility Interactive Inverter",6.0460000000000003,240,99,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",4.5199999999999996,null,null,360,395,480,0.5,1.3,1.9,3,4.3,5.8,97.17,98.61,98.9,98.95,98.95,98.98,98.96,96.95,98.51,98.82,98.89,98.9,98.95,98.79,96.65,98.32,98.7,98.83,98.85,98.71,98.7,"2017-07-01","2021-08-02"]
["SolarEdge Technologies Ltd.","SE7600A-US [208V]","N","Y","Y","Y","N","N","N","7.6 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter",7.56,208,97.5,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.75,null,null,325,375,480,0.75600000000000001,1.512,2.2679999999999998,3.78,5.67,7.56,96.3,97.4,97.6,97.6,97.5,97.3,97.5,96,97.2,97.5,97.5,97.4,97.2,97.3,95.2,96.8,97.1,97.2,97.1,96.8,97,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE7600H-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",7.6159999999999997,240,99,"Intertek","[04/02/2020]","[2.0.820]","2018-10-15","[04/02/2020]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",4.5199999999999996,null,null,360,395,480,0.7,1.6,2.4,3.6,5.5,7.3,97.72,98.8,98.97,98.97,99.04,98.73,98.94,97.52,98.7,98.91,98.93,99.02,98.69,98.89,97.24,98.57,98.83,98.87,98.75,98.71,98.71,"2017-07-01","2020-11-23"]
["SolarEdge Technologies Ltd.","SE7600A-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter",7.625,240,97.5,"Intertek","[6/7/2017]","[2.52.507]","2018-10-15","[6/7/2017]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",2.16,null,null,360,400,480,0.76249999999999996,1.5249999999999999,2.2879999999999998,3.8130000000000002,5.7190000000000003,7.625,97,97.9,98,97.9,97.7,97.3,97.7,96.6,97.8,97.9,97.9,97.6,97.3,97.7,95.7,97.4,97.6,97.6,97.5,97.1,97.5,"2017-07-01","2020-01-21"]
["SolarEdge Technologies Ltd.","SE9KUS [208V]","N","Y","Y","Y","Y","Y*","Y","9 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter",8.9629999999999992,208,96.5,"Intertek","[9/20/2017]","[2.19.1207]","2018-10-15","[9/20/2017]","2020-02-03","Intertek","2019-12-16","2020-02-03",null,"Y","N",3.08,null,null,384,424,504,0.9,1.79,2.69,4.4800000000000004,6.72,8.9600000000000009,95.2,96.5,96.8,96.6,96.3,96.1,96.4,94.9,96.3,96.7,96.5,96.3,96,96.3,94.3,96,96.4,96.4,96.1,95.8,96.1,"2017-07-01","2020-02-03"]
["SolarEdge Technologies Ltd.","SE10KUS [480V]","N","Y","Y","Y","N","N","N","10 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",9.85,480,98,"Intertek","[6/8/2017]","[2.19.759]","2018-10-15","[6/8/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",3.13,null,null,100,882,962,0.98,1.97,2.95,4.92,7.38,9.85,95.5,97.4,97.8,98.1,98.1,98,97.9,95.1,97.3,97.7,98,98,97.9,97.8,94.2,97,97.5,97.9,98,97.9,97.7,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE10000A-US [208V]","N","Y","Y","Y","N","N","N","10 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter",9.93,208,97,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.75,null,null,325,375,480,0.99299999999999999,1.986,2.9790000000000001,4.9649999999999999,7.4480000000000004,9.93,96.8,97.6,97.7,97.5,97.4,97.1,97.4,96.5,97.4,97.5,97.4,97.2,96.9,97.3,96.2,97,97.2,97.1,96.9,96.7,96.9,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE10000A-US [240V]","N","Y","Y","Y","N","N","N","10 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",9.94,240,97.5,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.95,null,null,360,400,480,0.99,1.99,2.98,4.97,7.46,9.94,96.8,97.6,97.8,97.8,97.7,97.5,97.7,96.6,97.5,97.7,97.6,97.6,97.4,97.6,96.4,97.3,97.5,97.4,97.4,97.2,97.3,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE10000H-US [240V]","N","Y","Y","Y","Y","Y*","Y","10 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter",9.9939999999999998,240,99,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"N","N",6,null,null,360,395,480,0.999,1.9990000000000001,2.9980000000000002,4.9969999999999999,7.4960000000000004,9.9939999999999998,97.86,98.83,98.94,99.23,98.95,98.63,98.94,97.69,98.74,98.88,99.18,98.91,98.55,98.89,97.44,98.54,98.68,98.7,98.62,98.1,98.57,"2018-04-02","2020-01-21"]
["SolarEdge Technologies Ltd.","SE11400H-US [208V]","N","Y","Y","Y","Y","Y*","Y","11.4 kW, 208 Vac, HD-Wave technology Grid Support Utility Interactive Inverter",10.000999999999999,208,98.5,"Intertek","[04/02/2020]","[2.0.820]","2020-06-22","[04/02/2020]","2020-06-22","Intertek","2019-12-16","2020-06-22",null,"N","N",5.71,null,null,360,395,480,1.0000564000000003,2.0001128000000006,3.0001692000000006,5.0002820000000012,7.5004230000000014,10.000564000000002,97.768239599999987,98.7284674,98.832207999999994,99.069845200000003,98.668149999999997,98.174745799999997,98.714542195999996,97.653916800000005,98.660750199999995,98.77102099999999,98.969542799999985,98.575444200000007,98.090773400000003,98.624844786000011,97.439042199999989,98.535696600000009,98.697926200000012,98.6959892,98.620025600000005,98.097229400000003,98.567730432000005,"2020-06-22"]
["SolarEdge Technologies Ltd.","SE11400A-US [240V]","N","Y","Y","Y","N","N","N","11.4 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",11.39,240,97.5,"Intertek","[6/7/2017]","[2.52.326]","2018-10-15","[6/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",5.95,null,null,360,400,480,1.139,2.278,3.4169999999999998,5.6950000000000003,8.5429999999999993,11.39,96.9,97.7,97.8,97.8,97.6,97.4,97.7,96.8,97.6,97.7,97.6,97.5,97.3,97.5,96.5,97.4,97.5,97.5,97.3,97.1,97.3,"2017-07-01","2018-10-15"]
["SolarEdge Technologies Ltd.","SE11400H-US [240V]","N","Y","Y","Y","Y","Y*","Y","11.4 kW, 240 Vac, HD-Wave technology Grid Support Utility Interactive Inverter",11.393000000000001,240,99,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"N","N",6,null,null,360,395,480,1.139,2.2789999999999999,3.4180000000000001,5.6970000000000001,8.5449999999999999,11.393000000000001,97.88,98.84,98.95,99.16,98.82,98.41,98.85,97.91,98.83,98.93,99.17,98.83,98.4,98.85,97.42,98.63,98.79,98.82,98.8,98.39,98.72,"2018-04-02","2020-01-21"]
["SolarEdge Technologies Ltd.","SE14.4KUS [208V]","N","Y","Y","Y","Y","Y*","Y","14.4 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter",14.51,208,97,"Intertek","[9/20/2017]","[2.19.1207]","2018-10-15","[9/20/2017]","2020-02-03","Intertek","2019-12-16","2020-02-03",null,"Y","N",4.16,null,null,400,460,600,1.45,2.9,4.3499999999999996,7.26,10.88,14.51,95.9,97.3,97.5,97.5,97,96.6,97.1,95.2,97.1,97.2,97.3,97.2,96.8,97.1,94.7,96.3,96.7,96.9,96.4,96.2,96.4,"2017-07-01","2020-02-03"]
["SolarEdge Technologies Ltd.","SE43.2KUS [208V]","N","Y","Y","Y","Y","Y*","Y","43.2 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of three SE14.4KUS installed together rated max output power = 43.2kW)",14.51,208,97,"Intertek","[11/2/2017]","[2.19.1207]","2018-10-15","[11/2/2017]","2020-02-03","Intertek","2019-12-16","2020-02-03","Performance data is the same as SE14.4KUS.","Y","N",4.16,null,null,400,460,600,1.4510000000000001,2.9020000000000001,4.3529999999999998,7.2549999999999999,10.8825,14.51,95.892661799999999,97.278178400000002,97.483730999999992,97.461980600000004,97.009345999999994,96.643356999999995,97.111800267999996,95.225235800000007,97.08651660000001,97.192224999999993,97.304581999999996,97.196262000000004,96.801864999999992,97.114476592000003,94.66687300000001,96.286802999999992,96.672386199999991,96.856588399999993,96.388889000000006,96.175926200000006,96.436492458000004,"2018-02-01","2020-02-03"]
["SolarEdge Technologies Ltd.","SE17.3KUS [208V]","N","Y","Y","Y","Y","Y*","Y","17.3 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter",16.564,208,97,"Intertek","[07/07/2020]","[2.20.223]","2020-08-11","[07/07/2020]","2020-08-11","Intertek","2020-06-22","2020-08-11",null,"N","N",5.28,null,null,400,460,600,1.6563751519999999,3.3127503039999997,4.9691254559999987,8.2818757599999984,12.422813639999998,16.563751519999997,96.253999999999991,97.275999999999996,97.531999999999996,97.31,96.986000000000004,96.694000000000003,97.090180000000004,95.77,97.01,97.10799999999999,97.13,96.79,96.474000000000004,96.853960000000001,94.76,96.44,96.655999999999992,96.86,96.53,96.138000000000005,96.519520000000014,"2020-08-11"]
["SolarEdge Technologies Ltd.","SE20KUS [480V]","N","Y","Y","Y","Y","Y*","Y","20 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",20.05,480,98,"Intertek","[9/20/2017]","[2.19.1207]","2018-10-15","[9/20/2017]","2020-02-03","Intertek","2019-12-16","2020-02-03",null,"Y","N",3.48,null,null,842,882,962,2.0099999999999998,4.01,6.02,10.029999999999999,15.04,20.05,96.6,97.6,97.9,98,98,97.9,97.9,96.6,97.5,97.9,98,98,97.9,97.9,96,97.3,97.7,97.9,97.8,97.8,97.7,"2017-07-01","2020-02-03"]
["SolarEdge Technologies Ltd.","SE30KUS [480V]","N","Y","Y","Y","Y","Y*","Y","30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",30.158999999999999,480,98.5,"Intertek","[9/20/2017]","[2.19.1207]","2018-10-15","[9/20/2017]","2020-02-03","Intertek","2019-12-16","2020-02-03",null,"N","N",7.06,null,null,790,850,950,3,6,9,15,22.5,30,97.408512599999995,98.364666800000009,98.550598599999987,98.507541000000003,98.480424199999987,98.385566000000011,98.441132412000002,97.079442999999998,98.204926200000003,98.428963600000003,98.419413799999987,98.402914199999998,98.314027999999993,98.342222486000011,96.416390800000002,97.900681600000013,98.208887799999985,98.295271,98.262175800000009,98.199991199999999,98.167715892000004,"2018-01-02","2020-02-03"]
["SolarEdge Technologies Ltd.","SE100KUS [480V]","N","Y","Y","Y","Y","Y*","Y","100 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of three SE33.3KUS installed together rated max output power = 100kW).",33.299999999999997,480,98.5,"Intertek","[11/2/2017]","[2.19.1207]","2018-10-15","[11/2/2017]","2020-02-03","Intertek","2019-12-16","2020-02-03","Performance data is the same as SE33.3KUS.","Y","N",5.05,null,null,790,850,950,3.34,6.68,10.02,16.7,25.049999999999997,33.4,97.189196467488244,98.242947891445439,98.888888761904767,98.509803882352941,98.67768595041322,98.461538461538467,98.575691196790416,96.664031410256399,98.084400284495032,98.113207547169807,98.505882352941171,98.370370370370367,98.159509202453989,98.274873226832014,96.33825541401275,97.84397143659011,97.84276716981131,98.470588235294116,98.312757201646093,98.159509202453989,98.179421155174268,"2018-02-01","2020-02-03"]
["SolarEdge Technologies Ltd.","SE33.3KUS [480V]","N","Y","Y","Y","Y","Y*","Y","33.3 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",33.299999999999997,480,98.5,"Intertek","[9/20/2017]","[2.19.1207]","2018-10-15","[9/20/2017]","2020-02-03","Intertek","2019-12-16","2020-02-03",null,"Y","N",5.05,null,null,790,850,950,3.34,6.68,10.02,16.7,25.05,33.4,97.2,98.2,98.9,98.5,98.7,98.5,98.6,96.7,98.1,98.1,98.5,98.4,98.2,98.3,96.3,97.8,97.8,98.5,98.3,98.2,98.2,"2017-07-01","2020-02-03"]
["SolarEdge Technologies Ltd.","SE66.6KUS [480V]","N","Y","Y","Y","Y","Y*","Y","66.6 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of two SE33.3KUS installed together rated max output power = 66.6kW).",33.299999999999997,480,98.5,"Intertek","[11/2/2017]","[2.19.1207]","2018-10-15","[11/2/2017]","2020-02-03","Intertek","2019-12-16","2020-02-03","Performance data is the same as SE33.3KUS.","Y","N",5.05,null,null,790,850,950,3.34,6.68,10.02,16.7,25.049999999999997,33.4,97.189196467488244,98.242947891445439,98.888888761904767,98.509803882352941,98.67768595041322,98.461538461538467,98.575691196790416,96.664031410256399,98.084400284495032,98.113207547169807,98.505882352941171,98.370370370370367,98.159509202453989,98.274873226832014,96.33825541401275,97.84397143659011,97.84276716981131,98.470588235294116,98.312757201646093,98.159509202453989,98.179421155174268,"2018-02-01","2020-02-03"]
["SolarEdge Technologies Ltd.","SE120KUS [480V]","N","Y ","Y ","Y ","Y ","Y*","Y","120 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of three SE40KUS installed together rated max output power = 120kW).",40.252000000000002,480,98.5,"Intertek","[06/28/2021]","[2.19.1207]","2021-07-01","[06/28/2021]","2021-07-01","Intertek","2021-05-17","2021-07-01",null,"N","N",7.43,null,null,790,850,950,4.0252223332999995,8.0504446665999989,12.075666999899999,20.126111666499998,30.189167499749999,40.252223332999996,97.42,98.37,98.695999999999998,98.6,98.41,98.325999999999993,98.438420000000008,97.096000000000004,98.21,98.58,98.5,98.31,98.171999999999997,98.321840000000009,96.51,97.948000000000008,98.39,98.35,98.161999999999992,97.994,98.143659999999983,"2021-07-01"]
["SolarEdge Technologies Ltd.","SE40KUS [480V]","N","Y","Y","Y","Y","Y*","Y","40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter",40.252000000000002,480,98.5,"Intertek","[07/07/2020]","[2.20.223]","2020-08-11","[07/07/2020]","2020-08-11","Intertek","2020-06-22","2020-08-11",null,"N","N",7.43,null,null,790,850,950,4.0252223332999995,8.0504446665999989,12.075666999899999,20.126111666499998,30.189167499749999,40.252223332999996,97.42,98.37,98.695999999999998,98.6,98.41,98.325999999999993,98.438420000000008,97.096000000000004,98.21,98.58,98.5,98.31,98.171999999999997,98.321840000000009,96.51,97.948000000000008,98.39,98.35,98.161999999999992,97.994,98.143659999999983,"2020-08-11"]
["SolarEdge Technologies Ltd.","SE80KUS [480V]","N","Y ","Y ","Y ","Y ","Y*","Y","80 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of two SE40KUS installed together rated max output power = 80kW).",40.252000000000002,480,98.5,"Intertek","[06/28/2021]","[2.19.1207]","2021-07-01","[06/28/2021]","2021-07-01","Intertek","2021-05-17","2021-07-01",null,"N","N",7.43,null,null,790,850,950,4.0252223332999995,8.0504446665999989,12.075666999899999,20.126111666499998,30.189167499749999,40.252223332999996,97.42,98.37,98.695999999999998,98.6,98.41,98.325999999999993,98.438420000000008,97.096000000000004,98.21,98.58,98.5,98.31,98.171999999999997,98.321840000000009,96.51,97.948000000000008,98.39,98.35,98.161999999999992,97.994,98.143659999999983,"2021-07-01"]
["Solaria Corporation","Solaria PowerXT-345R-AC [240V]","N","Y","Y","Y","N","N","N","345 W Monocrystalline ACPV Module. DC Module:  Solaria PowerXT-345R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V].",0.28999999999999998,240,97,"TUV Rheinland of North America","[05/03/2018]","[V02.10.00];[V02.12.00];[V02.14.02]","2018-10-15","[05/03/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,36,45,0.03,0.06,0.09,0.15,0.22,0.28999999999999998,95,96.2,97.1,97.4,97.2,96.6,97.1,94.2,95.6,96.8,97.5,97.4,97.2,97.1,93.3,94.8,96.4,97.3,97.3,97.1,96.9,"2018-06-01","2019-05-01"]
["Solaria Corporation","Solaria PowerXT-350R-AC [240V]","N","Y","Y","Y","N","N","N","350 W Monocrystalline ACPV Module. DC Module:  Solaria PowerXT-350R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V].",0.28999999999999998,240,97,"TUV Rheinland of North America","[05/03/2018]","[V02.10.00];[V02.12.00];[V02.14.02]","2018-10-15","[05/03/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,36,45,0.03,0.06,0.09,0.15,0.22,0.28999999999999998,95,96.2,97.1,97.4,97.2,96.6,97.1,94.2,95.6,96.8,97.5,97.4,97.2,97.1,93.3,94.8,96.4,97.3,97.3,97.1,96.9,"2018-06-01","2019-05-01"]
["Solaria Corporation","Solaria PowerXT-355R-AC [240V]","N","Y","Y","Y","N","N","N","355 W Monocrystalline ACPV Module. DC Module:  Solaria PowerXT-355R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V].",0.28999999999999998,240,97,"TUV Rheinland of North America","[05/03/2018]","[V02.10.00];[V02.12.00];[V02.14.02]","2018-10-15","[05/03/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,36,45,0.03,0.06,0.09,0.15,0.22,0.28999999999999998,95,96.2,97.1,97.4,97.2,96.6,97.1,94.2,95.6,96.8,97.5,97.4,97.2,97.1,93.3,94.8,96.4,97.3,97.3,97.1,96.9,"2018-06-01","2019-05-01"]
["Solaria Corporation","Solaria PowerXT-360R-AC [240V]","N","Y","Y","Y","N","N","N","360 W Monocrystalline ACPV Module. DC Module:  Solaria PowerXT-360R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V] [SI1].",0.28999999999999998,240,97,"TUV Rheinland of North America","[05/03/2018]","[V02.10.00];[V02.12.00];[V02.14.02]","2018-10-15","[05/03/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,36,45,0.03,0.06,0.09,0.15,0.22,0.28999999999999998,95,96.2,97.1,97.4,97.2,96.6,97.1,94.2,95.6,96.8,97.5,97.4,97.2,97.1,93.3,94.8,96.4,97.3,97.3,97.1,96.9,"2018-06-01","2019-05-01"]
["Solaria Corporation","Solaria PowerXT-365R-AC [240V]","N","Y","Y","Y","N","N","N","365 W Monocrystalline ACPV Module. DC Module:  Solaria PowerXT-365R-PD. Microinverter IQ7PLUS-72-x-ACM-US [240V].",0.28999999999999998,240,97,"TUV Rheinland of North America","[05/03/2018]","[V02.10.00];[V02.12.00];[V02.14.02]","2019-05-01","[05/03/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.5000000000000001E-2,null,null,27,36,45,2.8999999999999998E-2,5.7999999999999996E-2,8.6999999999999994E-2,0.14499999999999999,0.21749999999999997,0.28999999999999998,95.003640000000004,96.245670000000004,97.147700000000015,97.42907000000001,97.164060000000006,96.603870000000001,97.057403100000016,94.161959999999993,95.57517,96.780239999999992,97.495289999999983,97.442819999999998,97.156899999999993,97.135416199999995,93.321410000000014,94.805890000000005,96.394019999999983,97.27315999999999,97.309510000000003,97.07574000000001,96.8956242,"2019-05-01"]
["Solaria Corporation","Solaria PowerXT-395R-PM-AC [240V]","N","Y","Y","Y","Y","Y*","Y","395 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Solaria PowerXT-395R-PM. Microinverter: IQ7A-72-2-US [240V] ",0.34869800000000001,240,97,"UL","[04/23/2020]","[V04.18.02]","2020-06-01","[04/23/2020]","2020-06-01","UL","2020-03-18","2020-06-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-06-01"]
["Solaria Corporation","Solaria PowerXT-400R-PM-AC [240V]","N","Y","Y","Y","Y","Y*","Y","400 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Solaria PowerXT-400R-PM. Microinverter: IQ7A-72-2-US [240V] ",0.34869800000000001,240,97,"UL","[04/23/2020]","[V04.18.02]","2020-06-01","[04/23/2020]","2020-06-01","UL","2020-03-18","2020-06-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-06-01"]
["Solaria Corporation","Solaria PowerXT-410R-PM-AC [240V]","N","Y","Y","Y","Y","Y*","Y","410 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Solaria PowerXT-410R-PM. Microinverter: IQ7A-72-2-US [240V] ",0.34869800000000001,240,97,"UL","[04/23/2020]","[V04.18.02]","2020-06-01","[04/23/2020]","2020-06-01","UL","2020-03-18","2020-06-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-06-01"]
["Solaria Corporation","Solaria PowerXT-420R-PM-AC [240V]","N","Y","Y","Y","Y","Y*","Y","420 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Solaria PowerXT-420R-PM. Microinverter: IQ7A-72-2-US [240V] ",0.34869800000000001,240,97,"UL","[04/23/2020]","[V04.18.02]","2020-06-01","[04/23/2020]","2020-06-01","UL","2020-03-18","2020-06-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-06-01"]
["SolarJuice American Inc.","S4A-H60 [240V]","Y","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",5.57,240,94,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",25,null,null,240,335,425,0.57500000000000007,1.1500000000000001,1.7249999999999999,2.875,4.3125,5.75,86.869682822533804,91.494323337741122,93.197507125817154,94.277347956539373,94.528577104512152,94.419480087783,93.852567275540324,86.534692544508331,91.719237390678572,93.532641876704261,94.760758659216464,95.116012615226765,95.142514472111017,94.339638324629973,85.944083659918661,91.055826867889806,93.119565276460762,94.55685225894733,95.055933937626449,95.188812247401856,94.160927096657588,"2021-07-12"]
["SolarJuice American Inc.","S4A-H70 [240V]","Y","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",6.6660000000000004,240,94.5,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",25,null,null,290,360,425,0.66660000000000008,1.3332000000000002,1.9998,3.3330000000000002,4.9995000000000003,6.6660000000000004,88.19254532766071,92.480024599906656,93.864222646892841,94.728177374748682,94.859277550957373,94.661603922022621,94.31682430753466,87.895016741997523,92.552209013216427,93.98568096527471,94.939255036123782,95.145985429310571,95.084346217536066,94.540525982171076,87.188290385772305,91.840278359010497,93.665346252959509,94.812415113107377,95.188151694943144,95.183576013873704,94.438893456502669,"2021-07-12"]
["SolarJuice American Inc.","S4A-H76 [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",7.6420000000000003,240,95.5,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",44,null,null,304,402,500,0.76415320000000009,1.5283064000000002,2.2924595999999999,3.8207660000000003,5.7311490000000003,7.6415320000000007,91.707418177902383,94.572943893510569,95.343208396678733,95.732834528334209,95.650063634275952,95.385614239539109,95.40583861848647,90.557349146015056,94.483695582739486,95.237254457268747,95.752187855671906,95.755162516040727,95.573013398331213,95.411795532959076,93.454639453611506,95.564299299611108,96.165924657149233,96.488739138122966,96.365110394539414,96.144925249431296,96.199701492566206,"2021-07-12"]
["SolarJuice American Inc.","S4A-H86 [240V]","Y","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",8.6039999999999992,240,96,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",40,null,null,258,379,500,0.8604440000000001,1.7208880000000002,2.5813320000000002,4.3022200000000002,6.4533300000000002,8.6044400000000003,92.699334355597514,94.539928618718363,95.297824749048559,95.613611296666747,95.424147601271741,94.940413722572345,95.271386062148309,92.844051102514101,95.289415785898782,95.970144903059008,96.182450712551415,95.871598553910871,95.529337174346537,95.781378963688468,93.694083911121623,95.776806518196878,96.274499321609412,96.519408732377741,96.296844266964186,95.892164355116009,96.19055511399398,"2021-07-12"]
["Sol-Ark","Sol-Ark-8k-48-ST [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","8 KW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality",7.8390000000000004,208,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-08-01","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.78392807600000003,1.5678561520000001,2.3517842279999996,3.9196403799999997,5.8794605699999991,7.8392807599999994,91.486264550039337,94.760248969262392,95.352663162123591,97.296267712149941,97.185123619139432,96.859870192303077,96.623107857230082,91.699965357816623,94.963850615122325,95.495711668085661,97.428829723597843,97.231635305996946,96.929680695919046,96.714981534168942,91.907256517136105,94.928995056460167,95.369819427808693,97.318654328391062,96.925617369279323,97.063119550059341,96.527768937028625,"2019-08-01","2021-07-12"]
["Sol-Ark","Sol-Ark-8k-48-ST [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","8 KW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality",7.976,240,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-08-01","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.79761655200000003,1.5952331040000001,2.3928496559999997,3.9880827599999997,5.9821241399999998,7.9761655199999995,91.819615795312856,94.910997776364283,95.520513772204296,97.079550873826477,96.988012087484861,97.130498991107089,96.527673212721126,91.670908997205146,95.000841359179049,95.707732171504404,97.546548492774008,97.445862228404309,97.08346102095264,96.887061504012152,91.551333333333318,95.071706716631525,95.858438563503356,97.600636400067273,97.273962762904389,97.086789328574284,96.824324671567467,"2019-08-01","2021-07-12"]
["Sol-Ark","Sol-Ark-12K-P [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","9 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality",8.8179999999999996,208,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-12-23","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.88180885940000009,1.7636177188000002,2.6454265781999999,4.4090442970000003,6.6135664455000001,8.8180885940000007,91.466335419848761,94.733829955347005,95.331023522356261,97.277883440309353,97.171192835821699,96.824261660440328,96.60536854571653,91.67953424672848,94.934963045425178,95.479041347900221,97.405444606925556,97.215616325861205,96.903746610114041,96.696021834554926,91.88088933294037,94.895522896509419,95.314066949266319,97.244283347858328,96.88071561768912,97.009765877392653,96.476266826350155,"2019-12-23","2021-07-12"]
["Sol-Ark","Sol-Ark-9k-48-ST [208V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter    ",8.8179999999999996,208,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-12-23","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.88180885940000009,1.7636177188000002,2.6454265781999999,4.4090442970000003,6.6135664455000001,8.8180885940000007,91.466335419848761,94.733829955347005,95.331023522356261,97.277883440309353,97.171192835821699,96.824261660440328,96.60536854571653,91.67953424672848,94.934963045425178,95.479041347900221,97.405444606925556,97.215616325861205,96.903746610114041,96.696021834554926,91.88088933294037,94.895522896509419,95.314066949266319,97.244283347858328,96.88071561768912,97.009765877392653,96.476266826350155,"2019-12-23","2020-07-21"]
["Sol-Ark","Sol-Ark-12K-P [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","9 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality",8.9819999999999993,240,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-12-23","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.89821683780000017,1.7964336756000003,2.6946505134000001,4.4910841890000004,6.7366262835000006,8.9821683780000008,91.817370955953706,94.888333470547522,95.567760080849254,97.132142929471669,96.971545040244834,97.124294697876351,96.534126342880057,91.636458971417213,94.970390519246919,95.669651822789049,97.515106010634426,97.412239578354487,97.052223139745195,96.853606499302103,91.551333333333318,95.04856690772759,95.824316992250942,97.559470524973804,97.225099944122846,97.049443787713827,96.78266368780514,"2019-12-23","2021-07-12"]
["Sol-Ark","Sol-Ark-9k-48-ST [240V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter    ",8.9819999999999993,240,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-12-23","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.89821683780000017,1.7964336756000003,2.6946505134000001,4.4910841890000004,6.7366262835000006,8.9821683780000008,91.817370955953706,94.888333470547522,95.567760080849254,97.132142929471669,96.971545040244834,97.124294697876351,96.534126342880057,91.636458971417213,94.970390519246919,95.669651822789049,97.515106010634426,97.412239578354487,97.052223139745195,96.853606499302103,91.551333333333318,95.04856690772759,95.824316992250942,97.559470524973804,97.225099944122846,97.049443787713827,96.78266368780514,"2019-12-23","2020-07-21"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Hybrid-6.0-US [240V]","Y","Y","Y","Y","Y","Y*","Y","6.0 kW, 240 Vac Transformerless Hybrid Grid Support Utility Interactive Inverter with PV arc detector",5.57,240,94,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2020-11-23","[10/21/2020]","2020-11-23","Intertek","2020-09-11","2020-11-23",null,"N","N",25,null,null,240,335,425,0.57500000000000007,1.1500000000000001,1.7249999999999999,2.875,4.3125,5.75,86.869682822533804,91.494323337741122,93.197507125817154,94.277347956539373,94.528577104512152,94.419480087783,93.852567275540324,86.534692544508331,91.719237390678572,93.532641876704261,94.760758659216464,95.116012615226765,95.142514472111017,94.339638324629973,85.944083659918661,91.055826867889806,93.119565276460762,94.55685225894733,95.055933937626449,95.188812247401856,94.160927096657588,"2020-11-23"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Hybrid-7.0-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.0 kW, 240 Vac Transformerless Hybrid Grid Support Utility Interactive Inverter with PV arc detector",6.6660000000000004,240,94.5,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2020-11-23","[10/21/2020]","2020-11-23","Intertek","2020-09-11","2020-11-23",null,"N","N",25,null,null,290,360,425,0.66660000000000008,1.3332000000000002,1.9998,3.3330000000000002,4.9995000000000003,6.6660000000000004,88.19254532766071,92.480024599906656,93.864222646892841,94.728177374748682,94.859277550957373,94.661603922022621,94.31682430753466,87.895016741997523,92.552209013216427,93.98568096527471,94.939255036123782,95.145985429310571,95.084346217536066,94.540525982171076,87.188290385772305,91.840278359010497,93.665346252959509,94.812415113107377,95.188151694943144,95.183576013873704,94.438893456502669,"2020-11-23"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Hybrid-7.6-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",7.6420000000000003,240,95.5,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2019-06-01","[10/21/2020]","2021-01-21","Intertek","2020-09-11","2021-01-21",null,"N","N",44,null,null,304,402,500,0.76415320000000009,1.5283064000000002,2.2924595999999999,3.8207660000000003,5.7311490000000003,7.6415320000000007,91.707418177902383,94.572943893510569,95.343208396678733,95.732834528334209,95.650063634275952,95.385614239539109,95.40583861848647,90.557349146015056,94.483695582739486,95.237254457268747,95.752187855671906,95.755162516040727,95.573013398331213,95.411795532959076,93.454639453611506,95.564299299611108,96.165924657149233,96.488739138122966,96.365110394539414,96.144925249431296,96.199701492566206,"2019-06-03","2021-01-21"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Hybrid-8.6-US [240V]","Y","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",8.6039999999999992,240,96,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2019-06-01","[10/21/2020]","2021-01-21","Intertek","2020-09-11","2021-01-21",null,"N","N",40,null,null,258,379,500,0.8604440000000001,1.7208880000000002,2.5813320000000002,4.3022200000000002,6.4533300000000002,8.6044400000000003,92.699334355597514,94.539928618718363,95.297824749048559,95.613611296666747,95.424147601271741,94.940413722572345,95.271386062148309,92.844051102514101,95.289415785898782,95.970144903059008,96.182450712551415,95.871598553910871,95.529337174346537,95.781378963688468,93.694083911121623,95.776806518196878,96.274499321609412,96.519408732377741,96.296844266964186,95.892164355116009,96.19055511399398,"2019-06-03","2021-01-21"]
["Sparq Systems","Q1200-4101 [240V]","N","Y","Y","Y","N","N","N","1200 W, 240 Vac, 60Hz Grid Support Utility Interactive Inverter",1.165,240,96.5,"Intertek","[06/29/2018]","[1.20.62]","2018-10-15","[06/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",0.04,null,null,28,29,31,0.12,0.24,0.36,0.6,0.89999999999999991,1.2,91.269300000000015,95.441199999999995,96.573599999999999,97.136399999999995,97.054799999999986,96.799900000000008,96.689346999999998,90.98299999999999,95.51400000000001,96.582300000000004,97.041900000000012,96.980500000000006,96.757300000000001,96.62122500000001,89.75,95.235099999999989,96.421300000000016,97.011700000000019,96.993900000000011,96.816299999999998,96.542350000000013,"2018-08-01","2018-10-15"]
["Sparq Systems","Q1200-4102 [240V]","N","Y","Y","Y","N","N","N","1200 W, 240 Vac, 60 Hz Grid Support Utility Interactive Inverter    ",1.2030000000000001,240,96.5,"Intertek","[10/31/2018]","[1.20.62]","2019-02-01","[10/31/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",0.04,null,null,36,37,38,0.12032000000000001,0.24064000000000002,0.36096,0.60160000000000002,0.90240000000000009,1.2032,88.21,94.580000000000013,96.049999999999983,97.188000000000017,97.440000000000012,97.345000000000027,96.703330000000008,87.276299999999992,94.771999999999991,96.190000000000012,97.210000000000008,97.36,97.235000000000014,96.649101999999999,87.138299999999987,95.036999999999992,96.348000000000013,97.160999999999973,97.327000000000012,97.225000000000009,96.647512000000006,"2019-02-01"]
["Sungrow Power Supply Co., Ltd.","SG36CX-US [480V]","N","Y","Y","Y","Y","Y*","Y","36 kVA, 480 Vac Grid Support Utility Interactive Inverter\n\n",36.045999999999999,480,98,"CSA Group","[09/30/2020]","[MDSP_AGATE-S_V11_V01_A]","2020-12-21","[09/30/2020]","2020-12-21","CSA Group","2020-09-15","2020-12-21",null,"N","N",3.7,null,null,550,710,850,3.6046319999999996,7.2092639999999992,10.813895999999998,18.023159999999997,27.034739999999996,36.046319999999994,96.11747142857142,97.205490476190477,97.533461904761907,97.747947619047608,97.742042857142877,97.506547619047623,97.61466790476193,97.173190476190484,98.279861904761901,98.525428571428577,98.596704761904761,98.521019047619049,98.245142857142852,98.457677380952376,96.40943333333334,97.738738095238091,98.065047619047618,98.255847619047614,98.229599999999991,98.15487142857144,98.114279523809515,"2020-12-21"]
["Sungrow Power Supply Co., Ltd.","SG60KU-M [480V]","N","Y","Y","Y","N","N","N","60 kW, 480 Vac transformerless Grid Support Utility Interactive Inverter",60,480,98.5,"CSA Group","[07/07/2017];[05/13/2019]","[DSP_SG60KU-M_V14_A];[DSP_SG60KU-M_V14_B]","2018-10-15","[05/13/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",0.88,null,null,550,700,850,6,12,18,30,45,60,97.8,98.2,98.2,98.4,98.4,98,98.3,97.8,98.6,98.8,98.9,98.7,98.5,98.7,97.5,98.6,98.5,98.8,98.5,98.4,98.5,"2017-11-15","2019-06-03"]
["Sungrow Power Supply Co., Ltd.","SG60CX-US [480V]","N","Y","Y","Y","Y","Y*","Y","60 kVA, 480 Vac Grid Support Utility Interactive Inverter",60.182000000000002,480,98,"CSA Group","[09/30/2020]","[MDSP_AGATE-S_V11_V01_A]","2020-12-21","[09/30/2020]","2020-12-21","CSA Group","2020-09-15","2020-12-21",null,"N","N",3.38,null,null,550,710,850,6.0181520000000006,12.036304000000001,18.054455999999998,30.09076,45.136139999999997,60.181519999999999,96.92018095238096,97.610871428571414,97.793199999999999,97.909485714285708,97.805871428571436,97.525809523809514,97.766929142857151,98.196128571428559,98.713709523809513,98.842790476190473,98.809938095238095,98.652257142857138,98.266533333333328,98.673775428571432,97.45259047619048,98.149104761904752,98.2802619047619,98.338480952380976,98.210423809523803,98.021209523809517,98.202856380952397,"2020-12-21"]
["Sungrow Power Supply Co., Ltd.","SG125HV [600V]","N","Y","Y","Y","N","N","N","125 kW, 600 Vac transformerless Grid Support Utility Interactive Inverter.",125,600,98.5,"CSA Group","[07/07/2017];[05/13/2019]","[DSP_SG125KHV_V11_A];[DSP_SG125KHV_V11_B]","2018-10-15","[05/13/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",5.59,null,null,860,945,1200,12.5,25,37.5,62.5,93.75,125,98.58616564175307,98.826538452883796,98.882920668787548,98.682111571152404,98.446188385118617,98.255485255906706,98.563221565419028,98.289599609219081,98.583945292274365,98.588970137552224,98.493674639210937,98.359556350960816,98.10571225553511,98.410979818509034,98.084763214122049,98.42607546143779,98.477766582060369,98.383879856604054,98.097144355565277,97.626852759517618,98.195470207796347,"2017-11-01","2019-06-03"]
["Sungrow Power Supply Co., Ltd.","SG250HX-US [800V]","Y","Y","Y","Y","Y","Y*","Y","250 kW, 800 Vac, 3-phase, Transformerless Grid Support Utility Interactive Battery and Solar Inverter",226.99700000000001,800,98.5,"CSA Group","[08/04/2020]","[MDSP_DIAMOND-S_V11_V01_A]","2020-09-21","[08/04/2020]","2021-02-22","CSA Group","2020-12-07","2021-02-22",null,"N","N",5.21,null,null,860,1080,1300,22.699720000000003,45.399440000000006,68.099159999999998,113.49860000000001,170.24790000000002,226.99720000000002,97.057745574954694,98.250621131215539,98.468961755451389,98.570823670838692,98.462127815632613,98.262002467504104,98.40901712674976,98.194991347702199,98.76272324549052,98.946095857679211,99.010097962841797,98.86901346612548,98.677924712757914,98.866061263985301,97.998276444662039,98.661181448293519,98.899728984680351,98.947823888300505,98.81777374729441,98.631959848062522,98.805018703375069,"2020-09-21","2021-02-22"]
["Sungrow Power Supply Co., Ltd.","SC1000KU [540V]","Y","Y","Y","N","N","N","N","1000 kW, 540 Vac Grid Support Utility Interactive Storage Inverter,  bi-directional for use with battery management system, intended to be used in conjunction with a 1000 KVA (min) rated isolation transformer",1001.306,540,96.5,"CSA Group","[09/19/2019]","[DSP_SC1000KU_V1_B_M]","2019-02-01","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 1 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",83.764600000000002,null,null,810,1005,1200,100.13060000000002,200.26120000000003,300.39179999999999,500.65300000000002,750.97950000000003,1001.306,94.9956293648696,96.814367115577753,97.243680299436662,97.315507163897323,97.02864130176718,96.663267169452439,97.004384919133727,94.281076304463951,96.34437633335655,96.904741277777674,97.04790286747415,96.801692495979225,96.438994201912251,96.72393715731387,93.689401171763706,95.927478731094439,96.5802450520018,96.832373527564641,96.597834177749448,96.188205595675555,96.474640224445039,"2019-02-01"]
["Sungrow Power Supply Co., Ltd.","SG2500U [550V]","N","Y","Y","N","N","N","N","2500kW, 550Vac Grid Support Utility Interactive Inverter connect to grid via a 2500kVA medium voltage transformer.",2500,550,98,"CSA Group","[5/16/2017]","[DSP_SG2500U_V11_V1_A, LCD_SG2500U_V1_A_M]   ","2018-10-15","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted"," Weighted Efficiency includes efficiency of ABB ZGSB-H-25/35.","N","N",651.36,null,null,800,900,1200,250,500,750,1250,1875,2500,98,98.6,98.8,98.8,98.6,98.4,97.9,97.8,98.5,98.6,98.6,98.5,98.3,97.7,97.4,98.2,98.4,98.5,98.3,98.2,97.7,"2018-02-01","2018-10-15"]
["SunPower","SPR-E19-320-BLK-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","320 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-E19-320-BLK. Microinverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2019-01-02","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","Y","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2020-01-02","2020-04-01"]
["SunPower","SPR-E19-320-BLK-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","320 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-E19-320-BLK. Microinverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2019-01-02","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","Y","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2020-01-02","2020-04-01"]
["SunPower","SPR-E19-320-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","320 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-E19-320. Micro-inverter:  IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2019-01-02","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2019-01-02","2020-04-01"]
["SunPower","SPR-E19-320-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","320 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-E19-320. Micro-inverter:  IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2019-01-02","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2019-01-02","2020-04-01"]
["SunPower","SPR-E20-325-BLK-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","325 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-E20-325-BLK. Microinverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2019-01-02","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","Y","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2020-01-02","2020-04-01"]
["SunPower","SPR-E20-325-BLK-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","325 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-E20-325-BLK. Microinverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2019-01-02","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","Y","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2020-01-02","2020-04-01"]
["SunPower","SPR-E20-327-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","327 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-E20-327. Micro-inverter:  IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2019-01-02","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2019-01-02","2020-04-01"]
["SunPower","SPR-E20-327-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","327 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-E20-327. Micro-inverter:  IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2019-01-02","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2019-01-02","2020-04-01"]
["SunPower","SPR-E20-335-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","335 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X21-335. Micro-inverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97.5,"UL","[06/18/2019]","[V04.14.05];[V04.18.02]","2019-08-15","[06/18/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2019-08-15","2020-04-01"]
["SunPower","SPR-E20-335-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","335 W, 240 Vac, Grid Support Utility Interactive,  monocrystalline ACPV Module, white backsheet. DC Module:  SPR-E20-335. Micro-inverter:  IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[06/18/2019]","[V04.14.05];[V04.18.02]","2019-08-15","[06/18/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to SunPower ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2019-08-15","2020-04-01"]
["SunPower","SPR-X20-327-BLK-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","327 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X20-327-BLK. Micro-inverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2018-11-15","2020-04-01"]
["SunPower","SPR-X20-327-BLK-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","327 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X20-327-BLK. Micro-inverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2018-11-15","2020-04-01"]
["SunPower","SPR-X20-327-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","327 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X20-327. Micro-inverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2018-11-15","2020-04-01"]
["SunPower","SPR-X20-327-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","327 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X20-327. Micro-inverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2018-11-15","2020-04-01"]
["SunPower","SPR-X21-335-BLK-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","335 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X21-335-BLK. Micro-inverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2018-11-15","2020-04-01"]
["SunPower","SPR-X21-335-BLK-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","335 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X21-335-BLK. Micro-inverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2018-11-15","2020-04-01"]
["SunPower","SPR-X21-335-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","335 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X21-335. Micro-inverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2018-11-15","2020-04-01"]
["SunPower","SPR-X21-335-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","335 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X21-335. Micro-inverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2018-11-15","2020-04-01"]
["SunPower","SPR-X21-345-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","345 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X21-345. Micro-inverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2018-11-15","2020-04-01"]
["SunPower","SPR-X21-345-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","345 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X21-345. Micro-inverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2018-11-15","2020-04-01"]
["SunPower","SPR-X21-350-BLK-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","350 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X21-350-BLK. Micro-inverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2018-11-15","2020-04-01"]
["SunPower","SPR-X21-350-BLK-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","350 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: SPR-X21-350-BLK. Micro-inverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2018-11-15","2020-04-01"]
["SunPower","SPR-X22-360-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","360 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X22-360. Micro-inverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2018-11-15","2020-04-01"]
["SunPower","SPR-X22-360-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","360 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X22-360. Micro-inverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2018-11-15","2020-04-01"]
["SunPower","SPR-X22-370-E-AC [208V]","N","Y","Y","Y","Y","Y*","Y","370 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X22-370. Micro-inverter: IQ7XS-96-x-ACM-US-y [208V].",0.315,208,97,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,90.483609999999999,96.662759999999992,97.099880000000013,97.635729999999995,97.524219999999985,97.103530000000006,97.150984399999999,95.414170000000013,96.465389999999999,96.900779999999997,97.542020000000008,97.461279999999988,97.049990000000008,97.258731999999981,95.270490000000009,96.333490000000012,96.813520000000011,97.502470000000002,97.42989,97.019700000000014,97.209461900000008,"2018-11-15","2020-04-01"]
["SunPower","SPR-X22-370-E-AC [240V]","N","Y","Y","Y","Y","Y*","Y","370 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-X22-370. Micro-inverter: IQ7XS-96-x-ACM-US-y [240V].",0.315,240,97.5,"UL","[09/22/2018]","[V04.14.05];[V04.18.02]","2018-11-15","[09/22/2018]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",2.1000000000000001E-2,null,null,53,60,64,3.15E-2,6.3E-2,9.4500000000000001E-2,0.1575,0.23625000000000002,0.315,95.734780000000015,96.840240000000009,96.996160000000003,97.762709999999998,97.755849999999981,97.46862999999999,97.525143499999984,95.610320000000002,96.678239999999988,96.754879999999986,97.666660000000007,97.739180000000005,97.513729999999981,97.456360900000007,95.436540000000008,96.497949999999989,96.657110000000017,97.603840000000019,97.700140000000005,97.48254,97.393219900000005,"2018-11-15","2020-04-01"]
["SunPower","MI-C-320-US208/240-1X [208V]","N","Y","Y","Y","Y","Y*","Y","320 W, 208 Vac Grid Support Utility Interactive Microinverter",0.32,208,95.5,"UL","[7/11/2017];[06/07/2018];[06/07/2018]","[15732];[16143];[16332]","2018-10-15","[06/07/2018]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.\r\n\r\nPreviously listed as MI-C-32-US28-1X","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2017-07-01","2020-04-01"]
["SunPower","MI-C-320-US208/240-1X [240V]","N","Y","Y","Y","Y","Y*","Y","320 W, 240 Vac Grid Support Utility Interactive Microinverter",0.32,240,96,"UL","[7/11/2017];[06/07/2018];[06/07/2018]","[15732];[16143];[16332]","2018-10-15","[06/07/2018]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.\r\n\r\nPreviously listed as MI-C-32-US24-1X","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2017-07-01","2020-04-01"]
["SunPower","SPR-E19-320-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","320 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-E19-320. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2017-09-01","2020-04-01"]
["SunPower","SPR-E19-320-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","320 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-E19-320. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2017-09-01","2020-04-01"]
["SunPower","SPR-E20-327-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","327 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E20-327. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2017-09-01","2020-04-01"]
["SunPower","SPR-E20-327-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","327 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-E20-327. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2017-09-01","2020-04-01"]
["SunPower","SPR-X20-327-BLK-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","327 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module:  SPR-X20-327-BLK. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2017-09-01","2020-04-01"]
["SunPower","SPR-X20-327-BLK-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","327 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module:  SPR-X20-327-BLK. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2017-09-01","2020-04-01"]
["SunPower","SPR-X20-327-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","327 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X20-327. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2017-09-01","2020-04-01"]
["SunPower","SPR-X20-327-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","327 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X20-327. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2017-09-01","2020-04-01"]
["SunPower","SPR-X21-335-BLK-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","335 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module:  SPR-X21-335-BLK. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2017-09-01","2020-04-01"]
["SunPower","SPR-X21-335-BLK-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","335 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module:  SPR-X21-335-BLK. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2017-09-01","2020-04-01"]
["SunPower","SPR-X21-335-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","335 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X21-335. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2017-09-01","2020-04-01"]
["SunPower","SPR-X21-335-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","335 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X21-335. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2017-09-01","2020-04-01"]
["SunPower","SPR-X21-345-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","345 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X21-345. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2017-09-01","2020-04-01"]
["SunPower","SPR-X21-345-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","345 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X21-345. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2017-09-01","2020-04-01"]
["SunPower","SPR-X21-350-BLK-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","350 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module:  SPR-X21-350-BLK. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2018-01-16","2020-04-01"]
["SunPower","SPR-X21-350-BLK-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","350 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module:  SPR-X21-350-BLK. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2018-01-16","2020-04-01"]
["SunPower","SPR-X22-360-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","360 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X22-360. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2017-09-01","2020-04-01"]
["SunPower","SPR-X22-360-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","360 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X22-360. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2017-09-01","2020-04-01"]
["SunPower","SPR-X22-370-D-AC [208V]","N","Y","Y","Y","Y","Y*","Y","370 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X22-370. Microinverter:  MI-C-320-US208/240-1X [208V].",0.32,208,95.5,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.02,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,90.8,94.5,95.5,96.2,96.1,95.9,95.7,90.2,94.5,95.5,96.2,96.1,95.9,95.7,89.4,94.1,95.3,96.2,96.2,95.9,95.7,"2018-01-16","2020-04-01"]
["SunPower","SPR-X22-370-D-AC [240V]","N","Y","Y","Y","Y","Y*","Y","370 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module:  SPR-X22-370. Microinverter:  MI-C-320-US208/240-1X [240V].",0.32,240,96,"UL","[6/21/2017]","[15732];[16143];[16332]","2018-10-15","[10/03/2017]","2020-04-01","UL","2019-12-20","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",0.1,null,null,53,60,64,0.03,0.06,0.1,0.16,0.24,0.32,89.7,94.1,95.3,96.2,96.1,95.9,95.7,90,94.3,95.4,96.3,96.3,96.2,95.8,89.6,94,95.2,96.3,96.4,96.2,95.8,"2018-01-16","2020-04-01"]
["SunPower","SPR-A380-BLK-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","380 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-A380-BLK. Micro-inverter: IQ7AS-66-x-ACM-US-y-z-& [240V].",0.34899999999999998,240,97,"UL","[10/23/2020]","[V04.17.01]","2020-12-11","[10/23/2020]","2020-12-11","UL","2020-03-18","2020-12-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-12-11","2021-01-04"]
["SunPower","SPR-A385-BLK-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","385 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-A385-BLK. Micro-inverter: IQ7AS-66-x-ACM-US-y-z-& [240V].",0.34899999999999998,240,97,"UL","[10/23/2020]","[V04.17.01]","2020-12-11","[10/23/2020]","2020-12-11","UL","2020-03-18","2020-12-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-12-11","2021-01-04"]
["SunPower","SPR-A390-BLK-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","390 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-A390-BLK. Micro-inverter: IQ7AS-66-x-ACM-US-y-z-& [240V].",0.34899999999999998,240,97,"UL","[10/23/2020]","[V04.17.01]","2020-12-11","[10/23/2020]","2020-12-11","UL","2020-03-18","2020-12-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-12-11","2021-01-04"]
["SunPower","SPR-A390-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","390 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: SPR-A390. Microinverter: IQ7AS-66-x-ACM-US-y [240V].",0.34899999999999998,240,97,"UL","[02/22/2019]","[V04.17.01];[V04.18.02]","2019-07-15","[02/22/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2019-07-15","2020-04-01"]
["SunPower","SPR-A395-BLK-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","395 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-A395-BLK. Micro-inverter: IQ7AS-66-x-ACM-US-y-z-& [240V].",0.34899999999999998,240,97,"UL","[10/23/2020]","[V04.17.01]","2020-12-11","[10/23/2020]","2020-12-11","UL","2020-03-18","2020-12-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-12-11","2021-01-04"]
["SunPower","SPR-A395-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","395 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A395. Micro-inverter: IQ7AS-66-x-ACM-US-y [240V].",0.34899999999999998,240,97,"UL","[02/22/2019]","[V04.17.01];[V04.18.02]","2019-04-02","[02/22/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2019-04-02","2020-04-01"]
["SunPower","SPR-A400-BLK-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","400 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-A400-BLK. Micro-inverter: IQ7AS-66-x-ACM-US-y-z-& [240V].",0.34899999999999998,240,97,"UL","[10/23/2020]","[V04.17.01]","2020-12-11","[10/23/2020]","2020-12-11","UL","2020-03-18","2020-12-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-12-11","2021-01-04"]
["SunPower","SPR-A400-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","400 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A400. Micro-inverter: IQ7AS-66-x-ACM-US-y [240V].",0.34899999999999998,240,97,"UL","[02/22/2019]","[V04.17.01];[V04.18.02]","2019-04-02","[02/22/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2019-04-02","2020-04-01"]
["SunPower","SPR-A405-BLK-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","405 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-A405-BLK. Micro-inverter: IQ7AS-66-x-ACM-US-y-z-& [240V].",0.34899999999999998,240,97,"UL","[10/23/2020]","[V04.17.01]","2020-12-11","[10/23/2020]","2020-12-11","UL","2020-03-18","2020-12-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-12-11","2021-01-04"]
["SunPower","SPR-A405-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","405 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A405. Micro-inverter: IQ7AS-66-x-ACM-US-y [240V].",0.34899999999999998,240,97,"UL","[02/22/2019]","[V04.17.01];[V04.18.02]","2019-04-02","[02/22/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2019-04-02","2020-04-01"]
["SunPower","SPR-A410-BLK-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","410 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-A410-BLK. Micro-inverter: IQ7AS-66-x-ACM-US-y-z-& [240V].",0.34899999999999998,240,97,"UL","[10/23/2020]","[V04.17.01]","2020-12-11","[10/23/2020]","2020-12-11","UL","2020-03-18","2020-12-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-12-11","2021-01-04"]
["SunPower","SPR-A410-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","410W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A410. Micro-inverter: IQ7AS-66-x-ACM-US-y [240V].",0.34899999999999998,240,97,"UL","[02/22/2019]","[V04.17.01];[V04.18.02]","2019-04-02","[02/22/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2019-04-02","2020-04-01"]
["SunPower","SPR-A415-BLK-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","415 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, black backsheet. DC Module: SPR-A415-BLK. Micro-inverter: IQ7AS-66-x-ACM-US-y-z-& [240V].",0.34899999999999998,240,97,"UL","[10/23/2020]","[V04.17.01]","2020-12-11","[10/23/2020]","2020-12-11","UL","2020-03-18","2020-12-11","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2020-12-11","2021-01-04"]
["SunPower","SPR-A415-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","415 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A415. Micro-inverter: IQ7AS-66-x-ACM-US-y [240V].",0.34899999999999998,240,97,"UL","[02/22/2019]","[V04.17.01];[V04.18.02]","2019-04-02","[02/22/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2019-04-02","2020-04-01"]
["SunPower","SPR-A420-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","420 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A420. Micro-inverter: IQ7AS-66-x-ACM-US-y [240V].",0.34899999999999998,240,97,"UL","[02/22/2019]","[V04.17.01];[V04.18.02]","2019-04-02","[02/22/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2019-04-02","2020-04-01"]
["SunPower","SPR-A425-G-AC [240V]","N","Y","Y","Y","Y","Y*","Y","425 W, 240 Vac Grid Support Utility Interactive, monocrystalline ACPV Module, white backsheet. DC Module: SPR-A425. Micro-inverter: IQ7AS-66-x-ACM-US-y [240V].",0.34899999999999998,240,97,"UL","[02/22/2019]","[V04.17.01];[V04.18.02]","2019-04-02","[02/22/2019]","2020-04-01","UL","2020-03-18","2020-04-01","This component is specific to ACPV modules and is not available as an individual unit.","N","Y",1.9E-2,null,null,38,40.5,43,3.4869799999999999E-2,6.9739599999999999E-2,0.10460940000000001,0.174349,0.26152350000000002,0.34869800000000001,95.154589999999999,95.805639999999997,96.649199999999993,97.148089999999996,96.970150000000004,96.471029999999999,96.813199499999996,95.067850000000007,95.709400000000002,96.570779999999999,97.112740000000002,96.976960000000005,96.463949999999997,96.791339300000004,95.00121,95.632999999999996,96.469070000000002,97.071960000000004,96.959519999999998,96.460440000000006,96.754666,"2019-04-02","2020-04-01"]
["SunPower","SPR-A380-BLK-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","380 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A380-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A385-BLK-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","385 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A385-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A390-BLK-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","390 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A390-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A390-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","390 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A390. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A395-BLK-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","395 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A395-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A395-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","395 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A395. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A400-BLK-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","400 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A400-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A400-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","400 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A400. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A405-BLK-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","405 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A405-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A405-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","405 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A405. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A410-BLK-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","410 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A410-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A410-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","410 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A410. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A415-BLK-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","415 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A415-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A415-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","415 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A415. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A420-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","420 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A420. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-A425-H-AC [208V]","N","Y ","Y","Y ","Y","Y*","Y","425 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A425. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-05-21"]
["SunPower","SPR-M415-H-AC [208V]","N","Y","Y ","Y ","Y ","Y*","Y","415 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M415. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-09-21"]
["SunPower","SPR-M420-H-AC [208V]","N","Y","Y ","Y ","Y ","Y*","Y","420 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M420. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-09-21"]
["SunPower","SPR-M425-H-AC [208V]","N","Y","Y ","Y ","Y ","Y*","Y","425 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M425. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-09-21"]
["SunPower","SPR-M430-H-AC [208V]","N","Y","Y ","Y ","Y ","Y*","Y","430 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M430. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-09-21"]
["SunPower","SPR-M435-H-AC [208V]","N","Y","Y ","Y ","Y ","Y*","Y","435 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M435. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-09-21"]
["SunPower","SPR-M440-H-AC [208V]","N","Y","Y ","Y ","Y ","Y*","Y","440 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M440. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.36699999999999999,208,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.05,null,null,38,40.5,43,3.6702600000000002E-2,7.3405200000000004E-2,0.11010780000000001,0.18351300000000001,0.2752695,0.36702600000000002,95.431117996588256,96.215531301918574,97.270499630199083,97.415658920710527,96.979566847901197,96.409250836143869,96.977402585127379,95.49117964077368,96.22218182360966,97.214966446111063,97.431013126425924,97.043729085553622,96.51769954037745,97.016126399256507,95.477302494346617,96.233929690364732,97.123615008240648,97.384916211379007,97.029213560240237,96.51847533450389,96.987861743323094,"2021-09-21"]
["SunPower","SPR-A380-BLK-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","380 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A380-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [208V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A385-BLK-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","385 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A385-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A390-BLK-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","390 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A390-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A390-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","390 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A390. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A395-BLK-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","395 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A395-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A395-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","395 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A395. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A400-BLK-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","400 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A400-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A400-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","400 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A400. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A405-BLK-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","405 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A405-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A405-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","405 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A405. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A410-BLK-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","410 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A410-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A410-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","410 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A410. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A415-BLK-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","415 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A415-BLK. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A415-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","415 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A415. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A420-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","420 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A420. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-A425-H-AC [240V]","N","Y ","Y","Y ","Y","Y*","Y","425 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. monocrystalline ACPV module, black backsheet. DC Module: SPR-A425. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[05/06/2021]","[V04.21.04]","2021-05-21","[05/06/2021]","2021-05-21","UL","2020-01-24","2021-05-21","This model is specifically for the ACPV module.  The microinverter is also sold as an individual unit.","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-05-21"]
["SunPower","SPR-M415-H-AC [240V]","N","Y","Y ","Y ","Y ","Y*","Y","415 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M415. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-09-21"]
["SunPower","SPR-M420-H-AC [240V]","N","Y","Y ","Y ","Y ","Y*","Y","420 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M420. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-09-21"]
["SunPower","SPR-M425-H-AC [240V]","N","Y","Y ","Y ","Y ","Y*","Y","425 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M425. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-09-21"]
["SunPower","SPR-M430-H-AC [240V]","N","Y","Y ","Y ","Y ","Y*","Y","430 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M430. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-09-21"]
["SunPower","SPR-M435-H-AC [240V]","N","Y","Y ","Y ","Y ","Y*","Y","435 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M435. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-09-21"]
["SunPower","SPR-M440-H-AC [240V]","N","Y","Y ","Y ","Y ","Y*","Y","440 W, 66 cell monocrystalline ACPV module, white backsheet. DC Module: SPR-M440. Microinverter: IQ7HS-66-x-ACM-US-y [240V].",0.38400000000000001,240,97,"UL","[08/20/2021]","[V04.21.04]","2021-09-21","[08/20/2021]","2021-09-21","UL","2020-01-24","2021-09-21","This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y [208V].","N","Y",0.06,null,null,38,40.5,43,3.8380000000000004E-2,7.6760000000000009E-2,0.11514000000000001,0.19190000000000002,0.28785000000000005,0.38380000000000003,95.588183400999995,96.348297395049997,97.283627574819988,97.530906411290005,97.150011332639991,96.713578017699987,97.121652768325987,95.602970191369991,96.234615145629988,97.282900707300001,97.591651171449982,97.32291619902,96.986655462789983,97.234522754436895,95.733749363749993,96.35247455355001,97.167865976979996,97.627104695389988,97.403108815929997,97.085447759969995,97.28672966593841,"2021-09-21"]
["SunPower","SPR-12000m-3 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 12 kW, 480 Vac 3-phase, Grid Support Utility Interactive Inverter",12,480,97.5,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,300,675,800,1.2000000000000002,2.4000000000000004,3.5999999999999996,6,9,12,92.894674644817883,95.825371847114951,96.49457533743761,96.690700406340042,96.627312947730815,96.507013910909436,96.429278261815185,94.885736215076193,96.883040483522223,97.494372087983805,97.777000604401067,97.832115333209018,97.811357024005105,97.613665228062487,94.154840052277819,97.204030409030267,97.700750214004856,98.014008962786292,98.183788377033963,98.189784411397596,97.880324090806212,"2017-09-01","2018-10-15"]
["SunPower","SPR-12000m-3-H [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 12 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter",12,480,97.5,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,300,675,800,1.2000000000000002,2.4000000000000004,3.5999999999999996,6,9,12,92.894674644817883,95.825371847114951,96.49457533743761,96.690700406340042,96.627312947730815,96.507013910909436,96.429278261815185,94.885736215076193,96.883040483522223,97.494372087983805,97.777000604401067,97.832115333209018,97.811357024005105,97.613665228062487,94.154840052277819,97.204030409030267,97.700750214004856,98.014008962786292,98.183788377033963,98.189784411397596,97.880324090806212,"2017-09-01","2018-10-15"]
["SunPower","SPR-15000m-3 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 15 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter",15,480,97.5,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,300,675,800,1.5,3,4.5,7.5,11.25,15,93.855655768325036,96.220132968022185,96.731415475995405,96.662686184447367,96.525350018358225,96.347074199043405,96.447956054669547,95.495928692020158,97.192892755040859,97.796289926240703,97.802899005800356,97.832975895750408,97.777428409336565,97.693994013014347,95.552946082935037,97.515080368134008,97.923591757588014,98.172996722782088,98.214818639191321,98.157219501191648,98.02674703824988,"2017-09-01","2018-10-15"]
["SunPower","SPR-15000m-3-H [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 15 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter",15,480,97.5,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,300,675,800,1.5,3,4.5,7.5,11.25,15,93.855655768325036,96.220132968022185,96.731415475995405,96.662686184447367,96.525350018358225,96.347074199043405,96.447956054669547,95.495928692020158,97.192892755040859,97.796289926240703,97.802899005800356,97.832975895750408,97.777428409336565,97.693994013014347,95.552946082935037,97.515080368134008,97.923591757588014,98.172996722782088,98.214818639191321,98.157219501191648,98.02674703824988,"2017-09-01","2018-10-15"]
["SunPower","SPR-20000m-3 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 20 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter",20,480,97.5,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,380,695,800,2,4,6,10,15,20,95.166002573680657,96.960461207919593,97.206210307973649,97.083526385263212,96.934118174722499,96.705141513761617,96.917288649496328,97.228849010193727,98.289481853362432,98.509907734190421,98.548489172388329,97.836810327646688,97.705085096687185,98.058763435867391,96.492868266958425,97.86877684687623,98.130627177880115,98.219804322689427,98.174642673551418,98.04215458277919,98.089656088253761,"2017-09-01","2018-10-15"]
["SunPower","SPR-20000m-3-H [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 20 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter",20,480,97.5,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,380,695,800,2,4,6,10,15,20,95.166002573680657,96.960461207919593,97.206210307973649,97.083526385263212,96.934118174722499,96.705141513761617,96.917288649496328,97.228849010193727,98.289481853362432,98.509907734190421,98.548489172388329,97.836810327646688,97.705085096687185,98.058763435867391,96.492868266958425,97.86877684687623,98.130627177880115,98.219804322689427,98.174642673551418,98.04215458277919,98.089656088253761,"2017-09-01","2018-10-15"]
["SunPower","SPR-24000m-3 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 24 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter",24.06,480,98,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,450,712,800,2.4060000000000001,4.8120000000000003,7.2179999999999991,12.03,18.044999999999998,24.06,96.082505616067209,97.424181190564596,97.444656931781154,97.315063669223932,97.122156907959265,96.865885453167053,97.162068920398454,97.45990452259629,98.348028973855392,98.503124414275888,98.531362070230031,98.435119435359169,98.266514886637623,98.411697639130281,96.909942056488973,98.004925627161398,98.188558637442924,98.204070345596193,98.076628570877034,97.882251177120239,98.056851474106807,"2017-09-01","2018-10-15"]
["SunPower","SPR-24000m-3-H [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US 24 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter",24.06,480,98,"UL","[7/13/2017]","[2.03.04.R]","2018-10-15","[7/13/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.79,null,null,450,712,800,2.4060000000000001,4.8120000000000003,7.2179999999999991,12.03,18.044999999999998,24.06,96.082505616067209,97.424181190564596,97.444656931781154,97.315063669223932,97.122156907959265,96.865885453167053,97.162068920398454,97.45990452259629,98.348028973855392,98.503124414275888,98.531362070230031,98.435119435359169,98.266514886637623,98.411697639130281,96.909942056488973,98.004925627161398,98.188558637442924,98.204070345596193,98.076628570877034,97.882251177120239,98.056851474106807,"2017-09-01","2018-10-15"]
["SunPower","SPR-30000m-3 [480V]","N","Y","Y","Y","N","N","N","Sunny Tripower TL-US, 30kW, 480Vac 3-phase, Transformerless, Grid Support Utility Interactive Inverter",30.01,480,98,"UL","[7/6/2017]","[2.03.04.R]","2018-10-15","[7/6/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",1.22,null,null,500,720,800,3.0010000000000003,6.0020000000000007,9.0030000000000001,15.005000000000001,22.5075,30.01,96.587999999999994,97.715999999999994,97.926000000000016,97.97999999999999,97.838000000000008,97.622,97.811480000000017,97.588000000000008,98.448000000000008,98.690000000000012,98.602000000000004,98.537999999999982,98.328000000000003,98.516679999999994,97.025999999999996,98.059999999999988,98.451999999999998,98.385999999999996,98.281999999999996,98.08,98.252799999999993,"2017-09-01","2018-10-15"]
["Tabuchi Electric Co., Ltd.","THD-S55P3BB-US [240V]","Y","Y","Y","Y","N","N","N","5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 3.3 kW Discharge Rate/20 kWh Storage Capacity",5.5189199999999996,240,94.5,"Intertek","[9/20/2017]","[4.1]","2018-10-15","[9/20/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",10.1,null,null,240,380,520,0.55188999999999999,1.10378,1.65568,2.7594599999999998,4.1391900000000001,5.5189199999999996,89.3,93.3,94.3,94.7,94.1,94.2,94,89.7,93.7,94.7,95.4,95.5,95.4,95.1,88.8,93.1,94.3,95.1,95.2,94.9,94.7,"2017-12-15","2018-10-15"]
["Tabuchi Electric Co., Ltd.","THD-S55P3B-US [240V]","Y","Y","Y","Y","N","N","N","5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 2 kW Discharge Rate/10 kWh Storage Capacity",5.5189199999999996,240,94.5,"Intertek","[9/20/2017]","[4.1]","2018-10-15","[9/20/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",10.1,null,null,240,380,520,0.55188999999999999,1.10378,1.65568,2.7594599999999998,4.1391900000000001,5.5189199999999996,89.3,93.3,94.3,94.7,94.1,94.2,94,89.7,93.7,94.7,95.4,95.5,95.4,95.1,88.8,93.1,94.3,95.1,95.2,94.9,94.7,"2017-12-15","2018-10-15"]
["Tabuchi Electric Co., Ltd.","THE-S55P3BB-USW [240V]","Y","Y","Y","Y","N","N","N","5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 4.0 kW Discharge Rate/20 kWh Storage Capacity\n",5.5189199999999996,240,94.5,"Intertek","[04/26/2018]","[4.11]","2018-10-15","[04/26/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",10.1,null,null,240,380,520,0.55189200000000005,1.1037840000000001,1.6556759999999999,2.7594599999999998,4.1391900000000001,5.5189199999999996,89.325999999999993,93.286000000000001,94.304000000000002,94.656000000000006,94.048000000000002,94.174000000000007,93.985720000000001,89.688000000000002,93.665999999999997,94.706000000000003,95.44,95.498000000000005,95.41,95.062380000000005,88.78,93.075999999999993,94.275999999999996,95.093999999999994,95.165999999999997,94.921999999999997,94.671940000000006,"2018-06-01","2018-10-15"]
["Tesla Inc.","1534000-xx-y [208V]","N","Y","Y","Y","Y","Y*","Y","3.336 kW, 208 Vac Grid Support Utility Interactive Inverter, where xx is two numbers and y is a letter",3.3359999999999999,208,97.5,"Intertek","[11/30/20]","[1217B43E9B859EAB26ECB10B5FBECC64/8A3CA3F2]","2021-01-21","[11/30/20]","2021-01-21","Intertek","2020-08-06","2021-01-21",null,"N","N",3.8925000000000001,null,null,270,375,480,0.33356659999999999,0.66713319999999998,1.0006997999999998,1.6678329999999999,2.5017494999999998,3.3356659999999998,94.501537675574227,95.40516681303049,96.92551906390986,97.389894267285129,97.338965833771979,97.04291162861719,97.075057404803559,97.510851241073013,95.480546368676045,97.253753813449762,96.814766244737427,97.962144047363537,97.438413024223422,97.467869733399411,95.408122835035016,96.001801813946457,96.412251505034419,97.331884010090761,97.839880271075998,97.5200710935773,97.356720925171061,"2021-01-21","2021-04-12"]
["Tesla Inc.","1534000-xx-y [240V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac Grid Support Utility Interactive Inverter, where xx is two numbers and y is a letter",3.8,240,97.5,"Intertek","[11/30/20]","[1217B43E9B859EAB26ECB10B5FBECC64/8A3CA3F2]","2021-01-21","[11/30/20]","2021-01-21","Intertek","2020-08-06","2021-01-21",null,"N","N",4.6639999999999997,null,null,270,350,425,0.38004180000000004,0.76008360000000008,1.1401254000000001,1.900209,2.8503134999999999,3.8004180000000001,93.395183110691448,96.68182243904316,96.826930817800388,97.652294418668859,97.788988320739165,97.133920610678956,97.380971812962031,94.034359125081806,97.504644633001547,97.663068944715192,98.023975507105348,98.074027114058197,97.686506565530564,97.804769425238675,92.463056776294351,96.097043433384627,97.706462966014129,98.110713820736009,98.054792113367185,97.937976457541609,97.697338543958949,"2021-01-21","2021-04-12"]
["Tesla Inc.","1538000-xx-y [208V]","N","Y","Y","Y","Y","Y*","Y","6.656 kW, 208 Vac Grid Support Utility Interactive Inverter, where xx is two numbers and y is a letter. This inverter can be a component of the Energy Storage System 1850000-XX-Y.",6.5609999999999999,208,97.5,"Intertek","[11/19/2020]","[1217B43E9B859EAB26ECB10B5FBECC64/D85CAB80]","2021-01-04","[11/19/2020]","2021-01-04","Intertek","2020-08-06","2021-01-04",null,"N","N",6.7176,null,null,270,375,480,0.65614440000000007,1.3122888000000001,1.9684332000000002,3.2807220000000004,4.9210830000000003,6.5614440000000007,93.437986998259277,98.447501034151898,97.303668686176053,97.839295674716425,97.625547916509674,96.869231406595077,97.46758883174941,95.099079469586599,98.09571076748351,98.060752870581837,98.157518288221155,97.895511871022251,98.221274735138081,97.884802930552596,95.105413790278902,96.613080193903627,96.409709992479208,97.89878567721351,97.547498344625211,97.040175603623439,97.314963655451209,"2021-01-04","2021-07-01"]
["Tesla Inc.","1538000-xx-y [240V]","N","Y","Y","Y","Y","Y*","Y","7.68 kW, 240 Vac Grid Support Utility Interactive Inverter, where xx is two numbers and y is a letter. This inverter can be a component of the Energy Storage System 1850000-XX-Y.",7.5750000000000002,240,98,"Intertek","[11/19/2020]","[1217B43E9B859EAB26ECB10B5FBECC64/D85CAB80]","2021-01-04","[11/19/2020]","2021-01-04","Intertek","2020-08-06","2021-01-04",null,"N","N",6.9130000000000003,null,null,270,375,480,0.7574936000000001,1.5149872000000002,2.2724807999999999,3.7874680000000001,5.6812019999999999,7.5749360000000001,93.574394993326536,97.811869474825102,98.380266336783421,98.203385322092188,97.867094536118643,97.255365983892375,97.794240554865183,96.846002298757611,97.873140974079519,98.222459895896307,98.565173339598658,98.242634205884926,97.698307360677831,98.206390226630461,95.924430657516652,96.839938514129457,98.117017181277333,98.35718119452217,98.089927777931763,97.644352552091902,97.977903614518496,"2021-01-04","2021-07-01"]
["TMEIC","PVU-L0840GR [630V]","N","Y","Y","Y","N","N","N","840 kW, 630Vac, Grid Support Utility Interactive Photovoltaic Inverter",794.69299999999998,630,97.5,"CSA Group","[10/14/2019]","[DSP: HM0041, FPGA: HF0008]","2020-07-01","[10/14/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 2500 kVA Low-Voltage Liquid-Immersed Distribution Transformers Table in DOE2016.","N","N",47.17,null,null,915,1150,1200,79.468999999999994,158.93899999999999,23.840699999999998,397.346,596.02,794.69299999999998,93.556170612079015,97.225299567218897,97.904343961119025,98.452694873404326,98.639011539913369,98.721613367799236,98.24185578613735,93.051225321899096,96.799502304324605,97.574906100998859,98.103160656625249,98.315835009254968,98.27234243614464,97.893686274815721,92.814887684312879,96.617929115617216,97.435376970846335,98.010565612880228,98.23163494367175,98.20475813926268,97.790960405468937,"2020-07-01"]
["Trina Energy Storage Solutions (Jiangsu) Co., Ltd","TB6000SHU [208V]","N","Y","Y","Y","N","N","N","4992 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",4.992,208,97,"CSA Group","[03/03/2018]","[1.4.1]","2018-10-15","[03/03/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.86,null,null,200,380,460,0.49920000000000003,0.99840000000000007,1.4976,2.496,3.7439999999999998,4.992,92.956999999999994,94.948666666666682,95.97671428571428,96.759333333333316,96.816285714285712,96.580619047619038,96.44404142857141,95.57180952380952,97.207999999999984,97.745380952380955,97.944952380952373,97.716190476190476,97.311761904761894,97.636327142857141,94.611999999999995,96.611142857142866,97.398047619047603,97.739666666666679,97.623999999999995,97.279714285714292,97.43283857142859,"2018-08-01","2018-10-15"]
["Trina Energy Storage Solutions (Jiangsu) Co., Ltd","TB6000SHU [240V]","N","Y","Y","Y","N","N","N","5760 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",5.76,240,97.5,"CSA Group","[03/03/2018]","[1.4.1]","2018-10-15","[03/03/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.25,null,null,200,380,460,0.57599999999999996,1.1519999999999999,1.728,2.88,4.32,5.76,93.648190476190493,95.423047619047608,96.470714285714294,97.089095238095226,97.087285714285713,96.810714285714297,96.779072857142864,96.162285714285716,97.584714285714284,98.080285714285694,98.165000000000006,97.933999999999983,97.580333333333328,97.894048095238091,95.235428571428571,97.047761904761927,97.773428571428582,98.000142857142848,97.859285714285733,97.505095238095237,97.715322857142866,"2018-08-01","2018-10-15"]
["Trina Energy Storage Solutions (Jiangsu) Co., Ltd","TB8000SHU [208V]","N","Y","Y","Y","N","N","N","6656W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter\n",6.6559999999999997,208,97.5,"CSA Group","[03/03/2018]","[1.4.1]","2018-10-15","[03/03/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.1499999999999999,null,null,270,380,460,0.66559999999999997,1.3311999999999999,1.9967999999999999,3.3279999999999998,4.992,6.6559999999999997,94.577142857142846,96.30147619047618,96.99633333333334,97.387761904761902,97.294809523809505,96.929047619047623,97.101850952380943,95.905285714285696,97.331380952380954,97.763285714285729,97.861904761904768,97.586190476190467,97.213761904761895,97.566743809523814,94.978142857142871,96.881095238095227,97.418238095238095,97.692761904761923,97.498619047619044,97.152476190476165,97.380740952380961,"2018-08-01","2018-10-15"]
["Trina Energy Storage Solutions (Jiangsu) Co., Ltd","TB8000SHU [240V]","N","Y","Y","Y","N","N","N","7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",7.68,240,97.5,"CSA Group","[03/03/2018]","[1.4.1]","2018-10-15","[03/03/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.19,null,null,270,380,460,0.76800000000000002,1.536,2.3039999999999998,3.84,5.76,7.68,95.141761904761907,96.556571428571417,97.332523809523806,97.597190476190477,97.510428571428591,97.13038095238096,97.345858095238114,96.495714285714271,97.678238095238086,98.032761904761898,98.064428571428579,97.776238095238099,97.431095238095239,97.794162857142865,95.663714285714278,97.276809523809519,97.747523809523798,97.93119047619048,97.734619047619049,97.423238095238091,97.656151904761899,"2018-08-01","2018-10-15"]
["TSUNESS Co., Ltd","TSOL-M1600P [240V]","N","Y","Y","Y","N","N","N","1.5 kW, 240 Vac Grid Support Utility Interactive Microinverters",1.5509999999999999,240,96.5,"CSA Group","[03/17/2020]","[V01.01.00]","2020-06-01","[03/17/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","Y",0.03,null,null,36,42,48,0.15507199999999999,0.31014399999999998,0.46521600000000002,0.77536000000000005,1.1630400000000001,1.5507200000000001,95.952784289999997,96.053996350000006,96.305971659999997,96.640993429999995,96.740058950000005,95.897398159999995,96.55923756,95.944835400000002,95.651087070000003,96.355402620000007,96.304572280000002,96.719099679999999,96.426669689999997,96.489412580000007,95.141461660000004,95.86745372,96.451621450000005,96.166729340000003,96.673241599999997,96.590981229999997,96.434606000000002,"2020-06-01"]
["WSTECH GmbH","APS800-PV-1-440-5 [440V]","N","Y","Y","Y","N","N","N","800 kW, 440 Vac, Grid Support Utility Interactive Centeral PV Inverter",814.16700000000003,440,97.5,"MET","[10/12/2020]","[APU V3130 APMC V2040]","2020-11-12","[10/12/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 1000 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",91.4,null,null,648,1000,1500,81.416693333333342,162.83338666666668,244.25007999999997,407.08346666666665,610.62519999999995,814.1669333333333,96.899355530950103,97.920707265792174,98.147190760869563,98.085463040000008,97.731682555419141,97.300539581134942,97.810438447660857,97.156025349874199,97.903118886806737,98.084511645962735,97.981152853333356,97.697036658005203,97.27509500499103,97.770764634043147,96.518204331811816,97.351769103912844,97.62585192805382,97.667947145904762,97.341867071756937,96.957097736075085,97.39273219530952,"2020-11-12"]
["WSTECH GmbH","APS870-PV-1-480-5 [480V]","N","Y ","Y ","Y ","Y ","N","N","870 kW, 480 Vac, Grid Support Utility Interactive Centeral PV Inverter",872.029,480,98,"MET","[04/08/2021]","[APU V3130 APMC V2050]","2021-07-01","[04/08/2021]","2021-07-01","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",91.402000000000001,null,null,770,1000,1470,87.202903333333339,174.40580666666668,261.60870999999997,436.01451666666668,654.02177500000005,872.02903333333336,97.081535640215748,98.188326536251608,98.416188156702887,98.401719417256189,98.132164669461218,97.756162785201553,98.164836822923888,95.766437110691712,97.280734052016285,97.833944012368789,98.04081271586206,97.85925870133093,97.52706667584556,97.765098584341445,96.937363573018132,97.639693816860969,97.84646181596699,97.794618856551736,97.559243378111034,97.17562500327,97.603104852118037,"2021-07-01"]
["WSTECH GmbH","APS1600-PV-2-440-5 [440V]","N","Y","Y","Y","N","N","N","1600 kW, 440 Vac, Grid Support Utility Interactive Centeral PV Inverter",1626.952,440,98,"MET","[10/12/2020]","[APU V3130 APMC V2040]","2020-11-12","[10/12/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",91.4,null,null,648,1000,1500,162.69520149253731,325.39040298507462,488.08560447761192,813.47600746268654,1220.2140111940298,1626.9520149253731,98.039564384810532,98.583932832285171,98.668427958751352,98.532876253333342,98.2150718555353,97.858468021735675,98.329806069777334,96.983648481562426,97.910572913334434,98.115708519049306,98.108532687142869,97.852695689547474,97.453039923442418,97.886132183147424,96.317955371488225,97.379170135459674,97.660767145350476,97.701669861904762,97.437048453413212,97.002759893817952,97.450093125074474,"2020-11-12"]
["WSTECH GmbH","APS1740-PV-2-480-5 [480V]","N","Y ","Y ","Y ","Y ","N","N","1735 kW, 480 Vac, Grid Support Utility Interactive Centeral PV Inverter",1735.36,480,97.5,"MET","[04/08/2021]","[APU V3130 APMC V2050]","2021-07-01","[04/08/2021]","2021-07-01","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",91.402000000000001,null,null,770,1000,1470,173.53604761904762,347.07209523809524,520.60814285714287,867.68023809523811,1301.5203571428572,1735.3604761904762,96.201849245365011,97.635415202832306,98.024327642348112,98.123863291080468,97.916855850022969,97.597507221863992,97.874584299770262,95.6962644026314,97.274574959056025,97.780480876315039,97.951872039712796,97.757716524196624,97.433202078371636,97.678380019298359,94.384457837533915,96.470678221985494,97.070575922965205,97.416133179833338,97.340286289845665,97.060011305722696,97.148121602025796,"2021-07-01"]
["Xiamen Kehua Hengsheng Co., Ltd.","SPI50K-BHV [480V]","N","Y","Y","Y","N","N","N","50 kW, 480 Vac Grid Support Utility Interactive Inverter",49.825000000000003,480,98,"Intertek","[11/27/2017]","[Main CPU(28335):V1]","2018-10-15","[11/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.8,null,null,540,695,850,4.9829999999999997,9.9659999999999993,14.949,24.914999999999999,37.372500000000002,49.83,96.770330000000001,96.972989999999996,97.363749999999996,97.680459999999997,97.704480000000004,97.678489999999996,97.583309999999997,97.315259999999995,98.495379999999997,98.618930000000006,98.769819999999996,98.661100000000005,98.283559999999994,98.59787,96.552090000000007,97.895690000000002,98.155159999999995,98.330029999999994,98.28304,98.088130000000007,98.179209999999998,"2018-01-02","2018-10-15"]
["Xiamen Kehua Hengsheng Co., Ltd.","SPI60K-BHV [480V]","N","Y","Y","Y","N","N","N","60 kW, 480 Vac Grid Support Utility Interactive Inverter",59.667999999999999,480,98,"Intertek","[11/27/2017]","[Main CPU(28335):V1]","2018-10-15","[11/27/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",2.8,null,null,540,695,850,5.9670000000000005,11.934000000000001,17.901,29.835000000000001,44.752499999999998,59.67,97.011400860603928,97.631529378232045,97.640880301858914,97.91217849877566,97.592676780514722,97.371389602654588,97.633183798107254,98.571429438759566,98.853763236653847,98.841635491890969,98.720500594806055,98.605791036857624,98.347566863262372,98.656294316016925,97.757887544738608,98.375136518373779,98.52299435222767,98.37578536371538,98.164768431150804,97.952672077286579,98.235707448730039,"2018-01-02","2018-10-15"]
["Yaskawa Solectria Solar","PVI20TL-480-R [480V]","N","Y","Y","Y","Y","Y*","Y","20 kW, 480 Vac Grid Support Utility Interactive Inverter",20,480,98,"Intertek","[01/20/2020]","[00.02.00]","2020-02-21","[01/20/2020]","2020-08-11","Intertek","2020-03-20","2020-08-11",null,"N","N",3,null,null,560,735,850,2.0111933333333334,4.0223866666666668,6.0335799999999997,10.055966666666666,15.08395,20.111933333333333,96.981509777777802,97.665209777777775,97.801241333333337,97.831345777777784,97.602279111111102,97.256001333333302,97.635260448888886,97.901590222222211,98.330456888888875,98.481923555555554,98.413890222222236,98.295634666666686,98.149012444444466,98.321471222222243,97.53970133333334,98.21510099999999,98.312145777777772,98.268437999999975,98.198667999999998,97.988923555555544,98.190912794444444,"2020-02-21","2021-04-12"]
["Yaskawa Solectria Solar","PVI 25TL-208 [208V]","N","Y","Y","Y","Y","Y*","Y","25 kW, 208 Vac Grid Support Utility Interactive Inverter",25,208,96.5,"CSA Group","[09/10/2020]","[V01.01.00]","2020-10-21","[09/10/2020]","2020-10-21","Intertek","2020-09-11","2020-10-21",null,"N","N",2.9,null,null,480,575,850,2.5432000000000001,5.0864000000000003,7.629599999999999,12.715999999999999,19.073999999999998,25.431999999999999,95.686990530657496,96.805469029935551,97.031082017127943,97.042352525770227,96.776890574103703,96.473458639563972,96.805801881443344,95.307142857142864,96.284285714285716,96.787142857142854,96.781428571428577,96.482857142857142,96.118571428571428,96.506899999999987,93.594285714285704,95.617142857142866,96.122857142857143,96.335714285714289,96.151428571428568,95.850000000000023,96.04262857142858,"2020-10-21","2021-04-12"]
["Yaskawa Solectria Solar","PVI25TL-480-R [480V]","N","Y","Y","Y","Y","Y*","Y","25 kW, 480 Vac Grid Support Utility Interactive Inverter",25,480,98,"Intertek","[01/20/2020]","[00.02.00]","2020-02-21","[01/20/2020]","2020-08-11","Intertek","2020-03-20","2020-08-11",null,"N","N",3,null,null,560,735,850,2.5258733333333332,5.0517466666666664,7.5776199999999996,12.629366666666666,18.944049999999997,25.258733333333332,96.911910371269158,97.698228393841575,97.82952991949324,97.839929437398695,97.597147898886149,97.286821705426348,97.638146078416753,97.89734543415868,98.32561756529762,98.477298970263973,98.408187377201003,98.281658579248486,98.094613938471952,98.309179665200418,97.500273558455632,98.156221457435635,98.313740711134443,98.279290178911168,98.185350638522294,97.996273689551259,98.182171361011868,"2020-02-21","2021-04-12"]
["Yaskawa Solectria Solar","PVI 36TL-480 [480V]","N","Y","Y","Y","Y","Y*","Y","36 kVA, 480 Vac, 1000 Vdc, 3-phase, non-isolated Grid Support Utility Interactive Inverter",36,480,98,"CSA Group","[12/10/2020]","[V0.90]","2018-10-15","[12/10/2020]","2021-02-01","CSA Group","2020-12-16","2021-02-01","Formerly \"Solectria Renewables, LLC\"","N","N",0,null,null,540,730,800,3.6,7.2,10.8,18,27,36,95.5,96.8,97.2,97.5,97.5,97.3,97.3,97.4,98.3,98.5,98.5,98.5,98.3,98.4,97.1,98,98.3,98.4,98.3,98.2,98.3,"2017-10-01","2021-02-01"]
["Yaskawa Solectria Solar","PVI 50TL-480 [480V]","N","Y","Y","Y","Y","Y*","Y","50 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc",50,480,98.5,"CSA Group","[7/6/2017];[03/19/2019]","[V5.00];[V01.09.00]","2018-10-15","[03/19/2019]","2020-08-11","Intertek","2020-03-20","2020-08-11","Formerly \"Solectria Renewables, LLC\"","Y","N",0.88,null,null,480,730,850,5,10,15,25,37.5,50,95.6,96.8,97.5,97.9,97.8,97.7,97.6,98,98.6,98.8,98.8,98.7,98.6,98.7,97.7,98.5,98.6,98.7,98.6,98.5,98.6,"2017-10-01","2020-08-11"]
["Yaskawa Solectria Solar","PVI 60TL-480 [480V]","N","Y","Y","Y","Y","Y*","Y","60 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc",60,480,98.5,"CSA Group","[7/6/2017];[03/19/2019]","[V5.00];[V01.09.00]","2018-10-15","[03/19/2019]","2020-08-11","Intertek","2020-03-20","2020-08-11","Formerly\"Solectria Renewables, LLC\"","Y","N",0.88,null,null,540,730,850,6,12,18,30,45,60,96.5,97.5,97.9,98.1,97.9,97.7,97.9,98.2,98.7,98.8,98.8,98.7,98.5,98.7,98,98.6,98.7,98.7,98.5,98.4,98.5,"2017-10-01","2020-08-11"]
["Yaskawa Solectria Solar","XGI 1500-125/125 [600V]","N","Y","Y","Y","Y","Y*","Y","125 KW, 125KVA, 600 Vac, 3-phase Grid Support Utility Interactive Inverter  ",124.6175583,600,98.5,"Intertek","[05/13/2019]","[3.0.0]","2019-06-03","[05/13/2019]","2020-07-21","Intertek","2020-03-20","2020-07-21",null,"N","N",3.8421052630000001,null,null,860,1050,1250,12.46175583,24.92351167,37.385267499999998,62.308779170000001,93.463168749999994,124.6175583,98.421599999999998,98.869799999999998,98.943399999999997,98.894400000000005,98.806200000000004,98.720399999999998,98.824691999999999,97.0398,98.3964,98.441999999999993,98.546199999999999,98.506399999999999,98.452200000000005,98.440156000000002,95.852199999999996,97.525599999999997,98.153400000000005,98.242800000000003,98.248999999999995,98.262200000000007,98.104844,"2019-06-03","2020-07-21"]
["Yaskawa Solectria Solar","XGI 1500-125/150 [600V]","N","Y","Y","Y","Y","Y*","Y","125 KW, 150KVA, 600 Vac, 3-phase Grid Support Utility Interactive Inverter\r\n",124.6175583,600,98.5,"Intertek","[05/13/2019]","[3.0.0]","2019-06-03","[05/13/2019]","2020-07-21","Intertek","2020-03-20","2020-07-21",null,"N","N",3.8421052630000001,null,null,860,1050,1250,12.46175583,24.92351167,37.385267499999998,62.308779170000001,93.463168749999994,124.6175583,98.421599999999998,98.869799999999998,98.943399999999997,98.894400000000005,98.806200000000004,98.720399999999998,98.824691999999999,97.0398,98.3964,98.441999999999993,98.546199999999999,98.506399999999999,98.452200000000005,98.440156000000002,95.852199999999996,97.525599999999997,98.153400000000005,98.242800000000003,98.248999999999995,98.262200000000007,98.104844,"2019-06-03","2020-07-21"]
["Yaskawa Solectria Solar","XGI 1500-150/166 [600V]","N","Y","Y","Y","Y","Y*","Y","150 KW, 166KVA, 600 Vac, 3-phase Grid Support Utility Interactive Inverter",150,600,98.5,"Intertek","[05/13/2019]","[3.0.0]","2019-06-03","[05/13/2019]","2020-07-21","Intertek","2020-03-20","2020-07-21",null,"N","N",2.75,null,null,860,1100,1250,15,30,45,75,112.5,150,98.468800000000002,98.933199999999999,98.986199999999997,98.887200000000007,98.808800000000005,98.718000000000004,98.834631999999999,98.194800000000001,98.229799999999997,98.505399999999995,98.542400000000001,98.497600000000006,98.38,98.476562000000001,98.259600000000006,98.259600000000006,98.278599999999997,98.368399999999994,98.298000000000002,98.177999999999997,98.301000000000002,"2019-06-03","2020-07-21"]
["Yaskawa Solectria Solar","XGI 1500-166/166 [600V]","N","Y","Y","Y","Y","Y*","Y","166 KW, 166KVA, 600 Vac, 3-phase Grid Support Utility Interactive Inverter ",165.13934,600,98.5,"Intertek","[05/13/2019]","[3.0.0]","2019-06-03","[05/13/2019]","2020-07-21","Intertek","2020-03-20","2020-07-21",null,"N","N",3.8421052630000001,null,null,860,1050,1250,16.513933999999999,33.027867999999998,49.541801999999997,82.569670000000002,123.854505,165.13934,98.551599999999993,99.010800000000003,99.026600000000002,98.872200000000007,98.7684,98.602599999999995,98.816339999999997,97.598799999999997,98.605800000000002,98.669799999999995,98.588800000000006,98.488600000000005,98.306600000000003,98.492553999999998,96.512,97.893600000000006,98.131600000000006,98.269000000000005,98.183400000000006,98.080799999999996,98.108683999999997,"2019-06-03","2020-07-21"]
["Yaskawa Solectria Solar","SGI 500XTM [380V]","N","Y","N","N","N","N","N","500 kW, 1000 Vdc, 380 Vac, 3-Phase Grid Support Utility Interactive Inverter",507,380,96.5,"Intertek","[01/09/2018]","[D003  Checksum- D9E00BD0]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data is inclusive of three Phase transformer from the CSA C82.2 table with transformer efficiency of 98.8%.","N","N",88.78,null,null,545,615,820,50.7,101.4,152.1,253.5,380.25,507,93.6,96.1,96.7,97.1,97.2,97.1,96.9,93.2,95.8,96.5,96.9,97,97,96.7,92.1,95.3,96.1,96.6,96.8,96.8,96.4,"2018-02-15"]
["Yaskawa Solectria Solar","SGI 750XTM [380V]","N","Y","N","N","N","N","N","750 kW, 1000 Vdc, 380Vac, 3-Phase Grid Support Utility Interactive Inverter",753.2,380,96.5,"Intertek","[01/09/2018]","[D003  Checksum- D9E00BD0]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data is inclusive of three Phase transformer from the CSA C82.2 table with transformer efficiency of 98.8%.","N","N",122.55,null,null,545,615,820,75.319999999999993,150.63999999999999,225.96,376.6,564.9,753.2,94,96.2,96.7,97,97,96.9,96.8,93.7,96.2,96.7,97.1,97.1,97,96.9,91.9,95.3,96.2,96.7,96.7,96.8,96.4,"2018-02-15"]

{"sheet":"Battery_Inverters","index":1,"n_rows":232,"n_cols":60,"rows_kept":232,"cut":false,"hidden":false,"merged":[]}
["Grid Support Battery Inverter List (Full Data)"]
["Data has not changed since October 21, 2021"]
["This list contains an extensive amount of equipment information. If you require any assistance, please reach out to us at SolarEquipment@energy.ca.gov or 916-654-4120."]
["Inverter List Notes"]
["This row is intentionally left blank."]
["% Equipment is in the process of being removed from the list of eligible equipment pursuant to Appendix A, Section B, of the Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1) at:  "]
["Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1)"]
["(1) Any text in brackets at the end of the Model Number is not part of the Manufacturer's Model Number.  Part of the text in brackets indicates the specified voltage option for that model number, if provided; models with multiple voltage options will have multiple row entries, with one for each eligible option."]
["(2) Hybrid inverters are capable of taking DC power input from both a solar system and an energy storage system. These models are listed on both the solar and battery inverter lists to reflect the dual functionality. Refer to the manufacturer's documentation for more information on the exact functionality and limitations."]
["(3) RPP: UL 1741 SA13 tested with reactive power priority enabled (when operating at apparent power capacity, inverter will reduce active power as needed to ensure curve-required reactive power is provided)"]
["(4) A Y* notes the inverter has not been certified according to CSIP, but instead NRTL reported inverter was connected to a gateway during compatibility testing."]
["(5) The listed Firmware Version is the version used during the inverter's UL 1741 Supplement SA (SA8-SA13) testing and certified on the listed Certificate Date; multiple firmware versions may be listed for a single certificate date if all are required to comply with Supplement SA. Multiple certificate dates with different firmware versions may be listed if new firmware versions were certified under Supplement SA and reported by the manufacturer. Additional firmware versions may be certified but not reported. Check with NRTL for the most current information."]
["(6) Inverter CSIP conformance information refers to the entity responsible for the documentation provided to the manufacturer. If the inverter is certified to CSIP, then the information refers to the certifying entity and the certificate date. Otherwise, the information refers to the NRTL that issued the compatibility report and the date of the report."]
["Blue colored text indicates that the model number occurs multiple times on the list under different manufacturer names."]
["Manufacturer Name","Model Number1","Hybrid Inverter2","UL 1741 Supplement SA Testing","UL 1741 SA13 Volt-Var","UL 1741 SA\nFreq-Watt\nVolt-Watt","UL 1741 SA\nDisable Permit Service\nLimit Active Power","Common Smart Inverter Profile Conformance","Monitor Key Data\nScheduling","Description","Maximum Continuous Output Power at Unity Power Factor","Nominal Voltage","Weighted Efficiency","UL 1741 Supplement SA \nCertification (SA8-SA13)5",null,null,"UL 1741 SA13  Volt-Var","UL 1741 SA\nFreq-Watt\nVolt-Watt","UL 1741 SA\nDisable Permit Service\nLimit Active Power","Inverter CSIP Conformance6",null,"Monitor Key Data\nScheduling\nAttestation","Notes","Built-In Meter","Microinverter","Night Tare Loss","Power Rating, Continuous, 40 deg C","Night\nTare Loss, 40 deg C","Voltage Minimum","Voltage Nominal","Voltage Maximum","Power Level","Power Level","Power Level","Power Level","Power Level","Power Level","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vmin,","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vnom","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Efficiency @Vmax","Grid Support Listing Date","Last Update"]
[null,null,"PV and Battery","SA8-SA13","RPP3","SA14-SA15","SA17-SA18","CSIP4","Attestation",null,"(kW)","(Vac)","(%)","Certifying Entity","Certificate Date [mo/day/yr]","Firmware Version(s) Tested","Listing Date (mo/day/yr)","Certificate Date [mo/day/yr]","Listing Date (mo/day/yr)","Issuing Entity","Document Date (mo/day/yr)","Listing Date",null,null,null,"(W)","(kW)","(W)","(Vdc)","(Vdc)","(Vdc)","10% (kW)","20% (kW)","30% (kW)","50% (kW)","75% (kW)","100% (kW)","10% Pwr Lvl (%)","20% Pwr Lvl (%)","30% Pwr Lvl (%)","50% Pwr Lvl (%)","75% Pwr Lvl (%)","100% Pwr Lvl (%)","Wtd (%)","10% Pwr Lvl (%)","20% Pwr Lvl (%)","30% Pwr Lvl (%)","50% Pwr Lvl (%)","75% Pwr Lvl (%)","100% Pwr Lvl (%)","Wtd (%)","10% Pwr Lvl (%)","20% Pwr Lvl (%)","30% Pwr Lvl (%)","50% Pwr Lvl (%)","75% Pwr Lvl (%)","100% Pwr Lvl (%)","Wtd (%)"]
["BYD Auto Industry Company Limited","BEG60KTL-U-R1 [480V]","N","Y","Y","Y","N","N","N","60 kVA, 480 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter",60.276000000000003,480,95.5,"CSA Group","[06/17/2019]","[4.0]","2019-12-11","[06/17/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 6 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",98,null,null,750,850,950,6.0276000000000005,12.055200000000001,18.082799999999999,30.138000000000002,45.207000000000001,60.276000000000003,92.263877618214693,95.092454594879612,95.942067621391487,96.374153135355002,96.219940794387412,95.952632048118147,95.990998330895337,91.64347702244784,94.652932894143404,95.552648411714628,96.040657998094431,95.949118638076357,95.657344012050473,95.669141793393663,91.217879656652897,94.373499874530822,95.317484017490955,95.825891278353566,95.75815891917216,95.462206965876248,95.45386000600088,"2019-12-11"]
["BYD Auto Industry Company Limited","BEG500KTL-U [480V]","N","Y","Y","Y","N","N","N","500 kVA, 480 Vac, Grid Support Utility Interactive Battery Inverter, permanently connected, bi-directional for use with battery management system",501.75599999999997,480,96,"CSA Group","[01/31/2019]","[V002.18]","2019-06-17","[01/31/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 5 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",2,null,null,780,890,1000,50.175600000000003,100.35120000000001,150.52679999999998,250.87799999999999,376.31700000000001,501.75599999999997,90.958029972476254,94.532188562498717,95.735257919064097,96.397146690091319,96.492303944580257,96.358663157741589,96.055416630745484,90.550616532879019,94.242556358693463,95.383548684652467,96.175725324137147,96.270715930184949,96.117643261110658,95.806442245530476,89.914552634073303,93.847654625541466,95.078591746021019,95.94973301357517,96.07268995674913,95.902819861870213,95.561506449183867,"2019-06-17"]
["BYD Auto Industry Company Limited","BEG500KTL-U/01 [480V]","N","Y","Y","Y","N","N","N","500 kVA, 480 Vac, Grid Support Utility Interactive Battery Inverter, permanently connected, bi-directional for use with battery management system. This model does not have protective cover for cooling fans.",501.75599999999997,480,96,"CSA Group","[01/31/2019]","[V002.18]","2019-06-17","[01/31/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 5 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",2,null,null,780,890,1000,50.175600000000003,100.35120000000001,150.52679999999998,250.87799999999999,376.31700000000001,501.75599999999997,90.958029972476254,94.532188562498717,95.735257919064097,96.397146690091319,96.492303944580257,96.358663157741589,96.055416630745484,90.550616532879019,94.242556358693463,95.383548684652467,96.175725324137147,96.270715930184949,96.117643261110658,95.806442245530476,89.914552634073303,93.847654625541466,95.078591746021019,95.94973301357517,96.07268995674913,95.902819861870213,95.561506449183867,"2019-06-17"]
["CE+T Energy Solutions Inc.","30C [480V]","N","Y","Y","Y","N","N","N","30 kW, 480 Vac Grid Support Utility Interactive Battery Charge controller",29.99,480,95,"UL","[10/31/2018];[10/31/2018];[10/31/2018];[10/31/2018];[03/22/2019]","[3.2.42];[3.2.60];[3.2.90];[3.2.91];[3.2.106]","2018-10-15","[03/22/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Formerly Ideal Power Inc. 30C [480V]","N","N",56.8,null,null,550,700,850,3,6,9,15,22.49,29.99,92.7,94.3,94.8,95.2,95.1,94.8,94.9,92.2,94.2,94.6,95.3,95.4,95.5,95.1,89.6,92.8,93.3,94.8,95.2,95.4,94.6,"2018-02-01","2020-03-11"]
["CE+T Energy Solutions Inc.","30C3 [480V]","Y","Y","Y","Y","N","N","N","30 kW, 480 Vac Grid Support Utility Interactive Battery Charge controller with additional Photovoltaic input",29.99,480,95,"UL","[10/31/2018];[10/31/2018];[10/31/2018];[10/31/2018];[03/22/2019]","[3.2.42];[3.2.60];[3.2.90];[3.2.91];[3.2.106]","2018-10-15","[03/22/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Formerly Ideal Power Inc. 30C3 [480V]","N","N",56.8,null,null,550,700,850,3,6,9,15,22.49,29.99,92.7,94.3,94.8,95.2,95.1,94.8,94.9,92.2,94.2,94.6,95.3,95.4,95.5,95.1,89.6,92.8,93.3,94.8,95.2,95.4,94.6,"2018-02-01","2020-03-11"]
["Chint Power Systems America","CPS ECB30KTL-O/US [480V]","N","Y","Y","Y","Y","Y*","Y","30 kW, 480 Vac, Bi-directional Grid Support Utility Interactive Battery Inverter",30.26,480,97,"CSA Group","[01/29/2019]","[1.01.00]","2019-05-01","[01/29/2019]","2020-09-01","CSA Group","2020-07-21","2020-09-01",null,"N","N",20,null,null,450,660,800,3.0260000000000002,6.0520000000000005,9.0779999999999994,15.13,22.695,30.26,94.650549450549448,96.014145313854698,96.064140587128364,96.638393035728811,96.725422757237041,96.610667520072766,96.503496089012444,94.958847736625515,96.639455782312936,97.06512226512227,97.26634431964176,97.306673196986623,97.205048552911052,97.13686289956857,96.046130952380935,97.482087912087906,97.708787218591155,98.011066617712572,97.951717272274763,97.797109100820805,97.827593698996878,"2019-05-01","2020-09-01"]
["Chint Power Systems America","CPS ECB62.5KTL-M/US-480 [480V]","N","Y","Y","Y","Y","Y*","Y","62.5 kVA, 1000 Vdc, 480 Vac, 3-phase, Bi-directional Transformerless Grid Support Utility Interactive Battery Inverter",62.552,480,97.5,"CSA Group","[09/29/2020]","[1.02.00]","2020-11-12","[09/29/2020]","2020-11-12","CSA Group","2020-09-30","2020-11-12",null,"N","N",6.1,null,null,750,925,1100,6.2552000000000003,12.510400000000001,18.765599999999999,31.276,46.914000000000001,62.552,97.346515825250776,97.992136863574174,98.094953563750565,98.116532263671346,97.976211060128321,97.754133457869003,97.984432213971246,95.968490133276774,97.316111612598391,97.571984442117326,97.717492171733213,97.602474719538264,97.357614842011387,97.531049018534901,94.564370480075084,96.473040084755922,97.0909889252288,97.270714939770031,97.194974164137221,96.964707005761142,97.045567289100745,"2020-11-12"]
["Chint Power Systems America","CPS ECB125KTL-M/US-480 [480V]","N","Y","Y","Y","Y","Y*","Y","125 kVA, 1000 Vdc, 480 Vac, 3-phase, Bi-directional Transformerless Grid Support Utility Interactive Battery Inverter",125.188,480,97.5,"CSA Group","[09/29/2020]","[1.02.00]","2020-11-12","[09/29/2020]","2020-11-12","CSA Group","2020-09-30","2020-11-12",null,"N","N",5.8,null,null,750,925,1100,12.518800000000001,25.037600000000001,37.556399999999996,62.594000000000001,93.891000000000005,125.188,97.382682226495604,97.832246869955299,98.084409039795432,98.047906685281035,97.836792596046521,97.541906266365842,97.877704510465009,96.696778233550376,97.394668603677914,97.556210775649447,97.64742867305695,97.480947165519979,97.185239630307379,97.474473853186765,95.971547041268892,96.954896303779066,97.038254715271208,97.264035416809762,97.126936397787958,96.840528427031558,97.075947412381495,"2020-11-12"]
["Darfon Electronics Corp.","HB51xxxxxx [240V]","N","Y","Y","Y","Y","Y*","Y","5000 W, 240 Vac, Grid Support Utility Interactive Battery Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality.",4.665,240,90,"Intertek","[06/16/2019]","[DSP1: PV_Inverter Ver 5.2, DSP2: Charger\nVer33.8]","2019-08-01","[06/16/2019]","2020-09-11","Intertek","2020-09-02","2020-09-11",null,"N","N",0.60209999999999997,null,null,48,53,56.5,0.46648040000000002,0.93296080000000003,1.3994412000000001,2.3324020000000001,3.4986030000000001,4.6648040000000002,82.117947999999984,89.1570854,90.215769399999999,90.006299400000003,88.786562600000011,86.890373199999999,88.871184230000011,82.005393799999993,89.687109800000002,91.170325399999996,91.382553000000001,90.554287599999995,89.469502599999998,90.362593977999992,80.886379600000012,89.174117199999998,90.992482999999993,91.440130600000003,91.1443522,90.180666800000012,90.631226436000006,"2019-08-01","2020-12-21"]
["Darfon Electronics Corp.","H5001xxxxxx [240V]","Y","Y","Y","Y","Y","Y*","Y","5000 W, 240 Vac, Hybrid PV and Battery Grid Support Utility Interactive Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality.",4.8440000000000003,240,94.5,"Intertek","[07/28/2020]","[82,372]","2020-11-02","[07/28/2020]","2020-11-02","Intertek","2020-08-12","2020-11-02",null,"N","N",28.48,null,null,300,360,380,0.4844174,0.9688348,1.4532521999999999,2.4220869999999999,3.6331305,4.8441739999999998,86.673553799999993,92.816092799999979,94.3501902,95.2023346,95.057924999999983,94.444936200000001,94.525206941999997,87.1365476,93.167628599999986,94.647862400000008,95.485913400000001,95.379741600000003,94.801270200000005,94.844955193999994,87.172866200000001,93.194648799999996,94.652253000000002,95.484140800000006,95.349433199999993,94.771366400000005,94.830354931999992,"2020-11-02","2021-01-11"]
["Darfon Electronics Corp.","H5000xxxxxx [240V]","Y","Y","Y","Y","Y","Y*","Y","5000 W, 240 Vac, Hybrid PV and Battery Grid support Utility Interactive Inverter with PCS functionality, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality.",5.0739999999999998,240,95.5,"Intertek","[07/28/2020]","[82,372]","2018-10-15","[07/28/2020]","2020-09-11","Intertek","2020-09-02","2020-09-11",null,"N","N",0.43,null,null,300,360,380,0.50800000000000001,1.016,1.524,2.54,3.81,5.0759999999999996,89.228338400000013,93.736259799999999,94.907423600000001,95.751822599999997,95.886322399999997,95.612956999999994,95.353118825999999,89.489125199999989,93.948561799999993,95.256629000000004,95.913850999999994,96.033797399999997,95.885842800000006,95.54190204999999,89.3176694,94.004821399999997,95.202498000000006,95.947675400000008,96.0160956,95.91960379999999,95.530770297999993,"2018-03-15","2021-01-11"]
["Delta Electronics","E4-TL-US [208V]","Y","Y","Y","Y","Y","Y*","Y","3328 W, 208 Vac, transformerless, Bi-directional, Multi-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",3.36,208,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2020-08-11","[07/07/2020]","2020-08-11","CSA Group","2020-05-27","2020-08-11",null,"Y","N",1.21,null,null,200,380,480,0.33598600000000001,0.67197200000000001,1.0079579999999999,1.6799299999999999,2.519895,3.3598599999999998,92.7057619047619,95.315952380952382,96.079380952380944,96.937476190476204,97.260999999999996,97.257904761904769,96.771649047619036,94.671571428571426,96.743333333333325,97.430952380952377,97.883190476190478,97.934238095238101,97.830571428571417,97.667888571428577,93.533380952380966,96.078619047619057,96.919190476190479,97.56452380952382,97.760333333333321,97.674666666666681,97.360829047619063,"2020-08-11"]
["Delta Electronics","E4-TL-US(AC) [208V]","N","Y","Y","Y","Y","Y*","Y","3328 W, 208 Vac Transformerless Grid Support Utility Interactive Energy Storagy Inverter",3.3639999999999999,208,98,"CSA Group","[07/07/2020]","[1.5.4]","2020-08-11","[07/07/2020]","2020-08-11","CSA Group","2020-05-27","2020-08-11",null,"Y","N",1.23,null,null,350,400,480,0.33643800000000001,0.67287600000000003,1.009314,1.6821900000000001,2.523285,3.3643800000000001,95.428619047619051,97.272047619047626,97.882142857142853,98.253999999999991,98.314809523809501,98.197238095238077,98.076655238095213,94.814285714285717,96.932857142857159,97.615857142857152,98.097095238095221,98.197619047619042,98.116190476190482,97.90405476190476,93.918380952380957,96.387095238095228,97.172761904761913,97.798190476190484,97.993047619047616,97.933999999999997,97.607456666666664,"2020-08-11"]
["Delta Electronics","E4-TL-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3840 W, 240 Vac, transformerless, Bi-directional, Multi-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",3.87,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2020-08-11","[07/07/2020]","2020-08-11","CSA Group","2020-05-27","2020-08-11",null,"Y","N",1.27,null,null,200,380,400,0.38695799999999997,0.77391599999999994,1.1608739999999997,1.9347899999999998,2.9021849999999998,3.8695799999999996,92.857285714285709,95.303238095238086,96.081619047619043,97.007952380952389,97.343285714285713,97.360904761904749,96.840904285714288,95.302476190476199,97.104857142857128,97.726142857142847,98.093285714285713,98.142904761904759,98.111380952380941,97.915377619047632,94.284999999999997,96.453619047619028,97.277333333333345,97.860761904761901,98.00376190476193,97.944809523809525,97.657355238095249,"2020-08-11"]
["Delta Electronics","E4-TL-US(AC) [240V]","N","Y","Y","Y","Y","Y*","Y","3840 W, 240 Vac Transformerless Grid Support Utility Interactive Energy Storage Inverter",3.8879999999999999,240,98.5,"CSA Group","[07/07/2020]","[1.5.4]","2020-08-11","[07/07/2020]","2020-08-11","CSA Group","2020-05-27","2020-08-11",null,"Y","N",1.28,null,null,350,400,480,0.38875600000000005,0.77751200000000009,1.1662680000000001,1.9437800000000001,2.91567,3.8875600000000001,95.948095238095235,97.614428571428576,98.153047619047612,98.406714285714287,98.614619047619044,98.392380952380947,98.347788095238087,95.475714285714275,97.349761904761905,97.976619047619039,98.371571428571443,98.711952380952383,98.517714285714291,98.344961428571438,94.657047619047631,96.799285714285716,97.543000000000006,98.103571428571414,98.616,98.425190476190465,98.120895714285709,"2020-08-11"]
["Delta Electronics","E6-TL-US [208V]","Y","Y","Y","Y","Y","Y*","Y","4992 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",4.992,208,97,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.86,null,null,200,380,480,0.49920000000000003,0.99840000000000007,1.4976,2.496,3.7439999999999998,4.992,94.001552279710452,95.64854413845292,96.470502310715119,97.031778029948327,96.98839431139308,96.678915967705834,96.733417745109648,95.696002839548186,97.220439644049392,97.652205765380231,97.83623139070302,97.667061705813495,97.349085557061244,97.583732361611879,94.631669734067614,96.516985505297939,97.173540834476398,97.541628657333121,97.47105873269301,97.173936814249188,97.274040951844484,"2018-08-01","2020-08-11"]
["Delta Electronics","E6-TL-US(AC) [208V]","N","Y","Y","Y","Y","Y*","Y","5000 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter",5,208,98,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.85,null,null,350,400,480,0.5,1,1.5,2.5,3.75,5,96.357619047619053,97.710380952380973,98.120142857142852,98.208238095238102,98.033666666666676,97.687619047619037,97.980195238095249,95.697428571428574,97.377047619047616,97.868190476190492,98.05714285714285,97.920047619047622,97.611000000000004,97.811107619047618,94.798285714285726,96.77690476190476,97.453619047619057,97.765047619047621,97.721095238095231,97.430952380952377,97.519599047619039,"2018-08-01","2020-08-11"]
["Delta Electronics","E6-TL-US(AC) [240V]","N","Y","Y","Y","Y","Y*","Y","5000 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter",5,240,98,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",2.0499999999999998,null,null,350,400,480,0.5,1,1.5,2.5,3.75,5,96.480904761904767,97.584571428571422,98.116714285714281,98.473571428571418,98.323761904761909,97.935095238095229,98.200269047619059,95.893809523809523,97.550809523809534,98.008380952380961,98.450666666666663,98.350333333333339,98.123761904761906,98.18080333333333,94.871809523809517,96.934095238095253,97.58580952380953,98.19490476190478,98.167285714285725,97.967238095238102,97.899827619047642,"2018-08-01","2020-08-11"]
["Delta Electronics","E6-TL-US [240V]","Y","Y","Y","Y","Y","Y*","Y","5760 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",5.76,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",2.25,null,null,200,380,480,0.57599999999999996,1.1519999999999999,1.728,2.88,4.32,5.76,93.963625969438439,95.732446384706193,96.532807684212585,97.118348653429621,97.062377987109016,96.774553568769321,96.805745508944824,96.257434448555912,97.61499418821316,97.981948161933175,98.081440619035661,97.680440613673383,97.626730315988667,97.737953437828693,95.238569980658667,96.982509064759839,97.535664405666651,97.834209595941928,97.754794153662942,97.458502206940707,97.591098008080536,"2018-08-01","2020-08-11"]
["Delta Electronics","E8-TL-US(AC) [240V]","N","Y","Y","Y","Y","Y*","Y","6500 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter",6.4939999999999998,240,98,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",2.1,null,null,350,400,480,0.65,1.3,1.95,3.25,4.875,6.5,96.563999999999993,97.95338095238094,98.173095238095243,98.382476190476183,98.296190476190489,98.085619047619048,98.202582380952393,95.994095238095227,97.682761904761918,98.118190476190463,98.371190476190478,98.35938095238096,98.092285714285723,98.191120952380956,95.036000000000016,97.145571428571429,97.744428571428571,98.115476190476201,98.178190476190494,97.914095238095243,97.922445714285729,"2018-08-01","2020-08-11"]
["Delta Electronics","E8-TL-US(AC) [208V]","N","Y","Y","Y","Y","Y*","Y","6500 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter",6.5,208,98,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.91,null,null,350,400,480,0.65,1.3,1.95,3.25,4.875,6.5,96.526761904761912,97.805142857142854,98.160714285714292,98.27128571428571,98.070952380952363,97.744761904761887,98.032426190476187,95.993761904761897,97.540190476190475,97.940857142857141,98.143666666666647,97.973190476190467,97.653476190476198,97.888297619047606,95.077238095238087,96.976809523809521,97.571476190476204,97.884095238095242,97.770190476190464,97.46442857142857,97.607589523809523,"2018-08-01","2020-08-11"]
["Delta Electronics","E8-TL-US [208V]","Y","Y","Y","Y","Y","Y*","Y","6656 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter\n",6.6559999999999997,208,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.1499999999999999,null,null,270,380,480,0.66559999999999997,1.3311999999999999,1.9967999999999999,3.3279999999999998,4.992,6.6559999999999997,95.230826251614573,96.891036349418002,97.383516545836727,97.634333677831506,97.427625078509706,97.050617106357407,97.332189072308523,95.947578725965741,97.410382433977375,97.794550069017504,97.948730653616494,97.699721373214217,97.39175599472415,97.663441843818802,94.854996124491507,96.776328670410962,97.373903337051033,97.660373266831044,97.517427624777397,97.162060564850904,97.36890273435543,"2018-08-01","2020-08-11"]
["Delta Electronics","E8-TL-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",7.68,240,97.5,"CSA Group","[07/07/2020]","[1.5.4]","2018-10-15","[07/07/2020]","2020-03-11","CSA Group","2020-01-16","2020-03-11",null,"Y","N",1.19,null,null,270,380,480,0.76800000000000002,1.536,2.3039999999999998,3.84,5.76,7.68,95.220244762392653,96.786476523169469,97.360484342448359,97.661527866722594,97.514706743622483,97.063283332614333,97.376271330510363,96.557058272771911,97.768154171688977,98.091693567287209,98.164435292147104,97.997075218849318,97.640443280171482,97.956696708919409,95.553280568100988,97.213562614555073,97.733873018671247,97.947621890495725,97.848069433399232,97.50177995994143,97.714440510395107,"2018-08-01","2020-08-11"]
["Delta Electronics","E30-TL [277V]","Y","Y","Y","Y","N","N","N","30 kW, 277 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter",30.488,277,98,"CSA Group","[07/01/2019]","[Controller A: V1.1.3, Controller B: V1.1.1]","2019-08-01","[07/01/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1.59,null,null,515,750,830,3.048756,6.097512,9.1462679999999992,15.243779999999999,22.865669999999998,30.487559999999998,95.922154835817892,97.135291210035561,97.544908906393758,97.751463175700522,97.700984927947204,97.479578495437408,97.582348026182757,97.446064997289312,98.320910511694706,98.555546035701482,98.626573936177579,98.580992908231693,98.464732043126773,98.523297019876921,96.972530703660837,98.105529055929964,98.382049606322511,98.480939986559989,98.451648843723589,98.316574438180396,98.366223639961746,"2019-08-01"]
["Delta Electronics","DES10JB125K01 [480V]","N","Y","Y","Y","Y","Y*","Y","125 kW, 480 Vac, 3-phase bi-directional Grid Support Utility Interactive Inverter",125,480,97,"CSA Group","[3/24/2020]","[1.1.8.4]","2018-10-15","[3/24/2020]","2020-05-11","CSA Group","2020-03-05","2020-05-11",null,"N","N",22.4,null,null,750,900,1000,12.5,25,37.5,62.5,93.75,125,95.730999999999995,97.198189999999997,97.548190000000005,97.647239999999996,97.441190000000006,97.214240000000004,97.4054,93.804569999999998,96.323999999999998,96.933099999999996,97.278049999999993,97.268619999999999,97.116900000000001,97.036959999999993,92.311189999999996,95.662189999999995,96.477620000000002,96.970429999999993,97.034760000000006,96.800430000000006,96.685109999999995,"2017-11-01","2020-05-11"]
["Delta Electronics","PCS125 [480V]","N","Y","Y","Y","Y","Y*","Y","125 kW, 480 Vac, 3-phase bi-directional Grid Support Utility Interactive Inverter",125,480,97,"CSA Group","[3/24/2020]","[1.1.8.4]","2018-10-15","[3/24/2020]","2020-05-11","CSA Group","2020-03-05","2020-05-11",null,"N","N",22.4,null,null,750,900,1000,12.5,25,37.5,62.5,93.75,125,95.730999999999995,97.198189999999997,97.548190000000005,97.647239999999996,97.441190000000006,97.214240000000004,97.4054,93.804569999999998,96.323999999999998,96.933099999999996,97.278049999999993,97.268619999999999,97.116900000000001,97.036959999999993,92.311189999999996,95.662189999999995,96.477620000000002,96.970429999999993,97.034760000000006,96.800430000000006,96.685109999999995,"2020-05-11"]
["Delta Electronics","DWE2100-US [480V]","N","Y","Y","Y","Y","Y*","Y","2100 kW, 480 Vac Bi-directional, Multi-Mode Grid Support Utility Interactive Battery Inverter",1887.74,480,96.5,"CSA Group","[04/13/2020]","[V01.02]","2021-01-21","[04/13/2020]","2021-03-01","CSA Group","2021-01-22","2021-03-01","Efficiency data inclusive of transformer effect based on a 2100 kVA medium voltage transformer where suitability is to be determined in the end application.","N","N",18.253,null,null,760,900,1200,188.774,377.548,566.322,943.87,1415.8050000000001,1887.74,93.78,96.05,96.72,97.12,97.15,96.97,96.9,92.72,95.43,96.24,96.74,96.83,96.68,96.5,90.39,94.23,95.23,95.96,96.14,96.03,95.66,"2021-01-21","2021-03-01"]
["Delta Electronics","DWE2800-US [480V]","N","Y","Y","Y","Y","Y*","Y","2800 kW, 480 Vac Bi-directional, Multi-Mode Grid Support Utility Interactive Battery Inverter",2513.3879999999999,480,96,"CSA Group","[04/13/2020]","[V01.02]","2020-11-02","[04/13/2020]","2021-03-01","CSA Group","2021-01-22","2021-03-01","Efficiency data inclusive of transformer effect based on a 2800 kVA medium voltage transformer where suitability is to be determined in the end application.","N","N",1114,null,null,760,900,1200,251.33879999999999,502.67759999999998,754.01639999999998,1256.694,1885.0409999999999,2513.3879999999999,93.927829556293958,95.520627718572783,96.405199922360225,96.89505801904761,96.920301038424554,96.670040935839339,96.650992340020608,92.903993541605814,94.731356044510989,95.801259057970995,96.4366208,96.54931098483766,96.37858779910448,96.190633210765498,90.696598418166701,93.408080751697852,94.759110377846767,95.669848266666662,95.864784253257554,95.739807090094999,95.355355364384423,"2020-11-02","2021-03-01"]
["DYNAPOWER COMPANY LLC","MPS-100 [480V]","N","Y","N","Y","N","N","N","100 kVA, 3-phase, 4-quadrant, bidirectional, 350-600VDC, 422-528VAC Grid Support Utility Interactive Battery Inverter with optional standalone mode. Inclusive of internal isolation transformer.",98.861000000000004,480,93,"Intertek","[12/06/2017]","[251.25]","No Information Submitted","[12/06/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",803.97,null,null,350,475,600,9.8861000000000008,19.772200000000002,29.658300000000001,49.430500000000002,74.145750000000007,98.861000000000004,81.549729106029986,89.974538943904108,92.764837199052181,95.055380945060605,95.953827167765624,96.267397566741934,94.523024851038272,76.874045814495673,87.524622336294613,90.726104555513842,93.685847560399708,95.08111701541732,95.578909890744185,93.184290996448553,73.017968946607908,84.96456393307723,89.04085254118921,92.381166211031143,94.006967161842141,94.6159056750584,91.808382043306679,"2018-06-15"]
["DYNAPOWER COMPANY LLC","MPS-250 [480V]","N","Y","Y","Y","N","N","N","250 kVA, 3-phase, 4-quadrant, bidirectional, 350-600 VDC, 422-528 VAC Grid Support Utility Interactive Battery Inverter with optional standalone mode. Inclusive of internal isolation transformer.",248.91,480,95,"Intertek","[12/06/2017];[12/06/2017]","[V251.125];[251.25]","2018-10-15","[12/06/2017];[12/06/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1638.5,null,null,350,475,600,24.890999999999998,49.781199999999998,74.671800000000005,124.453,186.68,248.90600000000001,89.1,93.5,95,95.9,96,95.8,95.4,87.1,92.3,94.1,95.3,95.6,95.3,94.8,85.6,91.1,93,94.5,94.9,94.6,94,"2018-02-15","2018-10-15"]
["DYNAPOWER COMPANY LLC","MPS-250HV [480V]","N","Y","N","Y","N","N","N","250 kVA, 3-phase, 4-quadrant, bidirectional, 580-835VDC, 422-528VAC Grid Support Utility Interactive Battery Inverter with optional standalone mode. Inclusive of internal isolation transformer.",249.619,480,95.5,"Intertek","[12/06/2017]","[252.01]","No Information Submitted","[12/06/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",437.7,null,null,580,705,830,24.9619,49.9238,74.8857,124.8095,187.21424999999999,249.619,89.162466516547994,93.277754264854138,94.943555359960015,96.635173224369893,96.507332319035953,96.498078452399824,95.890789445926558,87.144291364515993,92.741010595800759,94.160585089985801,95.689372013838948,96.324363830329986,96.198182836470266,95.378682489973556,86.216690625126006,91.839437084992426,93.700243580581926,95.085162831933602,95.787663326950479,95.881905115268637,94.814109722677742,"2018-06-15"]
["DYNAPOWER COMPANY LLC","CPS-1500 Gen4 [480V]","N","Y","Y","Y","N","N","N","1200 kW, 480Vac Grid Support Utility Interactive Battery Inverter",1199.6400000000001,480,96.5,"Intertek","[08/31/2020]","[1500.01.27]","2020-10-21","[08/31/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",438.5,null,null,740,1000,1500,119.96400000000001,239.92800000000003,359.892,599.82000000000005,899.73,1199.6400000000001,95.147498334416795,96.626382668199156,97.079259863348213,97.001149634156008,96.684037495935385,96.161173848590266,96.707570238836439,95.008868875902834,96.244392988598548,97.038467222619744,96.873920585897096,96.630029611511205,96.166427960493465,96.622950886344412,95.053968193125485,95.947722522669906,97.16667743603594,96.682406035865029,95.759271749570985,96.135797289759665,96.122055305475087,"2020-10-21"]
["DYNAPOWER COMPANY LLC","CPS-1500 Gen4 [600V]","N","Y","Y","Y","N","N","N","1500 kW, 600Vac Grid Support Utility Interactive Battery Inverter",1498.66,600,97,"Intertek","[08/31/2020]","[1500.01.27]","2020-10-21","[08/31/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1241,null,null,900,1200,1500,149.86600000000001,299.73200000000003,449.59800000000001,749.33,1123.9950000000001,1498.66,93.951580230959209,95.149459179892204,98.052992384574097,97.385983904368572,97.351594799610012,97.083990126769621,97.183496624431058,93.452986966797837,94.826834212068519,98.42382887039507,97.407643663413211,97.374520817332353,97.049556830677403,97.206899697759525,93.069485370096771,94.545601311233114,98.619431482396053,97.46061605586965,97.388074382633874,96.977872654059155,97.215693685484581,"2020-10-21"]
["Enphase Energy Inc.","IQ8X-BAT-US [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 V, Grid Support Utility Interactive Microinverter for use in Enphase's storage system\n",0.318,240,96.5,"UL","[11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021]","[v01.30.01];[v01.31.1];[V3.11.01];[V3.19.02]","2020-07-01","[11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021]","2020-07-01","UL","2020-06-11","2020-07-01","IQ8X-BAT-US is for use in Enphase Energy's energy storage product named Encharge in either an individual unit configuration (ENCHARGE-3-1P-NA), or as a trio of units (ENCHARGE-10-1P-NA). Model IQ8X-BAT-US is not intended for use with other third-party battery sources.","N","Y",2.4E-2,null,null,52.5,63,73.5,3.1775700000000004E-2,6.3551400000000008E-2,9.5327099999999998E-2,0.15887850000000001,0.23831774999999999,0.31775700000000001,88.119417075870004,93.971195188609983,96.154642328820003,97.399731335270005,97.482785964320001,97.200778418989984,96.741752584369493,87.771172329920006,93.412248920110002,95.687283421530012,97.199513583160012,97.436784551840006,97.264230302620007,96.580538529855701,87.069369141780001,92.80864764447999,95.292927229559993,96.995783221129997,97.30870907744,97.175219555569996,96.359849680701416,"2020-07-01","2021-10-11"]
["Enphase Energy Inc.","IQ8X-BAT-US-NB [240V]","N","Y","Y ","Y ","Y ","Y*","Y","315 VA, 240 V, Grid Support Utility Interactive Microinverter for use in Enphase's energy storage system\n\n",0.318,240,96.5,"UL","[06/11/2020];[11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021]","[v01.27.01];[v01.30.01];[v01.31.1];[V3.11.01];[V3.19.02]","2021-01-21","[06/11/2020];[11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021]","2021-01-21","UL","2020-12-14","2021-01-21","IQ8X-BAT-US-NB is for use in Enphase Energy's energy storage product named Encharge in either an individual unit configuration (ENCHARGE-3T-1P-NA), or as a trio of units (ENCHARGE-10T-1P-NA). Model IQ8X-BAT-US-NB is not intended for use with other third-party battery sources.","N","Y",2.4E-2,null,null,52.5,63,73.5,3.1775700000000004E-2,6.3551400000000008E-2,9.5327099999999998E-2,0.15887850000000001,0.23831774999999999,0.31775700000000001,88.119417075870004,93.971195188609983,96.154642328820003,97.399731335270005,97.482785964320001,97.200778418989984,96.741752584369493,87.771172329920006,93.412248920110002,95.687283421530012,97.199513583160012,97.436784551840006,97.264230302620007,96.580538529855701,87.069369141780001,92.80864764447999,95.292927229559993,96.995783221129997,97.30870907744,97.175219555569996,96.359849680701416,"2021-01-21","2021-10-11"]
["EPC Power Corp.","HY LC12/6-7 [480V]","Y","Y","Y","Y","N","N","N","220 kVA, 480 Vac, 3 phase Grid Support Utility Interactive Hybrid Inverter with PV MPPT and DC input",220.03299999999999,480,96,"TUV Rheinland of North America","[09/25/2018]","[042C314]","2019-01-15","[09/25/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",19.2,null,null,455,475,600,22.003332999999998,44.006665999999996,66.009998999999993,110.01666499999999,165.02499749999998,220.03332999999998,95.015714285714282,96.159999999999982,96.411428571428573,96.357142857142861,96.094285714285732,95.765714285714282,96.131257142857166,93.96142857142857,95.395714285714263,95.672857142857154,95.734285714285718,95.52428571428571,95.179999999999993,95.500057142857145,94.338571428571427,95.8,96.09714285714287,96.165714285714259,96.01428571428572,95.718571428571437,95.963499999999996,"2019-01-15"]
["EPC Power Corp.","50-100122 [480V]","N","Y","Y","Y","Y","N","N","250 kVA, 480Vac, 3 phase Grid Support Utility Interactive Battery Inverter",250.19,480,97,"TUV Rheinland of North America","[2/26/2019]","[8669C3F];[a501a47];[fe924e5]","2019-04-15","[2/26/2019]","2021-05-03","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",20,null,null,710,950,1250,25.018999999999998,50.037999999999997,75.057000000000002,125.095,187.643,250.19,94.8,96.79,97.38,97.66,97.6,97.44,97.42,94.12,96.48,97.08,97.37,97.29,97.04,97.1,92.55,95.64,96.52,96.95,96.97,96.78,96.66,"2019-04-15","2021-05-03"]
["EPC Power Corp.","50-100205 [480V]","N","Y","Y","Y","Y","N","N","250 kVA, 480Vac, 3 phase Grid Support Utility Interactive Battery Inverter",250.19,480,97,"TUV Rheinland of North America","[07/27/2020]","[a501a47];[fe924e5]","2021-05-03","[07/27/2020]","2021-05-03","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",20,null,null,710,950,1250,25.018999999999998,50.037999999999997,75.057000000000002,125.095,187.643,250.19,94.8,96.79,97.38,97.66,97.6,97.44,97.42,94.12,96.48,97.08,97.37,97.29,97.04,97.1,92.55,95.64,96.52,96.95,96.97,96.78,96.66,"2021-05-03"]
["EPC Power Corp.","50-100100 [208V]","N","Y ","Y ","Y ","Y ","N","N","450 kVA, 208Vac, 3 phase Grid Support Utility Interactive Battery Inverter",452.6,208,95.5,"TUV Rheinland of North America","[07/07/2021];[07/07/2021]","[a501a47];[fe924e5]","2021-08-02","[07/07/2021];[07/07/2021]","2021-08-02","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",0,null,null,400,700,1000,45.260000000000005,90.52000000000001,135.78,226.3,339.45000000000005,452.6,94.656800000000004,96.929400000000001,97.285799999999995,97.273200000000003,96.041200000000003,93.865799999999993,96.329536000000004,92.543599999999998,95.28240000000001,96.103999999999999,96.376200000000011,95.149000000000015,92.789199999999994,95.305776000000023,90.080800000000011,93.678799999999995,94.780599999999993,95.311800000000019,94.371000000000009,92.633400000000009,94.324622000000005,"2021-08-02"]
["EPC Power Corp.","50-100A-BCDEF-G [480V]","N","Y","Y","Y","N","N","N","500 kVA, 480 Vac, 3 phase, 3 wire, Bi-directional Grid Support Utility Interactive Battery Inverter, where A=099, B=61-64 or 81-84, C=A or B or D or Z, D=1-3, E=A or B, F=1 or 3, G=Re or EX or N.",499.13,480,97,"TUV Rheinland of North America","[03/21/2019]","[042c314]","2019-05-01","[03/21/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",20,null,null,710,950,1250,49.913000000000004,99.826000000000008,149.739,249.565,374.34749999999997,499.13,96.530252664758535,97.750141265774261,98.003014174261708,98.055295844503107,97.914563022140598,97.73542885739927,97.88218084274061,96.080763662093631,97.544849203203171,97.861813306303574,97.925566759494714,97.738743549342772,97.468819838194577,97.703234695955629,93.730818541709866,95.609575391984791,96.014955652044037,96.137758090238663,95.982042871958058,95.734372288891578,95.897636725045388,"2019-05-01"]
["EPC Power Corp.","50-100100 [480V]","N","Y ","Y ","Y ","Y ","N","N","1000 kVA, 480Vac, 3 phase Grid Support Utility Interactive Battery Inverter",1036.8399999999999,480,97.5,"TUV Rheinland of North America","[07/07/2021];[07/07/2021]","[a501a47];[fe924e5]","2021-08-02","[07/07/2021];[07/07/2021]","2021-08-02","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",0,null,null,750,1000,1250,103.684,207.36799999999999,311.05199999999996,518.41999999999996,777.62999999999988,1036.8399999999999,96.616599999999991,98.131799999999998,98.507400000000018,98.670600000000007,97.705799999999982,95.871399999999994,97.89061199999999,95.133999999999986,97.31,97.913600000000002,98.23960000000001,97.184200000000004,95.033800000000014,97.310124000000002,93.407799999999995,96.411599999999993,97.255600000000015,97.771800000000013,96.929600000000008,95.128999999999991,96.888779999999997,"2021-08-02"]
["EPC Power Corp.","50-100100 [690V]","N","Y ","Y ","Y ","Y ","N","N","1500 kVA, 690Vac, 3 phase Grid Support Utility Interactive Battery Inverter",1499.86,690,98,"TUV Rheinland of North America","[07/07/2021];[07/07/2021]","[a501a47];[fe924e5]","2021-08-02","[07/07/2021];[07/07/2021]","2021-08-02","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",0,null,null,1050,1150,1250,149.98599999999999,299.97199999999998,449.95799999999997,749.93,1124.895,1499.86,95.8536,98.143400000000014,98.634399999999999,98.878799999999998,98.005799999999994,96.358599999999996,98.102993999999995,95.738799999999998,97.789199999999994,98.384799999999998,98.73299999999999,97.908600000000007,96.281000000000006,97.964725999999999,95.638199999999998,97.677799999999991,98.260199999999998,98.587999999999994,97.756200000000007,96.174799999999991,97.823648000000006,"2021-08-02"]
["GE Renewable Energy","RIU-2500-U [550V]","Y","Y","Y","Y","N","N","N","2500 kVA, 550 Vac, Bi-directional, Grid Support Utility Interactive Hybrid Inverter",2507.194,550,97.5,"CSA Group","[11/01/2019]","[DSP_RIU-2500-U_V11_V1_A, LCD_RIU-2500-U_V1_A]   ","2020-03-23","[11/01/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 2500 kVA Medium-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",62.8,null,null,800,975,1500,250.71940000000001,501.43880000000001,752.15819999999997,1253.597,1880.3955000000001,2507.194,96.165587825617536,97.496024626913893,97.84611827224451,97.917731002770864,97.654712804724852,97.323989855524346,97.64887972690201,96.024564148543945,97.239077966047518,97.730826426636156,97.852050543793169,97.544402877512624,97.189977456983456,97.537598647567904,95.432639383368937,96.821878647291854,97.345753997551,97.466367294046691,97.19680752091476,96.942642988776186,97.169267254678914,"2020-03-23","2021-03-01"]
["Generac Power Systems","X7602 [240V]","Y","Y","Y","Y","Y","Y","Y","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS Functionality",7.5860000000000003,240,96.5,"Intertek","[10/09/2020]","[13430];[13590]","2020-02-03","[10/09/2020]","2020-03-23","SunSpec Alliance","2019-11-26","2020-02-03","Model number formerly listed as Pika Energy","N","N",1.2917000000000001,null,null,390,400,420,0.75900000000000001,1.5169999999999999,2.2759999999999998,3.7930000000000001,5.6890000000000001,7.5860000000000003,91.67,95.89,96.62,97.26,97.24,97.04,96.87,91.01,95.4,96.52,97.26,97.15,97.01,96.75,90.48,95.21,96.33,96.86,97.02,96.91,96.55,"2020-02-03","2021-04-01"]
["Generac Power Systems","XVT076A03 [240V]","Y","Y","Y","Y","Y","Y","Y","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS Functionality\n",7.8390000000000004,240,97,"Intertek","[10/09/2020]","[13430];[13590]","2020-10-01","[10/09/2020]","2020-10-01","SunSpec Alliance","2019-11-26","2020-10-01",null,"N","N",1.29,null,null,390,400,420,0.78386000000000011,1.5677200000000002,2.3515800000000002,3.9193000000000002,5.8789500000000006,7.8386000000000005,93.677571661912438,95.998695918204376,96.532584169437186,97.203606428872618,97.160321284506622,97.104690959587344,96.893909941550305,92.823435812878273,95.608312530903618,96.668103505003316,97.212868781288137,97.223080010698936,97.133748280222818,96.893147743412783,92.288725595479406,95.332004693618927,96.190215837424773,96.986588538568142,97.129959421275132,97.018910806982078,96.69798278571534,"2020-10-01","2021-04-01"]
["Generac Power Systems","X11402 [208V]","Y","Y","Y","Y","Y","Y","Y","11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS Functionality",11.18,208,97.5,"Intertek","[10/09/2020]","[13430];[13590]","2020-02-03","[10/09/2020]","2020-03-23","SunSpec Alliance","2019-11-26","2020-02-03","Model number formerly listed as Pika Energy","N","N",0.125,null,null,390,400,420,1.1180000000000001,2.2360000000000002,3.3540000000000001,5.59,8.3849999999999998,11.18,97.25,97.35,97.58,97.65,97.44,97.06,97.47,97.03,97.35,97.67,97.54,97.25,96.93,97.34,95.83,97.24,97.27,97.39,97.08,96.89,97.12,"2020-02-03","2021-04-01"]
["Generac Power Systems","XVT114G03 [208V]","Y","Y","Y","Y","Y","Y","Y","11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS Functionality",11.747999999999999,208,97,"Intertek","[10/09/2020]","[13430];[13590]","2020-10-01","[10/09/2020]","2020-10-01","SunSpec Alliance","2019-11-26","2020-10-01",null,"N","N",0.13,null,null,390,400,420,1.1747799999999999,2.3495599999999999,3.52434,5.8738999999999999,8.8108500000000003,11.7478,94.395211446168631,96.361356960371879,96.984363713293462,97.348791855457421,97.391308612260303,97.322335432679594,97.158756577238563,93.83751781107668,96.115972231046584,96.813462247015622,97.3002678881099,97.255554722173059,97.114925605882902,97.011161333186209,92.903509361520491,95.765877282912555,96.540038288330763,97.077104337918129,97.168018148504345,97.065836329336818,96.827772179343086,"2020-10-01","2021-04-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P5K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",5.0030000000000001,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,115,330,450,0.5,1.0009999999999999,1.5009999999999999,2.5009999999999999,3.7519999999999998,5.0030000000000001,95.12,96.18,96.94,97.37,97.18,96.63,97.03,95.66,97.24,97.42,97.55,97.7,96.96,97.49,95.38,96.75,97.61,97.82,97.85,97.71,97.65,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P6K-HVES-5G [240V]    ","Y","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",6.0039999999999996,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,130,330,450,0.6,1.2010000000000001,1.8009999999999999,3.0019999999999998,4.5030000000000001,6.0039999999999996,94.9,96.12,96.76,97.3,97.32,96.48,97.05,95.55,96.98,97.4,97.42,97.37,97.95,97.32,95.31,96.91,97.48,97.59,97.58,97.58,97.45,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P7K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",7.0060000000000002,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,160,330,450,0.70099999999999996,1.401,2.1019999999999999,3.5030000000000001,5.2539999999999996,7.0060000000000002,94.96,96.16,96.83,97.36,97.35,96.54,97.1,95.58,97.01,97.43,97.5,97.51,97.04,97.37,95.32,96.96,97.52,97.66,97.6,97.6,97.48,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P7.6K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",7.6029999999999998,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,175,330,450,0.76,1.5209999999999999,2.2810000000000001,3.8010000000000002,5.702,7.6029999999999998,95.05,96.16,96.89,97.34,97.15,96.58,97,95.63,97.18,97.48,97.78,97.35,97.9,97.4,95.36,96.75,97.61,97.82,97.85,97.71,97.66,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P8K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","8 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",8.0060000000000002,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,185,330,450,0.80100000000000005,1.601,2.4020000000000001,4.0030000000000001,6.0039999999999996,8.0060000000000002,95.12,96.18,96.94,97.37,97.18,96.63,97.03,95.66,97.24,97.42,97.55,97.7,96.96,97.49,95.38,96.75,97.61,97.82,97.85,97.71,97.65,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P9K-HVES-5G [240V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",9.0060000000000002,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,210,330,450,0.90100000000000002,1.8009999999999999,2.702,4.5030000000000001,6.7539999999999996,9.0060000000000002,95.14,96.75,97,97.49,97.37,97,97.21,95.72,97.27,97.45,97.61,97.75,97.11,97.55,95.58,96.74,97.66,97.82,97.82,97.71,97.65,"2020-04-13","2020-10-01"]
["Ginlong Technologies Co., Ltd.","RHI-1P10K-HVES-5G [240V]    ","Y","Y","Y","Y","Y","Y*","Y","10 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter   ",10.005000000000001,240,97.5,"CSA Group","[08/30/2019]","[18]","2020-04-13","[08/30/2019]","2020-10-01","CSA Group","2020-08-20","2020-04-13",null,"N","N",1,null,null,230,330,450,1,2.0009999999999999,3.0009999999999999,5.0019999999999998,7.5039999999999996,10.005000000000001,95.18,96.78,97.08,97.55,97.61,97.06,97.37,95.3,96.32,97.58,97.66,97.73,97.21,97.5,95.6,96.8,97.68,97.79,97.81,97.71,97.65,"2020-04-13","2020-10-01"]
["Go Electric Inc.","250-480-60-HLT [480V]","N","Y ","Y ","Y ","N","N","N","250 kW, 480 Vac Grid Support Multi-Mode Utility Interactive Inverter",259.2,480,93,"UL","[04/14/2021]","[V21.01.6.1]","2021-08-23","[04/14/2021]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted"," ","N","N",748.7,null,null,540,700,780,25.92,51.84,77.760000000000005,129.6,194.4,259.2,80.327142859999995,90.341428570000005,93.491428569999997,95.501428570000002,95.088571430000002,95.407142859999993,94.171728569999999,78.959999999999994,88.09,91.61,93.81,94.57,94.5,93.1,76.661428569999998,86.562857140000006,90.274285710000001,92.807142859999999,93.642857140000004,93.762857139999994,92.03587143,"2021-08-23"]
["Hanwha Q CELLS America Inc.","Q.HOME+ HYB-G1-6.0 [240V]","Y","Y","Y","Y","Y","Y*","Y","6.0 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",5.57,240,94,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2021-01-11","[10/23/2020]","2021-01-11","Intertek","2020-09-11","2021-01-11",null,"N","N",25,null,null,240,335,425,0.57500000000000007,1.1500000000000001,1.7249999999999999,2.875,4.3125,5.75,86.869682822533804,91.494323337741122,93.197507125817154,94.277347956539373,94.528577104512152,94.419480087783,93.852567275540324,86.534692544508331,91.719237390678572,93.532641876704261,94.760758659216464,95.116012615226765,95.142514472111017,94.339638324629973,85.944083659918661,91.055826867889806,93.119565276460762,94.55685225894733,95.055933937626449,95.188812247401856,94.160927096657588,"2021-01-11"]
["HANWHA Q CELLS AMERICA INC.","Q.HOME+ AC-G1-6.0 [240V]","N","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",5.7320000000000002,240,94,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2021-02-01","[10/23/2020]","2021-02-01","Intertek","2020-09-25","2021-02-01",null,"N","N",25,null,null,360,430,500,0.57320000000000004,1.1464000000000001,1.7196,2.8660000000000001,4.2990000000000004,5.7320000000000002,86.110434735585883,91.388494641122492,93.351087437054758,94.749762095940312,94.838108561535265,95.050604461357111,94.130150414755136,85.907427686004169,91.677523734783577,93.545896297167019,95.09320205514625,94.944898410684885,95.311789274125047,94.301638902789335,85.575624491941767,91.818698446692835,93.691816188753108,94.566832524118155,94.967972150718609,95.209424564294565,94.209509142823094,"2021-02-01"]
["Hanwha Q CELLS America Inc.","Q.HOME+ HYB-G1-7.0 [240V]","Y","Y","Y","Y","Y","Y*","Y","7.0 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",6.6660000000000004,240,94.5,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2021-01-11","[10/23/2020]","2021-01-11","Intertek","2020-09-11","2021-01-11",null,"N","N",25,null,null,290,360,425,0.66660000000000008,1.3332000000000002,1.9998,3.3330000000000002,4.9995000000000003,6.6660000000000004,88.19254532766071,92.480024599906656,93.864222646892841,94.728177374748682,94.859277550957373,94.661603922022621,94.31682430753466,87.895016741997523,92.552209013216427,93.98568096527471,94.939255036123782,95.145985429310571,95.084346217536066,94.540525982171076,87.188290385772305,91.840278359010497,93.665346252959509,94.812415113107377,95.188151694943144,95.183576013873704,94.438893456502669,"2021-01-11"]
["HANWHA Q CELLS AMERICA INC.","Q.HOME+ AC-G1-7.0 [240V]","N","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",6.68,240,95,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2021-02-01","[10/23/2020]","2021-02-01","Intertek","2020-09-25","2021-02-01",null,"N","N",25,null,null,280,390,500,0.66800000000000004,1.3360000000000001,2.004,3.34,5.01,6.68,88.292377200011984,93.483852175415123,94.882481845799276,95.530016091163603,95.113519083961407,94.475920679886698,94.787050045905389,88.563863096046475,92.576227224590028,94.65479402447454,95.55142668227154,95.427835917164501,95.233936899721115,94.934190652368585,87.563113100140896,92.158097577473129,94.261243287927726,95.392763954066183,95.226593134621183,94.673328104323886,94.658019794349954,"2021-02-01"]
["Hanwha Q CELLS America Inc.","Q.HOME+ HYB-G1-7.6 [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",7.6420000000000003,240,95.5,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2020-04-13","[10/23/2020]","2020-12-11","Intertek","2020-09-25","2020-10-12",null,"N","N",44,null,null,304,402,500,0.76415320000000009,1.5283064000000002,2.2924595999999999,3.8207660000000003,5.7311490000000003,7.6415320000000007,91.707418177902383,94.572943893510569,95.343208396678733,95.732834528334209,95.650063634275952,95.385614239539109,95.40583861848647,90.557349146015056,94.483695582739486,95.237254457268747,95.752187855671906,95.755162516040727,95.573013398331213,95.411795532959076,93.454639453611506,95.564299299611108,96.165924657149233,96.488739138122966,96.365110394539414,96.144925249431296,96.199701492566206,"2020-04-13","2020-12-11"]
["Hanwha Q CELLS America Inc.","Q.HOME+ AC-G1-7.6 [240V]","N","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",7.8319999999999999,240,95.5,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2020-04-13","[10/23/2020]","2020-12-11","Intertek","2020-09-25","2020-10-12",null,"N","N",49.5,null,null,320,375,430,0.78320560000000006,1.5664112000000001,2.3496167999999997,3.9160279999999998,5.8740419999999993,7.8320559999999997,91.431173544170591,94.962219303103637,95.624199158360184,95.75096782329237,95.440095960384738,94.975882487212104,95.320010032181145,92.295163238555702,94.869357976832788,95.609461165370504,95.935786658817605,95.741421969872519,95.332046361434294,95.564480928684176,92.761799110093776,95.061640260152643,95.714885238474494,95.902818050237826,95.763217781087064,95.436868928337617,95.61528086697129,"2020-04-13","2020-12-11"]
["Hanwha Q CELLS America Inc.","Q.HOME+ HYB-G1-8.6 [240V]","Y","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",8.6039999999999992,240,96,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2020-04-13","[10/23/2020]","2020-12-11","Intertek","2020-09-25","2020-10-12",null,"N","N",40,null,null,258,379,500,0.8604440000000001,1.7208880000000002,2.5813320000000002,4.3022200000000002,6.4533300000000002,8.6044400000000003,92.699334355597514,94.539928618718363,95.297824749048559,95.613611296666747,95.424147601271741,94.940413722572345,95.271386062148309,92.844051102514101,95.289415785898782,95.970144903059008,96.182450712551415,95.871598553910871,95.529337174346537,95.781378963688468,93.694083911121623,95.776806518196878,96.274499321609412,96.519408732377741,96.296844266964186,95.892164355116009,96.19055511399398,"2020-04-13","2020-12-11"]
["Hanwha Q CELLS America Inc.","Q.HOME+ AC-G1-8.6 [240V]","N","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",8.6129999999999995,240,95.5,"CSA Group","[10/23/2020]","[V1.07, V1.03]","2020-04-13","[10/23/2020]","2020-12-11","Intertek","2020-09-25","2020-10-12",null,"N","N",42,null,null,363,396.5,430,0.86129999999999995,1.7225999999999999,2.5838999999999999,4.3064999999999998,6.4597499999999997,8.6129999999999995,93.013508600881977,95.280549182880833,95.808820184682801,95.929597652810443,95.631206739051237,95.189392810224234,95.57085094463983,92.858426013211542,95.24742892388474,95.806799660978314,95.998886513281505,95.747373582335698,95.322727925739699,95.645535008754109,92.575709670533442,95.119762364187309,95.72335138420506,95.988280372552211,95.834603768861626,95.452411361897447,95.668318114962801,"2020-04-13","2020-12-11"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 610TL U B220 [220V]","Y","Y","Y","Y","N","N","N","610 kW, 220 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",610,220,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,440,590,740,61,122,183,305,457.5,610,97.11,98.06,98.25,98.17,97.74,97.1,97.85,96.37,97.64,98.01,97.9,97.48,96.73,97.56,95.53,97.29,97.68,97.72,97.45,96.53,97.41,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 830TL U B300 [300V]","Y","Y","Y","Y","N","N","N","830 kW, 300 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",830,300,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,440,590,740,83,166,249,415,622.5,830,97.21,98.13,98.27,98.16,97.74,97.18,97.86,96.5,97.77,97.96,97.92,97.55,97.06,97.62,95.7,97.41,97.7,97.66,97.36,96.88,97.38,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 915TL U B330 [330V]","Y","Y","Y","Y","N","N","N","915 kW, 330 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",915,330,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,485,613,740,91.5,183,274.5,457.5,686.25,915,97.17,98.13,98.33,98.22,97.86,97.27,97.95,96.5,97.84,98.09,98.05,97.69,97.15,97.75,95.82,97.49,97.82,97.81,97.51,97.17,97.53,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1000TL U B360 [360V]","Y","Y","Y","Y","N","N","N","1000 kW, 360 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1000,360,98,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,524,632,740,100,200,300,500,750,1000,97.34,98.14,98.33,98.21,97.83,97.31,97.94,96.84,97.92,98.13,98.08,97.7,97.09,97.78,96.36,97.64,97.97,97.94,97.55,96.97,97.61,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1140TL U B410 [410V]","Y","Y","Y","Y","N","N","N","1136 kVA, 410 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1027.752,410,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,595,668,800,102.7752,205.5504,308.32559999999995,513.87599999999998,770.81399999999996,1027.752,95.862485381251901,97.441697492401133,97.811332352904088,97.891168179619768,97.74411648135623,97.382896895342981,97.674616069824722,95.673585519005911,97.378077219658323,97.755703475534403,97.860554231371538,97.719335061881765,97.378124414474883,97.637401890916379,95.140003898891223,97.080090167707112,97.524003696301421,97.689736564126648,97.556122921873055,97.213022129275785,97.442726041420286,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1245TL U B480 [480V]","Y","Y","Y","Y","N","N","N","1247 kVA, 480 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1042.22,480,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,697,949,1200,104.22200000000001,208.44400000000002,312.666,521.11,781.66499999999996,1042.22,96.903698050438123,97.618814750297517,97.802986930357335,97.739491462227122,97.501507681732335,97.117409292811473,97.550409834201687,96.404674685259025,97.431021008596332,97.599251152283387,97.471936920226455,97.282213741029167,96.858978778224767,97.31127715101843,96.025957796716156,97.074663463996743,97.397898680593329,97.226770294224494,96.990291244472502,96.513792986680627,97.030685097431302,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1190TL U B430 [430V]","Y","Y","Y","Y","N","N","N","1192 kVA, 430 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1048.5940000000001,430,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,624,682,800,104.85940000000001,209.71880000000002,314.57819999999998,524.29700000000003,786.44550000000004,1048.5940000000001,96.004131167883529,97.481140832780383,97.837312964836116,97.923089297190614,97.789347637594915,97.413812385648953,97.717593463752465,95.869210079707514,97.430341823072879,97.796576602197305,97.903911963788389,97.781005512397059,97.450615230613408,97.698159882102303,95.382516161655985,97.183226707302126,97.593498616554569,97.741068874937696,97.649566841568571,97.317414469035342,97.531447429037911,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1220TL U B440 [440V]","Y","Y","Y","Y","N","N","N","1217 kVA, 440 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1099.306,440,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,638,689,800,109.93060000000001,219.86120000000003,329.79180000000002,549.65300000000002,824.47950000000003,1099.306,95.932010276324007,97.49265051753207,97.867964868192075,97.948666576433268,97.8105002896787,97.453652066344446,97.737536459010528,95.83631075130819,97.465193905098587,97.850931329649029,97.944192380988355,97.803900269609201,97.467666751246611,97.726554765327904,95.426130372969482,97.239481090374937,97.647783531418611,97.803695764929572,97.683236673332686,97.351408834240246,97.575215282421311,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1110TL U B400 [400V]","Y","Y","Y","Y","N","N","N","1110 kW, 400 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1110,400,98,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,580,660,740,111,222,333,555,832.5,1110,97.16,98.08,98.29,98.27,97.94,97.39,98,96.8,97.93,98.19,98.25,97.8,97.32,97.89,96.54,97.71,98.06,98.12,97.67,97.35,97.75,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1250TL U B450 [450V]","Y","Y","Y","Y","N","N","N","1247 kVA, 450 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1114.104,450,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,652,696,800,111.41040000000001,222.82080000000002,334.2312,557.05200000000002,835.57799999999997,1114.104,95.970642143925957,97.501616847126058,97.868762712731552,97.936366948280323,97.810266840204704,97.496823165386601,97.739077696357825,95.900121191315378,97.483655278990469,97.854994237938826,97.974343165614329,97.831573475816199,97.520426325602784,97.754154243396542,95.507328978243521,97.260350661207383,97.698182169906815,97.844321173743367,97.717172632052652,97.413248464368081,97.615163917271346,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1275TL U B460 [460V]","Y","Y","Y","Y","N","N","N","1275 kVA, 460 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1128.4760000000001,460,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",2550.2775000000001,null,null,666,703,800,112.84760000000001,225.69520000000003,338.5428,564.23800000000006,846.35700000000008,1128.4760000000001,95.99382220256561,97.507971055551451,97.861674580167048,97.970563015992951,97.844152982532691,97.627833420787141,97.771163375640441,95.888817550203342,97.482348805456581,97.870894574140294,97.991603253818624,97.86706263712847,97.559672152450915,97.779940979780349,95.542870550986734,97.320155042788016,97.733441007951882,97.912252424669219,97.763481981035881,97.490549414914128,97.666481425008357,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1165TL U B420 [420V]","Y","Y","Y","Y","N","N","N","1165 kW, 420 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1165,420,98,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",80,null,null,610,675,740,116.5,233,349.5,582.5,873.75,1165,97.28,98.08,98.28,98.26,98.01,97.47,98.04,96.99,97.92,98.18,98.24,97.91,97.53,97.95,96.74,97.75,98.03,98.15,97.85,97.42,97.87,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1740TL U B670 [670V]","Y","Y","Y","Y","N","N","N","1741 kVA, 670 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1272.412,670,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,962,1081,1200,127.24120000000001,254.48240000000001,381.72359999999998,636.20600000000002,954.30899999999997,1272.412,95.964557738299547,97.374808884374247,97.690183597413451,97.760353023553648,97.628674276890095,97.348016627916479,97.570417118534152,95.731305317544397,97.287881016192969,97.557286456785931,97.696974511284054,97.544160408187125,97.222955419255484,97.47643807299734,95.377827614865865,97.136475191779098,97.419043572372345,97.50595040476847,97.402036743097852,97.143998142972393,97.318751058860144,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1800TL U B690 [690V]","Y","Y","Y","Y","N","N","N","1793 kVA, 690 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1300.644,690,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,962,1081,1200,130.06440000000001,260.12880000000001,390.19319999999999,650.322,975.48299999999995,1300.644,96.671689964420295,97.66516992006899,97.878799533636567,97.902063780379663,97.7538343845995,97.399010071196059,97.734498159893917,96.472240657415441,97.596088832359982,97.804012362449711,97.827986624285316,97.677848526433479,97.335621108278545,97.655093516932169,96.333523362786579,97.514469835502524,97.708216936425416,97.734575890986818,97.562504003544106,97.257914519181156,97.549334243602317,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1665TL U B640 [640V]","Y","Y","Y","Y","N","N","N","1663 kVA, 640 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1367.076,640,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,919,1060,1200,136.70760000000001,273.41520000000003,410.12279999999998,683.53800000000001,1025.307,1367.076,96.249477763929832,97.442263685687166,97.720428241358945,97.755000523746432,97.618394959633193,97.312262443393948,97.580456244566648,95.97723736896917,97.314091902113276,97.590648097722578,97.669729930664502,97.506129753944407,97.192912859076884,97.464209559575082,95.515538943736459,97.14010892160556,97.406387717096251,97.452868370901456,97.342606406702743,97.037111326595536,97.274932849652814,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1690TL U B650 [650V]","Y","Y","Y","Y","N","N","N","1689 kVA, 650 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1375.2819999999999,650,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,933,1067,1200,137.5282,275.0564,412.58459999999997,687.64099999999996,1031.4614999999999,1375.2819999999999,96.288130060211245,97.505114184155389,97.775673492269448,97.818326185609266,97.661944150947051,97.358128241493759,97.630447041743125,96.000786646427244,97.401582473417079,97.663816807220741,97.740457877121727,97.573571682822731,97.250069712731133,97.531761238122598,95.667576566877756,97.262672977755344,97.541939152838466,97.557458698480445,97.423828212721602,97.085137641245751,97.370821571389115,"2019-05-01"]
["INGETEAM POWER TECHNOLOGY S.A.","INGECON SUN 1715TL U B660 [660V]","Y","Y","Y","Y","N","N","N","1715 kVA, 660 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications.",1390.614,660,97.5,"SGS","[5/5/2018]","ABK1000","2019-05-01","[5/5/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Overall efficiency includes Ingeteam transformer packaged with product.\nPer SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance.","N","N",459.07241666666664,null,null,948,1074,1200,139.06140000000002,278.12280000000004,417.18419999999998,695.30700000000002,1042.9605000000001,1390.614,96.062235468670153,97.403376404219202,97.686348745965319,97.753615279858352,97.622034950443336,97.339232986027454,97.569919470280212,95.841890787129174,97.270665199007212,97.550170030702319,97.700887549968797,97.538433991441593,97.230456630980342,97.47730852762632,95.364706922046778,97.109170250043064,97.400495619794086,97.525329846750523,97.403401392754972,97.086498890356509,97.316553214254895,"2019-05-01"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW5000H-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, Bi-directional Grid Support Utility Interactive PV and Battery Inverter\n",4.9889999999999999,240,95.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21","Efficiency data includes external Isolation transformer GW5000G-TF effect.","N","N",47.36,null,null,300,400,480,0.499,0.998,1.4970000000000001,2.4950000000000001,3.742,4.9889999999999999,87.29,92.59,94.36,95.51,95.76,95.68,95.04,88.08,93.35,94.82,95.82,96.09,96.05,95.42,87.62,93.17,94.65,95.74,96.09,96.02,95.36,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW5000A-BP [240V]","N","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter\n",5.0309999999999997,240,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",11.16,null,null,200,350,495,0.50309999999999999,1.0062,1.5092999999999999,2.5154999999999998,3.77325,5.0309999999999997,92.345481710328173,95.039117620281488,95.888032341337279,96.373996242390405,96.440975242815426,96.332082103020085,96.121199225132841,93.241271810267037,95.833999179591757,96.432537841588925,96.977591759724518,97.149667212950277,97.073771491227532,96.801561839348111,92.008329383185583,95.282711047121964,96.189368841715478,96.806494881079018,96.957672151712913,96.925439810870429,96.550395144667348,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW5000A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",5.0674999999999999,240,97.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",11.24,null,null,300,400,480,0.50675000000000003,1.0135000000000001,1.5202499999999999,2.5337499999999999,3.8006250000000001,5.0674999999999999,93.992476056920239,96.231582104991659,96.87969976945854,97.251681481939372,97.264304783943217,97.148369422310324,97.027195237674107,94.930731020114379,96.945902871292461,97.409766453632315,97.610278961161072,97.595850265342534,97.502117238035311,97.432761443182216,94.878227293429546,96.521480497356563,97.218071317052377,97.726646497952842,97.660705236860736,97.550888024748616,97.447685615995027,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW6000A-BP [240V]","N","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter\n",6.03,240,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",11.3,null,null,200,350,495,0.60300000000000009,1.2060000000000002,1.8089999999999999,3.0150000000000001,4.5225,6.03,93.177140627474131,95.286047258275076,96.056081515192133,96.419542839211061,96.346585846222311,96.134597716526159,96.136642150394238,93.972241383190891,96.630574060685646,96.63986315419298,97.039150660651416,97.077869867448726,96.91078836424478,96.862234023561939,93.571466933033676,95.706874626975932,96.474495974427327,96.887940090824856,96.910754849545953,96.805150976544979,96.654566963761255,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW6000A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",6.109,240,97.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.3000000000000007,null,null,360,400,480,0.6109,1.2218,1.8327,3.0545,4.5817499999999995,6.109,95.14283831972466,96.913830426935164,97.275137375470692,97.447186137333162,97.362356981640659,97.164551444090662,97.248607400506273,95.691697753666503,97.203139768646707,97.571283957447903,97.670891443681271,97.558718660861786,97.375615123802234,97.482167823092681,95.30478006405103,96.964657812904804,97.384951167238,97.593041379831604,97.486119591339204,97.319569027926988,97.374778757846599,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7000A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",7.0570000000000004,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.48,null,null,210,400,480,0.7057000000000001,1.4114000000000002,2.1171000000000002,3.5285000000000002,5.2927499999999998,7.0570000000000004,94.369339307317915,95.914408634886016,96.382125133264552,96.542539075369675,96.39475419219211,96.151942144376292,96.307099054937026,95.938380207142345,97.269437644857931,97.593466606285915,97.666041279987084,97.565094786802163,97.323216956127936,97.497752836891735,95.300635007015146,96.875512620957878,97.322855627787092,97.703348944915916,97.571113274784722,97.331880004510595,97.431531020956726,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7000A-BP [240V]","N","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter\n",7.0590000000000002,240,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.48,null,null,200,350,495,0.70590000000000008,1.4118000000000002,2.1177000000000001,3.5295000000000001,5.2942499999999999,7.0590000000000002,94.16242204907455,95.680825985460388,96.23871447284516,96.455606546714961,96.263211918481488,96.022878180189849,96.175507518592255,94.883737318106299,96.385581985131168,96.696760146136597,96.995519888411863,97.041140405511513,96.788893288505193,96.858548065430057,93.446082526072544,95.686493895996222,96.4108903738462,96.845230403282514,96.812454243773246,96.648844518073815,96.572016200497103,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7600A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",7.6440000000000001,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.44,null,null,230,400,480,0.76440000000000008,1.5288000000000002,2.2932000000000001,3.8220000000000001,5.7330000000000005,7.6440000000000001,94.86432445244229,96.149953043032909,96.525494022056179,96.684135072866653,96.444263220270798,96.198052414201712,96.4141604056517,96.219687597285059,97.362307295085614,97.653240048668309,97.681109246548189,97.529716382330108,97.260675494149226,97.502108073603424,95.620155916733026,97.011248908407268,97.397681606715153,97.588095450939136,97.44733372738483,97.197992135042753,97.363577001858815,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW7600A-BP [240V]","N","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter\n",7.6479999999999997,240,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.48,null,null,200,350,495,0.76480000000000004,1.5296000000000001,2.2944,3.8239999999999998,5.7359999999999998,7.6479999999999997,94.209068767242698,95.797098279589022,96.25024419945764,96.45075363743895,96.085974328890302,95.888423557906208,96.082892804673435,95.30282888799681,96.238798741698815,96.745570048713333,96.970228687039224,96.850808375131436,96.638116785640449,96.760103800830336,93.781862020374135,95.851470624208034,96.464066893417652,96.813732095281992,96.742982127188853,96.551997639698243,96.551800188639703,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW8600A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",8.6140000000000008,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.5399999999999991,null,null,260,400,480,0.86140000000000017,1.7228000000000003,2.5842000000000001,4.3070000000000004,6.4605000000000006,8.6140000000000008,95.373677152466954,96.487433823638668,96.788717049302946,96.874277196177204,96.597576834616589,96.306825604697224,96.609620036975826,96.49368114310478,97.470760932714583,97.660291531549063,97.644735792343837,97.423977151261667,97.105828723427095,97.447914118878046,95.859259081243209,97.154374622494856,97.450637203619138,97.500862861920851,97.320978717989959,97.012514180093632,97.29209118935151,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW8600A-BP [240V]","N","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter\n",8.68,240,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.4700000000000006,null,null,200,350,495,0.86799999999999999,1.736,2.6039999999999996,4.34,6.51,8.68,94.695823884932892,96.004282785400648,96.334304606163414,96.337077714653873,96.011528989815432,95.67957255522758,96.049038959847834,95.757271848345468,96.479971957972666,96.960511259795382,97.02247065181227,96.910557022443044,96.614847342631151,96.85760724891486,94.642227673948,96.076798825878086,96.460453126407018,96.739485079188881,96.756381284217341,96.508652994964805,96.586390020433768,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW9600H-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","9.6 kW, 240 Vac, Bi-directional Grid Support Utility Interactive PV and Battery Inverter\n",9.5190000000000001,240,95.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21","Efficiency data includes external Isolation transformer GW9600G-TF effect.","N","N",45.22,null,null,300,400,480,0.95190000000000008,1.9038000000000002,2.8557000000000001,4.7595000000000001,7.1392500000000005,9.5190000000000001,92.207175576489959,94.739802327575902,95.389898486524004,95.547136746174431,95.155745089088882,94.555175546089188,95.09726734903947,93.028476133424888,95.45290688904683,96.02106522502892,96.106223821347072,95.738404590589667,95.173183443465732,95.698632824461498,92.605062814602377,95.182922737469738,95.72324617626407,95.955750140480845,95.64133762082929,94.991757779862965,95.540342548142917,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW9600A-BP [240V]","N","Y","Y","Y","Y","Y*","Y","9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter\n",9.6159999999999997,240,96.5,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.5,null,null,200,350,495,0.96160000000000001,1.9232,2.8847999999999998,4.8079999999999998,7.2119999999999997,9.6159999999999997,95.01118779419798,96.103386379862386,96.334432770087602,96.288012914828968,95.860129747950822,95.40932924493508,95.962566703946322,95.704054199392104,96.634561525256473,96.9841977895356,96.950529762512389,96.768371962910024,96.40984787868716,96.765334763387045,95.050392249302021,96.149318156063416,96.56900501178707,96.70481762858256,96.693803982974359,96.40076291568225,96.573528157952552,"2021-01-21"]
["Jiangsu Goodwe Power Supply Technology Co., LTD.","GW9600A-ES [240V]","Y","Y","Y","Y","Y","Y*","Y","9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter\n",9.6280000000000001,240,97,"CSA Group","[11/17/2020]","[00]","2021-01-21","[11/17/2020]","2021-01-21","CSA Group","2020-11-17","2021-01-21",null,"N","N",9.4,null,null,300,400,480,0.9628000000000001,1.9256000000000002,2.8883999999999999,4.8140000000000001,7.2210000000000001,9.6280000000000001,95.836106427217857,96.812128332124203,97.058225171112923,97.004010072682675,96.702213766782762,96.332883575991772,96.760697284686287,96.713422078214379,97.537176705477236,97.658937512311681,97.575299819457413,97.311454063738651,96.952366395631614,97.377970155528971,96.153120452251898,97.274799052286099,97.521554719784405,97.445565134331602,97.19826040742511,96.836918305803579,97.232943946513643,"2021-01-21"]
["LG Electronics Inc.","A005KEEN261 [208V]","N","Y","Y","Y","Y","Y*","Y","5000 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter",5,208,98,"CSA Group","[08/30/2018]","[1.4.1]","2018-10-15","[08/30/2018]","2020-05-11","CSA Group","2020-03-26","2020-05-11",null,"Y","N",1.85,null,null,350,400,450,0.5,1,1.5,2.5,3.75,5,96.357619047619053,97.710380952380973,98.120142857142852,98.208238095238102,98.033666666666676,97.687619047619037,97.980195238095249,95.697428571428574,97.377047619047616,97.868190476190492,98.05714285714285,97.920047619047622,97.611000000000004,97.811107619047618,95.111952380952388,97.007428571428576,97.61,97.870047619047611,97.801380952380967,97.505333333333326,97.630758095238107,"2018-10-01","2020-05-11"]
["LG Electronics Inc.","A005KEEN261 [240V]","N","Y","Y","Y","Y","Y*","Y","5000 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode, Grid Support Utility Interactive Energy Storage Inverter",5,240,98,"CSA Group","[08/30/2018]","[1.4.1]","2018-10-15","[08/30/2018]","2020-05-11","CSA Group","2020-03-26","2020-05-11",null,"Y","N",2.0499999999999998,null,null,350,400,450,0.5,1,1.5,2.5,3.75,5,96.480904761904767,97.584571428571422,98.116714285714281,98.473571428571418,98.323761904761909,97.935095238095229,98.200269047619059,95.893809523809523,97.550809523809534,98.008380952380961,98.450666666666663,98.350333333333339,98.123761904761906,98.18080333333333,95.24404761904762,97.157571428571444,97.753095238095213,98.295190476190484,98.245285714285714,98.033333333333331,98.011670000000009,"2018-10-01","2020-05-11"]
["LG Electronics Inc.","D007KEEN261 [208V]","Y","Y","Y","Y","Y","Y*","Y","6656W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter\n",6.6559999999999997,208,97.5,"CSA Group","[08/30/2018]","[1.4.1]","2018-10-15","[08/30/2018]","2020-05-11","CSA Group","2020-03-26","2020-05-11",null,"Y","N",1.1499999999999999,null,null,270,380,450,0.66559999999999997,1.3311999999999999,1.9967999999999999,3.3279999999999998,4.992,6.6559999999999997,94.577142857142846,96.30147619047618,96.99633333333334,97.387761904761902,97.294809523809505,96.929047619047623,97.101850952380943,95.905285714285696,97.331380952380954,97.763285714285729,97.861904761904768,97.586190476190467,97.213761904761895,97.566743809523814,95.039238095238076,96.954095238095235,97.465952380952373,97.73076190476192,97.510285714285715,97.146190476190469,97.406409523809529,"2018-10-01","2020-05-11"]
["LG Electronics Inc.","D007KEEN261 [240V]","Y","Y","Y","Y","Y","Y*","Y","7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter",7.68,240,97.5,"CSA Group","[08/30/2018]","[1.4.1]","2018-10-15","[08/30/2018]","2020-05-11","CSA Group","2020-03-26","2020-05-11",null,"Y","N",1.19,null,null,270,380,450,0.76800000000000002,1.536,2.3039999999999998,3.84,5.76,7.68,95.141761904761907,96.556571428571417,97.332523809523806,97.597190476190477,97.510428571428591,97.13038095238096,97.345858095238114,96.495714285714271,97.678238095238086,98.032761904761898,98.064428571428579,97.776238095238099,97.431095238095239,97.794162857142865,95.768333333333331,97.321714285714293,97.81547619047619,97.95814285714286,97.747952380952384,97.447142857142879,97.684658095238092,"2018-10-01","2020-05-11"]
["LG Electronics Inc.","P250KH53231 [480V]","N","Y","Y ","Y ","Y ","Y ","N","250 kW, 480 Vac, Bi-directional, 3 phase Grid Support Utility Interactive Battery Inverter   ",250.42500000000001,480,97,"TUV Rheinland of North America","[06/03/2021]","[01.00]","2021-10-21","[06/03/2021]","2021-10-21","SunSpec Alliance","2020-07-03","No Information Submitted","Efficiency data inclusive of transformer effect based on 300 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016.","N","N",4.21,null,null,750,881,1000,25.042520000000003,50.085040000000006,75.127560000000003,125.21260000000001,187.81890000000001,250.42520000000002,95.428089189679142,96.527979327080573,96.94462689858976,97.241355839055501,97.314740998854319,97.290027813345972,97.138876608033712,94.907985328815698,96.201442200674464,96.618918005805227,96.972903415544991,97.074210045385286,97.049110599614593,96.866758255182361,94.318765028926549,95.864747556512356,96.350077563214256,96.737666189763218,96.865124023368068,96.815237319833756,96.622184784795422,"2021-10-21"]
["LS Energy Solutions LLC","PBE-6140-R61-1A0-1000 [600V]","N","Y ","Y ","Y ","Y ","Y*","Y ","140 kVA, 600 Vac, Bi-directional Grid Support Utility Interactive Energy Storage Inverter",139.44900000000001,600,98,"Intertek","[06/18/2021]","[2.0]","2020-08-11","[06/18/2021]","2021-08-02","Intertek","2021-07-08","2021-08-02",null,"N","N",1.58,null,null,900,1125,1350,13.944879999999998,27.889759999999995,41.834639999999993,69.724399999999989,104.58659999999998,139.44879999999998,97.403600000000012,98.308999999999997,98.491200000000006,98.718199999999996,98.613799999999998,98.532999999999987,98.553324000000003,96.71520000000001,97.898200000000003,98.225200000000001,98.348800000000011,98.378,98.281999999999996,98.258230000000012,96.023800000000008,97.379400000000004,97.74,98.045600000000007,98.09020000000001,98.003399999999985,97.916274000000016,"2020-08-11","2021-08-02"]
["LS Energy Solutions LLC","PBE-5140-R61-1A0-1000 [480V]","N","Y ","Y","Y ","Y","Y*","Y ","140 kVA, 480 Vac, Bi-directional Grid Support Utility Interactive Energy Storage Inverter",140.48500000000001,480,98,"Intertek","[06/18/2021]","[2.0]","2020-08-11","[06/18/2021]","2021-08-02","Intertek","2021-07-08","2021-08-02",null,"N","N",1.5,null,null,720,935,1150,14.048500000000002,28.097000000000005,42.145500000000006,70.242500000000007,105.36375000000001,140.48500000000001,97.5,98.365800000000007,98.443799999999996,98.520399999999995,98.446600000000004,98.336200000000005,98.414338000000001,96.596000000000004,97.653000000000006,97.981400000000022,98.155799999999999,98.094399999999993,97.997317141935412,98.006873857096778,95.591999999999999,97.128200000000007,97.616399999999999,97.777199999999993,97.809400000000011,97.621400000000008,97.647322000000003,"2020-08-11","2021-08-02"]
["NeoVolta Inc.","NV7600 [208V]","Y","Y ","Y ","Y ","Y ","Y*","Y ","7680 W, 208 Vac, 1-phase hybrid Grid Support Utility Interactive Inverter that works with PV and energy storage. Inverter is capable of PCS functionality.",7.4473000000000003,208,96.5,"SGS","[02/18/2019]","[Ver1585]","2019-03-15","[02/18/2019]","2020-08-11","CSA Group","2020-06-22","2020-08-11","The NV7600 inverter and batteries are components of the NV14 Energy Storage System.","N","N",13.4,null,null,240,370,425,0.74473167219999992,1.4894633443999998,2.2341950165999998,3.7236583609999996,5.5854875414999992,7.4473167219999992,91.486264550039337,94.760248969262392,95.352663162123591,97.296267712149941,97.185123619139432,96.859870192303077,96.623107857230082,91.699965357816623,94.963850615122325,95.495711668085661,97.428829723597843,97.231635305996946,96.929680695919046,96.714981534168942,91.907256517136105,94.928995056460167,95.369819427808693,97.318654328391062,96.925617369279323,97.063119550059341,96.527768937028625,"2019-03-15","2021-08-11"]
["NeoVolta Inc.","NV7600 [240V]","Y","Y ","Y ","Y ","Y ","Y*","Y ","7680W, 240 Vac, 1-phase hybrid Grid Support Utility Interactive Inverter that works with PV and energy storage. Inverter is capable of PCS functionality.",7.657,240,96.5,"SGS","[02/18/2019]","[Ver1585]","2019-03-15","[02/18/2019]","2020-08-11","CSA Group","2020-06-22","2020-08-11","The NV7600 inverter and batteries are components of the NV14 Energy Storage System.","N","N",13.4,null,null,240,370,425,0.76571188991999994,1.5314237798399999,2.2971356697599994,3.8285594495999993,5.7428391743999985,7.6571188991999986,91.819615795312856,94.910997776364283,95.520513772204296,97.079550873826477,96.988012087484861,97.130498991107089,96.527673212721126,91.670908997205146,95.000841359179049,95.707732171504404,97.546548492774008,97.445862228404309,97.08346102095264,96.887061504012152,91.551333333333318,95.071706716631525,95.858438563503356,97.600636400067273,97.273962762904389,97.086789328574284,96.824324671567467,"2019-03-15","2021-08-11"]
["OutBack Power Technologies, Inc.","FXR3048A [120V]","N","Y","Y","Y","N","N","N","2.5 kW, 120 VAC Grid Support Utility Interactive Inverter with external battery backup",2.56,120,91,"Intertek","[11/7/2017]","[001.006.063]","2018-10-15","[11/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0,null,null,40,52,60,0.26,0.51,0.77,1.28,1.92,2.56,83.7,90.2,92.2,93.3,92.6,91.6,92.2,79.8,87.1,90,92,92,91.2,91,77.3,85.1,88.1,90.6,91,90.7,89.7,"2017-12-15","2018-10-15"]
["OutBack Power Technologies, Inc.","VFXR3524A [120V]","N","Y","Y","Y","N","N","N","3 kW, 120 VAC Grid Support Utility Interactive Inverter with external battery backup",2.96,120,90.5,"Intertek","[11/7/2017]","[001.006.063]","2018-10-15","[11/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0,null,null,22,24,28,0.3,0.59,0.89,1.48,2.2200000000000002,2.96,88.3,91.9,92.9,93,91.3,88.7,91.6,87.2,90.8,92.1,92.1,91,88.6,91.1,83.7,87.1,89.1,90.6,90,87.8,89.5,"2017-12-15","2018-10-15"]
["OutBack Power Technologies, Inc.","VFXR3648A [120V]","N","Y","Y","Y","N","N","N","4 kW, 120 VAC Grid Support Utility Interactive Inverter with external battery backup",3.0369999999999999,120,91,"Intertek","[11/7/2017]","[001.006.063]","2018-10-15","[11/7/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",0,null,null,40,51.2,60,0.3,0.61,0.91,1.52,2.2799999999999998,3.04,88,92.2,93.5,94,93,91.2,92.9,82.2,88.5,90.7,91.8,91.6,89.7,90.9,80.3,86.1,87.9,90.3,90.4,88.3,89.4,"2017-12-15","2018-10-15"]
["OutBack Power Technologies, Inc.","GS4048A [240V]","N","Y","Y","Y","Y","Y*","Y","3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with external battery backup and accessible neutral to allow 120 VAC loads to be backed up. Inverter is capable of PCS functionality",3.6,240,92.5,"Intertek","[11/7/2017]","[001.006.063]","2018-10-15","[11/7/2017]","2020-10-01","PCTEST Engineering Laboratory","2020-01-24","2020-05-01",null,"Y","N",0.1,null,null,44,48,56,0.72,1.44,2.16,3.6,5.4,7.2,92.6,94.4,93.7,94.4,93,90.4,93.3,91.5,93.4,93,93.3,92.7,90.8,92.7,89,91.6,92.2,92.1,91.5,89.9,91.5,"2017-12-15","2020-12-01"]
["OutBack Power Technologies, Inc.","SBX5048-120/240 [240V]","Y","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac, Multimode Grid Support Utility Interactive PV and Battery Inverter with PCS Functionality",4.9850000000000003,240,94,"UL","[08/08/2018];[08/08/2018];[01/28/2021]","[NPC:0.0.0.2.2.0.9352,PBM:0.3.1.0.0.0.9359];[NPC:0.0.0.3.0.2.10015,PBM:0.3.1.0.0.6.10006];[NPC:0.0.0.3.0.2.10164,PMB:0.3.1.0.0.6.10482]","2019-04-02","[08/08/2018];[08/08/2018];[01/28/2021]","2021-03-11","SunSpec Alliance","2020-01-28","2020-03-23",null,"Y","N",24.85,null,null,250,420,550,0.5,1,1.5,2.5,3.75,5,85.911187999999996,91.878574,93.403974000000005,94.205962,94.083302000000003,93.775123999999991,93.575011380000007,87.041831999999999,92.430833999999976,94.191839999999999,94.897618000000008,95.095255999999992,94.894152000000005,94.479928839999985,85.362352000000001,91.925973999999997,93.509060000000005,94.477918000000003,94.741786000000005,94.617313999999993,94.016255040000004,"2018-09-17","2021-03-11"]
["OutBack Power Technologies, Inc.","GS8048A [240V]","N","Y","Y","Y","Y","Y*","Y","7.2 kW, 240 Vac Grid Support Utility Interactive Inverter with external battery backup and accessible neutral to allow 120 VAC loads to be backed up. Inverter is capable of PCS functionality",7.2,240,92.5,"Intertek","[11/7/2017]","[001.006.063]","2018-10-15","[11/7/2017]","2020-10-01","PCTEST Engineering Laboratory","2020-01-24","2020-04-21",null,"Y","N",0.1,null,null,44,48,56,0.36,0.72,1.08,1.8,2.7,3.6,88.3,92.6,94.1,94.4,93.2,91.2,93.3,87.1,91.5,92.9,93.3,93,90.8,92.6,84,89,90.9,92.1,91.9,90.2,91.3,"2017-12-15","2020-12-01"]
["Oztek Corp.","OZPCS-RS40-Fxx [208V]","N","Y","Y ","Y ","Y ","Y*","Y","40 kVA, 208V, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, where xx = 00 or 01",17.515000000000001,208,93,"Intertek","[08/18/2021]","[Rev 6.1.3.0]","2020-07-13","[08/18/2021]","2021-10-11","Intertek","2021-08-23","2021-10-11",null,"N","N",202.52,null,null,550,700,820,1.7515279999999998,3.5030559999999995,5.2545839999999986,8.7576399999999985,13.136459999999998,17.515279999999997,78.632704935698598,88.486143728950879,91.073441301536846,92.854710187675366,93.527011712238775,93.407443823303964,92.237605878123489,82.275499909116746,90.311628128179535,92.049339959677638,93.719784794606156,93.952815707870101,93.922191290180891,93.024778894482466,84.964725805771678,91.744414863118052,92.924960085290522,94.135424699986658,94.596104183489089,94.211423952444903,93.751750587490292,"2020-07-13","2021-10-11"]
["Oztek Corp.","OZPCS-RS40-Bxx [208V]","N","Y","Y ","Y ","Y ","Y*","Y","40 kVA, 208V, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, where xx = 00 or 01",17.515999999999998,208,93.5,"Intertek","[08/18/2021]","[Rev 6.1.3.0]","2020-07-13","[08/18/2021]","2021-10-11","Intertek","2021-08-23","2021-10-11",null,"N","N",191.36,null,null,550,700,820,1.7516179999999999,3.5032359999999998,5.254853999999999,8.7580899999999993,13.137134999999999,17.516179999999999,78.163075189908369,89.264672084612585,91.740996188420411,93.241553674418213,93.838165779200835,93.688622471168216,92.598061412600103,81.262496868937504,90.478475074863553,92.829772749496271,93.972124396877888,94.390770940832553,94.222280477125466,93.38636510428212,84.642502867675788,92.00105994231771,93.407294818962967,94.64925046286146,94.888381377088962,94.552633719316105,94.089444903122342,"2020-07-13","2021-10-11"]
["Oztek Corp.","OZPCS-RS40-Fxx [480V]","N","Y","Y ","Y ","Y ","Y*","Y","40 kVA, 480V, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, where xx = 00 or 01",39.893999999999998,480,96,"Intertek","[08/18/2021]","[Rev 6.1.3.0]","2020-07-13","[08/18/2021]","2021-10-11","Intertek","2021-08-23","2021-10-11",null,"N","N",1105.0999999999999,null,null,550,700,820,3.9894440000000007,7.9788880000000013,11.968332,19.947220000000002,29.920830000000002,39.894440000000003,88.297390492768656,93.884586673372354,95.109922792817827,96.135107625065075,96.320780345281008,96.206905288643441,95.68804713721228,90.255771963018191,94.572393482101276,96.031746031746039,96.67298633145667,96.794071843549148,96.867469879518069,96.308218777098176,91.316639858075717,95.037007412512637,96.347540948497596,97.071678833233165,97.179981128920986,97.012573665651402,96.70729211535803,"2020-07-13","2021-10-11"]
["Oztek Corp.","OZPCS-RS40-Bxx [480V]","N","Y","Y ","Y ","Y ","Y*","Y","40 kVA, 480V, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, where xx = 00 or 01",39.912999999999997,480,96.5,"Intertek","[08/18/2021]","[Rev 6.1.3.0]","2020-07-13","[08/18/2021]","2021-10-11","Intertek","2021-08-23","2021-10-11",null,"N","N",1066.26,null,null,550,700,820,3.991298,7.982596,11.973894,19.956489999999999,29.934734999999996,39.912979999999997,89.347096374471306,94.176960899973849,95.702765904408778,96.576346797346247,96.776545593183343,96.595614963719981,96.169446548522487,91.23966363890797,94.775720603882675,96.264902504317163,97.05188129576355,97.242828915879301,97.123657762830945,96.715938161936435,92.480197203405154,95.57226065239557,96.790757101551364,97.419230638556826,97.504168491101524,97.400362847207504,97.097977649683259,"2020-07-13","2021-10-11"]
["Pika Energy","X7602 [240V]","Y","Y","Y","Y","Y","Y","Y","7.6 kW, 240 Vac Grid Support Utility Interactive Inverter",7.5869999999999997,240,96.5,"Intertek","[11/11/2019]","[12982]","2018-10-15","[11/11/2019]","2020-03-23","SunSpec Alliance","2019-11-26","2020-03-23",null,"N","N",1.29,null,null,390,400,420,0.75900000000000001,1.5169999999999999,2.2759999999999998,3.7930000000000001,5.6890000000000001,7.5860000000000003,91.67,95.89,96.62,97.26,97.24,97.04,96.87,91.01,95.4,96.52,97.26,97.15,97.01,96.75,90.48,95.21,96.33,96.86,97.02,96.91,96.55,"2020-03-23"]
["Pika Energy","X11402 [208V]","Y","Y","Y","Y","Y","Y","Y","11.4 kW, 208 Vac Grid Support Utility Interactive Inverter",11.186999999999999,208,97.5,"Intertek","[11/11/2019]","[12982]","2018-10-15","[11/11/2019]","2020-03-23","SunSpec Alliance","2019-11-26","2020-03-23",null,"N","N",0.13,null,null,390,400,420,1.1200000000000001,2.2400000000000002,3.36,5.59,8.39,11.19,97.2,97.4,97.6,97.6,97.4,97.1,97.5,97,97.3,97.7,97.5,97.3,96.9,97.3,95.8,97.2,97.3,97.4,97.1,96.9,97.1,"2020-03-23"]
["POMCube Inc.","PNZ-10K1N2-NA0 [240V]","Y","Y","Y","Y","Y","Y","Y","10kW, 240 Vac Split Phase, Transformerless Grid Support Utility Interactive Hybrid Inverter for PV and Energy Storage Application   ",9.923,240,94,"Intertek","[04/14/2021]","[UPCS-PV/V10039, UPCS-DCAC/V32011, UPCS-ARM/V32030]","2021-03-22","[04/14/2021]","2021-05-21","SunSpec Alliance","2021-03-23","2021-05-21",null,"N","N",21.92,null,null,250,360,530,0.99226600000000009,1.9845320000000002,2.9767980000000001,4.9613300000000002,7.4419950000000004,9.9226600000000005,91.272774666419039,93.866547913879771,92.84659327012335,93.981799893497353,94.188233466226848,93.891807441863762,93.836361661593429,94.433006068625858,94.228691789218004,93.578985142743548,93.090516726080907,94.039130481670156,94.297421038478006,93.822851769021241,93.369742705303821,95.176365403486585,93.792771682156086,94.576490734167592,94.884428609312039,95.158111517001529,94.656456373205856,"2021-03-22","2021-05-21"]
["Power Electronics","FP3000K3 [600V]","N","Y","Y","Y","N","N","N","3300 kW, 600 Vac, Grid Support Utility Interactive Battery Inverter",3116.9690000000001,600,98,"MET","[6/25/2019]","[1.0.0]","2020-05-21","[6/25/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","The inverter is central control composed by 6 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 3000 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",442.59,null,null,849,940,1200,311.69690000000003,623.39380000000006,935.09059999999999,1558.4839999999999,2337.7269999999999,3116.9690000000001,96.022999999999996,97.720680000000002,98.125159999999994,98.385980000000004,98.265690000000006,98.053079999999994,98.146500000000003,95.945809999999994,97.634129999999999,98.044780000000003,98.281790000000001,98.15804,97.929209999999998,98.044309999999996,95.920240000000007,97.623360000000005,98.033320000000003,98.287629999999993,98.172309999999996,97.944379999999995,98.050920000000005,"2020-05-21"]
["Power Electronics","FP3510M3 [34500V]","N","Y","Y","Y","N","N","N","3630 kW, 34500 Vac, with Internal Meduim Voltage Transformer, Grid Support Utility Interactive Centeral Battery Inverter",3630.0639999999999,34500,97.5,"MET","[12/05/2019]","[1.0.0]","2021-04-01","[12/05/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","The inverter is central control composed by 6 modules. No differences between modules, they use the same components. The equipment incorporates internal Medium Voltage transformer in order to provide a output voltage of 34.5 kVac.","N","N",7640,null,null,934,1000,1200,363.00639999999999,726.01279999999997,1089.0192,1815.0319999999999,2722.5479999999998,3630.0639999999999,95.063749999999999,96.910162,97.52923100000001,97.790173874999994,97.754976999999997,96.984503750000002,97.54686533124999,95.001326250000005,96.823667749999984,97.432096999999999,97.655216375000009,97.63020487499999,96.842880750000006,97.426836137500004,94.996758624999998,96.769361374999988,97.407150624999986,97.703986375000014,97.623095750000005,97.026312375000003,"1900-04-06T10:28:41","2021-04-01"]
["Princeton Power Systems, Inc.","GTIB-480-30-WZZZZZZ-G1.3 [480V]","Y","Y","Y","Y","N","N","N","30 kVA, 480 Vac, 830Vdc, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank.\nCannot accept PV and Battery DC input simultaneously.",29.443999999999999,480,93.5,"TUV Rheinland of North America","[05/09/2019]","[V2.4.2]","2019-06-17","[05/09/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",35.14,null,null,540,750,830,2.9444320000000004,5.8888640000000008,8.8332960000000007,14.722160000000001,22.08324,29.444320000000001,86.763266666666667,92.620999999999995,93.103199999999987,93.816300000000012,93.242133333333328,92.085366666666658,92.997986666666677,87.648466666666664,93.265666666666675,93.530033333333321,94.116299999999995,93.404066666666665,92.92046666666667,93.307427666666669,88.606333333333325,92.492433333333324,94.669099999999986,94.546866666666659,93.654933333333332,93.047166666666669,93.673481999999993,"2019-06-17"]
["Princeton Power Systems, Inc.","GTIB-480-30-ZZZZZZ-G1.3 [480V]","Y","Y","Y","Y","N","N","N","30 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank (Z≠-W).\nCannot accept PV and Battery DC input simultaneously.",29.956,480,97,"TUV Rheinland of North America","[05/09/2019]","[V2.4.2]","2019-06-17","[05/09/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",46.3,null,null,540,750,830,2.9955659999999997,5.9911319999999995,8.9866979999999987,14.977829999999997,22.466744999999996,29.955659999999995,92.6541,95.119433333333333,96.076666666666668,96.846399999999988,96.976966666666669,96.853766666666658,96.569560333333314,93.775933333333342,95.241533333333322,96.501333333333349,97.176799999999986,97.375799999999998,97.398533333333333,96.979502666666676,92.794166666666655,94.885466666666673,96.3887,97.057933333333338,97.19076666666669,97.425100000000015,96.787211333333346,"2019-06-17"]
["Princeton Power Systems, Inc.","GTIB-480-125XXXXXX-G1.5 [480V]","Y","Y","Y","Y","N","N","N","125 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank.\nCannot accept PV and Battery DC input simultaneously.",124.964,480,96,"TUV Rheinland of North America","[05/07/2019]","[V2.72]","2019-06-17","[05/07/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",68,null,null,350,710,830,12.496400000000001,24.992800000000003,37.489199999999997,62.481999999999999,93.722999999999999,124.964,87.119633333333326,92.941333333333333,94.972333333333353,95.217933333333335,95.659266666666667,95.211466666666666,94.984282666666672,91.918933333333342,95.376133333333343,95.897933333333327,96.625766666666664,96.886533333333333,96.648966666666652,96.427037999999996,91.559566666666655,95.713033333333343,96.424533333333343,96.968400000000003,96.936033333333313,96.892933333333332,96.60308666666667,"2019-06-17"]
["Princeton Power Systems, Inc.","GTIB-480-125XXXXXX-W-G1.5 [480V]","Y","Y","Y","Y","N","N","N","125 kVA, 480 Vac, 830Vdc, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank.\nCannot accept PV and Battery DC input simultaneously.",124.964,480,94.5,"TUV Rheinland of North America","[05/07/2019]","[V2.7.2]","2019-06-17","[05/07/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Weighted Efficiency includes efficiency of 125 kVA Jefferson Electric 423-D7-13 distribution transformer.","N","N",68,null,null,350,710,830,12.496400000000001,24.992800000000003,37.489199999999997,62.481999999999999,93.722999999999999,124.964,84.93873851222223,91.649448799999988,93.842162566666687,94.017129396296298,94.157416179999998,93.224720728888883,93.549345273555573,89.617896035555574,94.050405080000004,94.756747926666662,95.407208387037045,95.365414760000007,94.632224895555538,94.968840675477765,89.267525514444444,94.382622170000019,95.27708138666668,95.745520733333336,95.414137609999983,94.871100791111118,95.142689222333331,"2019-06-17"]
["Rhombus Energy Solutions","BESI-50kW-480 [480V]","N","Y","Y","Y","N","N","N","50kW, 480 Vac, transformer-less, 3-phase, Multi-Mode Grid Support Utility Interactive Energy Storage Inverter",49.35,480,94,"UL","[06/29/2018]","[00021618]","2018-10-15","[06/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",103,null,null,550,636,840,4.9350000000000005,9.870000000000001,14.805,24.675000000000001,37.012500000000003,49.35,76.571428571428569,88,92,95.142857142857139,96,96,94.162857142857135,79,89,92,95,96,96,94.279999999999987,79,88.857142857142861,92,94,96,96,94.062857142857141,"2018-08-15","2018-10-15"]
["Rhombus Energy Solutions","BESS-50kW-480 [480V]","N","Y","Y","Y","N","N","N","50kW, 480 Vac, transformer-less, 3-phase, Grid Support Utility Interactive Energy Storage Inverter",49.35,480,94,"UL","[06/29/2018]","[00021618]","2018-10-15","[06/29/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",103,null,null,550,636,840,4.9350000000000005,9.870000000000001,14.805,24.675000000000001,37.012500000000003,49.35,76.571428571428569,88,92,95.142857142857139,96,96,94.162857142857135,79,89,92,95,96,96,94.279999999999987,79,88.857142857142861,92,94,96,96,94.062857142857141,"2018-08-15","2018-10-15"]
["Rhombus Energy Solutions","RES-BESS60DP-480 [480V]","Y","Y","Y","Y","N","N","N","60 kW, 480 Vac Grid Support Utility Interactive PV and Battery Inverter",59.789000000000001,480,91.5,"UL","[09/03/2020]","[00020520]","2020-12-11","[09/03/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"Y","N",92,null,null,270,441,870,5.9789000000000003,11.957800000000001,17.936699999999998,29.894500000000001,44.841750000000005,59.789000000000001,82.328000000000003,88.789999999999992,91.343999999999994,93.2,93.729000000000013,93.631999999999991,92.623870000000011,81.460000000000008,87.411999999999992,90.408000000000001,92.421999999999997,93.1,93,91.879580000000004,79.440000000000012,86.038000000000011,88.893999999999977,91.278000000000006,92.025999999999996,92.06,90.691940000000002,"2020-12-11"]
["Schneider Electric Solar Inc.","XW Pro 6848 NA [120V]","N","Y ","Y ","Y ","Y ","Y*","Y","5.75 kW, 120 Vac, Special Purpose Grid Support Utility Interactive Battery Inverter/Charger/Stand-alone",5.7469999999999999,120,93.5,"[09/18/2020];[02/26/2021];[04/29/2021];[09/22/2021]","[V1.09BN09];[V1.11BN0028];[V1.11.BN0034];[V1.11.BN0049]","[V1.09BN09];[V1.11BN0028];[V1.11.BN0034]","2020-10-21","[09/18/2020];[02/26/2021];[04/29/2021];[09/22/2021]","2020-10-21","CSA Group","2019-12-18","2020-10-21",null,"N","N",17.399999999999999,null,null,47,52,58,0.57472000000000001,1.14944,1.7241599999999997,2.8735999999999997,4.3103999999999996,5.7471999999999994,92.058228571428572,94.572252380952392,94.803371428571424,94.504709523809524,93.345985714285703,92.034847619047611,93.708450142857146,91.825633333333343,94.464190476190467,94.700004761904765,94.426780952380952,93.244957142857146,91.975800000000007,93.608476714285715,91.666414285714296,94.232328571428553,94.591942857142854,94.247395238095237,93.138904761904755,91.893900000000016,93.479573666666667,"2020-10-21","2021-10-21"]
["Schneider Electric Solar Inc.","XW Pro 6848 NA [240V]","N","Y","Y ","Y ","Y ","Y*","Y ","6 kW, 240 Vac, Special Purpose Grid Support Utility Interactive Battery Inverter/Charger/Stand-alone",6.0190000000000001,240,94,"[09/18/2020];[02/26/2021];[04/29/2021];[09/22/2021]","[V1.09BN09];[V1.11BN0028];[V1.11.BN0034];[V1.11.BN0049]","[V1.09BN09];[V1.11BN0028];[V1.11.BN0034]","2019-04-02","[09/18/2020];[02/26/2021];[04/29/2021];[09/22/2021]","2020-04-13","CSA Group","2019-12-18","2020-01-21",null,"N","N",0.37,null,null,47,52,58,0.60185420000000001,1.2037084,1.8055625999999996,3.0092709999999996,4.5139064999999992,6.0185419999999992,92.929090476190481,94.494871428571415,94.755495238095236,95.180023809523817,93.909014285714278,92.242271428571442,94.184262761904748,92.824519047619034,94.41605238095238,94.673285714285726,95.149952380952385,93.82244285714286,92.159390476190467,94.109931904761922,92.702952380952382,94.331723809523822,94.553947619047605,95.091347619047625,93.721723809523823,92.059433333333345,94.015846285714289,"2019-04-02","2021-10-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 3000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","2.626 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",2.6259999999999999,208,96.5,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,125,380,480,0.26258900000000002,0.52517800000000003,0.787767,1.312945,1.9694175,2.6258900000000001,91.293362527464552,93.708658559402892,95.218322148376544,95.899659413730078,95.835549926366809,95.664474879366807,95.47835976869996,93.582341629764059,95.347659750064892,96.904180719033917,97.228300990567604,97.399142736962418,97.087584880562389,97.033046441615284,92.503804000061209,95.685759532945383,96.430082390113469,96.877896438894567,96.849878019802546,96.962369311400792,96.578962091696582,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 3000TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","2.93 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",2.9340000000000002,240,93.5,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.29343648072000006,0.58687296144000012,0.88030944216000018,1.4671824036000003,2.2007736054000002,2.9343648072000006,83.549447597810484,88.741950658627019,91.518725765277352,93.46602653202423,94.377813212031768,94.573535741134791,93.138105889835714,82.953075358727844,88.977420340672026,91.283975058713153,94.78210464330374,95.760908276236748,95.949289159354137,94.176058857895256,81.248869880822056,86.999197545521113,91.728314598977363,93.615573761261004,94.948738388584474,95.588909967888654,93.368859758595249,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 3000TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","3.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",2.9990000000000001,208,93.5,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.29986100000000004,0.59972200000000009,0.89958300000000002,1.4993050000000001,2.2489575000000004,2.9986100000000002,83.293362527464552,88.708658559402892,91.218322148376544,93.399659413730078,94.335549926366809,94.664474879366807,93.058359768699987,83.582341629764059,88.347659750064892,91.904180719033917,94.228300990567604,95.399142736962418,95.887584880562358,93.933046441615275,82.503804000061209,87.685759532945383,91.430082390113469,93.877896438894567,94.849878019802546,95.762369311400803,93.42896209169659,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 3000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3.095 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",3.0950000000000002,240,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,125,380,480,0.30950900000000003,0.61901800000000007,0.9285270000000001,1.5475450000000002,2.3213175000000001,3.0950900000000003,92.549447597810484,94.741950658627019,95.518725765277352,96.46602653202423,96.377813212031768,96.173535741134771,96.048105889835725,94.953075358727858,96.977420340672026,97.283975058713153,97.78210464330374,97.760908276236748,97.449289159354137,97.541058857895266,93.248869880822056,95.999197545521113,96.728314598977363,97.215573761261027,97.348738388584479,97.388909967888651,97.016859758595231,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 3800TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","3.324 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",3.3239999999999998,208,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,160,380,480,0.33238499999999999,0.66476999999999997,0.9971549999999999,1.6619249999999999,2.4928874999999997,3.3238499999999997,91.755180590217549,94.427054546325252,95.624985137332857,96.396791893422602,96.371596058447253,96.236486896009197,95.998654720801156,92.840136706007556,95.733247132067817,97.329294782796779,97.290815806914082,97.774711172919311,97.472718032005659,97.305087341478782,92.871659181712658,95.766799085310566,96.778444876002226,97.495296333055563,97.588435399550463,97.467180675267372,97.185861732121083,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 3600TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","3.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",3.581,208,94,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.35810000000000003,0.71620000000000006,1.0743,1.7905,2.6857500000000001,3.581,84.955180590217552,90.427054546325252,92.82498513733286,93.796791893422608,94.571596058447255,94.4364868960092,93.600654720801174,85.040136706007544,90.733247132067817,93.429294782796759,94.4908158069141,95.774711172919311,96.272718032005656,94.567087341478782,82.371659181712658,88.966799085310569,92.978444876002229,94.295296333055546,95.78843539955048,95.66718067526736,94.253861732121095,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 3600TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","3.61 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",3.6080000000000001,240,94,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.36083600000000005,0.72167200000000009,1.082508,1.8041800000000001,2.70627,3.6083600000000002,84.922591470532467,90.049537139188644,92.907915460636232,93.787520478526631,94.431767346826717,94.456005695413168,93.515346650136493,84.868082954696078,90.930025652086897,93.856690289605723,94.561956933570571,95.558319826046343,95.97270963170358,94.506583380984452,82.497692670536821,88.98865673613679,92.293512624245835,94.468661270738565,94.738149356716107,95.614391367395442,93.654919652822215,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 3800TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3.888 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",3.8879999999999999,240,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,160,380,480,0.38882100000000003,0.77764200000000006,1.166463,1.944105,2.9161574999999997,3.8882099999999999,92.922591470532453,95.049537139188644,95.907915460636232,96.587520478526628,96.731767346826715,96.456005695413168,96.352346650136496,95.868082954696078,97.430025652086897,97.856690289605723,98.061956933570571,98.058319826046343,97.97270963170358,97.911583380984425,93.497692670536821,96.48865673613679,97.193512624245841,97.668661270738568,97.738149356716107,97.614391367395442,97.41991965282223,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 4000TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","3.99 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",3.988,240,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,180,380,480,0.39883600000000002,0.79767200000000005,1.1965079999999999,1.9941800000000001,2.9912700000000001,3.9883600000000001,86.922591470532453,91.049537139188644,92.907915460636232,94.587520478526628,95.131767346826706,95.156005695413171,94.219346650136472,86.568082954696095,92.230025652086908,94.356690289605723,95.661956933570565,96.258319826046346,96.172709631703597,95.311583380984445,84.497692670536821,91.088656736136798,93.393512624245858,95.168661270738568,96.138149356716127,96.014391367395433,94.880919652822229,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 4000TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",4.0039999999999996,208,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,150,380,480,0.40039999999999998,0.80079999999999996,1.2011999999999998,2.0019999999999998,3.0029999999999997,4.0039999999999996,86.755180590217549,91.427054546325252,93.124985137332857,94.396791893422602,94.971596058447261,95.236486896009197,94.136654720801147,86.840136706007556,92.133247132067822,94.329294782796779,95.690815806914117,96.174711172919316,96.172718032005662,95.276087341478785,84.871659181712658,91.266799085310566,93.578444876002223,95.195296333055552,96.088435399550463,96.067180675267352,94.908861732121082,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 5000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","4.28 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",4.28,208,97.5,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,210,380,480,0.42804700000000007,0.85609400000000013,1.284141,2.1402350000000001,3.2103524999999999,4.2804700000000002,93.996851147427378,95.629087640627944,96.529188756944251,97.277007418730477,96.868530791047505,96.496785004728451,96.718163206186802,95.641514244657174,97.355583883477067,97.754499714035177,97.953556646908979,97.798943927134161,97.587203384819631,97.707027076117328,95.01366047546945,96.803364464641348,97.343448588191023,97.662867921364452,97.692424675265713,97.398466432447975,97.478039135833527,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 4600TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.6 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",4.5979999999999999,240,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,180,380,480,0.45977250000000008,0.91954500000000017,1.3793175000000002,2.2988625000000003,3.4482937500000004,4.5977250000000005,86.922591470532453,92.049537139188644,93.307915460636224,94.90952047852663,95.25376734682672,95.188005695413182,94.451226650136505,86.868082954696078,92.430025652086897,94.556690289605712,95.896956933570578,96.23231982604635,96.207709631703565,95.394903380984431,85.497692670536821,91.48865673613679,93.603512624245838,95.432661270738564,96.28214935671609,96.116391367395423,95.102979652822199,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 4600TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.6 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",4.6040000000000001,208,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,180,380,480,0.46040000000000003,0.92080000000000006,1.3812,2.302,3.4530000000000003,4.6040000000000001,86.755180590217549,91.62705454632524,93.42498513733284,94.796791893422608,95.171596058447264,95.236486896009197,94.372654720801165,87.840136706007556,92.833247132067811,94.729294782796771,95.790815806914082,96.274711172919311,96.272718032005656,95.478087341478769,85.871659181712658,92.566799085310564,94.078444876002223,95.295296333055546,96.388435399550474,96.267180675267355,95.263861732121086,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 5000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","4.943 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",4.9429999999999996,240,97.5,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,210,380,480,0.49432200000000004,0.98864400000000008,1.482966,2.4716100000000001,3.7074150000000001,4.9432200000000002,94.267366712449771,96.027866498551376,96.617657713229335,96.968808318480185,96.797623042865695,96.462603080710252,96.655527032648251,95.82744666782294,97.647557997532857,97.992889962034198,98.197719306174335,98.026200918261708,97.775702757962975,97.938815240907147,95.15481202687161,97.215513493715306,97.700506408141493,97.980163351059588,97.817020842814571,97.608867979129769,97.690327674108346,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 5000TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.95 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",4.9539999999999997,240,95,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,230,380,480,0.495367,0.990734,1.4861009999999999,2.4768349999999999,3.7152525000000001,4.9536699999999998,88.267366712449771,92.027866498551376,93.917657713229346,95.168808318480188,95.597623042865678,95.462603080710252,94.827527032648248,88.82744666782294,93.647557997532857,94.592889962034178,96.197719306174335,96.526200918261708,95.975702757962978,95.745815240907135,86.65481202687161,92.415513493715309,93.700506408141493,95.580163351059582,96.117020842814568,96.108867979129769,95.150327674108325,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 5000TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","4.97 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",4.9690000000000003,208,95.5,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,230,380,480,0.49687900000000007,0.99375800000000014,1.490637,2.4843950000000001,3.7265925000000002,4.9687900000000003,87.996851147427378,91.829087640627947,94.029188756944251,95.277007418730477,95.668530791047502,95.496785004728451,94.882163206186817,88.641514244657174,93.555583883477055,94.754499714035177,95.953556646908979,96.598943927134158,96.087203384819631,95.746027076117329,87.01366047546945,92.803364464641348,93.543448588191026,96.162867921364452,96.092424675265733,96.198466432447987,95.279039135833557,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 6000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","5.143 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",5.1429999999999998,208,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,170,380,480,0.51425799999999999,1.028516,1.5427739999999999,2.5712899999999999,3.856935,5.1425799999999997,93.481204082097847,95.143621894033842,95.921639978922201,96.414307307624739,96.408584395065049,96.201559738902532,96.160658306387077,95.740431907203799,97.20226392049122,97.675309910643875,97.727611859614214,97.705868499477219,97.20034672805248,97.577693793234516,94.530997034371978,96.528735819174116,97.183911209691985,97.484093465582191,97.499956580169822,97.125463339241861,97.27265579972098,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 6000TL BL-US [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","5.23 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",5.2320000000000002,208,96,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,230,380,480,0.52322481004999999,1.0464496201,1.5696744301499999,2.6161240502499998,3.9241860753749997,5.2322481004999997,91.621602813152066,94.380390480666662,95.003957489078005,95.641543682886891,95.647954359667054,95.64975677121727,95.344986357839431,94.005771170000003,96.332077925666653,96.65995075056712,96.844207319172924,96.805818328239184,96.521558970093878,96.646474032649166,93.966622391069833,96.000071433485644,96.412837938980843,96.864324446543876,96.731434588977862,96.495662704401141,96.562160621147314,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","SPH 6000TL BL-US [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","5.86 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",5.8639999999999999,240,96,"Intertek","[03/24/2021]","[RA1.0]","2021-05-11","[03/24/2021]","2021-05-11","Intertek","2021-01-25","2021-05-11",null,"N","N",15.128,null,null,230,380,480,0.58643299999999998,1.172866,1.7592989999999999,2.9321649999999999,4.3982475000000001,5.8643299999999998,91.58160281315206,94.360390480666666,94.953957489078022,95.591543682886879,95.627954359667058,95.639756771217264,95.314786357839438,93.965771170000011,96.30207792566668,96.579950750567122,96.814207319172922,96.755818328239172,96.521558970093878,96.600974032649162,93.926622391069841,95.970071433485643,96.382837938980842,96.834324446543889,96.71143458897788,96.475662704401145,96.537560621147321,"2021-05-11"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 6000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","5.918 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",5.9180000000000001,240,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,170,380,480,0.59177500000000005,1.1835500000000001,1.7753249999999998,2.9588749999999999,4.4383125000000003,5.9177499999999998,93.49312456280208,95.071290997799792,96.009128356856777,96.506775898448311,96.537491526800594,96.276974884360101,96.259527127321348,96.283551128782477,97.623502381955774,97.995012321707193,98.032333863869923,97.740454263659132,97.640683129965907,97.763183670504276,95.282875546127613,97.093459861238671,97.489948272311352,97.82790394763353,97.699789002409091,97.433325500633003,97.561196082895918,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 7600TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","6.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter",6.58,208,97,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.5760000000000001,null,null,212,380,480,0.65803500000000004,1.3160700000000001,1.974105,3.2901750000000001,4.9352625000000003,6.5803500000000001,93.7825737552172,95.54207098779338,96.606044154379617,96.83236417215366,96.8224267390096,96.441473859841409,96.593888138943328,95.614398932245905,97.20795693450485,97.628278749390489,97.712867337028214,97.808319239909849,97.38950013957637,97.62795359884889,94.065878474823975,96.343473361528524,97.314711226736364,97.379254821920298,97.445094589024549,97.221458351837427,97.214190716655892,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 8200TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","8.2 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",7.1660000000000004,208,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.71659000000000006,1.4331800000000001,2.1497699999999997,3.5829499999999999,5.3744249999999996,7.1658999999999997,93.818033333333332,95.946699999999993,96.5916,96.939433333333326,96.892099999999999,96.798100000000005,96.691047333333344,95.225833333333327,97.223066666666654,97.743199999999987,97.92383333333332,97.82286666666667,97.741233333333327,97.696556666666666,93.714700000000008,96.521599999999992,97.29516666666666,97.704099999999997,97.722104333333334,97.637333333333345,97.44253096333334,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 7600TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.524 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter",7.524,240,97.5,"Intertek","[11/17/2020]","[UE1.0]","2021-01-21","[11/17/2020]","2021-01-21","Intertek","2020-11-09","2021-01-21",null,"N","N",1.593,null,null,212,380,480,0.75241900000000006,1.5048380000000001,2.2572570000000001,3.762095,5.6431424999999997,7.5241899999999999,94.832082543720276,96.244283779082338,96.937158930899699,97.135867226709507,97.054923358633204,96.468059416272766,96.899001030909147,96.103067497597607,97.819996666854209,98.010339138278908,98.187485590498028,98.030191099852217,97.408123146556775,97.94214264409419,95.219109592524489,97.203381594479268,97.683785313190782,97.874941033588698,97.792657448404924,97.378203889786818,97.643743960205413,"2021-01-21"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 9000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",7.8739999999999997,208,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.78742000000000001,1.57484,2.36226,3.9371,5.9056499999999996,7.8742000000000001,93.982933333333335,96.079733333333337,96.698633333333333,97.030366666666666,96.912666666666667,96.784599999999998,96.746460333333332,95.587166666666661,97.35263333333333,97.782000000000011,97.92376666666668,97.770499999999998,97.671266666666668,97.690877666666665,94.584666666666664,96.692033333333342,97.396033333333335,97.712033333333324,97.66746666666667,97.580600000000004,97.467826666666667,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 8200TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","8.2 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",8.2509999999999994,240,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.8251400000000001,1.6502800000000002,2.4754200000000002,4.1257000000000001,6.1885500000000002,8.2514000000000003,93.925766666666661,96.12466666666667,96.814266666666668,97.266599999999997,97.26166666666667,97.072066666666657,97.009248666666664,95.572199999999995,97.486333333333334,97.99163333333334,98.239066666666659,98.184200000000004,98.016600000000011,98.024860666666669,93.774266666666662,96.673366666666666,97.486766666666668,97.960933333333315,97.966002777777788,97.922899999999998,97.672973472222225,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 10000TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","10 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",8.76,208,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.87595000000000001,1.7519,2.6278499999999996,4.3797499999999996,6.5696249999999994,8.7594999999999992,94.714666666666659,96.187166666666656,96.764099999999999,96.945633333333348,96.722566666666665,96.626966666666675,96.662528666666674,96.189833333333326,97.494733333333329,97.833133333333336,97.854666666666674,97.653033333333326,97.544166666666669,97.645101999999994,94.884033333333335,96.995766666666682,97.535266666666658,97.725966666666665,97.613433333333333,97.51509999999999,97.482709333333332,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 9000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",9.0630000000000006,240,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,0.90625,1.8125,2.71875,4.53125,6.796875,9.0625,94.238433333333347,96.270200000000003,96.907966666666667,97.323466666666675,97.200033333333351,97.040300000000002,97.017964000000006,95.948166666666665,97.602599999999995,98.070666666666668,98.251533333333342,98.142799999999994,97.991399999999985,98.034612666666661,94.371600000000001,96.898499999999999,97.634733333333344,98.022900000000021,98.040899999999993,97.941199999999995,97.779502999999991,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 11400TL-XH-US [208V]","Y","Y","Y","Y","Y","Y*","Y","11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",10.039999999999999,208,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,1.0039800000000001,2.0079600000000002,3.0119399999999996,5.0198999999999998,7.5298499999999997,10.0398,95.028400000000005,96.561569440212068,97.015406666666678,97.18135333333332,96.902286666666654,96.856743333333327,96.880196572010604,95.703000000000003,97.529443333333347,97.858743333333337,97.873270000000005,97.760676666666669,97.717863333333327,97.700079866666655,95.102010000000007,97.007023333333336,97.502409999999998,97.687100000000015,97.627340000000004,97.601256666666671,97.49156480000002,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 10000TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","10 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",10.082000000000001,240,97.5,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,1.0082000000000002,2.0164000000000004,3.0246,5.0410000000000004,7.5615000000000006,10.082000000000001,95.127566666666667,96.497600000000006,97.06753333333333,97.329633333333334,97.198499999999996,96.922933333333333,97.078661333333343,96.325299999999999,97.761799999999994,98.138366666666656,98.291933333333333,98.146199999999993,97.931600000000003,98.073077999999995,95.013433333333325,97.198399999999992,97.780266666666677,98.051733333333331,98.009233333333327,97.871933333333331,97.823443666666662,"2021-03-22","2021-04-01"]
["Shenzhen Growatt New Energy Technology Co., Ltd","MIN 11400TL-XH-US [240V]","Y","Y","Y","Y","Y","Y*","Y","11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality",11.52,240,98,"Intertek","[03/17/2021]","[UE1.0]","2021-03-22","[03/17/2021]","2021-03-22","Intertek","2020-11-09","2021-03-22",null,"N","N",10,null,null,250,380,480,1.1519999999999999,2.3039999999999998,3.456,5.76,8.64,11.52,95.362579999999994,96.957206666666679,97.477490000000003,97.684960000000004,97.543343333333354,97.353883333333343,97.439170066666676,96.581923333333322,98.027549999999991,98.399886666666674,98.527416666666653,98.435103333333331,98.253936666666661,98.346699933333326,95.457046666666685,97.191386666666659,97.74481333333334,97.97084666666666,97.831793333333337,97.658173333333337,97.71486573333334,"2021-03-22","2021-04-01"]
["Shenzhen Sinexcel Electric Co., Ltd","PWS2-30K-NA [480V]","N","Y","Y ","Y ","Y ","Y*","Y","30 kW, 480 Vac wall-mounted, bi-directional Grid Support Utility Interactive Energy Storage Inverter",30.02,480,96.5,"Intertek","[9/18/2017]","[V126]","2018-10-15","[9/18/2017]","2021-10-01","Intertek","2021-09-13","2021-10-01",null,"N","N",1.857,null,null,350,600,750,3.0020000000000002,6.0040000000000004,9.0060000000000002,15.01,22.515000000000001,30.02,91.232795624893384,94.277589242188768,95.180370789174333,95.634277535394332,95.561081132163324,95.189468782718862,95.274880503421414,94.080385566728907,95.918546060046893,96.606888485455713,97.008558536409453,97.030608016695339,96.872169309812364,96.793597350911327,94.989078239317621,96.634957862780169,97.181154036798375,97.444638792448188,97.447094622802723,97.266416161831131,97.266704611718652,"2017-11-01","2021-10-01"]
["Shenzhen Sinexcel Electric Co., Ltd","PWS1-50K-NA [480V]","N","Y","Y","Y","N","N","N","50 kW, 480 Vac Grid Support Utility Interactive Inverter with 1 Inverter modules",48.58,480,94,"Intertek","[4/23/2017]","[1320, 130, 1420]","2018-10-15","[4/23/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",860,null,null,500,650,850,4.8579999999999997,9.7159999999999993,14.574,24.29,36.435000000000002,48.58,87.323880000000003,92.417400000000001,93.964190000000002,94.910979999999995,94.934809999999999,94.62491,94.367530000000002,86.479619999999997,91.834270000000004,93.521519999999995,94.538150000000002,94.624470000000002,94.313730000000007,93.99315,85.50658,91.214849999999998,92.892110000000002,94.127089999999995,94.148269999999997,93.923240000000007,93.489490000000004,"2017-07-01","2018-10-15"]
["Shenzhen Sinexcel Electric Co., Ltd","PWS1-100K-NA [480V]","N","Y","Y","Y","N","N","N","100 kW, 480 Vac Grid Support Utility Interactive Inverter with 2 Inverter modules",98.013000000000005,480,94,"Intertek","[4/23/2017]","[1320, 130, 1420]","2018-10-15","[4/23/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",997,null,null,500,650,850,9.8012999999999995,19.602599999999999,29.4039,49.006500000000003,73.509749999999997,98.013000000000005,87.311549999999997,92.459919999999997,94.048630000000003,95.034940000000006,95.106219999999993,94.79683,94.504769999999994,86.571629999999999,91.932190000000006,93.578500000000005,94.542100000000005,94.643979999999999,94.38073,94.023079999999993,85.595879999999994,91.278369999999995,92.999359999999996,94.071690000000004,94.262630000000001,94.043989999999994,93.564130000000006,"2017-07-01","2018-10-15"]
["Shenzhen Sinexcel Electric Co., Ltd","PWS1-150K-NA [480V]","N","Y","Y","Y","N","N","N","150 kW, 480 Vac Grid Support Utility Interactive Inverter with 3 Inverter modules",147.47,480,94.5,"Intertek","[4/23/2017]","[1320, 130, 1420]","2018-10-15","[4/23/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1360,null,null,500,650,850,14.747,29.494,44.241,73.734999999999999,110.60250000000001,147.47,88.591089999999994,93.098050000000001,94.450109999999995,95.172200000000004,95.219030000000004,94.892799999999994,94.72945,87.832819999999998,92.61909,94.083389999999994,94.967160000000007,95.022580000000005,94.700680000000006,94.474379999999996,86.74418,91.896339999999995,93.455410000000001,94.34769,94.47269,94.236149999999995,93.874579999999995,"2017-07-01","2018-10-15"]
["Shenzhen Sinexcel Electric Co., Ltd","PWS1-250K-NA [480V]","N","Y","Y","Y","N","N","N","250 kW, 480 Vac Grid Support Utility Interactive Inverter with 5 Inverter modules",244.02600000000001,480,95,"Intertek","[4/23/2017]","[1320, 130, 1420]","2018-10-15","[4/23/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",1860,null,null,500,650,850,24.4026,48.805199999999999,73.207800000000006,122.01300000000001,183.01949999999999,244.02600000000001,91.392179999999996,94.968000000000004,95.701229999999995,96.032960000000003,95.780090000000001,95.415419999999997,95.589370000000002,90.445620000000005,94.396190000000004,95.214219999999997,95.574529999999996,95.383780000000002,95.019170000000003,95.138350000000003,89.216269999999994,93.574600000000004,94.598749999999995,95.079480000000004,94.960419999999999,94.629959999999997,94.626440000000002,"2017-07-01","2018-10-15"]
["Shenzhen Sinexcel Electric Co., Ltd","PWS1-500KTL-NA [400V]","N","Y","Y","Y","N","N","N","500 kW, 400 Vac Grid Support Utility-Interactive Energy Storage Inverter",498.34,400,96,"Intertek","[02/26/2018]","[1400]","2018-10-15","[02/26/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 5 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",289.89999999999998,null,null,640,750,900,49.83,99.67,149.5,249.17,373.76,498.34,93.95,96,96.6,96.83,96.64,96.31,96.52,93.16,95.61,96.3,96.61,96.47,96.13,96.28,92.19,95.03,95.86,96.27,96.14,95.84,95.9,"2018-05-01","2018-10-15"]
["SMA America","SBS3.8-US-10 [240V]","N","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac, 1-phase, Sunny Boy Storage- Permanently-connected, Transformerless Multimode - Grid Support Utility Interactive and Standalone functionality - Inverter",3.8,240,96.5,"UL","[12/14/2017]","[1.00.04.R]","2018-10-15","[12/14/2017]","2020-01-13","UL","2019-12-16","2020-01-13",null,"N","N",6.53,null,null,220,360,550,0.38128600000000001,0.76257200000000003,1.143858,1.9064300000000001,2.859645,3.8128600000000001,92.693600000000004,95.522000000000006,96.098799999999997,96.434799999999996,96.412400000000005,96.287400000000005,96.179950000000005,93.605999999999995,96.45620000000001,97.102199999999996,97.421599999999984,97.465600000000009,97.377600000000001,97.20349800000001,88.564400000000006,94.722799999999992,96.086799999999997,96.848199999999991,97.025800000000004,97.020600000000002,96.421958000000004,"2018-07-02","2020-01-13"]
["SMA America","SBS5.0-US-10 [240V]","N","Y","Y","Y","Y","Y*","Y","5.0 kW, 240 Vac, 1-phase, Sunny Boy Storage- Permanently-connected, Transformerless Multimode - Grid Support Utility Interactive and Standalone functionality - Inverter",5,240,96.5,"UL","[12/14/2017]","[1.00.04.R]","2018-10-15","[12/14/2017]","2020-01-13","UL","2019-12-16","2020-01-13",null,"N","N",6.53,null,null,220,360,550,0.50159500000000001,1.00319,1.504785,2.5079750000000001,3.7619625000000001,5.0159500000000001,93.757199999999997,95.994399999999999,96.353399999999993,96.433800000000005,96.308200000000014,96.110399999999998,96.212379999999996,94.613599999999991,96.931399999999996,97.316400000000016,97.451200000000014,97.395399999999995,97.210799999999992,97.25393600000001,92.417600000000007,95.739599999999996,96.530400000000014,96.997200000000007,97.034000000000006,96.590800000000002,96.694304000000002,"2018-07-02","2020-01-13"]
["SMA America","SBS6.0-US-10 [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW, 240 Vac, 1-phase, Sunny Boy Storage- Permanently-connected, Transformerless Multimode - Grid Support Utility Interactive and Standalone functionality - Inverter",6,240,96.5,"UL","[12/14/2017]","[1.00.04.R]","2018-10-15","[12/14/2017]","2020-01-13","UL","2019-12-16","2020-01-13",null,"N","N",6.53,null,null,220,360,550,0.60219600000000006,1.2043920000000001,1.8065879999999999,3.01098,4.51647,6.02196,94.464199999999991,96.154599999999988,96.429000000000002,96.400399999999991,96.191599999999994,95.956600000000009,96.181240000000003,95.848199999999991,97.198400000000007,97.401399999999995,97.4512,97.284000000000006,96.992200000000011,97.256897999999993,93.253399999999999,96.238799999999998,96.799000000000007,97.026600000000002,96.966400000000007,96.80019999999999,96.765744000000012,"2018-07-02","2020-01-13"]
["SMA America","SCS 2475-US [385V]","N","Y ","Y ","Y ","N","N","N","2475 kVA, 385 Vac, 3 phase Grid Support Utility Interactive Battery Inverter ",2078.89,385,97,"UL","[03/25/2020]","[05.01.15.R]","2021-08-23","[03/25/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on Eaton 34.5kV transformer.","Y","N",297,null,null,577,673,950,207.88900000000001,415.77800000000002,623.66700000000003,1039.4449999999999,1559.1679999999999,2078.89,96.63,97.68,97.8,97.69,97.33,96.68,97.42,96.07,97.38,97.58,97.53,97.21,96.57,97.25,94.45,96.53,96.96,97.05,96.73,96.18,96.69,"2021-08-23"]
["SMA America","SC 4000 UP-US 600V 3850A [600V]","Y","Y","Y","Y","N","N","N","4000 kVA, 600 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter   ",3650.134,600,98.5,"UL","[09/06/2019]","[06.00.33.R]","2020-04-21","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",453.5,null,null,880,970,1200,365.01340000000005,730.02680000000009,1095.0401999999999,1825.067,2737.6005,3650.134,98.280699999999996,98.700099999999992,98.720499999999987,98.624899999999997,98.491099999999989,98.160600000000002,98.532235,98.052499999999995,98.589100000000002,98.62730000000002,98.555199999999985,98.395299999999992,98.022900000000007,98.434076999999988,97.322699999999998,98.2881,98.412900000000008,98.417600000000007,98.220200000000006,97.843699999999984,98.233447999999996,"2020-04-21"]
["SMA America","SC 4200 UP-US 630V 3850A [630V]","Y","Y","Y","Y","N","N","N","4200 kVA, 630 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter   ",3832.828,630,98.5,"UL","[09/06/2019]","[06.00.33.R]","2020-04-21","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",451.8,null,null,921,1001,1200,383.28280000000001,766.56560000000002,1149.8483999999999,1916.414,2874.6210000000001,3832.828,98.269400000000005,98.702100000000002,98.667400000000001,98.646600000000007,98.528700000000015,98.211899999999986,98.552561000000026,97.990299999999991,98.599700000000013,98.662200000000013,98.593899999999991,98.454599999999985,98.08720000000001,98.479077999999987,97.503999999999991,98.365799999999993,98.394700000000014,98.400899999999993,98.308099999999996,97.951899999999995,98.290890999999988,"2020-04-21"]
["SMA America","SC 4400 UP-US 660V 3850A [660V]","Y","Y","Y","Y","N","N","N","4400 kVA, 660 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter   ",4017.1129999999998,660,98.5,"UL","[09/06/2019]","[06.00.33.R]","2020-04-21","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",465.17,null,null,962,1032,1200,401.71129999999999,803.42259999999999,1205.1338999999998,2008.5564999999999,3012.83475,4017.1129999999998,98.287000000000006,98.733699999999999,98.710499999999996,98.707799999999992,98.6023,98.295000000000002,98.61603199999999,98.103800000000007,98.637100000000004,98.629199999999997,98.640600000000006,98.502400000000009,98.149000000000001,98.519759000000008,97.598199999999991,98.44959999999999,98.588400000000007,98.487300000000005,98.388600000000011,98.04010000000001,98.387312000000009,"2020-04-21"]
["SMA America","SC 4600 UP-US 690V 3850A [690V]","Y","Y","Y","Y","N","N","N","4600 kVA, 690 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter   ",4198.2349999999997,690,98.5,"UL","[09/06/2019]","[06.00.33.R]","2020-04-21","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",471.07,null,null,1003,1062,1200,419.82349999999997,839.64699999999993,1259.4704999999999,2099.1174999999998,3148.6762499999995,4198.2349999999997,98.272799999999989,98.742100000000008,98.724299999999985,98.735199999999992,98.647099999999995,98.347699999999989,98.649672999999993,98.149900000000017,98.674700000000001,98.686299999999989,98.691100000000006,98.565300000000008,98.214699999999993,98.577562000000015,97.740700000000004,98.529799999999994,98.643999999999991,98.595500000000001,98.455099999999987,98.12639999999999,98.465975999999984,"2020-04-21"]
["SolarEdge Technologies Ltd.","SE3000H-US [240V]","Y","Y ","Y ","Y ","Y ","Y*","Y ","3.0 kW, 240 Vac HD-Wave technology hybrid Grid Support Utility Interactive Inverter",2.9620000000000002,240,99,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",0,null,null,360,395,480,0.3,0.6,0.9,1.6,2.1,2.8,95.67,98.01,98.63,99.01,99.19,99.19,98.89,95.39,97.88,98.54,98.96,99.16,99.16,98.83,95.93,98.04,98.57,99,99.08,99.17,98.83,"2017-07-01","2021-08-02"]
["SolarEdge Technologies Ltd.","SE3800H-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter",3.7469999999999999,240,99,"Intertek","[04/02/2020]","[2.0.820]","2018-10-15","[04/02/2020]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",0,null,null,360,395,480,0.3,0.8,1.2,2,2.8,3.6,96.56,98.4,98.82,99.18,99.19,99.2,99,96.34,98.3,98.75,99.14,99.16,99.12,98.95,96.72,98.57,98.82,99.07,99.17,99.08,98.97,"2017-07-01"]
["SolarEdge Technologies Ltd.","SE3800A-US [240V]","Y","Y","Y","Y","Y","Y*","Y","3.8 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter",3.79,240,98,"Intertek","[6/7/2017]","[2.52.507]","2018-10-15","[6/7/2017]","2020-01-21","Intertek","2019-12-16","2020-01-21","Formerly SolarEdge Technologies Ltd. SE3800x [240V]","Y","N",2.2400000000000002,null,null,360,400,480,0.38,0.76,1.1399999999999999,1.9,2.84,3.79,96.1,97.6,98,98.1,98.1,98.2,98,95.7,97.3,97.8,98.1,98,98.2,97.9,94.6,96.8,97.5,97.9,97.9,97.8,97.6,"2020-01-21"]
["SolarEdge Technologies Ltd.","SE6000H-US [240V]","Y","Y ","Y ","Y ","Y ","Y*","Y ","6 kW, 240 Vac, 1-phase, HD-Wave technology hybrid Grid Support Utility Interactive Inverter",6.0460000000000003,240,99,"Intertek","[01/17/2018]","[2.0.525]","2018-10-15","[01/17/2018]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",4.5199999999999996,null,null,360,395,480,0.5,1.3,1.9,3,4.3,5.8,97.17,98.61,98.9,98.95,98.95,98.98,98.96,96.95,98.51,98.82,98.89,98.9,98.95,98.79,96.65,98.32,98.7,98.83,98.85,98.71,98.7,"2017-07-01","2021-08-02"]
["SolarEdge Technologies Ltd.","SE7600H-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter",7.6159999999999997,240,99,"Intertek","[04/02/2020]","[2.0.820]","2018-10-15","[04/02/2020]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",4.5199999999999996,null,null,360,395,480,0.7,1.6,2.4,3.6,5.5,7.3,97.72,98.8,98.97,98.97,99.04,98.73,98.94,97.52,98.7,98.91,98.93,99.02,98.69,98.89,97.24,98.57,98.83,98.87,98.75,98.71,98.71,"2017-07-01"]
["SolarEdge Technologies Ltd.","SE7600A-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter",7.625,240,97.5,"Intertek","[6/7/2017]","[2.52.507]","2018-10-15","[6/7/2017]","2020-01-21","Intertek","2019-12-16","2020-01-21",null,"Y","N",2.16,null,null,360,400,480,0.76249999999999996,1.5249999999999999,2.2879999999999998,3.8130000000000002,5.7190000000000003,7.625,97,97.9,98,97.9,97.7,97.3,97.7,96.6,97.8,97.9,97.9,97.6,97.3,97.7,95.7,97.4,97.6,97.6,97.5,97.1,97.5,"2020-01-21"]
["SolarJuice American Inc.","S4A-H60 [240V]","Y","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",5.57,240,94,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",25,null,null,240,335,425,0.57500000000000007,1.1500000000000001,1.7249999999999999,2.875,4.3125,5.75,86.869682822533804,91.494323337741122,93.197507125817154,94.277347956539373,94.528577104512152,94.419480087783,93.852567275540324,86.534692544508331,91.719237390678572,93.532641876704261,94.760758659216464,95.116012615226765,95.142514472111017,94.339638324629973,85.944083659918661,91.055826867889806,93.119565276460762,94.55685225894733,95.055933937626449,95.188812247401856,94.160927096657588,"2021-07-12"]
["SolarJuice American Inc.","S4A-A60 [240V]","N","Y","Y","Y","Y","Y*","Y","6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",5.7320000000000002,240,94,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",25,null,null,360,430,500,0.57320000000000004,1.1464000000000001,1.7196,2.8660000000000001,4.2990000000000004,5.7320000000000002,86.110434735585883,91.388494641122492,93.351087437054758,94.749762095940312,94.838108561535265,95.050604461357111,94.130150414755136,85.907427686004169,91.677523734783577,93.545896297167019,95.09320205514625,94.944898410684885,95.311789274125047,94.301638902789335,85.575624491941767,91.818698446692835,93.691816188753108,94.566832524118155,94.967972150718609,95.209424564294565,94.209509142823094,"2021-07-12"]
["SolarJuice American Inc.","S4A-H70 [240V]","Y","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",6.6660000000000004,240,94.5,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",25,null,null,290,360,425,0.66660000000000008,1.3332000000000002,1.9998,3.3330000000000002,4.9995000000000003,6.6660000000000004,88.19254532766071,92.480024599906656,93.864222646892841,94.728177374748682,94.859277550957373,94.661603922022621,94.31682430753466,87.895016741997523,92.552209013216427,93.98568096527471,94.939255036123782,95.145985429310571,95.084346217536066,94.540525982171076,87.188290385772305,91.840278359010497,93.665346252959509,94.812415113107377,95.188151694943144,95.183576013873704,94.438893456502669,"2021-07-12"]
["SolarJuice American Inc.","S4A-A70 [240V]","N","Y","Y","Y","Y","Y*","Y","7 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",6.68,240,95,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",25,null,null,280,390,500,0.66800000000000004,1.3360000000000001,2.004,3.34,5.01,6.68,88.292377200011984,93.483852175415123,94.882481845799276,95.530016091163603,95.113519083961407,94.475920679886698,94.787050045905389,88.563863096046475,92.576227224590028,94.65479402447454,95.55142668227154,95.427835917164501,95.233936899721115,94.934190652368585,87.563113100140896,92.158097577473129,94.261243287927726,95.392763954066183,95.226593134621183,94.673328104323886,94.658019794349954,"2021-07-12"]
["SolarJuice American Inc.","S4A-H76 [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",7.6420000000000003,240,95.5,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",44,null,null,304,402,500,0.76415320000000009,1.5283064000000002,2.2924595999999999,3.8207660000000003,5.7311490000000003,7.6415320000000007,91.707418177902383,94.572943893510569,95.343208396678733,95.732834528334209,95.650063634275952,95.385614239539109,95.40583861848647,90.557349146015056,94.483695582739486,95.237254457268747,95.752187855671906,95.755162516040727,95.573013398331213,95.411795532959076,93.454639453611506,95.564299299611108,96.165924657149233,96.488739138122966,96.365110394539414,96.144925249431296,96.199701492566206,"2021-07-12"]
["SolarJuice American Inc.","S4A-A76 [240V]","N","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",7.8319999999999999,240,95.5,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",49.5,null,null,320,375,430,0.78320560000000006,1.5664112000000001,2.3496167999999997,3.9160279999999998,5.8740419999999993,7.8320559999999997,91.431173544170591,94.962219303103637,95.624199158360184,95.75096782329237,95.440095960384738,94.975882487212104,95.320010032181145,92.295163238555702,94.869357976832788,95.609461165370504,95.935786658817605,95.741421969872519,95.332046361434294,95.564480928684176,92.761799110093776,95.061640260152643,95.714885238474494,95.902818050237826,95.763217781087064,95.436868928337617,95.61528086697129,"2021-07-12"]
["SolarJuice American Inc.","S4A-H86 [240V]","Y","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",8.6039999999999992,240,96,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",40,null,null,258,379,500,0.8604440000000001,1.7208880000000002,2.5813320000000002,4.3022200000000002,6.4533300000000002,8.6044400000000003,92.699334355597514,94.539928618718363,95.297824749048559,95.613611296666747,95.424147601271741,94.940413722572345,95.271386062148309,92.844051102514101,95.289415785898782,95.970144903059008,96.182450712551415,95.871598553910871,95.529337174346537,95.781378963688468,93.694083911121623,95.776806518196878,96.274499321609412,96.519408732377741,96.296844266964186,95.892164355116009,96.19055511399398,"2021-07-12"]
["SolarJuice American Inc.","S4A-A86 [240V]","N","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",8.6129999999999995,240,95.5,"CSA Group","[05/14/2021]","[V1.07]","2021-07-12","[05/14/2021]","2021-07-12","CSA Group","2021-06-22","2021-07-12",null,"N","N",42,null,null,363,396.5,430,0.86129999999999995,1.7225999999999999,2.5838999999999999,4.3064999999999998,6.4597499999999997,8.6129999999999995,93.013508600881977,95.280549182880833,95.808820184682801,95.929597652810443,95.631206739051237,95.189392810224234,95.57085094463983,92.858426013211542,95.24742892388474,95.806799660978314,95.998886513281505,95.747373582335698,95.322727925739699,95.645535008754109,92.575709670533442,95.119762364187309,95.72335138420506,95.988280372552211,95.834603768861626,95.452411361897447,95.668318114962801,"2021-07-12"]
["Sol-Ark","Sol-Ark-8k-48-ST [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","8 KW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality",7.8390000000000004,208,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-08-01","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.78392807600000003,1.5678561520000001,2.3517842279999996,3.9196403799999997,5.8794605699999991,7.8392807599999994,91.486264550039337,94.760248969262392,95.352663162123591,97.296267712149941,97.185123619139432,96.859870192303077,96.623107857230082,91.699965357816623,94.963850615122325,95.495711668085661,97.428829723597843,97.231635305996946,96.929680695919046,96.714981534168942,91.907256517136105,94.928995056460167,95.369819427808693,97.318654328391062,96.925617369279323,97.063119550059341,96.527768937028625,"2019-08-01","2021-07-12"]
["Sol-Ark","Sol-Ark-8k-48-ST [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","8 KW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality",7.976,240,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-08-01","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.79761655200000003,1.5952331040000001,2.3928496559999997,3.9880827599999997,5.9821241399999998,7.9761655199999995,91.819615795312856,94.910997776364283,95.520513772204296,97.079550873826477,96.988012087484861,97.130498991107089,96.527673212721126,91.670908997205146,95.000841359179049,95.707732171504404,97.546548492774008,97.445862228404309,97.08346102095264,96.887061504012152,91.551333333333318,95.071706716631525,95.858438563503356,97.600636400067273,97.273962762904389,97.086789328574284,96.824324671567467,"2019-08-01","2021-07-12"]
["Sol-Ark","Sol-Ark-12K-P [208V]","Y","Y ","Y ","Y ","Y","Y*","Y","9 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality",8.8179999999999996,208,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-12-23","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.88180885940000009,1.7636177188000002,2.6454265781999999,4.4090442970000003,6.6135664455000001,8.8180885940000007,91.466335419848761,94.733829955347005,95.331023522356261,97.277883440309353,97.171192835821699,96.824261660440328,96.60536854571653,91.67953424672848,94.934963045425178,95.479041347900221,97.405444606925556,97.215616325861205,96.903746610114041,96.696021834554926,91.88088933294037,94.895522896509419,95.314066949266319,97.244283347858328,96.88071561768912,97.009765877392653,96.476266826350155,"2019-12-23","2021-07-12"]
["Sol-Ark","Sol-Ark-9k-48-ST [208V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter    ",8.8179999999999996,208,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-12-23","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.88180885940000009,1.7636177188000002,2.6454265781999999,4.4090442970000003,6.6135664455000001,8.8180885940000007,91.466335419848761,94.733829955347005,95.331023522356261,97.277883440309353,97.171192835821699,96.824261660440328,96.60536854571653,91.67953424672848,94.934963045425178,95.479041347900221,97.405444606925556,97.215616325861205,96.903746610114041,96.696021834554926,91.88088933294037,94.895522896509419,95.314066949266319,97.244283347858328,96.88071561768912,97.009765877392653,96.476266826350155,"2019-12-23","2020-07-21"]
["Sol-Ark","Sol-Ark-12K-P [240V]","Y","Y ","Y ","Y ","Y","Y*","Y","9 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality",8.9819999999999993,240,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-12-23","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.89821683780000017,1.7964336756000003,2.6946505134000001,4.4910841890000004,6.7366262835000006,8.9821683780000008,91.817370955953706,94.888333470547522,95.567760080849254,97.132142929471669,96.971545040244834,97.124294697876351,96.534126342880057,91.636458971417213,94.970390519246919,95.669651822789049,97.515106010634426,97.412239578354487,97.052223139745195,96.853606499302103,91.551333333333318,95.04856690772759,95.824316992250942,97.559470524973804,97.225099944122846,97.049443787713827,96.78266368780514,"2019-12-23","2021-07-12"]
["Sol-Ark","Sol-Ark-9k-48-ST [240V]","Y","Y","Y","Y","Y","Y*","Y","9 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter    ",8.9819999999999993,240,96.5,"SGS","[10/09/2019]","[Ver3965]","2019-12-23","[10/09/2019]","2020-07-21","PCTEST","2020-06-11","2020-07-21",null,"N","N",13.4,null,null,240,370,425,0.89821683780000017,1.7964336756000003,2.6946505134000001,4.4910841890000004,6.7366262835000006,8.9821683780000008,91.817370955953706,94.888333470547522,95.567760080849254,97.132142929471669,96.971545040244834,97.124294697876351,96.534126342880057,91.636458971417213,94.970390519246919,95.669651822789049,97.515106010634426,97.412239578354487,97.052223139745195,96.853606499302103,91.551333333333318,95.04856690772759,95.824316992250942,97.559470524973804,97.225099944122846,97.049443787713827,96.78266368780514,"2019-12-23","2020-07-21"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Hybrid-6.0-US [240V]","Y","Y","Y","Y","Y","Y*","Y","6.0 kW, 240 Vac Transformerless Hybrid Grid Support Utility Interactive Inverter with PV arc detector",5.57,240,94,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2020-11-23","[10/21/2020]","2020-11-23","Intertek","2020-09-11","2020-11-23",null,"N","N",25,null,null,240,335,425,0.57500000000000007,1.1500000000000001,1.7249999999999999,2.875,4.3125,5.75,86.869682822533804,91.494323337741122,93.197507125817154,94.277347956539373,94.528577104512152,94.419480087783,93.852567275540324,86.534692544508331,91.719237390678572,93.532641876704261,94.760758659216464,95.116012615226765,95.142514472111017,94.339638324629973,85.944083659918661,91.055826867889806,93.119565276460762,94.55685225894733,95.055933937626449,95.188812247401856,94.160927096657588,"2020-11-23"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Fit-6.0-US [240V]","N","Y","Y","Y","Y","Y*","Y","6.0 kW, 240 Vac Transformerless Bi-directional Grid Support Utility Interactive Battery Inverter",5.7320000000000002,240,94,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2020-11-23","[10/21/2020]","2020-11-23","Intertek","2020-09-11","2020-11-23",null,"N","N",25,null,null,360,430,500,0.57320000000000004,1.1464000000000001,1.7196,2.8660000000000001,4.2990000000000004,5.7320000000000002,86.110434735585883,91.388494641122492,93.351087437054758,94.749762095940312,94.838108561535265,95.050604461357111,94.130150414755136,85.907427686004169,91.677523734783577,93.545896297167019,95.09320205514625,94.944898410684885,95.311789274125047,94.301638902789335,85.575624491941767,91.818698446692835,93.691816188753108,94.566832524118155,94.967972150718609,95.209424564294565,94.209509142823094,"2020-11-23"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Hybrid-7.0-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.0 kW, 240 Vac Transformerless Hybrid Grid Support Utility Interactive Inverter with PV arc detector",6.6660000000000004,240,94.5,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2020-11-23","[10/21/2020]","2020-11-23","Intertek","2020-09-11","2020-11-23",null,"N","N",25,null,null,290,360,425,0.66660000000000008,1.3332000000000002,1.9998,3.3330000000000002,4.9995000000000003,6.6660000000000004,88.19254532766071,92.480024599906656,93.864222646892841,94.728177374748682,94.859277550957373,94.661603922022621,94.31682430753466,87.895016741997523,92.552209013216427,93.98568096527471,94.939255036123782,95.145985429310571,95.084346217536066,94.540525982171076,87.188290385772305,91.840278359010497,93.665346252959509,94.812415113107377,95.188151694943144,95.183576013873704,94.438893456502669,"2020-11-23"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Fit-7.0-US [240V]","N","Y","Y","Y","Y","Y*","Y","7.0 kW, 240 Vac Transformerless Bi-directional Grid Support Utility Interactive Battery Inverter",6.68,240,95,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2020-11-23","[10/21/2020]","2020-11-23","Intertek","2020-09-11","2020-11-23",null,"N","N",25,null,null,280,390,500,0.66800000000000004,1.3360000000000001,2.004,3.34,5.01,6.68,88.292377200011984,93.483852175415123,94.882481845799276,95.530016091163603,95.113519083961407,94.475920679886698,94.787050045905389,88.563863096046475,92.576227224590028,94.65479402447454,95.55142668227154,95.427835917164501,95.233936899721115,94.934190652368585,87.563113100140896,92.158097577473129,94.261243287927726,95.392763954066183,95.226593134621183,94.673328104323886,94.658019794349954,"2020-11-23"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Hybrid-7.6-US [240V]","Y","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",7.6420000000000003,240,95.5,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2019-06-01","[10/21/2020]","2021-01-21","Intertek","2020-09-11","2021-01-21",null,"N","N",44,null,null,304,402,500,0.76415320000000009,1.5283064000000002,2.2924595999999999,3.8207660000000003,5.7311490000000003,7.6415320000000007,91.707418177902383,94.572943893510569,95.343208396678733,95.732834528334209,95.650063634275952,95.385614239539109,95.40583861848647,90.557349146015056,94.483695582739486,95.237254457268747,95.752187855671906,95.755162516040727,95.573013398331213,95.411795532959076,93.454639453611506,95.564299299611108,96.165924657149233,96.488739138122966,96.365110394539414,96.144925249431296,96.199701492566206,"2019-06-03","2021-01-21"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Fit-7.6-US [240V]","N","Y","Y","Y","Y","Y*","Y","7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",7.8319999999999999,240,95.5,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2019-06-01","[10/21/2020]","2021-01-21","Intertek","2020-09-11","2021-01-21",null,"N","N",49.5,null,null,320,375,430,0.78320560000000006,1.5664112000000001,2.3496167999999997,3.9160279999999998,5.8740419999999993,7.8320559999999997,91.431173544170591,94.962219303103637,95.624199158360184,95.75096782329237,95.440095960384738,94.975882487212104,95.320010032181145,92.295163238555702,94.869357976832788,95.609461165370504,95.935786658817605,95.741421969872519,95.332046361434294,95.564480928684176,92.761799110093776,95.061640260152643,95.714885238474494,95.902818050237826,95.763217781087064,95.436868928337617,95.61528086697129,"2019-06-03","2021-01-21"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Hybrid-8.6-US [240V]","Y","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector",8.6039999999999992,240,96,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2019-06-01","[10/21/2020]","2021-01-21","Intertek","2020-09-11","2021-01-21",null,"N","N",40,null,null,258,379,500,0.8604440000000001,1.7208880000000002,2.5813320000000002,4.3022200000000002,6.4533300000000002,8.6044400000000003,92.699334355597514,94.539928618718363,95.297824749048559,95.613611296666747,95.424147601271741,94.940413722572345,95.271386062148309,92.844051102514101,95.289415785898782,95.970144903059008,96.182450712551415,95.871598553910871,95.529337174346537,95.781378963688468,93.694083911121623,95.776806518196878,96.274499321609412,96.519408732377741,96.296844266964186,95.892164355116009,96.19055511399398,"2019-06-03","2021-01-21"]
["SolaX Power Network Technology (Zhe jiang) Co., Ltd.","A1-Fit-8.6-US [240V]","N","Y","Y","Y","Y","Y*","Y","8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter",8.6129999999999995,240,95.5,"CSA Group","[10/21/2020]","[V1.07, V1.03]","2019-06-01","[10/21/2020]","2021-01-21","Intertek","2020-09-11","2021-01-21",null,"N","N",42,null,null,363,396.5,430,0.86129999999999995,1.7225999999999999,2.5838999999999999,4.3064999999999998,6.4597499999999997,8.6129999999999995,93.013508600881977,95.280549182880833,95.808820184682801,95.929597652810443,95.631206739051237,95.189392810224234,95.57085094463983,92.858426013211542,95.24742892388474,95.806799660978314,95.998886513281505,95.747373582335698,95.322727925739699,95.645535008754109,92.575709670533442,95.119762364187309,95.72335138420506,95.988280372552211,95.834603768861626,95.452411361897447,95.668318114962801,"2019-06-03","2021-01-21"]
["Sungrow Power Supply Co., Ltd.","SC60HV [480V]","N","Y","Y","Y","Y","Y*","Y","66 kW, 480 Vac, Bi-directional, Stand-Alone or Grid Support Utility Interactive Energy Storage Inverter",66,480,98,"CSA Group","[06/14/2019]","[MDSP_AGATE-S_V11_V01_A]","2019-08-01","[06/14/2019]","2020-10-12","CSA Group","2020-07-22","2020-10-12",null,"N","N",0.26,null,null,700,850,1300,6.6280720000000004,13.256144000000001,19.884215999999999,33.140360000000001,49.710540000000002,66.280720000000002,97.363848547225487,98.298882122318815,98.571240208591959,98.528086504675755,98.328628608808017,98.169143704807567,98.351575386926541,96.721534430627571,97.824971274231629,98.134240941349461,98.145794142211201,98.038299898475287,97.835902752491947,97.998929707579464,94.537855684545477,96.537923870828806,97.200870332317592,97.502078735504739,97.464807753349049,97.304281675166564,97.269513588290692,"2019-08-01","2020-10-12"]
["Sungrow Power Supply Co., Ltd.","SC75HV [600V]","N","Y","Y","Y","Y","Y*","Y","82.5 kW, 600 Vac, Bi-directional, Stand-Alone or Grid Support Utility Interactive Energy Storage Inverter",82.5,600,98,"CSA Group","[06/14/2019]","[MDSP_AGATE-S_V11_V01_A]","2019-08-01","[06/14/2019]","2020-10-12","CSA Group","2020-07-22","2020-10-12",null,"N","N",5.35,null,null,870,1000,1300,8.2568440000000027,16.513688000000005,24.770532000000006,41.284220000000012,61.926330000000021,82.568440000000024,97.528931780448531,98.335585860853868,98.533250952566817,98.593104194141901,98.428093147095026,98.268910658042543,98.426813460200947,96.874189377638785,97.980369395618098,98.207699296851942,98.26668766633621,98.135135081080833,97.922821045186694,98.102677015671475,94.773183057743793,97.14997558995681,97.604866732722471,97.839247116464691,97.77586042125526,97.57378687037567,97.607147370975952,"2019-08-01","2020-10-12"]
["Sungrow Power Supply Co., Ltd.","SG250HX-US [800V]","Y","Y","Y","Y","Y","Y*","Y","250 kW, 800 Vac, 3-phase, Transformerless Grid Support Utility Interactive Battery and Solar Inverter",226.99700000000001,800,98.5,"CSA Group","[08/04/2020]","[MDSP_DIAMOND-S_V11_V01_A]","2020-09-21","[08/04/2020]","2021-02-22","CSA Group","2020-12-07","2021-02-22",null,"N","N",5.21,null,null,860,1080,1300,22.699720000000003,45.399440000000006,68.099159999999998,113.49860000000001,170.24790000000002,226.99720000000002,97.057745574954694,98.250621131215539,98.468961755451389,98.570823670838692,98.462127815632613,98.262002467504104,98.40901712674976,98.194991347702199,98.76272324549052,98.946095857679211,99.010097962841797,98.86901346612548,98.677924712757914,98.866061263985301,97.998276444662039,98.661181448293519,98.899728984680351,98.947823888300505,98.81777374729441,98.631959848062522,98.805018703375069,"2020-09-21","2021-02-22"]
["Sungrow Power Supply Co., Ltd.","SC250KU [480V]","N","Y","Y ","Y ","Y ","Y*","Y","250 kW, 480 Vac Grid Support Utility Interactive Storage Inverter, bi-directional for use with battery management system\n",250,480,96,"CSA Group","[05/11/2018];[04/29/2019]","[DSP_SC250-V13_V1_B_M];[DSP_SC250-V13_V1_C_M]","2019-02-01","[04/29/2019]","2021-09-13","CSA Group","2021-08-11","2021-09-13",null,"N","N",93.64,null,null,500,675,850,25.329040000000003,50.658080000000005,75.987120000000004,126.6452,189.96780000000001,253.29040000000001,95.00187387100128,96.556118328410463,96.92214212788042,96.741893611038066,96.300772781652114,95.805386905261415,96.404014504462907,94.020920157396432,96.306372978730423,96.51625739034175,96.345368144348029,96.190161533672537,95.769098856476674,96.159874208056749,92.857142857142861,94.897475395503236,96.09990424669283,96.022243149960559,95.953360762054828,95.574083993670925,95.789804458728341,"2019-02-01","2021-09-13"]
["Sungrow Power Supply Co., Ltd.","SC1000KU [540V]","Y","Y","Y","N","N","N","N","1000 kW, 540 Vac Grid Support Utility Interactive Storage Inverter,  bi-directional for use with battery management system, intended to be used in conjunction with a 1000 KVA (min) rated isolation transformer",1001.306,540,96.5,"CSA Group","[09/19/2019]","[DSP_SC1000KU_V1_B_M]","2019-02-01","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 1 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",83.764600000000002,null,null,810,1005,1200,100.13060000000002,200.26120000000003,300.39179999999999,500.65300000000002,750.97950000000003,1001.306,94.9956293648696,96.814367115577753,97.243680299436662,97.315507163897323,97.02864130176718,96.663267169452439,97.004384919133727,94.281076304463951,96.34437633335655,96.904741277777674,97.04790286747415,96.801692495979225,96.438994201912251,96.72393715731387,93.689401171763706,95.927478731094439,96.5802450520018,96.832373527564641,96.597834177749448,96.188205595675555,96.474640224445039,"2019-02-01"]
["Sungrow Power Supply Co., Ltd.","SC1200UD-US [480V]","N","Y","Y ","Y ","Y ","Y*","Y","1200 kVA, 480 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter",1203.0519999999999,480,98.5,"SGS","[12/30/2020]","[MDSP_AMBER_B_V11_V1_A, SDSP_AMBER_B_V11_V1_A]","2021-05-03","[12/30/2020]","2021-05-03","SGS","2021-09-14","2021-09-21",null,"N","N",146.929,null,null,700,900,1500,120.3052,240.6104,360.91559999999998,601.52599999999995,902.28899999999999,1203.0519999999999,98.488138045009322,98.782916823941591,98.794241584702917,98.627317197343316,98.326805279653399,98.057819877837872,98.461814756712101,98.174322360107922,98.575348053171425,98.597971361677722,98.481565120000724,98.218069579667016,97.945056503012779,98.321455238038538,97.233607031196598,98.00285743928336,98.215281444164177,98.228256035618614,98.015039641108743,97.769830338470044,98.039717220702784,"2021-05-03","2021-09-21"]
["Sungrow Power Supply Co., Ltd.","SC1375UD-US [550V]","N","Y","Y ","Y ","Y ","Y*","Y","1375 kVA, 550 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter",1378.9359999999999,550,98.5,"SGS","[12/30/2020]","[MDSP_AMBER_B_V11_V1_A, SDSP_AMBER_B_V11_V1_A]","2021-05-03","[12/30/2020]","2021-05-03","SGS","2021-09-14","2021-09-21",null,"N","N",144.25399999999999,null,null,800,975,1500,137.89359999999999,275.78719999999998,413.68079999999998,689.46799999999996,1034.202,1378.9359999999999,98.497218029256274,98.81731159234657,98.887291890710983,98.756170043081184,98.519547966726364,98.233469722184637,98.613058945194155,98.287104853415897,98.712520180196762,98.789299270335647,98.673931917755951,98.448126541226685,98.147109524489537,98.528214361390127,97.692823228284709,98.332759643011769,98.48723736818495,98.403175568777698,98.203508163931403,98.016274231204378,98.256159303351353,"2021-05-03","2021-09-21"]
["Sungrow Power Supply Co., Ltd.","SC1575UD-US [630V]","N","Y","Y ","Y ","Y ","Y*","Y","1575 kVA, 630 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter",1582.9960000000001,630,98.5,"SGS","[12/30/2020]","[MDSP_AMBER_B_V11_V1_A, SDSP_AMBER_B_V11_V1_A]","2021-05-03","[12/30/2020]","2021-05-03","SGS","2021-09-14","2021-09-21",null,"N","N",144.10400000000001,null,null,915,1062,1500,158.29960000000003,316.59920000000005,474.89879999999999,791.49800000000005,1187.2470000000001,1582.9960000000001,98.517147641139928,98.872784131169041,98.956454949051249,98.843150816726705,98.669566385391278,98.308010844218501,98.726432104071108,98.27263056304578,98.772607556419956,98.86284400219192,98.78280430374501,98.598865131595304,98.271191664461071,98.648423887360877,97.890131095451579,98.477120613140599,98.642772577325431,98.589430365038169,98.441281761472922,98.129892145647574,98.460748301275203,"2021-05-03","2021-09-21"]
["Sungrow Power Supply Co., Ltd.","SC1725UD-US [690V]","N","Y","Y ","Y ","Y ","Y*","Y","1725 kVA, 690 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter",1728.4059999999999,690,98.5,"SGS","[12/30/2020]","[MDSP_AMBER_B_V11_V1_A, SDSP_AMBER_B_V11_V1_A]","2021-05-03","[12/30/2020]","2021-05-03","SGS","2021-09-14","2021-09-21",null,"N","N",141.72499999999999,null,null,1000,1125,1500,172.84059999999999,345.68119999999999,518.52179999999998,864.20299999999997,1296.3045,1728.4059999999999,98.505680221734821,98.892674187322925,99.015956375975591,98.955215960451469,98.729758688204086,98.445933360469169,98.796439807819056,98.243883064986093,98.782024291511561,98.904571192216892,98.856538325286479,98.677380938324745,98.346048225341107,98.713592437130387,97.958025674173015,98.594995632175696,98.745380500244735,98.725737416536248,98.590619705717017,98.230180566592679,98.594458798437344,"2021-05-03","2021-09-21"]
["Sungrow Power Supply Co., Ltd.","SC2500U [550V]","N","Y","Y","Y","N","N","N","2500 Kva, 550 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter",2507.194,550,97.5,"CSA Group","[10/30/2019]","[DSP_SC2500U_V11_V1_A, LCD_SC2500U_V1_A]   ","2020-01-02","[10/30/2019]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 2500 kVA Medium-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",62.8,null,null,800,975,1500,250.71940000000001,501.43880000000001,752.15819999999997,1253.597,1880.3955000000001,2507.194,96.165587825617536,97.496024626913893,97.84611827224451,97.917731002770864,97.654712804724852,97.323989855524346,97.64887972690201,96.024564148543945,97.239077966047518,97.730826426636156,97.852050543793169,97.544402877512624,97.189977456983456,97.537598647567904,95.432639383368937,96.821878647291854,97.345753997551,97.466367294046691,97.19680752091476,96.942642988776186,97.169267254678914,"2020-01-02","2020-03-23"]
["Tabuchi Electric Co., Ltd.","THD-S55P3BB-US [240V]","Y","Y","Y","Y","N","N","N","5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 3.3 kW Discharge Rate/20 kWh Storage Capacity",5.5189199999999996,240,94.5,"Intertek","[9/20/2017]","[4.1]","2018-10-15","[9/20/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",10.1,null,null,240,380,520,0.55188999999999999,1.10378,1.65568,2.7594599999999998,4.1391900000000001,5.5189199999999996,89.3,93.3,94.3,94.7,94.1,94.2,94,89.7,93.7,94.7,95.4,95.5,95.4,95.1,88.8,93.1,94.3,95.1,95.2,94.9,94.7,"2017-12-15","2018-10-15"]
["Tabuchi Electric Co., Ltd.","THD-S55P3B-US [240V]","Y","Y","Y","Y","N","N","N","5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 2 kW Discharge Rate/10 kWh Storage Capacity",5.5189199999999996,240,94.5,"Intertek","[9/20/2017]","[4.1]","2018-10-15","[9/20/2017]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",10.1,null,null,240,380,520,0.55188999999999999,1.10378,1.65568,2.7594599999999998,4.1391900000000001,5.5189199999999996,89.3,93.3,94.3,94.7,94.1,94.2,94,89.7,93.7,94.7,95.4,95.5,95.4,95.1,88.8,93.1,94.3,95.1,95.2,94.9,94.7,"2017-12-15","2018-10-15"]
["Tabuchi Electric Co., Ltd.","THE-S55P3BB-USW [240V]","Y","Y","Y","Y","N","N","N","5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 4.0 kW Discharge Rate/20 kWh Storage Capacity\n",5.5189199999999996,240,94.5,"Intertek","[04/26/2018]","[4.11]","2018-10-15","[04/26/2018]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",10.1,null,null,240,380,520,0.55189200000000005,1.1037840000000001,1.6556759999999999,2.7594599999999998,4.1391900000000001,5.5189199999999996,89.325999999999993,93.286000000000001,94.304000000000002,94.656000000000006,94.048000000000002,94.174000000000007,93.985720000000001,89.688000000000002,93.665999999999997,94.706000000000003,95.44,95.498000000000005,95.41,95.062380000000005,88.78,93.075999999999993,94.275999999999996,95.093999999999994,95.165999999999997,94.921999999999997,94.671940000000006,"2018-06-01","2018-10-15"]
["WSTECH GmbH","APS800-ES-1-440-5 [440V]","N","Y","Y","Y","N","N","N","800 kW, 440 Vac, Grid Support Utility Interactive Centeral Battery Inverter",814.16700000000003,440,97.5,"MET","[10/12/2020]","[APU V3130 APMC V2040]","2020-11-12","[10/12/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 1000 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216.","N","N",91.4,null,null,648,1000,1500,81.416693333333342,162.83338666666668,244.25007999999997,407.08346666666665,610.62519999999995,814.1669333333333,96.899355530950103,97.920707265792174,98.147190760869563,98.085463040000008,97.731682555419141,97.300539581134942,97.810438447660857,97.156025349874199,97.903118886806737,98.084511645962735,97.981152853333356,97.697036658005203,97.27509500499103,97.770764634043147,96.518204331811816,97.351769103912844,97.62585192805382,97.667947145904762,97.341867071756937,96.957097736075085,97.39273219530952,"2020-11-12"]
["WSTECH GmbH","APS870-ES-1-480-5 [480V]","N","Y ","Y ","Y ","Y ","N","N","870 kW, 480 Vac, Grid Support Utility Interactive Centeral Battery Inverter",872.029,480,98,"MET","[04/08/2021]","[APU V3130 APMC V2050]","2021-07-01","[04/08/2021]","2021-07-01","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",91.402000000000001,null,null,770,1000,1470,87.202903333333339,174.40580666666668,261.60870999999997,436.01451666666668,654.02177500000005,872.02903333333336,97.081535640215748,98.188326536251608,98.416188156702887,98.401719417256189,98.132164669461218,97.756162785201553,98.164836822923888,95.766437110691712,97.280734052016285,97.833944012368789,98.04081271586206,97.85925870133093,97.52706667584556,97.765098584341445,96.937363573018132,97.639693816860969,97.84646181596699,97.794618856551736,97.559243378111034,97.17562500327,97.603104852118037,"2021-07-01"]
["WSTECH GmbH","APS1600-ES-2-440-5 [440V]","N","Y","Y","Y","N","N","N","1600 kW, 440 Vac, Grid Support Utility Interactive Centeral Battery Inverter",1626.952,440,98,"MET","[10/12/2020]","[APU V3130 APMC V2040]","2020-11-12","[10/12/2020]","No Information Submitted","No Information Submitted","No Information Submitted","No Information Submitted","Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE216.","N","N",91.4,null,null,648,1000,1500,162.69520149253731,325.39040298507462,488.08560447761192,813.47600746268654,1220.2140111940298,1626.9520149253731,98.039564384810532,98.583932832285171,98.668427958751352,98.532876253333342,98.2150718555353,97.858468021735675,98.329806069777334,96.983648481562426,97.910572913334434,98.115708519049306,98.108532687142869,97.852695689547474,97.453039923442418,97.886132183147424,96.317955371488225,97.379170135459674,97.660767145350476,97.701669861904762,97.437048453413212,97.002759893817952,97.450093125074474,"2020-11-12"]
["WSTECH GmbH","APS1740-ES-2-480-5 [480V]","N","Y ","Y ","Y ","Y ","N","N","1735 kW, 480 Vac, Grid Support Utility Interactive Centeral Battery Inverter",1735.36,480,97.5,"MET","[04/08/2021]","[APU V3130 APMC V2050]","2021-07-01","[04/08/2021]","2021-07-01","No Information Submitted","No Information Submitted","No Information Submitted",null,"N","N",91.402000000000001,null,null,770,1000,1470,173.53604761904762,347.07209523809524,520.60814285714287,867.68023809523811,1301.5203571428572,1735.3604761904762,96.201849245365011,97.635415202832306,98.024327642348112,98.123863291080468,97.916855850022969,97.597507221863992,97.874584299770262,95.6962644026314,97.274574959056025,97.780480876315039,97.951872039712796,97.757716524196624,97.433202078371636,97.678380019298359,94.384457837533915,96.470678221985494,97.070575922965205,97.416133179833338,97.340286289845665,97.060011305722696,97.148121602025796,"2021-07-01"]