## PV Module-Full
PV Module List (Full Data)
Data has not changed since October 21, 2021
This list contains an extensive amount of equipment information. If you require any assistance, please reach out to us at SolarEquipment@energy.ca.gov or 916-654-4120.
PV Module List Notes
* BIPV = Building Integrated Photovoltaics
**Any text in brackets at the end of the Model Number is not part of the Manufacturer's Model Number. The bracketed text (e.g. "[Wht]") is shown only if the model number is available in different backsheet colors and the manufacturer has provided different test data for the different options.
PTC refers to PVUSA Test Conditions, which were developed to test and compare PV systems as part of the PVUSA (Photovoltaics for Utility Scale Applications) project. PTC are 1,000 Watts per square meter solar irradiance, 20 degrees C air temperature, and wind speed of 1 meter per second at 10 meters above ground level. PV manufacturers use Standard Test Conditions, or STC, to rate their PV products. STC are 1,000 Watts per square meter solar irradiance, 25 degrees C cell temperature, air mass equal to 1.5, and ASTM G173-03 standard spectrum. The PTC rating, which is lower than the STC rating, is generally recognized as a more realistic measure of PV output because the test conditions better reflect "real-world" solar and climatic conditions, compared to the STC rating. All ratings in the list are DC (direct current) watts.
Neither PTC nor STC account for all "real-world" losses. Actual solar systems will produce lower outputs due to soiling, shading, module mismatch, wire losses, inverter and transformer losses, shortfalls in actual nameplate ratings, panel degradation over time, and high-temperature losses for arrays mounted close to or integrated within a roofline. These loss factors can vary by season, geographic location, mounting technique, azimuth, and array tilt. Examples of estimated losses from varying factors can be found at:
PVWatts Tool
Please note that PTC values presented on the PV Module List are calculated using laboratory-tested parameter values. After July 1, 2009, if a California solar electric incentive program uses PTC values, the SB 1 Guidelines compliant PTC values must be used for new reservation applications.
Design qualification certification and performance evaluation testing are not required in order to be included on the PV Module List. If applicable, the date of the certificate or test report is listed. Otherwise, the field will be marked as "No Information Submitted".
*** Equipment is in the process of being removed from the list of eligible equipment pursuant to Appendix A, Section B, of the Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1).
Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1)
Blue colored text indicates that the model number occurs multiple times on the list under different manufacturer names.
Archive of the Prior Incentive Eligible Photovoltaic Modules Expired July 1, 2009.
Intentionally Left Blank
Manufacturer | Model Number | Description | Safety Certification | Nameplate Pmax | PTC | Notes | Design Qualification Certification (Optional Submission) | Performance Evaluation (Optional Submission) | Family | Technology | A_c | N_s | N_p | BIPV | Nameplate Isc | Nameplate Voc | Nameplate Ipmax | Nameplate Vpmax | Average NOCT | γPmax | αIsc | βVoc | αIpmax | βVpmax | IPmax, low | VPmax, low | IPmax, NOCT | VPmax, NOCT | Mounting | Type | Short Side | Long Side | Geometric Multiplier | P2/Pref | CEC Listing Date | Last Update
|  |  |  | (W) |  |  | IEC 61215:2016 | IEC 61853-1:2011 |  |  | (m2) |  |  |  | (A) | (V) | (A) | (V) | (°C) | (%/°C) | (%/°C) | (%/°C) | (%/°C) | (%/°C) | (A) | (V) | (A) | (V) |  |  | (m) | (m)
Ablytek | 6MN6A270 | 270 W Monocrystalline Module | UL 1703 | 270 | 242.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.34 | 38.63 | 8.81 | 30.72 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.2417 | 29.8406 | 8.81 | 26.3425 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24775
Ablytek | 6MN6A275 | 275 W Monocrystalline Module | UL 1703 | 275 | 246.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.42 | 38.97 | 8.88 | 30.99 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.2595 | 30.1029 | 8.88 | 26.574 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24733
Ablytek | 6MN6A280 | 280 W Monocrystalline Module | UL 1703 | 280 | 251.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.51 | 39.31 | 8.96 | 31.26 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.2798 | 30.3652 | 8.96 | 26.8055 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24724
Ablytek | 6MN6A285 | 285 W Monocrystalline Module | UL 1703 | 285 | 256 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.59 | 39.65 | 9.04 | 31.53 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.3002 | 30.6274 | 9.04 | 27.037 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24719
Ablytek | 6MN6A290 | 290 W Monocrystalline Module | UL 1703 | 290 | 260.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.67 | 39.99 | 9.12 | 31.8 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.3205 | 30.8897 | 9.12 | 27.2686 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24718
Advance Power | API-P210 | 210 W Polycrystalline Module | UL 1703 | 210 | 186.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 7.6 | 35.94 | 7.09 | 29.64 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.43 | 29.16 | 5.71 | 26.86 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19857
Advance Power | API-P215 | 215 W Polycrystalline Module | UL 1703 | 215 | 191.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 7.83 | 36 | 7.18 | 29.94 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.44 | 29.46 | 5.78 | 27.13 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19731
Advance Power | API-P220 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 7.95 | 36.06 | 7.3 | 30.12 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.47 | 29.63 | 5.88 | 27.29 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19798
Advance Power | API-M225 | 225 W Monocrystalline Module | UL 1703 | 225 | 200.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.11 | 37.02 | 7.5 | 30 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.56 | 29.67 | 5.99 | 27.45 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20571
Advance Power | API-P225 | 225 W Polycrystalline Module | UL 1703 | 225 | 200.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.1 | 36.42 | 7.41 | 30.36 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.49 | 29.87 | 5.96 | 27.51 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19781
Advance Power | API-M230 | 230 W Monocrystalline Module | UL 1703 | 230 | 205.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.18 | 37.32 | 7.55 | 30.48 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.57 | 30.14 | 6.03 | 27.89 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20574
Advance Power | API-P230 | 230 W Polycrystalline Module | UL 1703 | 230 | 205 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.17 | 36.6 | 7.55 | 30.48 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.52 | 29.99 | 6.08 | 27.62 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19819
Advance Power | API-M235 | 235 W Monocrystalline Module | UL 1703 | 235 | 209.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.26 | 37.5 | 7.59 | 30.96 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.58 | 30.61 | 6.06 | 28.33 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.2058
Advance Power | API-P235 | 235 W Polycrystalline Module | UL 1703 | 235 | 209.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.23 | 36.72 | 7.68 | 30.6 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.59 | 29.82 | 6.18 | 27.73 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20176
Advance Power | API-M240 | 240 W Monocrystalline Module | UL 1703 | 240 | 214.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.29 | 37.56 | 7.69 | 31.2 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.6 | 30.85 | 6.14 | 28.55 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20567
Advance Power | API-P240 | 240 W Polycrystalline Module | UL 1703 | 240 | 214.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.42 | 36.72 | 7.9 | 30.54 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.63 | 29.76 | 6.36 | 27.67 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20212
Advance Power | API-M245 | 245 W Monocrystalline Module | UL 1703 | 245 | 219 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.32 | 37.62 | 7.78 | 31.5 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.63 | 31.31 | 6.2 | 28.85 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20831
Advance Power | API-P245 | 245 W Polycrystalline Module | UL 1703 | 245 | 218.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.46 | 36.9 | 8 | 30.84 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.65 | 30.05 | 6.44 | 27.95 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20238
Advance Power | API-M250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.59 | 37.62 | 8.17 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.71 | 30.42 | 6.51 | 28.03 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20807
Advance Power | API-P250 | 250 W Polycrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.52 | 37.2 | 8.03 | 31.2 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.66 | 30.4 | 6.46 | 28.27 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20186
Advance Power | API-M255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.67 | 37.68 | 8.35 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.75 | 30.42 | 6.66 | 28.03 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20876
Advance Power | API-P255 | 255 W Polycrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.56 | 37.5 | 8.08 | 31.56 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.67 | 30.76 | 6.5 | 28.6 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20145
Advance Power | API-M260 | 260 W Monocrystalline Module | UL 1703 | 260 | 232.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.8 | 37.8 | 8.5 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.78 | 30.42 | 6.78 | 28.03 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20826
Advance Power | API-P260 | 260 W Polycrystalline Module | UL 1703 | 260 | 231.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 7.83 | 43.2 | 7.24 | 35.93 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.46 | 35.3 | 5.85 | 32.39 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19822
Advance Power | API-M265 | 265 W Monocrystalline Module | UL 1703 | 265 | 235.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.11 | 44.42 | 7.36 | 36 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.45 | 35.49 | 5.94 | 32.51 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19419
Advance Power | API-P265 | 265 W Polycrystalline Module | UL 1703 | 265 | 236 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 7.95 | 43.27 | 7.33 | 36.14 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.48 | 35.5 | 5.93 | 32.58 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19826
Advance Power | API-M270 | 270 W Monocrystalline Module | UL 1703 | 270 | 240.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.14 | 44.64 | 7.44 | 36.21 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.47 | 35.7 | 6.01 | 32.7 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19437
Advance Power | API-P270 | 270 W Polycrystalline Module | UL 1703 | 270 | 240.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.1 | 43.7 | 7.41 | 36.43 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.48 | 36.46 | 5.99 | 33.1 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19985
Advance Power | API-M275 | 275 W Monocrystalline Module | UL 1703 | 275 | 244.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.18 | 44.78 | 7.52 | 36.58 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.55 | 36.25 | 6.04 | 32.97 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20432
Advance Power | API-P275 | 275 W Polycrystalline Module | UL 1703 | 275 | 245.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.17 | 43.92 | 7.52 | 36.58 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.51 | 36.61 | 6.08 | 33.24 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20102
Advance Power | API-M280 | 280 W Monocrystalline Module | UL 1703 | 280 | 249.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.21 | 44.86 | 7.6 | 36.86 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.57 | 36.53 | 6.11 | 33.22 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20483
Advance Power | API-P280 | 280 W Polycrystalline Module | UL 1703 | 280 | 249.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.23 | 44.06 | 7.63 | 36.72 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.53 | 36.75 | 6.16 | 33.37 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20081
Advance Power | API-M285 | 285 W Monocrystalline Module | UL 1703 | 285 | 254 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.39 | 44.21 | 7.77 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6 | 36.39 | 6.24 | 33.1 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20429
Advance Power | API-P285 | 285 W Polycrystalline Module | UL 1703 | 285 | 256.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.32 | 44.21 | 7.75 | 36.79 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6 | 36.17 | 6.21 | 33.88 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20306
Advance Power | API-M290 | 290 W Monocrystalline Module | UL 1703 | 290 | 258.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.48 | 44.43 | 7.9 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.63 | 36.37 | 6.35 | 33.21 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20442
Advance Power | API-P290 | 290 W Polycrystalline Module | UL 1703 | 290 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.46 | 44.28 | 7.96 | 36.79 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.65 | 36.17 | 6.38 | 33.88 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20579
Advance Power | API-P295 | 295 W Polycrystalline Module | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.49 | 44.42 | 8 | 37.01 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.66 | 36.39 | 6.41 | 34.08 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20477
Advance Power | API-P300 | 300 W Polycrystalline Module | UL 1703 | 300 | 270.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.54 | 44.86 | 8.05 | 37.66 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.67 | 37.02 | 6.45 | 34.68 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20608
Advance Power | API-P305 | 305 W Polycrystalline Module | UL 1703 | 305 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.56 | 45 | 8.08 | 37.87 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.67 | 37.23 | 6.48 | 34.88 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20385
Advance Power | API-P310 | 310 W Polycrystalline Module | UL 1703 | 310 | 277.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.62 | 45.22 | 8.16 | 38.02 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.69 | 37.35 | 6.57 | 34.41 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20362
Advance Power | API-P315 | 315 W Polycrystalline Module | UL 1703 | 315 | 281.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.67 | 45.58 | 8.24 | 38.45 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.71 | 37.78 | 6.63 | 34.8 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20509
Advance Power | API-P320 | 320 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 320 | 288.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.38 | 45.51 | 8.75 | 36.59 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7396 | 35.4395 | 7.0207 | 33.2073 | [6 empty] | 2018-09-04
Advance Power | API-P325 | 325 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 325 | 293.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.44 | 45.79 | 8.81 | 36.88 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7516 | 35.7204 | 7.0689 | 33.4705 | [6 empty] | 2018-09-04
Advance Power | API-M330 | 330 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 330 | 302.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.57 | 46.76 | 8.75 | 37.71 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7322 | 36.2337 | 7.0079 | 34.1233 | [6 empty] | 2018-09-04
Advance Power | API-P330 | 330 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 330 | 298 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.5 | 46.08 | 8.87 | 37.22 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7635 | 36.0497 | 7.117 | 33.7791 | [6 empty] | 2018-09-04
Advance Power | API-M335 | 335 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 335 | 307.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.61 | 47.04 | 8.82 | 37.98 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.746 | 36.4931 | 7.064 | 34.3676 | [6 empty] | 2018-09-04
Advance Power | API-P335 | 335 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 335 | 302.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.56 | 46.37 | 8.94 | 37.55 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7774 | 36.3693 | 7.1732 | 34.0786 | [6 empty] | 2018-09-04
Advance Power | API-M340 | 340 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 340 | 311.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.64 | 47.18 | 8.96 | 38.32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7738 | 36.8198 | 7.1761 | 34.6753 | [6 empty] | 2018-09-04
Advance Power | API-M345 | 345 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 345 | 315.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.72 | 47.28 | 8.98 | 38.4 | 44.6 | -0.43 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7777 | 36.8967 | 7.1921 | 34.7477 | [6 empty] | 2018-09-04
Advance Power | API-M350 | 350 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 350 | 320.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.81 | 47.37 | 9.1 | 38.48 | 44.6 | -0.43 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8015 | 36.9736 | 7.2882 | 34.8201 | [6 empty] | 2018-09-04
Advance Power | API-M355 | 355 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 355 | 325.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.9 | 47.47 | 9.21 | 38.55 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8182 | 37.5082 | 7.381 | 35.3921 | [6 empty] | 2018-09-04
Advance Power | API-M360 | 360 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 360 | 330.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.99 | 47.56 | 9.32 | 38.63 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8401 | 37.5832 | 7.47 | 35.4629 | [6 empty] | 2018-09-04
Advance Power | API-M365 | 365 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 365 | 334.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 10.08 | 47.66 | 9.43 | 38.71 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.862 | 37.6584 | 7.5586 | 35.5338 | [6 empty] | 2018-09-04
Advance Power | API-M370 | 370 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 370 | 339.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 10.17 | 47.75 | 9.54 | 38.78 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8837 | 37.7337 | 7.6468 | 35.6049 | [6 empty] | 2018-09-04
Advanced Solar Power (Hangzhou) | ASP-S1-80 | 80 W Thin Film Module | UL 1703 | 80 | 75.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 145 | 1 | N | 0.95 | 118.9 | 0.85 | 94.1 | 45.2 | -0.2634 | 0.0897 | -0.3058 | 0.0933 | -0.3292 | 0.2 | 32.75 | 0.69 | 89.33 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.081875
Alps Technology | ATI-S572-175 | 175 W Monocrystalline Module | UL 1703 | 175 | 151.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2874 | 72 | 1 | N | 5.17 | 43.99 | 4.78 | 36.63 | 49.9 | -0.5072 | 0.0415 | -0.3616 | 0.0001 | -0.5073 | 0.99299 | 34.9239 | 3.6799 | 32.0437 | Rack | Flat Plate | 0.82 | 1.57 | 1 | 0.19817
Alps Technology | ATI-S572-180 | 180 W Monocrystalline Module | UL 1703 | 180 | 155.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2874 | 72 | 1 | N | 5.31 | 44.06 | 4.9 | 36.72 | 49.9 | -0.5072 | 0.0415 | -0.3616 | 0.0001 | -0.5073 | 1.0179 | 35.0098 | 3.7723 | 32.1225 | Rack | Flat Plate | 0.82 | 1.57 | 1 | 0.19798
Alps Technology | ATI-S572-185 | 185 W Monocrystalline Module | UL 1703 | 185 | 160.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2874 | 72 | 1 | N | 5.43 | 44.14 | 5.03 | 36.79 | 49.9 | -0.5072 | 0.0415 | -0.3616 | 0.0001 | -0.5073 | 1.0449 | 35.0765 | 3.8724 | 32.1837 | Rack | Flat Plate | 0.82 | 1.57 | 1 | 0.19812
Alps Technology | ATI-M660-220 | 220 W Polycrystalline Module | UL 1703 | 220 | 189.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 7.95 | 36.06 | 7.3 | 30.12 | 50.2 | -0.5196 | 0.0548 | -0.3624 | -0.0413 | -0.4835 | 1.4114 | 29.5053 | 5.5615 | 26.4728 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.18929
Alps Technology | ATI-M660-225 | 225 W Polycrystalline Module | UL 1703 | 225 | 193.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.04 | 36.24 | 7.44 | 30.24 | 50.2 | -0.5196 | 0.0548 | -0.3624 | -0.0413 | -0.4835 | 1.4385 | 29.6229 | 5.6681 | 26.5783 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.18938
Alps Technology | ATI-M660-230 | 230 W Polycrystalline Module | UL 1703 | 230 | 198 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.1 | 36.42 | 7.58 | 30.36 | 50.2 | -0.5196 | 0.0548 | -0.3624 | -0.0413 | -0.4835 | 1.4655 | 29.7404 | 5.7748 | 26.6838 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.1895
Alps Technology | ATI-M660-235 | 235 W Polycrystalline Module | UL 1703 | 235 | 202.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.23 | 36.72 | 7.68 | 30.6 | 50.2 | -0.5196 | 0.0548 | -0.3624 | -0.0413 | -0.4835 | 1.4849 | 29.9755 | 5.851 | 26.8947 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.1894
Alps Technology | ATI-M660-240 | 240 W Polycrystalline Module | UL 1703 | 240 | 207 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.32 | 36.84 | 7.83 | 30.72 | 50.2 | -0.5196 | 0.0548 | -0.3624 | -0.0413 | -0.4835 | 1.5139 | 30.0931 | 5.9652 | 27.0002 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.18982
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P30-245W | 245 W Polycrystalline Module | UL 1703 | 245 | 216.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.75 | 37.5 | 8.17 | 30 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.6614 | 29.2612 | 6.538 | 26.8552 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19842 |  | 2018-05-01
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P30-250W | 250 W Polycrystalline Module | UL 1703 | 250 | 221 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.83 | 37.7 | 8.28 | 30.2 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.6837 | 29.4563 | 6.626 | 27.0343 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19839 |  | 2018-05-01
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P30-255W | 255 W Polycrystalline Module | UL 1703 | 255 | 225.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.89 | 37.3 | 8.51 | 30 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.7305 | 29.2612 | 6.81 | 26.8552 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19858 |  | 2018-05-01
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P30-260W | 260 W Polycrystalline Module | UL 1703 | 260 | 230.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 9.01 | 38 | 8.5 | 30.6 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.7285 | 29.8465 | 6.802 | 27.3923 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19842 |  | 2018-05-01
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P30-265W | 265 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 265 | 241.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.611 | 60 | 1 | N | 9.24 | 38.29 | 8.62 | 30.74 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6859 | 30.425 | 6.8739 | 28.1906 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P30-270W | 270 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 270 | 246.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.611 | 60 | 1 | N | 9.31 | 38.72 | 8.72 | 30.97 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7054 | 30.6527 | 6.9537 | 28.4016 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P30-275W | 275 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 275 | 251.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.611 | 60 | 1 | N | 9.35 | 38.92 | 8.78 | 31.32 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7172 | 30.9991 | 7.0015 | 28.7225 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6M30-280W | 280 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P30-280W | 280 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 280 | 255.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.611 | 60 | 1 | N | 9.47 | 39.16 | 8.84 | 31.68 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7289 | 31.3554 | 7.0494 | 29.0527 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6M30-285W | 285 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P-320W | 320 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 320 | 291.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.923 | 72 | 1 | N | 9.24 | 45.94 | 8.62 | 37.13 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6619 | 36.8503 | 6.888 | 34.5528 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P-325W | 325 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 325 | 296.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.923 | 72 | 1 | N | 9.28 | 46.31 | 8.72 | 37.28 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6812 | 36.9992 | 6.9679 | 34.6924 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19139 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P-330W | 330 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 330 | 301.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.923 | 72 | 1 | N | 9.35 | 46.65 | 8.78 | 37.58 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6928 | 37.2969 | 7.0158 | 34.9715 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19132 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6M-335W | 335 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 | 1 | N | 9.33 | 46.75 | 8.83 | 37.94 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7244 | 37.0282 | 7.0957 | 34.8576 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1906 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6P-335W | 335 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 335 | 306 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.923 | 72 | 1 | N | 9.47 | 46.83 | 8.84 | 37.9 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7043 | 37.6145 | 7.0638 | 35.2693 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19137 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6M-340W | 340 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 340 | 310.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 | 1 | N | 9.41 | 46.91 | 8.91 | 38.17 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.74 | 37.2526 | 7.16 | 35.0689 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19065 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6M-345W | 345 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 | 1 | N | 9.48 | 47.13 | 8.99 | 38.38 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7556 | 37.4576 | 7.2243 | 35.2619 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19061 | 2018-04-02
Amerisolar-Worldwide Energy and Manufacturing USA Co., Ltd | AS-6M-350W | 350 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 | 1 | N | 9.59 | 47.64 | 9.09 | 38.51 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7752 | 37.5845 | 7.3046 | 35.3813 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062 | 2018-04-02
Andalay Solar | ST-175-1AC1-A-A | 175 W DC, Monocrystalline ACPV Module | UL 1741 | 175 | 157.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 44.2 | 4.95 | 35.2 | 46.4 | -0.435 | 0.044 | -0.322 | -0.027 | -0.412 | 0.98602 | 34.6198 | 4.0337 | 32.0088 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19506
Andalay Solar | ST-175-1AC3-B-A | 175 W DC, Monocrystalline ACPV Module | UL 1741 | 175 | 157.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 44.2 | 4.95 | 35.2 | 46.4 | -0.435 | 0.044 | -0.322 | -0.027 | -0.412 | 0.98602 | 34.6198 | 4.0337 | 32.0088 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19506
Andalay Solar | ST-185-1AC1-A-A | 185 W DC, Monocrystalline ACPV Module | UL 1741 | 185 | 167.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.43 | 45 | 5.09 | 36.4 | 45.8 | -0.436 | 0.055 | -0.326 | -0.025 | -0.413 | 1.0085 | 35.9261 | 4.0054 | 33.1129 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19584
Andalay Solar | ST-185-1AC1-A-B | 185 W DC, Monocrystalline ACPV Module | UL 1741 | 185 | 167.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.43 | 45 | 5.09 | 36.4 | 45.8 | -0.436 | 0.055 | -0.326 | -0.025 | -0.413 | 1.0085 | 35.9261 | 4.0054 | 33.1129 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19584
Andalay Solar | ST-185-1AC3-B-A | 185 W DC, Monocrystalline ACPV Module | UL 1741 | 185 | 167.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.43 | 45 | 5.09 | 36.4 | 45.8 | -0.436 | 0.055 | -0.326 | -0.025 | -0.413 | 1.0085 | 35.9261 | 4.0054 | 33.1129 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19584
Andalay Solar | ST-185-1AC3-B-B | 185 W DC, Monocrystalline ACPV Module | UL 1741 | 185 | 167.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.43 | 45 | 5.09 | 36.4 | 45.8 | -0.436 | 0.055 | -0.326 | -0.025 | -0.413 | 1.0085 | 35.9261 | 4.0054 | 33.1129 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19584
Andalay Solar | ST-190-1AC1-A-B | 190 W DC, Monocrystalline ACPV Module | UL 1741 | 190 | 171.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.62 | 45.2 | 5.2 | 36.6 | 45.8 | -0.436 | 0.055 | -0.326 | -0.025 | -0.413 | 1.0303 | 36.1235 | 4.092 | 33.2948 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19588
Andalay Solar | ST-190-1AC3-B-B | 190 W DC, Monocrystalline ACPV Module | UL 1741 | 190 | 171.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.62 | 45.2 | 5.2 | 36.6 | 45.8 | -0.436 | 0.055 | -0.326 | -0.025 | -0.413 | 1.0303 | 36.1235 | 4.092 | 33.2948 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19588
Andalay Solar | ST-195-1AC1-A-B | 195 W DC, Monocrystalline ACPV Module | UL 1741 | 195 | 176.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.69 | 45.4 | 5.33 | 36.6 | 45.8 | -0.436 | 0.055 | -0.326 | -0.025 | -0.413 | 1.056 | 36.1235 | 4.1943 | 33.2948 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19563
Andalay Solar | ST-195-1AC3-B-B | 195 W DC, Monocrystalline ACPV Module | UL 1741 | 195 | 176.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.69 | 45.4 | 5.33 | 36.6 | 45.8 | -0.436 | 0.055 | -0.326 | -0.025 | -0.413 | 1.056 | 36.1235 | 4.1943 | 33.2948 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19563
Andalay Solar | LW-230-1-AC0-D-B | 230 W DC, Polycrystalline ACPV Module | UL 1741 | 230 | 204.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.38 | 36.6 | 7.87 | 29.2 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.5813 | 28.4633 | 6.3833 | 25.9972 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19569
Andalay Solar | LW-230-1-AC1-A-B | 230 W DC, Polycrystalline ACPV Module | UL 1741 | 230 | 204.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.38 | 36.6 | 7.87 | 29.2 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.5813 | 28.4633 | 6.3833 | 25.9972 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19569
Andalay Solar | LW-230-1-AC2-D-B | 230 W DC, Polycrystalline ACPV Module | UL 1741 | 230 | 204.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.38 | 36.6 | 7.87 | 29.2 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.5813 | 28.4633 | 6.3833 | 25.9972 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19569
Andalay Solar | LW-230-1-AC3-B-B | 230 W DC, Polycrystalline ACPV Module | UL 1741 | 230 | 204.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.38 | 36.6 | 7.87 | 29.2 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.5813 | 28.4633 | 6.3833 | 25.9972 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19569
Andalay Solar | LW-235-1-AC0-D-B | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 209 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.45 | 37.2 | 8 | 29.6 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.6074 | 28.8532 | 6.4888 | 26.3533 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19736
Andalay Solar | LW-235-1-AC1-A-B | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 209 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.45 | 37.2 | 8 | 29.6 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.6074 | 28.8532 | 6.4888 | 26.3533 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19736
Andalay Solar | LW-235-1-AC2-D-B | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 209 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.45 | 37.2 | 8 | 29.6 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.6074 | 28.8532 | 6.4888 | 26.3533 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19736
Andalay Solar | LW-235-1-AC3-B-B | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 209 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.45 | 37.2 | 8 | 29.6 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.6074 | 28.8532 | 6.4888 | 26.3533 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19736
Andalay Solar | LW-240-1-AC0-D-B | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 213.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.56 | 37.4 | 8.05 | 29.8 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.6175 | 29.0481 | 6.5293 | 26.5314 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19577
Andalay Solar | LW-240-1-AC1-A-B | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 213.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.56 | 37.4 | 8.05 | 29.8 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.6175 | 29.0481 | 6.5293 | 26.5314 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19577
Andalay Solar | LW-240-1-AC2-D-B | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 213.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.56 | 37.4 | 8.05 | 29.8 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.6175 | 29.0481 | 6.5293 | 26.5314 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19577
Andalay Solar | LW-240-1-AC3-B-B | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 213.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.56 | 37.4 | 8.05 | 29.8 | 48.2 | -0.45 | 0.06 | -0.34 | -0.01 | -0.45 | 1.6175 | 29.0481 | 6.5293 | 26.5314 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19577
Andalay Solar | TW-240-1-AC2-D-B | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 212.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 8.48 | 36.2 | 7.86 | 30.5 | 48.8 | -0.49 | 0.06 | -0.36 | -0.01 | -0.48 | 1.5524 | 29.4554 | 6.2865 | 27.2532 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19053
Andalay Solar | TW-245-1-AC2-D-B | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 217 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 8.59 | 36.4 | 7.97 | 30.75 | 48.8 | -0.49 | 0.06 | -0.36 | -0.01 | -0.48 | 1.5741 | 29.6968 | 6.3744 | 27.4766 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.1908
Andalay Solar | TW-250-1-AC2-D-B | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 221.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 8.75 | 36.8 | 8.1 | 30.9 | 48.8 | -0.49 | 0.06 | -0.36 | -0.01 | -0.48 | 1.5998 | 29.8417 | 6.4784 | 27.6106 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19096
Anhui Rinengzhongtian Semiconductor Development | QJM160-72 | 160 W Monocrystalline Module | UL 1703 | 160 | 141.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.12 | 42.42 | 4.57 | 35.01 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.87 | 34.05 | 3.76 | 30.76 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18515
Anhui Rinengzhongtian Semiconductor Development | QJM165-72 | 165 W Monocrystalline Module | UL 1703 | 165 | 146 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.22 | 42.5 | 4.66 | 35.4 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.89 | 34.43 | 3.83 | 31.1 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18571
Anhui Rinengzhongtian Semiconductor Development | QJM170-72 | 170 W Monocrystalline Module | UL 1703 | 170 | 150.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.35 | 42.7 | 4.78 | 35.6 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.91 | 34.62 | 3.93 | 31.28 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18532
Anhui Rinengzhongtian Semiconductor Development | QJM175-72 | 175 W Monocrystalline Module | UL 1703 | 175 | 155.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.45 | 43.1 | 4.87 | 35.9 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.91 | 35.44 | 3.89 | 32.21 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18429
Anhui Rinengzhongtian Semiconductor Development | QJM180-72 | 180 W Monocrystalline Module | UL 1703 | 180 | 159.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.59 | 43.3 | 4.99 | 36.1 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.93 | 35.64 | 3.98 | 32.39 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18414
Anhui Rinengzhongtian Semiconductor Development | QJM185-72 | 185 W Monocrystalline Module | UL 1703 | 185 | 164.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.72 | 43.4 | 5.11 | 36.2 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.95 | 35.74 | 4.08 | 32.48 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18353
Anhui Rinengzhongtian Semiconductor Development | QJM190-72 | 190 W Monocrystalline Module | UL 1703 | 190 | 168.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.86 | 43.5 | 5.23 | 36.3 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.97 | 35.23 | 4.11 | 32.57 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17986
Anhui Rinengzhongtian Semiconductor Development | QJM195-72 | 195 W Monocrystalline Module | UL 1703 | 195 | 173.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 6.01 | 43.6 | 5.37 | 36.3 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 1 | 35.23 | 4.22 | 32.57 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18067
Anhui Rinengzhongtian Semiconductor Development | QJM200-72 | 200 W Monocrystalline Module | UL 1703 | 200 | 178 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.95 | 45.7 | 5.54 | 36.12 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 1.03 | 35.05 | 4.35 | 32.41 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18051
Anhui Rinengzhongtian Semiconductor Development | QJP205-60 | 205 W Polycrystalline Module | UL 1703 | 205 | 182.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 7.84 | 35.1 | 7 | 29.3 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.35 | 27.66 | 5.58 | 26.79 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18215
Anhui Rinengzhongtian Semiconductor Development | QJP210-60 | 210 W Polycrystalline Module | UL 1703 | 210 | 186.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.01 | 35.2 | 7.14 | 29.4 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.38 | 27.75 | 5.7 | 26.88 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18236
Anhui Rinengzhongtian Semiconductor Development | QJP215-60 | 215 W Polycrystalline Module | UL 1703 | 215 | 191.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.16 | 35.4 | 7.29 | 29.5 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.41 | 27.85 | 5.82 | 26.97 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18264
Anhui Rinengzhongtian Semiconductor Development | QJM220-60 | 220 W Monocrystalline Module | UL 1703 | 220 | 197.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 7.98 | 36.29 | 7.46 | 29.5 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.4619 | 28.9804 | 5.8261 | 26.9399 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19257
Anhui Rinengzhongtian Semiconductor Development | QJP220-60 | 220 W Polycrystalline Module | UL 1703 | 220 | 196 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.32 | 35.4 | 7.46 | 29.5 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.44 | 27.85 | 5.95 | 26.97 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18229
Anhui Rinengzhongtian Semiconductor Development | QJM225-60 | 225 W Monocrystalline Module | UL 1703 | 225 | 202.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.13 | 36.41 | 7.6 | 29.6 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.4899 | 29.0787 | 5.9378 | 27.0312 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19255
Anhui Rinengzhongtian Semiconductor Development | QJP225-60 | 225 W Polycrystalline Module | UL 1703 | 225 | 200.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.46 | 35.8 | 7.6 | 29.6 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.47 | 27.94 | 6.06 | 27.06 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18254
Anhui Rinengzhongtian Semiconductor Development | QJM230-60 | 230 W Monocrystalline Module | UL 1703 | 230 | 206.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.29 | 36.53 | 7.74 | 29.7 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.5179 | 29.1769 | 6.0496 | 27.1225 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19256
Anhui Rinengzhongtian Semiconductor Development | QJP230-60 | 230 W Polycrystalline Module | UL 1703 | 230 | 205.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.6 | 36 | 7.72 | 29.8 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.55 | 28.21 | 6.16 | 27.26 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19011
Anhui Rinengzhongtian Semiconductor Development | QJM235-60 | 235 W Monocrystalline Module | UL 1703 | 235 | 211.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.44 | 36.65 | 7.89 | 29.8 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.5458 | 29.2752 | 6.1605 | 27.2138 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19256
Anhui Rinengzhongtian Semiconductor Development | QJP235-60 | 235 W Polycrystalline Module | UL 1703 | 235 | 209.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.75 | 36.1 | 7.83 | 30 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.57 | 28.4 | 6.25 | 27.44 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18974
Anhui Rinengzhongtian Semiconductor Development | QJM240-60 | 240 W Monocrystalline Module | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.59 | 36.78 | 8.03 | 29.9 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.5734 | 29.3734 | 6.2706 | 27.3052 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19257
Anhui Rinengzhongtian Semiconductor Development | QJP240-60 | 240 W Polycrystalline Module | UL 1703 | 240 | 214.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.9 | 36.2 | 7.95 | 30.2 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.6 | 28.59 | 6.34 | 27.63 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1906
Anhui Rinengzhongtian Semiconductor Development | QJM245-60 | 245 W Monocrystalline Module | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.71 | 37.02 | 8.14 | 30.1 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.5854 | 29.4112 | 6.5249 | 27.4744 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19032
Anhui Rinengzhongtian Semiconductor Development | QJP245-60 | 245 W Polycrystalline Module | UL 1703 | 245 | 219 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.06 | 36.4 | 8.09 | 30.3 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.62 | 28.69 | 6.45 | 27.72 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18971
Anhui Rinengzhongtian Semiconductor Development | QJM250-60 | 250 W Monocrystalline Module | UL 1703 | 250 | 225.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.86 | 37.15 | 8.28 | 30.2 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.6122 | 29.5089 | 6.6355 | 27.5656 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1903
Anhui Rinengzhongtian Semiconductor Development | QJP250-60 | 250 W Polycrystalline Module | UL 1703 | 250 | 223.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.21 | 36.5 | 8.22 | 30.4 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.65 | 28.78 | 6.56 | 27.81 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18995
Anhui Rinengzhongtian Semiconductor Development | QJM255-60 | 255 W Monocrystalline Module | UL 1703 | 255 | 229.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.92 | 37.64 | 8.33 | 30.6 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.6158 | 30.7005 | 6.5965 | 28.6078 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19453
Anhui Rinengzhongtian Semiconductor Development | QJP255-60 | 255 W Polycrystalline Module | UL 1703 | 255 | 231 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.95 | 37.52 | 8.36 | 30.5 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6063 | 29.8981 | 6.6289 | 27.9636 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18834
Anhui Rinengzhongtian Semiconductor Development | QJP255-72 | 255 W Polycrystalline Module | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.13 | 42.1 | 7.26 | 35.1 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.3932 | 33.2884 | 5.7716 | 30.9463 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18187
Anhui Rinengzhongtian Semiconductor Development | QJM260-60 | 260 W Monocrystalline Module | UL 1703 | 260 | 234.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.15 | 37.39 | 8.55 | 30.4 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.6591 | 30.4998 | 6.7731 | 28.4208 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19462
Anhui Rinengzhongtian Semiconductor Development | QJP260-60 | 260 W Polycrystalline Module | UL 1703 | 260 | 235.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.09 | 37.64 | 8.5 | 30.6 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6324 | 29.9961 | 6.7367 | 28.0553 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18833
Anhui Rinengzhongtian Semiconductor Development | QJP260-72 | 260 W Polycrystalline Module | UL 1703 | 260 | 231.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.27 | 42.2 | 7.39 | 35.2 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.4181 | 33.3832 | 5.875 | 31.0345 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18208
Anhui Rinengzhongtian Semiconductor Development | QJM265-60 | 265 W Monocrystalline Module | UL 1703 | 265 | 239.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.3 | 37.52 | 8.69 | 30.5 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.6854 | 30.6002 | 6.8808 | 28.5143 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19462
Anhui Rinengzhongtian Semiconductor Development | QJP265-60 | 265 W Polycrystalline Module | UL 1703 | 265 | 240.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.24 | 37.76 | 8.63 | 30.7 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6584 | 30.0941 | 6.8438 | 28.1469 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18833
Anhui Rinengzhongtian Semiconductor Development | QJP265-72 | 265 W Polycrystalline Module | UL 1703 | 265 | 236.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.41 | 42.3 | 7.51 | 35.3 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.4411 | 33.478 | 5.9704 | 31.1227 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18206
Anhui Rinengzhongtian Semiconductor Development | QJM270-60 | 270 W Monocrystalline Module | UL 1703 | 270 | 243.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.44 | 37.64 | 8.82 | 30.6 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.7116 | 30.7005 | 6.9877 | 28.6078 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19462
Anhui Rinengzhongtian Semiconductor Development | QJM270-72 | 270 W Monocrystalline Module | UL 1703 | 270 | 242 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.14 | 43.67 | 7.61 | 35.5 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5317 | 34.6534 | 6.012 | 32.3498 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19658
Anhui Rinengzhongtian Semiconductor Development | QJP270-60 | 270 W Polycrystalline Module | UL 1703 | 270 | 245 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.38 | 37.88 | 8.77 | 30.8 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6841 | 30.1921 | 6.95 | 28.2386 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18832
Anhui Rinengzhongtian Semiconductor Development | QJP270-72 | 270 W Polycrystalline Module | UL 1703 | 270 | 240.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.57 | 42.4 | 7.65 | 35.3 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.4327 | 33.8279 | 6.0764 | 31.1239 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1795
Anhui Rinengzhongtian Semiconductor Development | QJM275-60 | 275 W Monocrystalline Module | UL 1703 | 275 | 248.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.55 | 37.88 | 8.93 | 30.8 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.732 | 30.9012 | 7.0709 | 28.7948 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19462
Anhui Rinengzhongtian Semiconductor Development | QJM275-72 | 275 W Monocrystalline Module | UL 1703 | 275 | 246.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.27 | 43.79 | 7.73 | 35.6 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5556 | 34.751 | 6.106 | 32.4409 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19658
Anhui Rinengzhongtian Semiconductor Development | QJP275-60 | 275 W Polycrystalline Module | UL 1703 | 275 | 249.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.52 | 38.01 | 8.9 | 30.9 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.7099 | 30.2902 | 7.0562 | 28.3303 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18833
Anhui Rinengzhongtian Semiconductor Development | QJP275-72 | 275 W Polycrystalline Module | UL 1703 | 275 | 245.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 42.6 | 7.75 | 35.5 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.4515 | 34.0196 | 6.1558 | 31.3002 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.17956
Anhui Rinengzhongtian Semiconductor Development | QJM280-72 | 280 W Monocrystalline Module | UL 1703 | 280 | 251.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.39 | 43.91 | 7.84 | 35.7 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5008 | 34.7851 | 6.1722 | 32.5512 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18645
Anhui Rinengzhongtian Semiconductor Development | QJP280-72 | 280 W Polycrystalline Module | UL 1703 | 280 | 249.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.78 | 42.8 | 7.84 | 35.7 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.4683 | 34.2113 | 6.2273 | 31.4765 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1794
Anhui Rinengzhongtian Semiconductor Development | QJM285-72 | 285 W Monocrystalline Module | UL 1703 | 285 | 255.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.52 | 44.03 | 7.96 | 35.8 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5234 | 34.8825 | 6.2651 | 32.6424 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18645
Anhui Rinengzhongtian Semiconductor Development | QJP285-72 | 285 W Polycrystalline Module | UL 1703 | 285 | 254.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.89 | 43.1 | 7.94 | 35.9 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.5043 | 34.6277 | 6.2197 | 32.1056 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18277
Anhui Rinengzhongtian Semiconductor Development | QJM290-72 | 290 W Monocrystalline Module | UL 1703 | 290 | 260.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.64 | 44.16 | 8.08 | 35.9 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5458 | 34.98 | 6.3571 | 32.7336 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18645
Anhui Rinengzhongtian Semiconductor Development | QJP290-72 | 290 W Polycrystalline Module | UL 1703 | 290 | 259.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.01 | 43.2 | 8.05 | 36 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.5251 | 34.7242 | 6.3059 | 32.1951 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18262
Anhui Rinengzhongtian Semiconductor Development | QJM295-72 | 295 W Monocrystalline Module | UL 1703 | 295 | 265.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.77 | 44.28 | 8.19 | 36 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.568 | 35.0774 | 6.4484 | 32.8247 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18644
Anhui Rinengzhongtian Semiconductor Development | QJP295-72 | 295 W Polycrystalline Module | UL 1703 | 295 | 263.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.15 | 43.3 | 8.17 | 36.1 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.5479 | 34.8206 | 6.3999 | 32.2845 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1827
Anhui Rinengzhongtian Semiconductor Development | QJM300-72 | 300 W Monocrystalline Module | UL 1703 | 300 | 269.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.31 | 44.4 | 8.31 | 36.1 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5902 | 35.1749 | 6.5397 | 32.9159 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18644
Anhui Rinengzhongtian Semiconductor Development | QJP300-72 | 300 W Polycrystalline Module | UL 1703 | 300 | 268.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.27 | 43.4 | 8.28 | 36.2 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.5687 | 34.9171 | 6.4861 | 32.3739 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18258
Anhui Rinengzhongtian Semiconductor Development | QJM305-72 | 305 W Monocrystalline Module | UL 1703 | 305 | 274.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.02 | 44.53 | 8.43 | 36.2 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.6232 | 35.4283 | 6.6483 | 33.2047 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18855
Anhui Rinengzhongtian Semiconductor Development | QJP305-72 | 305 W Polycrystalline Module | UL 1703 | 305 | 276.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.02 | 44.53 | 8.43 | 36.2 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6207 | 35.4946 | 6.7544 | 33.3727 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18861
Anhui Rinengzhongtian Semiconductor Development | QJM310-72 | 310 W Monocrystalline Module | UL 1703 | 310 | 278.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.14 | 44.65 | 8.54 | 36.3 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.6454 | 35.5262 | 6.7391 | 33.2964 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18856
Anhui Rinengzhongtian Semiconductor Development | QJP310-72 | 310 W Polycrystalline Module | UL 1703 | 310 | 281 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.14 | 44.65 | 8.54 | 36.3 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6429 | 35.5927 | 6.8466 | 33.4649 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18863
Anhui Rinengzhongtian Semiconductor Development | QJM315-72 | 315 W Monocrystalline Module | UL 1703 | 315 | 283.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.26 | 44.77 | 8.65 | 36.4 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.6673 | 35.624 | 6.829 | 33.3881 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18856
Anhui Rinengzhongtian Semiconductor Development | QJP315-72 | 315 W Polycrystalline Module | UL 1703 | 315 | 285.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.26 | 44.77 | 8.65 | 36.4 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6648 | 35.6907 | 6.938 | 33.557 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18863
Anhui Rinengzhongtian Semiconductor Development | QJM320-72 | 320 W Monocrystalline Module | UL 1703 | 320 | 288.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.38 | 44.9 | 8.77 | 36.5 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.6891 | 35.7219 | 6.9182 | 33.4798 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18856
Anhui Rinengzhongtian Semiconductor Development | QJP320-72 | 320 W Polycrystalline Module | UL 1703 | 320 | 290.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.38 | 44.9 | 8.77 | 36.5 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6865 | 35.7888 | 7.0286 | 33.6492 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18862
Anhui Rinengzhongtian Semiconductor Development | QJM325-72 | 325 W Monocrystalline Module | UL 1703 | 325 | 292.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.48 | 45.14 | 8.86 | 36.7 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.7062 | 35.9177 | 6.9884 | 33.6633 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18857
Anhui Rinengzhongtian Semiconductor Development | QJP325-72 | 325 W Polycrystalline Module | UL 1703 | 325 | 295 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.5 | 45.02 | 8.88 | 36.6 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.7083 | 35.8868 | 7.1192 | 33.7414 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18863
Anhui Rinengzhongtian Semiconductor Development | QJM330-72 | 330 W Monocrystalline Module | UL 1703 | 330 | 297.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.6 | 45.26 | 8.97 | 36.8 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.7276 | 36.0155 | 7.076 | 33.755 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18855
Anhui Rinengzhongtian Semiconductor Development | QJP330-72 | 330 W Polycrystalline Module | UL 1703 | 330 | 299.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.62 | 45.14 | 8.99 | 36.7 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.7298 | 35.9849 | 7.209 | 33.8336 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18863
Anhui Rinengzhongtian Semiconductor Development Co., Ltd | QJM335-72 | 335 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 335 | 304.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.335 | 46.848 | 8.724 | 38.4 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.6496 | 37.8557 | 6.98 | 35.3616 | [6 empty] | 2018-06-15 | 2018-08-15
Anhui Rinengzhongtian Semiconductor Development Co., Ltd | QJM340-72 | 340 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 340 | 309.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.449 | 46.97 | 8.831 | 38.5 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.6699 | 37.9543 | 7.0656 | 35.4537 | [6 empty] | 2018-06-15 | 2018-08-15
Anhui Rinengzhongtian Semiconductor Development Co., Ltd | QJM345-72 | 345 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 345 | 314 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.563 | 47.092 | 8.938 | 38.6 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.6901 | 38.0528 | 7.1512 | 35.5458 | [6 empty] | 2018-06-15 | 2018-08-15
Anhui Rinengzhongtian Semiconductor Development Co., Ltd | QJM350-72 | 350 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 350 | 318.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.677 | 47.214 | 9.044 | 38.7 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.7101 | 38.1514 | 7.236 | 35.6379 | [6 empty] | 2018-06-15 | 2018-08-15
Anhui Rinengzhongtian Semiconductor Development Co., Ltd | QJM355-72 | 355 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 355 | 323.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.79 | 47.336 | 9.149 | 38.8 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.73 | 38.25 | 7.32 | 35.73 | [6 empty] | 2018-06-15 | 2018-08-15
Anhui Rinengzhongtian Semiconductor Development Co., Ltd | QJM360-72 | 360 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 360 | 328.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.902 | 47.458 | 9.254 | 38.9 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.7499 | 38.3486 | 7.404 | 35.8221 | [6 empty] | 2018-06-15 | 2018-08-15
Anhui Rinengzhongtian Semiconductor Development Co., Ltd | QJM365-72 | 365 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 365 | 332.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 10.014 | 47.58 | 9.359 | 39 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.7697 | 38.4472 | 7.488 | 35.9142 | [6 empty] | 2018-06-15 | 2018-08-15
Anhui Rinengzhongtian Semiconductor Development Co., Ltd | QJM370-72 | 370 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 370 | 337.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 10.125 | 47.702 | 9.463 | 39.1 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.7894 | 38.5457 | 7.5712 | 36.0063 | [6 empty] | 2018-06-15 | 2018-08-15
Anji Dasol Solar Energy Science & Technology | DS-A4-210 | 210 W Polycrystalline Module | UL 1703 | 210 | 182.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6467 | 60 | 1 | N | 8 | 36.1 | 7.19 | 29.2 | 48.6 | -0.50533 | 0.086957 | -0.38696 | 0.021888 | -0.52517 | 1.4557 | 28.0924 | 5.5297 | 25.4644 | Rack | Flat Plate | 0.992 | 1.66 | 1 | 0.19473
Anji Dasol Solar Energy Science & Technology | DS-A4-215 | 215 W Polycrystalline Module | UL 1703 | 215 | 187.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6467 | 60 | 1 | N | 8 | 36.3 | 7.31 | 29.4 | 48.6 | -0.50533 | 0.086957 | -0.38696 | 0.021888 | -0.52517 | 1.48 | 28.2848 | 5.622 | 25.6388 | Rack | Flat Plate | 0.992 | 1.66 | 1 | 0.1947
Anji Dasol Solar Energy Science & Technology | DS-A4-220 | 220 W Polycrystalline Module | UL 1703 | 220 | 191.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6467 | 60 | 1 | N | 8.1 | 36.5 | 7.44 | 29.6 | 48.6 | -0.50533 | 0.086957 | -0.38696 | 0.021888 | -0.52517 | 1.5063 | 28.4772 | 5.722 | 25.8132 | Rack | Flat Plate | 0.992 | 1.66 | 1 | 0.19498
Anji Dasol Solar Energy Science & Technology | DS-A4-225 | 225 W Polycrystalline Module | UL 1703 | 225 | 196.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6467 | 60 | 1 | N | 8.2 | 36.7 | 7.55 | 29.8 | 48.6 | -0.50533 | 0.086957 | -0.38696 | 0.021888 | -0.52517 | 1.5286 | 28.6697 | 5.8066 | 25.9877 | Rack | Flat Plate | 0.992 | 1.66 | 1 | 0.19477
Anji Dasol Solar Energy Science & Technology | DS-A4-230 | 230 W Polycrystalline Module | UL 1703 | 230 | 200.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6467 | 60 | 1 | N | 8.3 | 36.9 | 7.67 | 30 | 48.6 | -0.50533 | 0.086957 | -0.38696 | 0.021888 | -0.52517 | 1.5529 | 28.8621 | 5.8989 | 26.1621 | Rack | Flat Plate | 0.992 | 1.66 | 1 | 0.19487
Anji Technology | AJP-S572-175 | 175 W Monocrystalline Module | UL 1703 | 175 | 151.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3002 | 72 | 1 | N | 5.17 | 43.99 | 4.78 | 36.63 | 49.9 | -0.5072 | 0.0415 | -0.3616 | 0.0001 | -0.5073 | 0.99299 | 34.9239 | 3.6799 | 32.0437 | Rack | Flat Plate | 0.825 | 1.576 | 1 | 0.19817
Anji Technology | AJP-S572-180 | 180 W Monocrystalline Module | UL 1703 | 180 | 155.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3002 | 72 | 1 | N | 5.31 | 44.06 | 4.9 | 36.72 | 49.9 | -0.5072 | 0.0415 | -0.3616 | 0.0001 | -0.5073 | 1.0179 | 35.0098 | 3.7723 | 32.1225 | Rack | Flat Plate | 0.825 | 1.576 | 1 | 0.19798
Anji Technology | AJP-S572-185 | 185 W Monocrystalline Module | UL 1703 | 185 | 160.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3002 | 72 | 1 | N | 5.43 | 44.14 | 5.03 | 36.72 | 49.9 | -0.5072 | 0.0415 | -0.3616 | 0.0001 | -0.5073 | 1.0449 | 35.0098 | 3.8724 | 32.1225 | Rack | Flat Plate | 0.825 | 1.576 | 1 | 0.19774
Anji Technology | AJP-M660-220 | 220 W Polycrystalline Module | UL 1703 | 220 | 189.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 7.95 | 36.06 | 7.3 | 30.12 | 50.2 | -0.5196 | 0.0548 | -0.3624 | -0.0413 | -0.4835 | 1.4114 | 29.5053 | 5.5615 | 26.4728 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.18929
Anji Technology | AJP-M660-225 | 225 W Polycrystalline Module | UL 1703 | 225 | 193.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.04 | 36.24 | 7.44 | 30.24 | 50.2 | -0.5196 | 0.0548 | -0.3624 | -0.0413 | -0.4835 | 1.4385 | 29.6229 | 5.6681 | 26.5783 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.18938
Anji Technology | AJP-M660-230 | 230 W Polycrystalline Module | UL 1703 | 230 | 204.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.1 | 36.42 | 7.58 | 30.36 | 46.4 | -0.493 | 0.097 | -0.359 | 0.047 | -0.531 | 1.4411 | 30.3465 | 6.0318 | 27.8504 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.19014
Anji Technology | AJP-M660-235 | 235 W Polycrystalline Module | UL 1703 | 235 | 208.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.23 | 36.72 | 7.68 | 30.6 | 46.4 | -0.493 | 0.097 | -0.359 | 0.047 | -0.531 | 1.4601 | 30.5864 | 6.1113 | 28.0706 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.19004
Anji Technology | AJP-M660-240 | 240 W Polycrystalline Module | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.32 | 36.84 | 7.83 | 30.72 | 46.4 | -0.493 | 0.097 | -0.359 | 0.047 | -0.531 | 1.4886 | 30.7063 | 6.2307 | 28.1807 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.19046
Anji Technology | AJP-M660-245 | 245 W Polycrystalline Module | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.43 | 37.08 | 7.94 | 30.84 | 46.4 | -0.493 | 0.097 | -0.359 | 0.047 | -0.531 | 1.5095 | 30.8263 | 6.3182 | 28.2908 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.18993
Anji Technology | AJP-M660-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 222.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.5 | 37.32 | 8.03 | 31.14 | 46.4 | -0.493 | 0.097 | -0.359 | 0.047 | -0.531 | 1.5267 | 31.1261 | 6.3899 | 28.566 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.19008
APOS Energy | AP130 | 130 W Polycrystalline Module | UL 1703 | 130 | 115.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.023 | 36 | 1 | N | 7.86 | 22.07 | 7.43 | 17.38 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5607 | 17.7886 | 5.9842 | 16.0914 | Rack | Flat Plate | 0.682 | 1.5 | 1 | 0.21356
APOS Energy | AP135 | 135 W Polycrystalline Module | UL 1703 | 135 | 119.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.023 | 36 | 1 | N | 7.94 | 22.21 | 7.54 | 17.58 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5838 | 17.9933 | 6.0728 | 16.2766 | Rack | Flat Plate | 0.682 | 1.5 | 1 | 0.21109
APOS Energy | AS135 | 135 W Monocrystalline Module | UL 1703 | 135 | 120.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.023 | 36 | 1 | N | 8.34 | 22.19 | 7.69 | 17.59 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6387 | 18.0537 | 6.2981 | 15.9619 | Rack | Flat Plate | 0.682 | 1.5 | 1 | 0.21914
APOS Energy | AP140 | 140 W Polycrystalline Module | UL 1703 | 140 | 124.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.023 | 36 | 1 | N | 8.05 | 22.39 | 7.69 | 17.93 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.6153 | 18.3515 | 6.1936 | 16.6007 | Rack | Flat Plate | 0.682 | 1.5 | 1 | 0.21174
APOS Energy | AS140 | 140 W Monocrystalline Module | UL 1703 | 140 | 125.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.023 | 36 | 1 | N | 8.51 | 22.33 | 7.84 | 17.76 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6707 | 18.2282 | 6.4209 | 16.1161 | Rack | Flat Plate | 0.682 | 1.5 | 1 | 0.21752
APOS Energy | AS145 | 145 W Monocrystalline Module | UL 1703 | 145 | 130 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.023 | 36 | 1 | N | 8.63 | 22.51 | 7.95 | 18.03 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6941 | 18.5053 | 6.511 | 16.3611 | Rack | Flat Plate | 0.682 | 1.5 | 1 | 0.21621
APOS Energy | AP175 | 175 W Polycrystalline Module | UL 1703 | 175 | 155.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.341 | 48 | 1 | N | 7.9 | 29.52 | 7.48 | 23.31 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5552 | 23.6752 | 6.0298 | 21.651 | Rack | Flat Plate | 1 | 1.341 | 1 | 0.21039
APOS Energy | AP180 | 180 W Polycrystalline Module | UL 1703 | 180 | 160 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.341 | 48 | 1 | N | 7.97 | 29.72 | 7.59 | 23.58 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.578 | 23.9494 | 6.1185 | 21.9017 | Rack | Flat Plate | 1 | 1.341 | 1 | 0.20996
APOS Energy | AS180 | 180 W Monocrystalline Module | UL 1703 | 180 | 161.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.341 | 48 | 1 | N | 8.34 | 29.59 | 7.69 | 23.45 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6443 | 23.7662 | 6.2524 | 21.1958 | Rack | Flat Plate | 1 | 1.341 | 1 | 0.21711
APOS Energy | AP185 | 185 W Polycrystalline Module | UL 1703 | 185 | 164.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.341 | 48 | 1 | N | 8.05 | 29.86 | 7.69 | 23.9 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5988 | 24.2744 | 6.1991 | 22.199 | Rack | Flat Plate | 1 | 1.341 | 1 | 0.20979
APOS Energy | AS185 | 185 W Monocrystalline Module | UL 1703 | 185 | 165.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.341 | 48 | 1 | N | 8.51 | 29.78 | 7.84 | 23.68 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6764 | 23.9993 | 6.3744 | 21.4037 | Rack | Flat Plate | 1 | 1.341 | 1 | 0.21747
APOS Energy | AP190 | 190 W Polycrystalline Module | UL 1703 | 190 | 168.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5 | 54 | 1 | N | 7.79 | 32.89 | 7.33 | 25.76 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5482 | 25.629 | 6.0016 | 23.5739 | Rack | Flat Plate | 1 | 1.5 | 1 | 0.20883
APOS Energy | AS190 | 190 W Monocrystalline Module | UL 1703 | 190 | 170.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.341 | 48 | 1 | N | 8.59 | 29.92 | 7.91 | 23.9 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6914 | 24.2223 | 6.4313 | 21.6025 | Rack | Flat Plate | 1 | 1.341 | 1 | 0.21563
APOS Energy | AP195 | 195 W Polycrystalline Module | UL 1703 | 195 | 173.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5 | 54 | 1 | N | 7.86 | 33.11 | 7.43 | 26.06 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5693 | 25.9275 | 6.0835 | 23.8484 | Rack | Flat Plate | 1 | 1.5 | 1 | 0.20866
APOS Energy | AS195 | 195 W Monocrystalline Module | UL 1703 | 195 | 174.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5 | 54 | 1 | N | 8.15 | 32.6 | 7.48 | 25.97 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.5555 | 25.8178 | 6.0685 | 23.6054 | Rack | Flat Plate | 1 | 1.5 | 1 | 0.20595
APOS Energy | AP200 | 200 W Polycrystalline Module | UL 1703 | 200 | 177.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5 | 54 | 1 | N | 7.94 | 33.32 | 7.54 | 26.37 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5925 | 26.2359 | 6.1736 | 24.1321 | Rack | Flat Plate | 1 | 1.5 | 1 | 0.20891
APOS Energy | AS200 | 200 W Monocrystalline Module | UL 1703 | 200 | 179.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5 | 54 | 1 | N | 8.28 | 32.97 | 7.62 | 26.18 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.5846 | 26.0265 | 6.1821 | 23.7963 | Rack | Flat Plate | 1 | 1.5 | 1 | 0.20621
APOS Energy | AP205 | 205 W Polycrystalline Module | UL 1703 | 205 | 182.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5 | 54 | 1 | N | 8.01 | 33.48 | 7.64 | 26.68 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.6137 | 26.5444 | 6.2554 | 24.4158 | Rack | Flat Plate | 1 | 1.5 | 1 | 0.20894
APOS Energy | AS205 | 205 W Monocrystalline Module | UL 1703 | 205 | 183.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5 | 54 | 1 | N | 8.42 | 33.34 | 7.77 | 26.38 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6158 | 26.2254 | 6.3038 | 23.9781 | Rack | Flat Plate | 1 | 1.5 | 1 | 0.20671
APOS Energy | AP210 | 210 W Polycrystalline Module | UL 1703 | 210 | 186.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.659 | 60 | 1 | N | 7.79 | 36.55 | 7.33 | 28.62 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5508 | 28.6502 | 6.0682 | 25.9706 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.21157
APOS Energy | AS210 | 210 W Monocrystalline Module | UL 1703 | 210 | 188.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5 | 54 | 1 | N | 8.51 | 33.5 | 7.84 | 26.63 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6304 | 26.4739 | 6.3606 | 24.2053 | Rack | Flat Plate | 1 | 1.5 | 1 | 0.20554
APOS Energy | AP215 | 215 W Polycrystalline Module | UL 1703 | 215 | 190.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.659 | 60 | 1 | N | 7.86 | 36.79 | 7.43 | 28.96 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5719 | 28.9906 | 6.151 | 26.2791 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.21196
APOS Energy | AS215 | 215 W Monocrystalline Module | UL 1703 | 215 | 192.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5 | 54 | 1 | N | 8.59 | 33.66 | 7.91 | 26.89 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.645 | 26.7324 | 6.4174 | 24.4416 | Rack | Flat Plate | 1 | 1.5 | 1 | 0.20453
APOS Energy | AP220 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.659 | 60 | 1 | N | 7.9 | 36.91 | 7.48 | 29.13 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.5825 | 29.1608 | 6.1924 | 26.4333 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.20976
APOS Energy | AS220 | 220 W Monocrystalline Module | UL 1703 | 220 | 197 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.659 | 60 | 1 | N | 8.28 | 36.63 | 7.62 | 29.08 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6378 | 29.08 | 6.198 | 23.252 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.21648
APOS Energy | AP225 | 225 W Polycrystalline Module | UL 1703 | 225 | 200 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.659 | 60 | 1 | N | 7.97 | 37.14 | 7.59 | 29.48 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.6058 | 29.5111 | 6.2834 | 26.7509 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.21061
APOS Energy | AS225 | 225 W Monocrystalline Module | UL 1703 | 225 | 201.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.659 | 60 | 1 | N | 8.34 | 36.99 | 7.69 | 29.31 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6528 | 29.31 | 6.2549 | 23.4359 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.21531
APOS Energy | AP230 | 230 W Polycrystalline Module | UL 1703 | 230 | 204.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.659 | 60 | 1 | N | 8.05 | 37.32 | 7.69 | 29.88 | 49.1 | -0.429 | 0.123 | -0.296 | 0.061 | -0.376 | 1.6269 | 29.9116 | 6.3662 | 27.1139 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.21158
APOS Energy | AS230 | 230 W Monocrystalline Module | UL 1703 | 230 | 206.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.659 | 60 | 1 | N | 8.46 | 37.11 | 7.82 | 29.42 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6807 | 29.42 | 6.3607 | 23.5239 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.21499
APOS Energy | AS235 | 235 W Monocrystalline Module | UL 1703 | 235 | 210.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.659 | 60 | 1 | N | 8.55 | 37.34 | 7.86 | 29.76 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.6893 | 29.76 | 6.3932 | 23.7957 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.21394
APOS Energy | AS240 | 240 W Monocrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.659 | 60 | 1 | N | 8.63 | 37.52 | 7.95 | 30.05 | 47.8 | -0.425 | 0.086 | -0.288 | 0.025 | -0.403 | 1.7087 | 30.05 | 6.4664 | 24.0276 | Rack | Flat Plate | 1 | 1.659 | 1 | 0.21394
Applied Materials | 1/4 Size Tandem Junction | 114 W Thin Film Tandem Junction Module | UL 1703 | 114 | 104.6 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.43 | 106 | 1 | N | 1.3 | 137.6 | 1.08 | 106 | 44.1 | -0.368 | 0.104 | -0.401 | 0.165 | -0.475 | 0.2052 | 98.7059 | 0.864 | 96.6536 | Rack | Flat Plate | 1.1 | 1.3 | 1 | 0.17767
Applied Materials | 1/4 Size Single Junction Version 1.0 | 116 W Thin Film Single Junction Amorphous Silicon Module | UL 1703 | 116 | 107.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.43 | 106 | 1 | N | 1.7 | 96.2 | 1.47 | 77.8 | 44.8 | -0.3 | 0.08 | -0.33 | 0.04 | -0.34 | 0.22936 | 80.2951 | 1.1989 | 70.5464 | Rack | Flat Plate | 1.1 | 1.3 | 1 | 0.15876
Applied Materials | 1/2-L Size Single Junction Version 1.0 | 207 W Thin Film Single Junction Amorphous Silicon Module | UL 1703 | 207 | 192.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 2.86 | 216 | 1 | N | 1.45 | 194.2 | 1.3 | 159.8 | 44.8 | -0.3 | 0.08 | -0.33 | 0.04 | -0.34 | 0.20284 | 164.9248 | 1.0603 | 144.9012 | Rack | Flat Plate | 1.3 | 2.2 | 1 | 0.16161
Applied Materials | 1/2-P Size Single Junction Version 1.0 | 207 W Thin Film Single Junction Amorphous Silicon Module | UL 1703 | 207 | 192.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 2.86 | 106 | 1 | N | 2.9 | 97.1 | 2.59 | 79.9 | 44.8 | -0.3 | 0.08 | -0.33 | 0.04 | -0.34 | 0.40411 | 82.4624 | 2.1124 | 72.4506 | Rack | Flat Plate | 1.1 | 2.6 | 1 | 0.16099
Applied Materials | 1/2-L Size Tandem Junction | 229 W Thin Film Tandem Junction Module | UL 1703 | 229 | 210.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 2.86 | 216 | 1 | N | 1.3 | 280 | 1.08 | 216 | 44.1 | -0.368 | 0.104 | -0.401 | 0.165 | -0.475 | 0.2052 | 201.1366 | 0.864 | 196.9545 | Rack | Flat Plate | 1.3 | 2.2 | 1 | 0.18023
Applied Materials | 1/2-P Size Tandem Junction | 229 W Thin Film Tandem Junction Module | UL 1703 | 229 | 210.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 2.86 | 106 | 1 | N | 2.6 | 137.6 | 2.16 | 106 | 44.1 | -0.368 | 0.104 | -0.401 | 0.165 | -0.475 | 0.4104 | 98.7059 | 1.728 | 96.6536 | Rack | Flat Plate | 1.1 | 2.6 | 1 | 0.17689
Applied Materials | Full Size Single Junction Version 1.0 | 414 W Thin Film Single Junction Amorphous Silicon Module | UL 1703 | 414 | 384.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 5.72 | 216 | 1 | N | 2.9 | 194.2 | 2.59 | 159.8 | 44.8 | -0.3 | 0.08 | -0.33 | 0.04 | -0.34 | 0.40411 | 164.9248 | 2.1124 | 144.9012 | Rack | Flat Plate | 2.2 | 2.6 | 1 | 0.16099
Applied Materials | Full Size Tandem Junction | 458 W Thin Film Tandem Junction Module | UL 1703 | 458 | 420.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 5.72 | 216 | 1 | N | 2.6 | 280 | 2.16 | 216 | 44.1 | -0.368 | 0.104 | -0.401 | 0.165 | -0.475 | 0.4104 | 201.1366 | 1.728 | 196.9545 | Rack | Flat Plate | 2.2 | 2.6 | 1 | 0.18023
Aptos Solar Technology LLC | DNA-120-BF23-320W | 320 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 320 | 296.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.658 | 60 | 2 | N | 10.13 | 40.18 | 9.7 | 32.99 | 46.38 | -0.358 | 0.046 | -0.275 |  |  | 1.859 | 31.9873 | 7.5338 | 30.6289 | [6 empty] | 2020-01-21 | 2020-11-02
Aptos Solar Technology LLC | DNA-120-MF23-320W [Blk] | 320 W, 120 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 320 | 290.2 | This model is also available with a white backsheet. Please refer to DNA-120-MF23-320W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6874 | 60 | 2 | N | 10.13 | 39.92 | 9.69 | 33.01 | 48.5 | -0.4034 | 0.0686 | -0.3162 |  |  | 2.3322 | 32.899 | 7.2895 | 30.2247 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-120-MF23-320W [Wht] | 320 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 320 | 299 | This model is also available with a black backsheet. Please refer to DNA-120-MF23-320W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.13 | 39.92 | 9.69 | 33.01 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.8819 | 32.7312 | 7.6098 | 31.4513 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-120-BF23-325W | 325 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 325 | 300.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.658 | 60 | 2 | N | 10.15 | 40.3 | 9.82 | 33.1 | 46.38 | -0.358 | 0.046 | -0.275 |  |  | 1.882 | 32.094 | 7.627 | 30.731 | [6 empty] | 2020-01-21 | 2020-11-02
Aptos Solar Technology LLC | DNA-120-MF23-325W [Blk] | 325 W, 120 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 325 | 294.8 | This model is also available with a white backsheet. Please refer to DNA-120-MF23-325W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6874 | 60 | 2 | N | 10.43 | 40.1 | 9.93 | 32.71 | 48.5 | -0.4034 | 0.0686 | -0.3162 |  |  | 2.39 | 32.6 | 7.47 | 29.95 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-120-MF23-325W [Wht] | 325 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 325 | 303.8 | This model is also available with a black backsheet. Please refer to DNA-120-MF23-325W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.43 | 40.1 | 9.93 | 32.71 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9285 | 32.4337 | 7.7983 | 31.1654 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-120-BF23-330W | 330 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 330 | 305.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.658 | 60 | 2 | N | 10.25 | 40.39 | 9.93 | 33.24 | 46.38 | -0.358 | 0.046 | -0.275 |  |  | 1.9031 | 32.2297 | 7.7124 | 30.861 | [6 empty] | 2020-01-21 | 2020-11-02
Aptos Solar Technology LLC | DNA-120-MF23-330W [Blk] | 330 W, 120 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 330 | 299.5 | This model is also available with a white backsheet. Please refer to DNA-120-MF23-330W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6874 | 60 | 2 | N | 10.51 | 40.27 | 10.02 | 32.91 | 48.5 | -0.4034 | 0.0686 | -0.3162 |  |  | 2.4117 | 32.7993 | 7.5377 | 30.1331 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-120-MF23-330W [Wht] | 330 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 330 | 308.6 | This model is also available with a black backsheet. Please refer to DNA-120-MF23-330W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.51 | 40.27 | 10.02 | 32.91 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.946 | 32.632 | 7.869 | 31.356 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-120-BF23-335W | 335 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 335 | 310.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.658 | 60 | 2 | N | 10.34 | 40.46 | 10.03 | 33.4 | 46.38 | -0.358 | 0.046 | -0.275 |  |  | 1.9222 | 32.3849 | 7.7901 | 31.0095 | [6 empty] | 2020-01-21 | 2020-11-02
Aptos Solar Technology LLC | DNA-120-MF23-335W [Blk] | 335 W, 120 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 335 | 304.2 | This model is also available with a white backsheet. Please refer to DNA-120-MF23-335W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6874 | 60 | 2 | N | 10.6 | 40.44 | 10.11 | 33.11 | 48.5 | -0.4034 | 0.0686 | -0.3162 |  |  | 2.4333 | 32.9987 | 7.6054 | 30.3162 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-120-MF23-335W [Wht] | 335 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 335 | 313.4 | This model is also available with a black backsheet. Please refer to DNA-120-MF23-335W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.6 | 40.44 | 10.11 | 33.11 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9635 | 32.8303 | 7.9397 | 31.5466 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-120-BF23-340W | 340 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 340 | 317.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.644 | 60 | 2 | N | 10.43 | 40.6 | 10.11 | 33.62 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9376 | 32.3321 | 7.845 | 31.2067 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-120-MF23-340W [Blk] | 340 W, 120 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 340 | 308.9 | This model is also available with a white backsheet. Please refer to DNA-120-MF23-340W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6874 | 60 | 2 | N | 10.69 | 40.62 | 10.21 | 33.31 | 48.5 | -0.4034 | 0.0686 | -0.3162 |  |  | 2.4574 | 33.198 | 7.6806 | 30.4994 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-120-MF23-340W [Wht] | 340 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 340 | 318.2 | This model is also available with a black backsheet. Please refer to DNA-120-MF23-340W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.69 | 40.62 | 10.21 | 33.31 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9829 | 33.0286 | 8.0182 | 31.7371 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-120-BF26-360W | 360 W, 120 half-cut cell bifacial monocrystalline module, transparent backsheet, 1000V max system Vdc | UL 61730 | 360 | 332 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.76 | 60 | 2 | N | 11.26 | 40.26 | 10.72 | 33.58 | 47.2 | -0.366 | 0.045 | -0.293 |  |  | 1.964 | 33.155 | 8.116 | 32.576 | [6 empty] | 2021-10-01
Aptos Solar Technology LLC | DNA-120-MF26-360W | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 328.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.76 | 60 | 2 | N | 11.24 | 40.6 | 10.66 | 33.8 | 48.4 | -0.392 | 0.011 | -0.278 |  |  | 2.15 | 32.43 | 8.11 | 25.01 | [6 empty] | 2021-06-21
Aptos Solar Technology LLC | DNA-120-BF26-365W | 365 W, 120 half-cut cell bifacial monocrystalline module, transparent backsheet, 1000V max system Vdc | UL 61730 | 365 | 336.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.76 | 60 | 2 | N | 11.28 | 40.59 | 10.75 | 34 | 47.2 | -0.366 | 0.045 | -0.293 |  |  | 1.9695 | 33.5697 | 8.1387 | 32.9834 | [6 empty] | 2021-10-01
Aptos Solar Technology LLC | DNA-120-MF26-365W | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 333.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.76 | 60 | 2 | N | 11.36 | 40.7 | 10.75 | 33.96 | 48.4 | -0.392 | 0.011 | -0.278 |  |  | 2.1682 | 32.5835 | 8.1785 | 25.1284 | [6 empty] | 2021-06-21
Aptos Solar Technology LLC | DNA-120-BF26-370W | 370 W, 120 half-cut cell bifacial monocrystalline module, transparent backsheet, 1000V max system Vdc | UL 61730 | 370 | 341.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.76 | 60 | 2 | N | 11.3 | 40.91 | 10.84 | 34.2 | 47.2 | -0.366 | 0.045 | -0.293 |  |  | 1.986 | 33.7672 | 8.2069 | 33.1775 | [6 empty] | 2021-10-01
Aptos Solar Technology LLC | DNA-120-MF26-370W | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 370 | 337.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.76 | 60 | 2 | N | 11.51 | 40.8 | 10.87 | 34.06 | 48.4 | -0.392 | 0.011 | -0.278 |  |  | 2.1924 | 32.6795 | 8.2698 | 25.2024 | [6 empty] | 2021-06-21
Aptos Solar Technology LLC | DNA-144-BF23-390W | 390 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 361 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.981 | 72 | 2 | N | 10.14 | 48.18 | 9.83 | 39.68 | 46.38 | -0.358 | 0.046 | -0.275 |  |  | 1.898 | 38.514 | 7.683 | 36.785 | [6 empty] | 2020-01-13 | 2020-11-02
Aptos Solar Technology LLC | DNA-144-MF23-390W [Blk] | 390 W, 144 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 390 | 353.5 | This model is also available with a white backsheet. Please refer to DNA-144-MF23-390W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 2 | N | 10.48 | 48.18 | 9.66 | 40.37 | 48.1 | -0.4149 | 0.0489 | -0.3182 |  |  | 2.38 | 39.21 | 7.45 | 36.29 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-144-MF23-390W [Wht] | 390 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 390 | 364.4 | This model is also available with a black backsheet. Please refer to DNA-144-MF23-390W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.48 | 48.18 | 9.66 | 40.37 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.9379 | 38.7253 | 7.8452 | 37.3321 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-144-BF23-395W | 395 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 365.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.981 | 72 | 2 | N | 10.23 | 48.26 | 9.92 | 39.82 | 46.38 | -0.358 | 0.046 | -0.275 |  |  | 1.9154 | 38.6499 | 7.7533 | 36.9148 | [6 empty] | 2020-01-13 | 2020-11-02
Aptos Solar Technology LLC | DNA-144-MF23-395W [Blk] | 395 W, 144 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 395 | 358.2 | This model is also available with a white backsheet. Please refer to DNA-144-MF23-395W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 2 | N | 10.56 | 48.37 | 9.74 | 40.55 | 48.1 | -0.4149 | 0.0489 | -0.3182 |  |  | 2.3997 | 39.3848 | 7.5117 | 36.4518 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-144-MF23-395W [Wht] | 395 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 395 | 369.1 | This model is also available with a black backsheet. Please refer to DNA-144-MF23-395W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.56 | 48.37 | 9.74 | 40.55 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.954 | 38.898 | 7.9102 | 37.4986 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-144-BF23-400W | 400 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 400 | 370.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.981 | 72 | 2 | N | 10.32 | 48.35 | 10 | 40 | 46.38 | -0.358 | 0.046 | -0.275 |  |  | 1.9308 | 38.8246 | 7.8159 | 37.0817 | [6 empty] | 2020-01-13 | 2020-11-02
Aptos Solar Technology LLC | DNA-144-MF23-400W [Blk] | 400 W, 144 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 400 | 362.9 | This model is also available with a white backsheet. Please refer to DNA-144-MF23-400W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 2 | N | 10.64 | 48.55 | 9.81 | 40.77 | 48.1 | -0.4149 | 0.0489 | -0.3182 |  |  | 2.417 | 39.5985 | 7.5657 | 36.6496 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-144-MF23-400W [Wht] | 400 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 400 | 373.9 | This model is also available with a black backsheet. Please refer to DNA-144-MF23-400W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.64 | 48.55 | 9.81 | 40.77 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.968 | 39.109 | 7.967 | 37.702 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-144-BF23-405W | 405 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 405 | 375.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.981 | 72 | 2 | N | 10.42 | 48.45 | 10.08 | 40.18 | 46.38 | -0.358 | 0.046 | -0.275 |  |  | 1.9463 | 38.9993 | 7.8784 | 37.2485 | [6 empty] | 2020-01-13 | 2020-11-02
Aptos Solar Technology LLC | DNA-144-MF23-405W [Blk] | 405 W, 144 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 405 | 367.6 | This model is also available with a white backsheet. Please refer to DNA-144-MF23-405W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 2 | N | 10.71 | 48.73 | 9.89 | 40.95 | 48.1 | -0.4149 | 0.0489 | -0.3182 |  |  | 2.4367 | 39.7733 | 7.6274 | 36.8114 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-144-MF23-405W [Wht] | 405 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 405 | 378.7 | This model is also available with a black backsheet. Please refer to DNA-144-MF23-405W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.71 | 48.73 | 9.89 | 40.95 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.984 | 39.2817 | 8.032 | 37.8685 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-144-BF23-410W | 410 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 410 | 382.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.51 | 48.56 | 10.16 | 40.38 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9347 | 39.0844 | 7.872 | 37.5271 | [6 empty] | 2020-01-13
Aptos Solar Technology LLC | DNA-144-MF23-410W [Blk] | 410 W, 144 half-cut cell monocrystalline module, 5 busbars, black backsheet and black aluminum frame, 1500V max system Vdc | UL 1703 | 410 | 372.3 | This model is also available with a white backsheet. Please refer to DNA-144-MF23-410W [Wht] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 2 | N | 10.79 | 48.91 | 9.97 | 41.12 | 48.1 | -0.4149 | 0.0489 | -0.3182 |  |  | 2.4564 | 39.9384 | 7.6891 | 36.9642 | [6 empty] | 2020-01-21
Aptos Solar Technology LLC | DNA-144-MF23-410W [Wht] | 410 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 410 | 383.5 | This model is also available with a black backsheet. Please refer to DNA-144-MF23-410W [Blk] | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.79 | 48.91 | 9.97 | 41.12 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 2.0001 | 39.4447 | 8.0969 | 38.0257 | [6 empty] | 2019-12-23
Aptos Solar Technology LLC | DNA-144-BF23-415W | 415 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 415 | 387.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.61 | 48.64 | 10.25 | 40.5 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9518 | 39.2005 | 7.9417 | 37.6387 | [6 empty] | 2020-01-13
Aptos Solar Technology LLC | DNA-144-BF26-430W | 430 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 430 | 396.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1 | 72 | 2 | N | 10.85 | 49.17 | 10.36 | 41.51 | 47.2 | -0.366 | 0.045 | -0.293 |  |  | 1.9636 | 39.6368 | 8.1339 | 39.0134 | [6 empty] | 2021-08-23
Aptos Solar Technology LLC | DNA-144-MF26-430W [Blk] | 430 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 430 | 394.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1 | 72 | 2 | N | 11.19 | 49.5 | 10.6 | 40.6 | 47.4 | -0.382 | 0.067 | -0.302 |  |  | 1.9571 | 38.6496 | 8.2654 | 31.9924 | [6 empty] | 2021-06-21
Aptos Solar Technology LLC | DNA-144-MF26-430W [Wht] | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 430 | 398.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1 | 72 | 2 | N | 11.19 | 49.5 | 10.6 | 40.6 | 44.9 | -0.382 | 0.067 | -0.302 |  |  | 1.9571 | 38.6496 | 8.2356 | 32.9775 | [6 empty] | 2021-06-21
Aptos Solar Technology LLC | DNA-144-BF26-435W | 435 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 435 | 401.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1 | 72 | 2 | N | 10.92 | 49.38 | 10.42 | 41.75 | 47.2 | -0.366 | 0.045 | -0.293 |  |  | 1.975 | 39.866 | 8.181 | 39.239 | [6 empty] | 2021-08-23
Aptos Solar Technology LLC | DNA-144-MF26-435W [Blk] | 435 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 435 | 399.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1 | 72 | 2 | N | 11.26 | 49.7 | 10.67 | 40.8 | 47.4 | -0.382 | 0.067 | -0.302 |  |  | 1.97 | 38.84 | 8.32 | 32.15 | [6 empty] | 2021-06-21
Aptos Solar Technology LLC | DNA-144-MF26-435W [Wht] | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 435 | 403.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1 | 72 | 2 | N | 11.26 | 49.7 | 10.67 | 40.8 | 44.9 | -0.382 | 0.067 | -0.302 |  |  | 1.97 | 38.84 | 8.29 | 33.14 | [6 empty] | 2021-06-21
Aptos Solar Technology LLC | DNA-144-BF26-440W | 440 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 440 | 406 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1 | 72 | 2 | N | 11 | 49.57 | 10.48 | 41.99 | 47.2 | -0.366 | 0.045 | -0.293 |  |  | 1.9864 | 40.0952 | 8.2281 | 39.4646 | [6 empty] | 2021-08-23
Aptos Solar Technology LLC | DNA-144-MF26-440W [Blk] | 440 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 440 | 404.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1 | 72 | 2 | N | 11.33 | 49.9 | 10.74 | 41 | 47.4 | -0.382 | 0.067 | -0.302 |  |  | 1.9829 | 39.0304 | 8.3746 | 32.3076 | [6 empty] | 2021-06-21
Aptos Solar Technology LLC | DNA-144-MF26-440W [Wht] | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 440 | 408.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1 | 72 | 2 | N | 11.33 | 49.9 | 10.74 | 41 | 44.9 | -0.382 | 0.067 | -0.302 |  |  | 1.9829 | 39.0304 | 8.3444 | 33.3025 | [6 empty] | 2021-06-21
AU Optronics | PM200M00_190 | 190 W Monocrystalline Module | UL 1703 | 190 | 172.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2956 | 48 | 1 | N | 8.6 | 30.23 | 8.07 | 24.01 | 45.1 | -0.4301 | 0.07828 | -0.3207 | 0.007509 | -0.4258 | 1.6524 | 23.7164 | 6.577 | 21.8131 | Rack | Flat Plate | 0.983 | 1.318 | 1 | 0.20626
AU Optronics | PM200M00_195 | 195 W Monocrystalline Module | UL 1703 | 195 | 177.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2956 | 48 | 1 | N | 8.68 | 30.29 | 8.26 | 24.08 | 45.1 | -0.4301 | 0.07828 | -0.3207 | 0.007509 | -0.4258 | 1.6913 | 23.7855 | 6.7318 | 21.8767 | Rack | Flat Plate | 0.983 | 1.318 | 1 | 0.2063
AU Optronics | PM200M00_200 | 200 W Monocrystalline Module | UL 1703 | 200 | 181.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2956 | 48 | 1 | N | 8.76 | 30.35 | 8.38 | 24.14 | 45.1 | -0.4301 | 0.07828 | -0.3207 | 0.007509 | -0.4258 | 1.7159 | 23.8448 | 6.8296 | 21.9312 | Rack | Flat Plate | 0.983 | 1.318 | 1 | 0.20457
AU Optronics | PM200M00_205 | 205 W Monocrystalline Module | UL 1703 | 205 | 186.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2956 | 48 | 1 | N | 8.84 | 30.41 | 8.52 | 24.21 | 45.1 | -0.4301 | 0.07828 | -0.3207 | 0.007509 | -0.4258 | 1.7446 | 23.9139 | 6.9437 | 21.9948 | Rack | Flat Plate | 0.983 | 1.318 | 1 | 0.20351
AU Optronics | PM200M00_210 | 210 W Monocrystalline Module | UL 1703 | 210 | 191.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2956 | 48 | 1 | N | 8.92 | 30.47 | 8.67 | 24.28 | 45.1 | -0.4301 | 0.07828 | -0.3207 | 0.007509 | -0.4258 | 1.7753 | 23.9831 | 7.066 | 22.0584 | Rack | Flat Plate | 0.983 | 1.318 | 1 | 0.20274
AU Optronics | PM220P00_215 | 215 W Polycrystalline Module | UL 1703 | 215 | 192.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 7.77 | 36.6 | 7.2 | 29.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.44 | 29.191 | 5.7875 | 27.8352 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19551
AU Optronics | PM220P02.0_215 | 215 W Polycrystalline Module | UL 1703 | 215 | 185.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 7.85 | 36.2 | 7.4 | 29.15 | 51.4 | -0.4817 | 0.0678 | -0.3598 | 0.0558 | -0.5325 | 1.4118 | 28.2667 | 5.7934 | 25.0646 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.18562
AU Optronics | PM220P00.4_220 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5847 | 60 | 1 | N | 7.85 | 36.9 | 7.28 | 30.2 | 47.4 | -0.467 | 0.0121 | -0.3128 | -0.0427 | -0.4239 | 1.4505 | 30.1495 | 5.7726 | 26.8188 | Rack | Flat Plate | 0.9684 | 1.6364 | 1 | 0.19878
AU Optronics | PM220P00_220 | 220 W Polycrystalline Module | UL 1703 | 220 | 197.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 7.85 | 36.9 | 7.28 | 30.2 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.456 | 29.474 | 5.8518 | 28.1051 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19506
AU Optronics | PM220P01.0_220 | 220 W Polycrystalline Module | UL 1703 | 220 | 189.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 7.95 | 36.06 | 7.3 | 30.12 | 50.2 | -0.5196 | 0.0548 | -0.3624 | -0.0413 | -0.4835 | 1.4114 | 29.5053 | 5.5615 | 26.4728 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.18929
AU Optronics | PM220P02.0_220 | 220 W Polycrystalline Module | UL 1703 | 220 | 190 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8 | 36.24 | 7.53 | 29.24 | 51.4 | -0.4817 | 0.0678 | -0.3598 | 0.0558 | -0.5325 | 1.4366 | 28.3539 | 5.8952 | 25.142 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.18516
AU Optronics | PM060P00_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.588 | 28.0517 | 6.4411 | 26.1009 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19798
AU Optronics | PM060P01_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.588 | 28.0517 | 6.4411 | 26.1009 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19798
AU Optronics | PM060P02_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.588 | 28.0517 | 6.4411 | 26.1009 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19798
AU Optronics | PM060PB0_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.05 | 6.44 | 26.1 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19822
AU Optronics | PM060PB1_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.05 | 6.44 | 26.1 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19822
AU Optronics | PM060PBR_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.05 | 6.44 | 26.1 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19822
AU Optronics | PM060PW0_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.05 | 6.44 | 26.1 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19822
AU Optronics | PM060PW1_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.05 | 6.44 | 26.1 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19822
AU Optronics | PM060PW8_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.05 | 6.44 | 26.1 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19822
AU Optronics | PM060PWR_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.05 | 6.44 | 26.1 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19822
AU Optronics | PM220P00.4_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 199.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5847 | 60 | 1 | N | 7.89 | 37 | 7.37 | 30.5 | 47.4 | -0.467 | 0.0121 | -0.3128 | -0.0427 | -0.4239 | 1.4684 | 30.449 | 5.844 | 27.0852 | Rack | Flat Plate | 0.9684 | 1.6364 | 1 | 0.19872
AU Optronics | PM220P00_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 201.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 7.89 | 37 | 7.37 | 30.5 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.474 | 29.7668 | 5.9242 | 28.3843 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19501
AU Optronics | PM220P01.0_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 193.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.04 | 36.24 | 7.44 | 30.24 | 50.2 | -0.5196 | 0.0548 | -0.3624 | -0.0413 | -0.4835 | 1.4385 | 29.6229 | 5.6681 | 26.5783 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.18938
AU Optronics | PM220P02.0_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 194 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.17 | 36.3 | 7.68 | 29.3 | 51.4 | -0.4882 | 0.0606 | -0.3363 | 0.0008 | -0.4892 | 1.4666 | 28.6938 | 5.926 | 25.5617 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.18704
AU Optronics | PM245P00_225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.79 | 7.91 | 28.91 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.588 | 28.0517 | 6.4411 | 26.1009 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19798
AU Optronics | PM060P00_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.594 | 28.3622 | 6.4656 | 26.3898 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19656
AU Optronics | PM060P01_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.594 | 28.3622 | 6.4656 | 26.3898 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19656
AU Optronics | PM060P02_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.594 | 28.3622 | 6.4656 | 26.3898 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19656
AU Optronics | PM060PB0_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.36 | 6.47 | 26.39 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19605
AU Optronics | PM060PB1_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.36 | 6.47 | 26.39 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19605
AU Optronics | PM060PBR_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.36 | 6.47 | 26.39 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19605
AU Optronics | PM060PW0_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.36 | 6.47 | 26.39 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19605
AU Optronics | PM060PW1_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.36 | 6.47 | 26.39 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19605
AU Optronics | PM060PW8_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.36 | 6.47 | 26.39 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19605
AU Optronics | PM060PWR_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.59 | 28.36 | 6.47 | 26.39 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19605
AU Optronics | PM220P00.4_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 204.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5847 | 60 | 1 | N | 8 | 37.32 | 7.48 | 30.84 | 47.4 | -0.467 | 0.0121 | -0.3128 | -0.0427 | -0.4239 | 1.4903 | 30.7885 | 5.9312 | 27.3871 | Rack | Flat Plate | 0.9684 | 1.6364 | 1 | 0.1995
AU Optronics | PM220P00_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 8 | 37.32 | 7.48 | 30.84 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.496 | 30.0987 | 6.0126 | 28.7007 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19577
AU Optronics | PM220P01.0_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 204.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.1 | 36.42 | 7.58 | 30.36 | 46.4 | -0.493 | 0.097 | -0.359 | 0.047 | -0.531 | 1.4411 | 30.3465 | 6.0318 | 27.8504 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.19014
AU Optronics | PM220P02.0_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 198.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.34 | 36.35 | 7.87 | 29.35 | 51.4 | -0.4882 | 0.0606 | -0.3363 | 0.0008 | -0.4892 | 1.5029 | 28.7428 | 6.0726 | 25.6053 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.18782
AU Optronics | PM240P00_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 8 | 37.32 | 7.48 | 30.84 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.5016 | 29.9244 | 6.091 | 27.8434 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19537
AU Optronics | PM245P00_230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.594 | 28.3622 | 6.4656 | 26.3898 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19656
AU Optronics | PM245P01_230 | 230 W Polycrystalline Module, Black Zep Frame | UL 1703 | 230 | 206.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.49 | 37.01 | 7.94 | 29.23 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.594 | 28.3622 | 6.4656 | 26.3898 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19656
AU Optronics | PM060P00_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM060P01_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM060P02_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM060PA0_235 | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 211.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM060PA1_235 | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 211.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM060PA2_235 | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 211.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM060PB0_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.57 | 6.53 | 26.58 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19573
AU Optronics | PM060PB1_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.57 | 6.53 | 26.58 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19573
AU Optronics | PM060PBR_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.57 | 6.53 | 26.58 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19573
AU Optronics | PM060PW0_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.57 | 6.53 | 26.58 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19573
AU Optronics | PM060PW1_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.57 | 6.53 | 26.58 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19573
AU Optronics | PM060PW8_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.57 | 6.53 | 26.58 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19573
AU Optronics | PM060PWR_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.57 | 6.53 | 26.58 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19573
AU Optronics | PM220P00.4_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5847 | 60 | 1 | N | 8.02 | 37.5 | 7.55 | 31.14 | 47.4 | -0.467 | 0.0121 | -0.3128 | -0.0427 | -0.4239 | 1.5043 | 31.088 | 5.9867 | 27.6535 | Rack | Flat Plate | 0.9684 | 1.6364 | 1 | 0.199
AU Optronics | PM220P00_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 8.02 | 37.5 | 7.55 | 31.14 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.5157 | 30.2155 | 6.148 | 28.1143 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19488
AU Optronics | PM220P01.0_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 208.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.23 | 36.72 | 7.68 | 30.6 | 46.4 | -0.493 | 0.097 | -0.359 | 0.047 | -0.531 | 1.4601 | 30.5864 | 6.1113 | 28.0706 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.19004
AU Optronics | PM240P00_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 8.02 | 37.5 | 7.55 | 31.14 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.5157 | 30.2155 | 6.148 | 28.1143 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19488
AU Optronics | PM240PA0_235 | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 211.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 8.02 | 37.5 | 7.55 | 31.14 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.5157 | 30.2155 | 6.148 | 28.1143 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19488
AU Optronics | PM245P00_235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM245P01_235 | 235 W Polycrystalline Module, Black Zep Frame | UL 1703 | 235 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM245PA0_235 | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 211.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM245PA1_235 | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 211.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM245PA2_235 | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 211.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.21 | 8.02 | 29.44 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 28.5659 | 6.5307 | 26.5794 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19571
AU Optronics | PM060MA0_240 | 240 W DC, Monocrystalline ACPV Module | UL 1741 | 240 | 214.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.54 | 37.74 | 7.97 | 30.73 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6006 | 29.6445 | 6.4023 | 26.9459 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1977
AU Optronics | PM060MA1_240 | 240 W DC, Monocrystalline ACPV Module | UL 1741 | 240 | 214.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.54 | 37.74 | 7.97 | 30.73 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6006 | 29.6445 | 6.4023 | 26.9459 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1977
AU Optronics | PM060MA2_240 | 240 W DC, Monocrystalline ACPV Module | UL 1741 | 240 | 214.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.54 | 37.74 | 7.97 | 30.73 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6006 | 29.6445 | 6.4023 | 26.9459 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1977
AU Optronics | PM060P00_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.6834 | 28.7132 | 6.5529 | 26.8764 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2014
AU Optronics | PM060P01_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.6834 | 28.7132 | 6.5529 | 26.8764 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2014
AU Optronics | PM060P02_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.6834 | 28.7132 | 6.5529 | 26.8764 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2014
AU Optronics | PM060PA0_240 | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 215.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6261 | 28.7697 | 6.5959 | 26.769 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19493
AU Optronics | PM060PA1_240 | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 215.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6261 | 28.7697 | 6.5959 | 26.769 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19493
AU Optronics | PM060PA2_240 | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 215.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6261 | 28.7697 | 6.5959 | 26.769 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19493
AU Optronics | PM060PB0_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.68 | 28.71 | 6.55 | 26.88 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20097
AU Optronics | PM060PB1_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.68 | 28.71 | 6.55 | 26.88 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20097
AU Optronics | PM060PBR_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.68 | 28.71 | 6.55 | 26.88 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20097
AU Optronics | PM060PW0_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.68 | 28.71 | 6.55 | 26.88 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20097
AU Optronics | PM060PW1_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.68 | 28.71 | 6.55 | 26.88 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20097
AU Optronics | PM060PW8_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.68 | 28.71 | 6.55 | 26.88 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20097
AU Optronics | PM060PWR_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 214.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.42 | 36.72 | 7.9 | 30.54 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.6312 | 29.7611 | 6.359 | 27.6735 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20228
AU Optronics | PM220P01.0_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6238 | 60 | 1 | N | 8.32 | 36.84 | 7.83 | 30.72 | 46.4 | -0.493 | 0.097 | -0.359 | 0.047 | -0.531 | 1.4886 | 30.7063 | 6.2307 | 28.1807 | Rack | Flat Plate | 0.995 | 1.632 | 1 | 0.19046
AU Optronics | PM240P00_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 215.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 8.5 | 37.32 | 7.9 | 30.68 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.5859 | 29.7691 | 6.433 | 27.6989 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19672
AU Optronics | PM240PA0_240 | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 215.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 8.5 | 37.32 | 7.9 | 30.68 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.5859 | 29.7691 | 6.433 | 27.6989 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19672
AU Optronics | PM245P00_240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.6834 | 28.7132 | 6.5529 | 26.8764 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2014
AU Optronics | PM245P01_240 | 240 W Polycrystalline Module, Black Zep Frame | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.6834 | 28.7132 | 6.5529 | 26.8764 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2014
AU Optronics | PM245PA0_240 | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 215.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6261 | 28.7697 | 6.5959 | 26.769 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19493
AU Optronics | PM245PA1_240 | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 215.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6261 | 28.7697 | 6.5959 | 26.769 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19493
AU Optronics | PM245PA2_240 | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 215.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.62 | 37.42 | 8.1 | 29.65 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6261 | 28.7697 | 6.5959 | 26.769 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19493
AU Optronics | PM250M00_240 | 240 W Monocrystalline Module | UL 1703 | 240 | 214.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.54 | 37.74 | 7.97 | 30.73 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6006 | 29.6445 | 6.4023 | 26.9459 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1977
AU Optronics | PM250M02_240 | 240 W Monocrystalline Module | UL 1703 | 240 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.54 | 37.74 | 7.97 | 30.73 | 45 | -0.4302 | 0.06427 | -0.3311 | 5.93e-05 | -0.431 | 1.6669 | 30.4458 | 6.4433 | 28.0418 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.21145
AU Optronics | PM250MA0_240 | 240 W DC, Monocrystalline ACPV Module | UL 1741 | 240 | 214.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.54 | 37.74 | 7.97 | 30.73 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6006 | 29.6445 | 6.4023 | 26.9459 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1977
AU Optronics | PM250MA1_240 | 240 W DC, Monocrystalline ACPV Module | UL 1741 | 240 | 214.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.54 | 37.74 | 7.97 | 30.73 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6006 | 29.6445 | 6.4023 | 26.9459 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1977
AU Optronics | PM250MA2_240 | 240 W DC, Monocrystalline ACPV Module | UL 1741 | 240 | 214.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.54 | 37.74 | 7.97 | 30.73 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6006 | 29.6445 | 6.4023 | 26.9459 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1977
AU Optronics | PM060MA0_245 | 245 W DC, Monocrystalline ACPV Module | UL 1741 | 245 | 219.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.6 | 37.8 | 8.09 | 30.78 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6249 | 29.6869 | 6.4994 | 26.9845 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19689
AU Optronics | PM060MA1_245 | 245 W DC, Monocrystalline ACPV Module | UL 1741 | 245 | 219.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.6 | 37.8 | 8.09 | 30.78 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6249 | 29.6869 | 6.4994 | 26.9845 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19689
AU Optronics | PM060MA2_245 | 245 W DC, Monocrystalline ACPV Module | UL 1741 | 245 | 219.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.6 | 37.8 | 8.09 | 30.78 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6249 | 29.6869 | 6.4994 | 26.9845 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19689
AU Optronics | PM060P00_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.9263 | 6.6176 | 27.0758 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM060P01_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.9263 | 6.6176 | 27.0758 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM060P02_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.9263 | 6.6176 | 27.0758 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM060PA0_245 | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 220.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6422 | 28.9832 | 6.661 | 26.9677 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19427
AU Optronics | PM060PA1_245 | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 220.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6422 | 28.9832 | 6.661 | 26.9677 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19427
AU Optronics | PM060PA2_245 | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 220.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6422 | 28.9832 | 6.661 | 26.9677 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19427
AU Optronics | PM060PB0_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.93 | 6.62 | 27.08 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20074
AU Optronics | PM060PB1_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.93 | 6.62 | 27.08 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20074
AU Optronics | PM060PBR_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.93 | 6.62 | 27.08 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20074
AU Optronics | PM060PW0_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.93 | 6.62 | 27.08 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20074
AU Optronics | PM060PW1_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.93 | 6.62 | 27.08 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20074
AU Optronics | PM060PW8_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.93 | 6.62 | 27.08 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20074
AU Optronics | PM060PWR_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 218.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.46 | 36.9 | 8 | 30.84 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.6519 | 30.0534 | 6.4395 | 27.9453 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20263
AU Optronics | PM240P00_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 220.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 8.59 | 37.56 | 8.02 | 30.88 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 29.9612 | 6.5307 | 27.8777 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19689
AU Optronics | PM240PA0_245 | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 220.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.668 | 60 | 1 | N | 8.59 | 37.56 | 8.02 | 30.88 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.61 | 29.9612 | 6.5307 | 27.8777 | Rack | Flat Plate | 1 | 1.668 | 1 | 0.19689
AU Optronics | PM245P00_245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.9263 | 6.6176 | 27.0758 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM245P01_245 | 245 W Polycrystalline Module, Black Zep Frame | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7 | 28.9263 | 6.6176 | 27.0758 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM245PA0_245 | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 220.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6422 | 28.9832 | 6.661 | 26.9677 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19427
AU Optronics | PM245PA1_245 | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 220.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6422 | 28.9832 | 6.661 | 26.9677 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19427
AU Optronics | PM245PA2_245 | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 220.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.63 | 8.18 | 29.87 | 45.7 | -0.461 | 0.059 | -0.337 | 0.039 | -0.485 | 1.6422 | 28.9832 | 6.661 | 26.9677 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19427
AU Optronics | PM250M00_245 | 245 W Monocrystalline Module | UL 1703 | 245 | 219.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.6 | 37.8 | 8.09 | 30.78 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6249 | 29.6869 | 6.4994 | 26.9845 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19689
AU Optronics | PM250MA0_245 | 245 W DC, Monocrystalline ACPV Module | UL 1741 | 245 | 219.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.6 | 37.8 | 8.09 | 30.78 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6249 | 29.6869 | 6.4994 | 26.9845 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19689
AU Optronics | PM250MA1_245 | 245 W DC, Monocrystalline ACPV Module | UL 1741 | 245 | 219.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.6 | 37.8 | 8.09 | 30.78 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6249 | 29.6869 | 6.4994 | 26.9845 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19689
AU Optronics | PM250MA2_245 | 245 W DC, Monocrystalline ACPV Module | UL 1741 | 245 | 219.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.6 | 37.8 | 8.09 | 30.78 | 46.9 | -0.4512 | 0.0544 | -0.3462 | -0.0067 | -0.4483 | 1.6249 | 29.6869 | 6.4994 | 26.9845 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19689
AU Optronics | PM060M00_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6614 | 30.4321 | 6.6169 | 27.7963 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20224
AU Optronics | PM060M01_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.66 | 30.43 | 6.62 | 27.8 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20206
AU Optronics | PM060M02_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.66 | 30.43 | 6.62 | 27.8 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20206
AU Optronics | PM060MA0_250 | 250 W DC, Monocrystalline ACPV Module | UL 1741 | 250 | 224.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6614 | 30.4321 | 6.6169 | 27.7963 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20224
AU Optronics | PM060MA1_250 | 250 W DC, Monocrystalline ACPV Module | UL 1741 | 250 | 224.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6614 | 30.4321 | 6.6169 | 27.7963 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20224
AU Optronics | PM060MA2_250 | 250 W DC, Monocrystalline ACPV Module | UL 1741 | 250 | 224.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6614 | 30.4321 | 6.6169 | 27.7963 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20224
AU Optronics | PM060MB0_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.6 | 30.38 | 6.64 | 27.79 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19443
AU Optronics | PM060MB1_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.6 | 30.38 | 6.64 | 27.79 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19443
AU Optronics | PM060MB2_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.6 | 30.38 | 6.64 | 27.79 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19443
AU Optronics | PM060MB3_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.6 | 30.38 | 6.64 | 27.79 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19443
AU Optronics | PM060MBR_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.59 | 37.62 | 8.17 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.708 | 30.4187 | 6.5146 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20783
AU Optronics | PM060MW0_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.6 | 30.38 | 6.64 | 27.79 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19443
AU Optronics | PM060MW1_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.6 | 30.38 | 6.64 | 27.79 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19443
AU Optronics | PM060MW2_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.6 | 30.38 | 6.64 | 27.79 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19443
AU Optronics | PM060MW3_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.6 | 30.38 | 6.64 | 27.79 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19443
AU Optronics | PM060MWR_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.59 | 37.62 | 8.17 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.708 | 30.4187 | 6.5146 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20783
AU Optronics | PM060P00_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM060P01_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM060P02_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM060PA0_250 | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 227.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM060PA1_250 | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 227.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM060PA2_250 | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 227.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM060PB0_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.72 | 29.13 | 6.68 | 27.27 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20041
AU Optronics | PM060PB1_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.72 | 29.13 | 6.68 | 27.27 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20041
AU Optronics | PM060PBR_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.72 | 29.13 | 6.68 | 27.27 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20041
AU Optronics | PM060PW0_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.72 | 29.13 | 6.68 | 27.27 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20041
AU Optronics | PM060PW1_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.72 | 29.13 | 6.68 | 27.27 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20041
AU Optronics | PM060PW8_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.72 | 29.13 | 6.68 | 27.27 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20041
AU Optronics | PM060PWR_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.52 | 37.2 | 8.03 | 31.2 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.6581 | 30.4043 | 6.4637 | 28.2716 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20165
AU Optronics | PM245P00_250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM245P01_250 | 250 W Polycrystalline Module, Black Zep Frame | UL 1703 | 250 | 227.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM245PA0_250 | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 227.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM245PA1_250 | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 227.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM245PA2_250 | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 227.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.75 | 37.83 | 8.26 | 30.08 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7167 | 29.1296 | 6.6824 | 27.2662 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20002
AU Optronics | PM250M00_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6614 | 30.4321 | 6.6169 | 27.7963 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20224
AU Optronics | PM250M01_250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.0001915 | -0.4546 | 1.5972 | 30.3841 | 6.6435 | 27.7898 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19411
AU Optronics | PM250MA0_250 | 250 W DC, Monocrystalline ACPV Module | UL 1741 | 250 | 224.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6614 | 30.4321 | 6.6169 | 27.7963 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20224
AU Optronics | PM250MA1_250 | 250 W DC, Monocrystalline ACPV Module | UL 1741 | 250 | 224.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6614 | 30.4321 | 6.6169 | 27.7963 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20224
AU Optronics | PM250MA2_250 | 250 W DC, Monocrystalline ACPV Module | UL 1741 | 250 | 224.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.66 | 37.86 | 8.22 | 30.82 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6614 | 30.4321 | 6.6169 | 27.7963 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20224
AU Optronics | PM060M00_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6856 | 30.4716 | 6.7135 | 27.8324 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20143
AU Optronics | PM060M01_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.69 | 30.47 | 6.71 | 27.83 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20194
AU Optronics | PM060M02_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.69 | 30.47 | 6.71 | 27.83 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20194
AU Optronics | PM060MA0_255 | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6856 | 30.4716 | 6.7135 | 27.8324 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20143
AU Optronics | PM060MA1_255 | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6856 | 30.4716 | 6.7135 | 27.8324 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20143
AU Optronics | PM060MA2_255 | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6856 | 30.4716 | 6.7135 | 27.8324 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20143
AU Optronics | PM060MB0_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.62 | 30.42 | 6.74 | 27.83 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19326
AU Optronics | PM060MB1_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.62 | 30.42 | 6.74 | 27.83 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19326
AU Optronics | PM060MB2_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.62 | 30.42 | 6.74 | 27.83 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19326
AU Optronics | PM060MB3_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.62 | 30.42 | 6.74 | 27.83 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19326
AU Optronics | PM060MBR_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.67 | 37.68 | 8.35 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.7457 | 30.4187 | 6.6581 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20824
AU Optronics | PM060MW0_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.62 | 30.42 | 6.74 | 27.83 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19326
AU Optronics | PM060MW1_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.62 | 30.42 | 6.74 | 27.83 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19326
AU Optronics | PM060MW2_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.62 | 30.42 | 6.74 | 27.83 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19326
AU Optronics | PM060MW3_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.62 | 30.42 | 6.74 | 27.83 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19326
AU Optronics | PM060MWR_255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.67 | 37.68 | 8.35 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.7457 | 30.4187 | 6.6581 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20824
AU Optronics | PM060P00_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM060P01_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM060P02_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM060PA0_255 | 255 W DC, Polycrystalline ACPV Module | UL 1741 | 255 | 231.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM060PA1_255 | 255 W DC, Polycrystalline ACPV Module | UL 1741 | 255 | 231.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM060PA2_255 | 255 W DC, Polycrystalline ACPV Module | UL 1741 | 255 | 231.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM060PB0_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.74 | 29.33 | 6.77 | 27.46 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20013
AU Optronics | PM060PB1_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.74 | 29.33 | 6.77 | 27.46 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20013
AU Optronics | PM060PBR_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.74 | 29.33 | 6.77 | 27.46 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20013
AU Optronics | PM060PW0_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.74 | 29.33 | 6.77 | 27.46 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20013
AU Optronics | PM060PW1_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.74 | 29.33 | 6.77 | 27.46 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20013
AU Optronics | PM060PW8_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.74 | 29.33 | 6.77 | 27.46 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20013
AU Optronics | PM060PWR_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.74 | 29.33 | 6.77 | 27.46 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20013
AU Optronics | PM245P00_255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM245P01_255 | 255 W Polycrystalline Module, Black Zep Frame | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM245PA0_255 | 255 W DC, Polycrystalline ACPV Module | UL 1741 | 255 | 231.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM245PA1_255 | 255 W DC, Polycrystalline ACPV Module | UL 1741 | 255 | 231.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM245PA2_255 | 255 W DC, Polycrystalline ACPV Module | UL 1741 | 255 | 231.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 38.03 | 8.37 | 30.29 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7395 | 29.333 | 6.7713 | 27.4566 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.2001
AU Optronics | PM250M00_255 | 255 W Monocrystalline Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6856 | 30.4716 | 6.7135 | 27.8324 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20143
AU Optronics | PM250M01_255 | 255 W Monocrystalline Module | UL 1741 | 255 | 228 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.0001915 | -0.4546 | 1.6205 | 30.4236 | 6.7405 | 27.8259 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19334
AU Optronics | PM250MA0_255 | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6856 | 30.4716 | 6.7135 | 27.8324 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20143
AU Optronics | PM250MA1_255 | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6856 | 30.4716 | 6.7135 | 27.8324 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20143
AU Optronics | PM250MA2_255 | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.72 | 37.92 | 8.34 | 30.86 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.6856 | 30.4716 | 6.7135 | 27.8324 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20143
AU Optronics | PM060M00_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7099 | 30.521 | 6.8101 | 27.8775 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM060M01_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.71 | 30.52 | 6.81 | 27.88 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20073
AU Optronics | PM060M02_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.71 | 30.52 | 6.81 | 27.88 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20073
AU Optronics | PM060MA0_260 | 260 W DC, Monocrystalline ACPV Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7099 | 30.521 | 6.8101 | 27.8775 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM060MA1_260 | 260 W DC, Monocrystalline ACPV Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7099 | 30.521 | 6.8101 | 27.8775 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM060MA2_260 | 260 W DC, Monocrystalline ACPV Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7099 | 30.521 | 6.8101 | 27.8775 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM060MB0_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.64 | 30.47 | 6.84 | 27.87 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1922
AU Optronics | PM060MB1_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.64 | 30.47 | 6.84 | 27.87 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1922
AU Optronics | PM060MB2_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.64 | 30.47 | 6.84 | 27.87 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1922
AU Optronics | PM060MB3_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.64 | 30.47 | 6.84 | 27.87 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1922
AU Optronics | PM060MBR_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.8 | 37.8 | 8.5 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.777 | 30.4187 | 6.7777 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.2079
AU Optronics | PM060MW0_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.64 | 30.47 | 6.84 | 27.87 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1922
AU Optronics | PM060MW1_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.64 | 30.47 | 6.84 | 27.87 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1922
AU Optronics | PM060MW2_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.64 | 30.47 | 6.84 | 27.87 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1922
AU Optronics | PM060MW3_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.64 | 30.47 | 6.84 | 27.87 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.1922
AU Optronics | PM060MWR_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.8 | 37.8 | 8.5 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.777 | 30.4187 | 6.7777 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.2079
AU Optronics | PM060P00_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM060P01_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM060P02_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM060PA0_260 | 260 W DC, Polycrystalline ACPV Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM060PA1_260 | 260 W DC, Polycrystalline ACPV Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM060PA2_260 | 260 W DC, Polycrystalline ACPV Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM060PB0_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.76 | 29.52 | 6.87 | 27.63 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19983
AU Optronics | PM060PB1_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.76 | 29.52 | 6.87 | 27.63 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19983
AU Optronics | PM060PBR_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.76 | 29.52 | 6.87 | 27.63 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19983
AU Optronics | PM060PW0_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.76 | 29.52 | 6.87 | 27.63 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19983
AU Optronics | PM060PW1_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.76 | 29.52 | 6.87 | 27.63 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19983
AU Optronics | PM060PW8_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.76 | 29.52 | 6.87 | 27.63 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19983
AU Optronics | PM060PWR_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 231.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 7.83 | 43.2 | 7.24 | 35.93 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.46 | 35.3 | 5.85 | 32.39 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19822
AU Optronics | PM245P00_260 | 260 W Polycrystalline Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM245P01_260 | 260 W Polycrystalline Module, Black Zep Frame | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM245PA0_260 | 260 W DC, Polycrystalline ACPV Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM245PA1_260 | 260 W DC, Polycrystalline ACPV Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM245PA2_260 | 260 W DC, Polycrystalline ACPV Module | UL 1741 | 260 | 236.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.89 | 38.23 | 8.49 | 30.48 | 45.3 | -0.4306 | 0.0728 | -0.3608 | 0.00944 | -0.4774 | 1.7645 | 29.517 | 6.8684 | 27.6288 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20032
AU Optronics | PM250M00_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7099 | 30.521 | 6.8101 | 27.8775 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM250M01_260 | 260 W Monocrystalline Module | UL 1741 | 260 | 232.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.0001915 | -0.4546 | 1.6438 | 30.4729 | 6.8375 | 27.871 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19266
AU Optronics | PM250MA0_260 | 260 W DC, Monocrystalline ACPV Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7099 | 30.521 | 6.8101 | 27.8775 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM250MA1_260 | 260 W DC, Monocrystalline ACPV Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7099 | 30.521 | 6.8101 | 27.8775 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM250MA2_260 | 260 W DC, Monocrystalline ACPV Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.98 | 8.46 | 30.91 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7099 | 30.521 | 6.8101 | 27.8775 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20072
AU Optronics | PM060M00_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7261 | 30.5703 | 6.8745 | 27.9226 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19912
AU Optronics | PM060M01_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.73 | 30.57 | 6.87 | 27.92 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19957
AU Optronics | PM060M02_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.73 | 30.57 | 6.87 | 27.92 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19957
AU Optronics | PM060MA0_265 | 265 W DC, Monocrystalline ACPV Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7261 | 30.5703 | 6.8745 | 27.9226 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19912
AU Optronics | PM060MA1_265 | 265 W DC, Monocrystalline ACPV Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7261 | 30.5703 | 6.8745 | 27.9226 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19912
AU Optronics | PM060MA2_265 | 265 W DC, Monocrystalline ACPV Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7261 | 30.5703 | 6.8745 | 27.9226 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19912
AU Optronics | PM060MB0_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 237.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.66 | 30.52 | 6.9 | 27.92 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19118
AU Optronics | PM060MB1_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 237.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.66 | 30.52 | 6.9 | 27.92 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19118
AU Optronics | PM060MB2_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 237.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.66 | 30.52 | 6.9 | 27.92 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19118
AU Optronics | PM060MB3_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 237.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.66 | 30.52 | 6.9 | 27.92 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19118
AU Optronics | PM060MBR_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 235.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.11 | 44.42 | 7.36 | 36 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.4505 | 35.4923 | 5.9437 | 32.506 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19427
AU Optronics | PM060MW0_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 237.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.66 | 30.52 | 6.9 | 27.92 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19118
AU Optronics | PM060MW1_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 237.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.66 | 30.52 | 6.9 | 27.92 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19118
AU Optronics | PM060MW2_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 237.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.66 | 30.52 | 6.9 | 27.92 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19118
AU Optronics | PM060MW3_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 237.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.000192 | -0.4546 | 1.66 | 30.52 | 6.9 | 27.92 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19118
AU Optronics | PM060MWR_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 235.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.11 | 44.42 | 7.36 | 36 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.4505 | 35.4923 | 5.9437 | 32.506 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19427
AU Optronics | PM060PWR_265 | 265 W Polycrystalline Module | UL 1741 | 265 | 236 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 7.95 | 43.27 | 7.33 | 36.14 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.48 | 35.5 | 5.93 | 32.58 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19826
AU Optronics | PM250M00_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7261 | 30.5703 | 6.8745 | 27.9226 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19912
AU Optronics | PM250M01_265 | 265 W Monocrystalline Module | UL 1741 | 265 | 237.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4556 | 0.0643 | -0.3459 | 0.0001915 | -0.4546 | 1.6593 | 30.5222 | 6.9021 | 27.9161 | Rack | Flat Plate | 0.992 | 1.651 | 1 | 0.19112
AU Optronics | PM250MA0_265 | 265 W DC, Monocrystalline ACPV Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7261 | 30.5703 | 6.8745 | 27.9226 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19912
AU Optronics | PM250MA1_265 | 265 W DC, Monocrystalline ACPV Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7261 | 30.5703 | 6.8745 | 27.9226 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19912
AU Optronics | PM250MA2_265 | 265 W DC, Monocrystalline ACPV Module | UL 1741 | 265 | 238.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.04 | 8.54 | 30.96 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7261 | 30.5703 | 6.8745 | 27.9226 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19912
AU Optronics | PM060M00_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060M01_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060M02_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MA0_270 | 270 W DC, Monocrystalline ACPV Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MA1_270 | 270 W DC, Monocrystalline ACPV Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MA2_270 | 270 W DC, Monocrystalline ACPV Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MB0_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MB1_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MB2_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MB3_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MBR_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 247.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.07 | 38.45 | 8.69 | 31.06 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7301 | 29.8164 | 6.9599 | 28.0735 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19106
AU Optronics | PM060MW0_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MW1_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MW2_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MW3_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM060MWR_270 | 270 W Monocrystalline Module | UL 1741 | 270 | 247.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.07 | 38.45 | 8.69 | 31.06 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7301 | 29.8164 | 6.9599 | 28.0735 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19106
AU Optronics | PM060PWR_270 | 270 W Polycrystalline Module | UL 1741 | 270 | 240.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.1 | 43.7 | 7.41 | 36.43 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.48 | 36.46 | 5.99 | 33.1 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19985
AU Optronics | PM072PB0_270 | 270 W Polycrystalline Module | UL 1741 | 270 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.1 | 43.7 | 7.41 | 36.43 | 47 | -0.61973 | 0.047647 | -0.42684 | -0.05367 | -0.56995 | 1.48 | 35.38 | 5.86 | 31.22 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19393
AU Optronics | PM072PB1_270 | 270 W Polycrystalline Module | UL 1741 | 270 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.1 | 43.7 | 7.41 | 36.43 | 47 | -0.61973 | 0.047647 | -0.42684 | -0.05367 | -0.56995 | 1.48 | 35.38 | 5.86 | 31.22 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19393
AU Optronics | PM072PBR_270 | 270 W Polycrystalline Module | UL 1741 | 270 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.1 | 43.7 | 7.41 | 36.43 | 47 | -0.61973 | 0.047647 | -0.42684 | -0.05367 | -0.56995 | 1.48 | 35.38 | 5.86 | 31.22 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19393
AU Optronics | PM072PW0_270 | 270 W Polycrystalline Module | UL 1703 | 270 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.1 | 43.7 | 7.41 | 36.43 | 47 | -0.61973 | 0.047647 | -0.42684 | -0.05367 | -0.56995 | 1.48 | 35.38 | 5.86 | 31.22 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19393
AU Optronics | PM072PW1_270 | 270 W Polycrystalline Module | UL 1703 | 270 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.1 | 43.7 | 7.41 | 36.43 | 47 | -0.61973 | 0.047647 | -0.42684 | -0.05367 | -0.56995 | 1.48 | 35.38 | 5.86 | 31.22 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19393
AU Optronics | PM250M00_270 | 270 W Monocrystalline Module | UL 1703 | 270 | 243.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.9 | 38.1 | 8.7 | 31 | 47.3 | -0.4373 | 0.05941 | -0.3014 | 0.003453 | -0.3976 | 1.7584 | 30.6098 | 7.0033 | 27.9587 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.19935
AU Optronics | PM250M01_270 | 270 W Monocrystalline Module | UL 1703 | 270 | 243.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM250MA0_270 | 270 W DC, Monocrystalline ACPV Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM250MA1_270 | 270 W DC, Monocrystalline ACPV Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM250MA2_270 | 270 W DC, Monocrystalline ACPV Module | UL 1741 | 270 | 243.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.5 | 8.5 | 31.8 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.31 | 6.86 | 28.56 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20062
AU Optronics | PM300P00_270 | 270 W Polycrystalline Module | UL 1703 | 270 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.1 | 43.7 | 7.41 | 36.43 | 47 | -0.61973 | 0.047647 | -0.42684 | -0.05367 | -0.56995 | 1.4782 | 35.3778 | 5.8555 | 31.2212 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19369
AU Optronics | PM060M00_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060M01_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060M02_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MA0_275 | 275 W DC, Monocrystalline ACPV Module | UL 1741 | 275 | 247.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MA1_275 | 275 W DC, Monocrystalline ACPV Module | UL 1741 | 275 | 247.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MA2_275 | 275 W DC, Monocrystalline ACPV Module | UL 1741 | 275 | 247.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MB0_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MB1_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MB2_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MB3_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MBR_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.2 | 38.77 | 8.79 | 31.29 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.75 | 30.0372 | 7.04 | 28.2813 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19115
AU Optronics | PM060MW0_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MW1_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MW2_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MW3_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM060MWR_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.2 | 38.77 | 8.79 | 31.29 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.75 | 30.0372 | 7.04 | 28.2813 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19115
AU Optronics | PM060PWR_275 | 275 W Polycrystalline Module | UL 1703 | 275 | 245.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.17 | 43.92 | 7.52 | 36.58 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.5063 | 36.6115 | 6.0753 | 33.2396 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20054
AU Optronics | PM072PW0_275 | 275 W Polycrystalline Module | UL 1703 | 275 | 235 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.17 | 43.92 | 7.52 | 36.58 | 47 | -0.61973 | 0.047647 | -0.42684 | -0.05367 | -0.56995 | 1.49 | 35.94 | 5.95 | 31.89 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19473
AU Optronics | PM072PW1_275 | 275 W Polycrystalline Module | UL 1703 | 275 | 235 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.17 | 43.92 | 7.52 | 36.58 | 47 | -0.61973 | 0.047647 | -0.42684 | -0.05367 | -0.56995 | 1.49 | 35.94 | 5.95 | 31.89 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19473
AU Optronics | PM250M01_275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM250MA0_275 | 275 W DC, Monocrystalline ACPV Module | UL 1741 | 275 | 247.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM250MA1_275 | 275 W DC, Monocrystalline ACPV Module | UL 1741 | 275 | 247.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM250MA2_275 | 275 W DC, Monocrystalline ACPV Module | UL 1741 | 275 | 247.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.03 | 38.7 | 8.52 | 32.3 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.73 | 31.8 | 6.87 | 29.01 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20005
AU Optronics | PM300P00_275 | 275 W Polycrystalline Module | UL 1703 | 275 | 235 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.17 | 43.92 | 7.52 | 36.58 | 47 | -0.61973 | 0.047647 | -0.42684 | -0.05367 | -0.56995 | 1.4868 | 35.9359 | 5.9474 | 31.8874 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19429
AU Optronics | PM060M00_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060M01_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060M02_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060MB0_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060MB1_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060MB2_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060MB3_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060MBR_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.34 | 39.1 | 8.88 | 31.53 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.768 | 30.2676 | 7.112 | 28.4983 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19111
AU Optronics | PM060MW0_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060MW1_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060MW2_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060MW3_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM060MWR_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.34 | 39.1 | 8.88 | 31.53 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.768 | 30.2676 | 7.112 | 28.4983 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19111
AU Optronics | PM060PWR_280 | 280 W Polycrystalline Module | UL 1703 | 280 | 249.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.23 | 44.06 | 7.63 | 36.72 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.5283 | 36.7516 | 6.1641 | 33.3669 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.2006
AU Optronics | PM072PB0_280 | 280 W Polycrystalline Module | UL 1703 | 280 | 254.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.34 | 43.63 | 7.79 | 36.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.59 | 34.71 | 6.44 | 34.13 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.1971
AU Optronics | PM072PB1_280 | 280 W Polycrystalline Module | UL 1703 | 280 | 254.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.34 | 43.63 | 7.79 | 36.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.59 | 34.71 | 6.44 | 34.13 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.1971
AU Optronics | PM072PBR_280 | 280 W Polycrystalline Module | UL 1703 | 280 | 254.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.34 | 43.63 | 7.79 | 36.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.59 | 34.71 | 6.44 | 34.13 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.1971
AU Optronics | PM072PW0_280 | 280 W Polycrystalline Module | UL 1703 | 280 | 254.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.34 | 43.63 | 7.79 | 36.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.59 | 34.71 | 6.44 | 34.13 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.1971
AU Optronics | PM072PW1_280 | 280 W Polycrystalline Module | UL 1703 | 280 | 254.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.34 | 43.63 | 7.79 | 36.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.59 | 34.71 | 6.44 | 34.13 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.1971
AU Optronics | PM072PWR_280 | 280 W Polycrystalline Module | UL 1703 | 280 | 254.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.34 | 43.63 | 7.79 | 36.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.59 | 34.71 | 6.44 | 34.13 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.1971
AU Optronics | PM250M01_280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.06 | 38.9 | 8.57 | 32.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.74 | 32.19 | 6.91 | 29.37 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20004
AU Optronics | PM300P00_280 | 280 W Polycrystalline Module | UL 1703 | 280 | 254.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.34 | 43.63 | 7.79 | 36.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.5931 | 34.7132 | 6.4406 | 34.1303 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19751
AU Optronics | PM060M00_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060M01_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060M02_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060MB0_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060MB1_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060MB2_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060MB3_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060MBR_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.48 | 39.43 | 8.97 | 31.76 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7859 | 30.4884 | 7.1841 | 28.7062 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19105
AU Optronics | PM060MW0_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060MW1_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060MW2_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060MW3_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM060MWR_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.48 | 39.43 | 8.97 | 31.76 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7859 | 30.4884 | 7.1841 | 28.7062 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19105
AU Optronics | PM072PB0_285 | 285 W Polycrystalline Module | UL 1703 | 285 | 258.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.53 | 43.92 | 7.96 | 36.86 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.63 | 34.98 | 6.58 | 34.39 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.20006
AU Optronics | PM072PB1_285 | 285 W Polycrystalline Module | UL 1703 | 285 | 258.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.53 | 43.92 | 7.96 | 36.86 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.63 | 34.98 | 6.58 | 34.39 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.20006
AU Optronics | PM072PBR_285 | 285 W Polycrystalline Module | UL 1703 | 285 | 258.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.53 | 43.92 | 7.96 | 36.86 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.63 | 34.98 | 6.58 | 34.39 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.20006
AU Optronics | PM072PW0_285 | 285 W Polycrystalline Module | UL 1703 | 285 | 256.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.32 | 44.21 | 7.75 | 36.79 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6048 | 36.1692 | 6.2135 | 33.8815 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20367
AU Optronics | PM072PW1_285 | 285 W Polycrystalline Module | UL 1703 | 285 | 258.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.53 | 43.92 | 7.96 | 36.86 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.63 | 34.98 | 6.58 | 34.39 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.20006
AU Optronics | PM072PWR_285 | 285 W Polycrystalline Module | UL 1703 | 285 | 258.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.53 | 43.92 | 7.96 | 36.86 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.63 | 34.98 | 6.58 | 34.39 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.20006
AU Optronics | PM250M01_285 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.08 | 39.2 | 8.59 | 33.2 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 32.68 | 6.93 | 29.82 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20067
AU Optronics | PM300P00_285 | 285 W Polycrystalline Module | UL 1703 | 285 | 258.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.53 | 43.92 | 7.96 | 36.86 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.6279 | 34.9789 | 6.5812 | 34.3915 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19979
AU Optronics | PM060M00_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM060M01_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM060M02_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM060MB0_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM060MB1_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM060MB2_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM060MB3_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM060MW0_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 258.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.48 | 44.43 | 7.9 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6346 | 36.3658 | 6.3519 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20498
AU Optronics | PM060MW1_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM060MW2_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM060MW3_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM072MB0_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 258.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.48 | 44.43 | 7.9 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6346 | 36.3658 | 6.3519 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20498
AU Optronics | PM072PB0_290 | 290 W Polycrystalline Module | UL 1703 | 290 | 263.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.6 | 44.14 | 8.02 | 37.15 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.25 | 6.63 | 34.66 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19934
AU Optronics | PM072PB1_290 | 290 W Polycrystalline Module | UL 1703 | 290 | 263.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.6 | 44.14 | 8.02 | 37.15 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.25 | 6.63 | 34.66 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19934
AU Optronics | PM072PBR_290 | 290 W Polycrystalline Module | UL 1703 | 290 | 263.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.6 | 44.14 | 8.02 | 37.15 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.25 | 6.63 | 34.66 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19934
AU Optronics | PM072PW0_290 | 290 W Polycrystalline Module | UL 1703 | 290 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.46 | 44.28 | 7.96 | 36.79 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6483 | 36.1692 | 6.3818 | 33.8815 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20558
AU Optronics | PM072PW1_290 | 290 W Polycrystalline Module | UL 1703 | 290 | 263.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.6 | 44.14 | 8.02 | 37.15 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.25 | 6.63 | 34.66 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19934
AU Optronics | PM072PWR_290 | 290 W Polycrystalline Module | UL 1703 | 290 | 263.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.6 | 44.14 | 8.02 | 37.15 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.25 | 6.63 | 34.66 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19934
AU Optronics | PM250M01_290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.11 | 39.5 | 8.61 | 33.7 | 46.5 | -0.4536 | 0.0635 | -0.3276 | -0.002917 | -0.4489 | 1.75 | 33.18 | 6.94 | 30.26 | Rack | Flat Plate | 0.983 | 1.639 | 1 | 0.20022
AU Optronics | PM300P00_290 | 290 W Polycrystalline Module | UL 1703 | 290 | 263.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.6 | 44.14 | 8.02 | 37.15 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.6401 | 35.2541 | 6.6308 | 34.6621 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19938
AU Optronics | PM060MW0_295 | 295 W Monocrystalline Module | UL 1703 | 295 | 263.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.52 | 44.57 | 8.04 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6635 | 36.3658 | 6.4645 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20507
AU Optronics | PM072MB0_295 | 295 W Monocrystalline Module | UL 1703 | 295 | 263.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.52 | 44.57 | 8.04 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6635 | 36.3658 | 6.4645 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20507
AU Optronics | PM072PB0_295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.66 | 44.28 | 8.08 | 37.3 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.56 | 6.31 | 33.64 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19769
AU Optronics | PM072PB1_295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.66 | 44.28 | 8.08 | 37.3 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.56 | 6.31 | 33.64 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19769
AU Optronics | PM072PBR_295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.66 | 44.28 | 8.08 | 37.3 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.56 | 6.31 | 33.64 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19769
AU Optronics | PM072PW0_295 | 295 W Polycrystalline Module | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.49 | 44.42 | 8 | 37.01 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6566 | 36.3855 | 6.4139 | 34.0841 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20432
AU Optronics | PM072PW1_295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.66 | 44.28 | 8.08 | 37.3 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.56 | 6.31 | 33.64 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19769
AU Optronics | PM072PWR_295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.66 | 44.28 | 8.08 | 37.3 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.64 | 35.56 | 6.31 | 33.64 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19769
AU Optronics | PM300P00_295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.66 | 44.28 | 8.08 | 37.3 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.639 | 35.5622 | 6.3144 | 33.64 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19758
AU Optronics | PM060MW0_300 | 300 W Monocrystalline Module | UL 1703 | 300 | 267.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.58 | 44.71 | 8.17 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6904 | 36.3658 | 6.569 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20491
AU Optronics | PM072MB0_300 | 300 W Monocrystalline Module | UL 1703 | 300 | 267.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.58 | 44.71 | 8.17 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6904 | 36.3658 | 6.569 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20491
AU Optronics | PM072PB0_300 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.42 | 8.14 | 37.44 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.65 | 35.7 | 6.36 | 33.77 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19635
AU Optronics | PM072PB1_300 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.42 | 8.14 | 37.44 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.65 | 35.7 | 6.36 | 33.77 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19635
AU Optronics | PM072PBR_300 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.42 | 8.14 | 37.44 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.65 | 35.7 | 6.36 | 33.77 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19635
AU Optronics | PM072PW0_300 | 300 W Polycrystalline Module | UL 1703 | 300 | 270.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.54 | 44.86 | 8.05 | 37.66 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6669 | 37.0245 | 6.454 | 34.6827 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20573
AU Optronics | PM072PW1_300 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.42 | 8.14 | 37.44 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.65 | 35.7 | 6.36 | 33.77 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19635
AU Optronics | PM072PWR_300 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.42 | 8.14 | 37.44 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.65 | 35.7 | 6.36 | 33.77 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19635
AU Optronics | PM300P00_300 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.42 | 8.14 | 37.44 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.6517 | 35.6957 | 6.3637 | 33.7663 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19653
AU Optronics | PM096B00_303 | 303 W Monocrystalline Module | UL 1703 | 303 | 276.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 5.81 | 64.1 | 5.52 | 53.6 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.09 | 51.91 | 4.5 | 48.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.18674
AU Optronics | PM072MB0_305 | 305 W Monocrystalline Module | UL 1703 | 305 | 272.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.72 | 44.86 | 8.31 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.7194 | 36.3658 | 6.6816 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20501
AU Optronics | PM072PB0_305 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.77 | 44.57 | 8.21 | 37.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.66 | 35.83 | 6.41 | 33.9 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19501
AU Optronics | PM072PB1_305 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.77 | 44.57 | 8.21 | 37.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.66 | 35.83 | 6.41 | 33.9 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19501
AU Optronics | PM072PBR_305 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.77 | 44.57 | 8.21 | 37.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.66 | 35.83 | 6.41 | 33.9 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19501
AU Optronics | PM072PW0_305 | 305 W Polycrystalline Module | UL 1703 | 305 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.56 | 45 | 8.08 | 37.87 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6732 | 37.231 | 6.478 | 34.8761 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20424
AU Optronics | PM072PW1_305 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.77 | 44.57 | 8.21 | 37.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.66 | 35.83 | 6.41 | 33.9 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19501
AU Optronics | PM072PWR_305 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.77 | 44.57 | 8.21 | 37.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.66 | 35.83 | 6.41 | 33.9 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19501
AU Optronics | PM096B00_305 | 305 W Monocrystalline Module | UL 1703 | 305 | 278.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.14 | 64.24 | 5.58 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.1 | 52.98 | 4.54 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19108
AU Optronics | PM300P00_305 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.77 | 44.57 | 8.21 | 37.58 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.6643 | 35.833 | 6.4121 | 33.8962 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19553
AU Optronics | PM096B00_308 | 308 W Monocrystalline Module | UL 1703 | 308 | 281.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 5.94 | 64.3 | 5.62 | 54 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.11 | 52.3 | 4.58 | 49.19 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.18848
AU Optronics | PM072MB0_310 | 310 W Monocrystalline Module | UL 1703 | 310 | 277 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.79 | 45 | 8.45 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.7484 | 36.3658 | 6.7941 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.2051
AU Optronics | PM072PB0_310 | 310 W Polycrystalline Module | UL 1703 | 310 | 282 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.87 | 44.86 | 8.31 | 37.94 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.69 | 36.18 | 6.5 | 34.22 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19724
AU Optronics | PM072PB1_310 | 310 W Polycrystalline Module | UL 1703 | 310 | 282 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.87 | 44.86 | 8.31 | 37.94 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.69 | 36.18 | 6.5 | 34.22 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19724
AU Optronics | PM072PBR_310 | 310 W Polycrystalline Module | UL 1703 | 310 | 282 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.87 | 44.86 | 8.31 | 37.94 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.69 | 36.18 | 6.5 | 34.22 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19724
AU Optronics | PM072PW0_310 | 310 W Polycrystalline Module | UL 1703 | 310 | 277.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.62 | 45.22 | 8.16 | 38.02 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.6889 | 37.3549 | 6.5659 | 34.4083 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20351
AU Optronics | PM072PW1_310 | 310 W Polycrystalline Module | UL 1703 | 310 | 282 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.87 | 44.86 | 8.31 | 37.94 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.69 | 36.18 | 6.5 | 34.22 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19724
AU Optronics | PM072PWR_310 | 310 W Polycrystalline Module | UL 1703 | 310 | 282 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.87 | 44.86 | 8.31 | 37.94 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.69 | 36.18 | 6.5 | 34.22 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19724
AU Optronics | PM096B00_310 | 310 W Monocrystalline Module | UL 1703 | 310 | 283.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.14 | 64.42 | 5.67 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.12 | 52.98 | 4.62 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19141
AU Optronics | PM300P00_310 | 310 W Polycrystalline Module | UL 1703 | 310 | 282 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.87 | 44.86 | 8.31 | 37.94 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.686 | 36.1762 | 6.4957 | 34.2209 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19675
AU Optronics | PM096B00_313 | 313 W Monocrystalline Module | UL 1703 | 313 | 286.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.07 | 64.5 | 5.72 | 54.6 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.13 | 52.88 | 4.66 | 49.74 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19091
AU Optronics | PM072MB0_315 | 315 W Monocrystalline Module | UL 1703 | 315 | 281.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.89 | 45.22 | 8.58 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.7753 | 36.3658 | 6.8986 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20495
AU Optronics | PM072PB0_315 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.92 | 45 | 8.36 | 38.16 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.7 | 36.38 | 6.53 | 34.42 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19634
AU Optronics | PM072PB1_315 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.92 | 45 | 8.36 | 38.16 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.7 | 36.38 | 6.53 | 34.42 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19634
AU Optronics | PM072PBR_315 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.92 | 45 | 8.36 | 38.16 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.7 | 36.38 | 6.53 | 34.42 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19634
AU Optronics | PM072PW0_315 | 315 W Polycrystalline Module | UL 1703 | 315 | 281.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.67 | 45.58 | 8.24 | 38.45 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.7055 | 37.7774 | 6.6303 | 34.7974 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20453
AU Optronics | PM072PW1_315 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.92 | 45 | 8.36 | 38.16 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.7 | 36.38 | 6.53 | 34.42 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19634
AU Optronics | PM072PWR_315 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.92 | 45 | 8.36 | 38.16 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.7 | 36.38 | 6.53 | 34.42 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19634
AU Optronics | PM096B00_315 | 315 W Monocrystalline Module | UL 1703 | 315 | 287.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.14 | 64.6 | 5.76 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.14 | 52.98 | 4.69 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19174
AU Optronics | PM300P00_315 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.92 | 45 | 8.36 | 38.16 | 45.1 | -0.4348 | 0.06261 | -0.3315 | 0.01182 | -0.4341 | 1.6952 | 36.3821 | 6.5309 | 34.4157 | Rack | Flat Plate | 0.983 | 1.956 | 1 | 0.19579
AU Optronics | PM096B00_318 | 318 W Monocrystalline Module | UL 1703 | 318 | 290.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.2 | 64.7 | 5.82 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.15 | 52.98 | 4.74 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19159
AU Optronics | PM072MB0_320 | 320 W Monocrystalline Module | UL 1703 | 320 | 293 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.46 | 45.97 | 8.58 | 37.3 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.6985 | 35.8398 | 6.8718 | 33.7523 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19023
AU Optronics | PM072PW0_320 | 320 W Polycrystalline Module | UL 1703 | 320 | 288.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.38 | 45.51 | 8.75 | 36.59 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7396 | 35.4395 | 7.0207 | 33.2073 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19266
AU Optronics | PM096B00_320 | 320 W Monocrystalline Module | UL 1703 | 320 | 292.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.27 | 64.8 | 5.86 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.16 | 52.98 | 4.77 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19205
AU Optronics | PM096B00_323 | 323 W Monocrystalline Module | UL 1703 | 323 | 295.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.33 | 64.8 | 5.9 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.17 | 52.98 | 4.81 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19191
AU Optronics | PM072MB0_325 | 325 W Monocrystalline Module | UL 1703 | 325 | 297.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.52 | 46.38 | 8.67 | 37.48 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7163 | 36.0127 | 6.9438 | 33.9152 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19019
AU Optronics | PM072MW0_325 | 325 W Monocrystalline Module | UL 1703 | 325 | 297.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.52 | 46.38 | 8.67 | 37.48 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7163 | 36.0127 | 6.9438 | 33.9152 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19019
AU Optronics | PM072PW0_325 | 325 W Polycrystalline Module | UL 1703 | 325 | 293.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.44 | 45.79 | 8.81 | 36.88 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7516 | 35.7204 | 7.0689 | 33.4705 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19251
AU Optronics | PM096B00_325 | 325 W Monocrystalline Module | UL 1703 | 325 | 297.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.39 | 64.9 | 5.94 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.17 | 52.98 | 4.84 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19073
AU Optronics | PM096B00_327 | 327 W Monocrystalline Module | UL 1703 | 327 | 299.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.46 | 64.9 | 5.98 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.18 | 52.98 | 4.87 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19118
AU Optronics | PM072MB0_330 | 330 W Monocrystalline Module | UL 1703 | 330 | 302.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.57 | 46.76 | 8.75 | 37.71 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7322 | 36.2337 | 7.0079 | 34.1233 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19019
AU Optronics | PM072MW0_330 | 330 W Monocrystalline Module | UL 1703 | 330 | 302.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.57 | 46.76 | 8.75 | 37.71 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7322 | 36.2337 | 7.0079 | 34.1233 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19019
AU Optronics | PM072PW0_330 | 330 W Polycrystalline Module | UL 1703 | 330 | 298 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.5 | 46.08 | 8.87 | 37.22 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7635 | 36.0497 | 7.117 | 33.7791 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19265
AU Optronics | PM096B00_330 | 330 W Monocrystalline Module | UL 1703 | 330 | 302.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.52 | 64.9 | 6.04 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.19 | 52.98 | 4.92 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19105
AU Optronics | PM096B00_333 | 333 W Monocrystalline Module | UL 1703 | 333 | 304.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6307 | 96 | 1 | N | 6.46 | 65.3 | 6.09 | 54.7 | 48.3 | -0.377 | 0.062 | -0.306 | 0.021 | -0.399 | 1.2 | 52.98 | 4.96 | 49.83 | Rack | Flat Plate | 1.046 | 1.559 | 1 | 0.19092
AU Optronics | PM072MB0_335 | 335 W Monocrystalline Module | UL 1703 | 335 | 307.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.61 | 47.04 | 8.82 | 37.98 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.746 | 36.4931 | 7.064 | 34.3676 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1902
AU Optronics | PM072MW0_335 | 335 W Monocrystalline Module | UL 1703 | 335 | 307.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.61 | 47.04 | 8.82 | 37.98 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.746 | 36.4931 | 7.064 | 34.3676 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1902
AU Optronics | PM072PW0_335 | 335 W Polycrystalline Module | UL 1703 | 335 | 302.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.56 | 46.37 | 8.94 | 37.55 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7774 | 36.3693 | 7.1732 | 34.0786 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19297
AU Optronics | PM072MB0_340 | 340 W Monocrystalline Module | UL 1703 | 340 | 311.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.64 | 47.18 | 8.96 | 38.32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7738 | 36.8198 | 7.1761 | 34.6753 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19209
AU Optronics | PM072MW0_340 | 340 W Monocrystalline Module | UL 1703 | 340 | 311.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.64 | 47.18 | 8.96 | 38.32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7738 | 36.8198 | 7.1761 | 34.6753 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19209
Auxin Solar | AXN6M409T130 | 130 W Monocrystalline Module | UL 1703 | 130 | 115.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.97969 | 36 | 1 | N | 7.83 | 21.6 | 7.24 | 17.96 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.4872 | 17.7087 | 5.765 | 16.3426 | Rack | Flat Plate | 0.666 | 1.471 | 1 | 0.20259
Auxin Solar | AXN6M409T135 | 135 W Monocrystalline Module | UL 1703 | 135 | 120.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.97969 | 36 | 1 | N | 8.1 | 21.58 | 7.41 | 18.22 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.5222 | 17.9651 | 5.9004 | 16.5792 | Rack | Flat Plate | 0.666 | 1.471 | 1 | 0.20256
Auxin Solar | AXN6M409T140 | 140 W Monocrystalline Module | UL 1703 | 140 | 125 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.97969 | 36 | 1 | N | 8.23 | 22.03 | 7.63 | 18.36 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.5673 | 18.1031 | 6.0756 | 16.7066 | Rack | Flat Plate | 0.666 | 1.471 | 1 | 0.20267
Auxin Solar | AXN6M409T145 | 145 W Monocrystalline Module | UL 1703 | 145 | 129.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.97969 | 36 | 1 | N | 8.42 | 22.46 | 7.9 | 18.36 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.6691 | 18.1021 | 6.3 | 16.7576 | Rack | Flat Plate | 0.666 | 1.471 | 1 | 0.20838
Auxin Solar | AXN6M409T150 | 150 W Monocrystalline Module | UL 1703 | 150 | 134.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.97969 | 36 | 1 | N | 8.59 | 22.57 | 8.19 | 18.36 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.7304 | 18.1021 | 6.5313 | 16.7576 | Rack | Flat Plate | 0.666 | 1.471 | 1 | 0.20883
Auxin Solar | AXN6M409T155 | 155 W Monocrystalline Module | UL 1703 | 155 | 138.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.97969 | 36 | 1 | N | 8.8 | 22.68 | 8.49 | 18.36 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.7938 | 18.1021 | 6.7705 | 16.7576 | Rack | Flat Plate | 0.666 | 1.471 | 1 | 0.20949
Auxin Solar | AXN6P610T210 | 210 W Polycrystalline Module | UL 1703 | 210 | 186.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 7.6 | 35.94 | 7.09 | 29.64 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.4258 | 29.16 | 5.7061 | 26.8555 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19799
Auxin Solar | AXN6P610T215 | 215 W Polycrystalline Module | UL 1703 | 215 | 191.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 7.83 | 36 | 7.18 | 29.94 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.4439 | 29.4552 | 5.7786 | 27.1273 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19782
Auxin Solar | AXN6P610T220 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 7.95 | 36.06 | 7.3 | 30.12 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.4681 | 29.6322 | 5.8751 | 27.2904 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19774
Auxin Solar | AXN6M610T225 | 225 W Monocrystalline Module | UL 1703 | 225 | 200.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.11 | 37.02 | 7.5 | 30 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.5592 | 29.6653 | 5.9858 | 27.4536 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20558
Auxin Solar | AXN6P610T225 | 225 W Polycrystalline Module | UL 1703 | 225 | 200.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.1 | 36.42 | 7.41 | 30.36 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.4902 | 29.8684 | 5.9637 | 27.5078 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19782
Auxin Solar | AXN6M610T230 | 230 W Monocrystalline Module | UL 1703 | 230 | 205.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.18 | 37.32 | 7.55 | 30.48 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.5696 | 30.14 | 6.0257 | 27.8929 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20569
Auxin Solar | AXN6P610T230 | 230 W Polycrystalline Module | UL 1703 | 230 | 205 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.17 | 36.6 | 7.55 | 30.48 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.5183 | 29.9864 | 6.0763 | 27.6166 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.19795
Auxin Solar | AXN6M610T235 | 235 W Monocrystalline Module | UL 1703 | 235 | 209.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.26 | 37.5 | 7.59 | 30.96 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.5779 | 30.6146 | 6.0576 | 28.3321 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20557
Auxin Solar | AXN6P610T235 | 235 W Polycrystalline Module | UL 1703 | 235 | 209.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.23 | 36.72 | 7.68 | 30.6 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.5858 | 29.8196 | 6.1819 | 27.7279 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20123
Auxin Solar | AXN6M610T240 | 240 W Monocrystalline Module | UL 1703 | 240 | 214.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.29 | 37.56 | 7.69 | 31.2 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.5987 | 30.852 | 6.1374 | 28.5517 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20552
Auxin Solar | AXN6P610T240 | 240 W Polycrystalline Module | UL 1703 | 240 | 214.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.42 | 36.72 | 7.9 | 30.54 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.6312 | 29.7611 | 6.359 | 27.6735 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20228
Auxin Solar | AXN6M610T245 | 245 W Monocrystalline Module | UL 1703 | 245 | 219 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.32 | 37.62 | 7.78 | 31.5 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.6265 | 31.3134 | 6.2036 | 28.8527 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20788
Auxin Solar | AXN6P610T245 | 245 W Polycrystalline Module | UL 1703 | 245 | 218.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.46 | 36.9 | 8 | 30.84 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.6519 | 30.0534 | 6.4395 | 27.9453 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20263
Auxin Solar | AXN6M610T250 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.59 | 37.62 | 8.17 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.708 | 30.4187 | 6.5146 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20783
Auxin Solar | AXN6P610T250 | 250 W Polycrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.52 | 37.2 | 8.03 | 31.2 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.6581 | 30.4043 | 6.4637 | 28.2716 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20165
Auxin Solar | AXN6M610T255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.67 | 37.68 | 8.35 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.7457 | 30.4187 | 6.6581 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20824
Auxin Solar | AXN6P610T255 | 255 W Polycrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.56 | 37.5 | 8.08 | 31.56 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.6684 | 30.7551 | 6.5039 | 28.5978 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.20122
Auxin Solar | AXN6M610T260 | 260 W Monocrystalline Module | UL 1703 | 260 | 232.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6378 | 60 | 1 | N | 8.8 | 37.8 | 8.5 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.777 | 30.4187 | 6.7777 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.2079
Auxin Solar | AXN6P610T260 | 260 W Polycrystalline Module | UL 1703 | 260 | 231.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 7.83 | 43.2 | 7.24 | 35.93 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.46 | 35.3 | 5.85 | 32.39 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19822
Auxin Solar | AXN6M612T265 | 265 W Monocrystalline Module | UL 1703 | 265 | 235.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.11 | 44.42 | 7.36 | 36 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.4505 | 35.4923 | 5.9437 | 32.506 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19427
Auxin Solar | AXN6P610T265 | 265 W Polycrystalline Module | UL 1703 | 265 | 236 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 7.95 | 43.27 | 7.33 | 36.14 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.48 | 35.5 | 5.93 | 32.58 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19826
Auxin Solar | AXN6M610T270 | 270 W Monocrystalline Module | UL 1703 | 270 | 247.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.07 | 38.45 | 8.69 | 31.06 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7301 | 29.8164 | 6.9599 | 28.0735 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19106
Auxin Solar | AXN6M612T270 | 270 W Monocrystalline Module | UL 1703 | 270 | 240.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.14 | 44.64 | 7.44 | 36.21 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.4663 | 35.6994 | 6.0083 | 32.6957 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19387
Auxin Solar | AXN6P610T270 | 270 W Polycrystalline Module | UL 1703 | 270 | 240.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.1 | 43.7 | 7.41 | 36.43 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.48 | 36.46 | 5.99 | 33.1 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.19985
Auxin Solar | AXN6M610T275 | 275 W Monocrystalline Module | UL 1703 | 275 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.2 | 38.77 | 8.79 | 31.29 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.75 | 30.0372 | 7.04 | 28.2813 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19115
Auxin Solar | AXN6M612T275 | 275 W Monocrystalline Module | UL 1703 | 275 | 244.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.18 | 44.78 | 7.52 | 36.58 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.5496 | 36.252 | 6.0432 | 32.9715 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20428
Auxin Solar | AXN6P610T275 | 275 W Polycrystalline Module | UL 1703 | 275 | 248.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.1 | 38.91 | 8.49 | 32.4 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.6803 | 31.4007 | 6.7999 | 28.9591 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19187
Auxin Solar | AXN6P612T275 | 275 W Polycrystalline Module | UL 1703 | 275 | 245.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.17 | 43.92 | 7.52 | 36.58 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.5063 | 36.6115 | 6.0753 | 33.2396 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20054
Auxin Solar | AXN6P612T275G | 275 W Polycrystalline Module | UL 1703 | 275 | 245.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.17 | 43.92 | 7.52 | 36.58 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.5063 | 36.6115 | 6.0753 | 33.2396 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20054
Auxin Solar | AXN6M610T280 | 280 W Monocrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.34 | 39.1 | 8.88 | 31.53 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.768 | 30.2676 | 7.112 | 28.4983 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19111
Auxin Solar | AXN6M612T280 | 280 W Monocrystalline Module | UL 1703 | 280 | 249.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.21 | 44.86 | 7.6 | 36.86 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.5661 | 36.5295 | 6.1075 | 33.2238 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20432
Auxin Solar | AXN6P610T280 | 280 W Polycrystalline Module | UL 1703 | 280 | 253 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.24 | 39.24 | 8.58 | 32.64 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.6981 | 31.6333 | 6.8719 | 29.1736 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19185
Auxin Solar | AXN6P612T280 | 280 W Polycrystalline Module | UL 1703 | 280 | 249.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.23 | 44.06 | 7.63 | 36.72 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.5283 | 36.7516 | 6.1641 | 33.3669 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.2006
Auxin Solar | AXN6P612T280G | 280 W Polycrystalline Module | UL 1703 | 280 | 249.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.23 | 44.06 | 7.63 | 36.72 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.5283 | 36.7516 | 6.1641 | 33.3669 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.2006
Auxin Solar | AXN6M610T285 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.48 | 39.43 | 8.97 | 31.76 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7859 | 30.4884 | 7.1841 | 28.7062 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19105
Auxin Solar | AXN6M612T285 | 285 W Monocrystalline Module | UL 1703 | 285 | 254 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.39 | 44.21 | 7.77 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6012 | 36.3908 | 6.2441 | 33.0976 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20445
Auxin Solar | AXN6P610T285 | 285 W Polycrystalline Module | UL 1703 | 285 | 257.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.38 | 39.57 | 8.67 | 32.89 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7159 | 31.8756 | 6.944 | 29.3971 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19192
Auxin Solar | AXN6P612T285 | 285 W Polycrystalline Module | UL 1703 | 285 | 256.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.32 | 44.21 | 7.75 | 36.79 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6048 | 36.1692 | 6.2135 | 33.8815 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20367
Auxin Solar | AXN6P612T285G | 285 W Polycrystalline Module | UL 1703 | 285 | 256.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.32 | 44.21 | 7.75 | 36.79 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6048 | 36.1692 | 6.2135 | 33.8815 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20367
Auxin Solar | AXN6M610B290 | 290 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 290 | 269.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.62 | 39.77 | 9.06 | 32 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7158 | 31.1445 | 6.9369 | 29.7943 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M610T290 | 290 W Monocrystalline Module | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.62 | 39.77 | 9.06 | 32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8038 | 30.7188 | 7.2562 | 28.9231 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19107 |  | 2019-08-15
Auxin Solar | AXN6M612T290 | 290 W Monocrystalline Module | UL 1703 | 290 | 258.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.48 | 44.43 | 7.9 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6346 | 36.3658 | 6.3519 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20498
Auxin Solar | AXN6P610T290 | 290 W Polycrystalline Module | UL 1703 | 290 | 262.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.52 | 39.91 | 8.75 | 33.14 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7318 | 32.1179 | 7.0081 | 29.6205 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1918
Auxin Solar | AXN6P612T290 | 290 W Polycrystalline Module | UL 1703 | 290 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.46 | 44.28 | 7.96 | 36.79 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6483 | 36.1692 | 6.3818 | 33.8815 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20558
Auxin Solar | AXN6P612T290G | 290 W Polycrystalline Module | UL 1703 | 290 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.46 | 44.28 | 7.96 | 36.79 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6483 | 36.1692 | 6.3818 | 33.8815 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20558
Auxin Solar | AXN6M610B295 | 295 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 295 | 274.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7328 | 31.3781 | 7.0058 | 30.0178 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M610T295 | 295 W Monocrystalline Module | UL 1703 | 295 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.814 | 31.2838 | 7.323 | 29.5803 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237 |  | 2019-08-15
Auxin Solar | AXN6M612T295 | 295 W Monocrystalline Module | UL 1703 | 295 | 263.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.52 | 44.57 | 8.04 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6635 | 36.3658 | 6.4645 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20507
Auxin Solar | AXN6P612T295 | 295 W Polycrystalline Module | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.49 | 44.42 | 8 | 37.01 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6566 | 36.3855 | 6.4139 | 34.0841 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20432
Auxin Solar | AXN6P612T295G | 295 W Polycrystalline Module | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.49 | 44.42 | 8 | 37.01 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6566 | 36.3855 | 6.4139 | 34.0841 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20432
Auxin Solar | AXN6M610B300 | 300 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 300 | 278.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7498 | 31.6117 | 7.0747 | 30.2412 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M610T300 | 300 W Monocrystalline Module | UL 1703 | 300 | 275.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8319 | 31.5167 | 7.395 | 29.8005 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19245 |  | 2019-08-15
Auxin Solar | AXN6M612T300 | 300 W Monocrystalline Module | UL 1703 | 300 | 267.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.58 | 44.71 | 8.17 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.6904 | 36.3658 | 6.569 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20491
Auxin Solar | AXN6P612T300 | 300 W Polycrystalline Module | UL 1703 | 300 | 270.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.54 | 44.86 | 8.05 | 37.66 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6669 | 37.0245 | 6.454 | 34.6827 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20573
Auxin Solar | AXN6P612T300G | 300 W Polycrystalline Module | UL 1703 | 300 | 270.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.54 | 44.86 | 8.05 | 37.66 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6669 | 37.0245 | 6.454 | 34.6827 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20573
Auxin Solar | AXN6M610B305 | 305 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 305 | 283.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 10.06 | 40.79 | 9.32 | 32.73 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.765 | 31.855 | 7.136 | 30.474 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M610T305 | 305 W Monocrystalline Module | UL 1703 | 305 | 279.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 10.0618 | 40.792 | 9.3191 | 32.7286 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8475 | 31.7578 | 7.4583 | 30.0285 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237 |  | 2019-08-15
Auxin Solar | AXN6M612T305 | 305 W Monocrystalline Module | UL 1703 | 305 | 272.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.72 | 44.86 | 8.31 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.7194 | 36.3658 | 6.6816 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20501
Auxin Solar | AXN6P612T305 | 305 W Polycrystalline Module | UL 1703 | 305 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.56 | 45 | 8.08 | 37.87 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6732 | 37.231 | 6.478 | 34.8761 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20424
Auxin Solar | AXN6P612T305G | 305 W Polycrystalline Module | UL 1703 | 305 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.56 | 45 | 8.08 | 37.87 | 46.2 | -0.4402 | 0.06001 | -0.3285 | -0.008008 | -0.4339 | 1.6732 | 37.231 | 6.478 | 34.8761 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20424
Auxin Solar | AXN6M610B310 | 310 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 310 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 10.21 | 41.14 | 9.4 | 32.97 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7802 | 32.0886 | 7.1973 | 30.6975 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M610T310 | 310 W Monocrystalline Module | UL 1703 | 310 | 284.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 10.2128 | 41.1387 | 9.4013 | 32.974 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8638 | 31.996 | 7.5242 | 30.2538 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237 |  | 2019-08-15
Auxin Solar | AXN6M612T310 | 310 W Monocrystalline Module | UL 1703 | 310 | 277 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.79 | 45 | 8.45 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.7484 | 36.3658 | 6.7941 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.2051
Auxin Solar | AXN6P612T310 | 310 W Polycrystalline Module | UL 1703 | 310 | 277.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.62 | 45.22 | 8.16 | 38.02 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.6889 | 37.3549 | 6.5659 | 34.4083 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20351
Auxin Solar | AXN6M610B315 | 315 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 315 | 293.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 10.37 | 41.49 | 9.48 | 33.22 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7953 | 32.3319 | 7.2585 | 30.9302 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M610T315 | 315 W Monocrystalline Module | UL 1703 | 315 | 289.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 10.366 | 41.4884 | 9.4819 | 33.2213 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8798 | 32.236 | 7.5886 | 30.4807 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237 |  | 2019-08-15
Auxin Solar | AXN6M612T315 | 315 W Monocrystalline Module | UL 1703 | 315 | 281.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9512 | 72 | 1 | N | 8.89 | 45.22 | 8.58 | 36.72 | 47.9 | -0.4485 | 0.05332 | -0.3244 | -0.0183 | -0.4339 | 1.7753 | 36.3658 | 6.8986 | 33.2132 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20495
Auxin Solar | AXN6P612T315 | 315 W Polycrystalline Module | UL 1703 | 315 | 281.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9512 | 72 | 1 | N | 8.67 | 45.58 | 8.24 | 38.45 | 47.6 | -0.4501 | 0.05758 | -0.3342 | -0.009288 | -0.4445 | 1.7055 | 37.7774 | 6.6303 | 34.7974 | Rack | Flat Plate | 0.995 | 1.961 | 1 | 0.20453
Auxin Solar | AXN6M610B320 | 320 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 320 | 297.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 10.52 | 41.84 | 9.56 | 33.47 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.8105 | 32.5752 | 7.3198 | 31.163 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M610T320 | 320 W Monocrystalline Module | UL 1703 | 320 | 294 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 10.5214 | 41.8411 | 9.5607 | 33.4705 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8954 | 32.4778 | 7.6517 | 30.7093 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
Auxin Solar | AXN6M612T320 | 320 W Monocrystalline Module | UL 1703 | 320 | 293 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.46 | 45.97 | 8.58 | 37.3 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.6985 | 35.8398 | 6.8718 | 33.7523 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19023
Auxin Solar | AXN6P612T320 | 320 W Polycrystalline Module | UL 1703 | 320 | 288.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.38 | 45.51 | 8.75 | 36.59 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7396 | 35.4395 | 7.0207 | 33.2073 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19266 |  | 2018-09-04
Auxin Solar | AXN6M610T325 | 325 W Monocrystalline Module | UL 1703 | 325 | 298.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 10.6793 | 42.1967 | 9.6378 | 33.7215 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.9107 | 32.7214 | 7.7134 | 30.9396 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
Auxin Solar | AXN6M612T325 | 325 W Monocrystalline Module | UL 1703 | 325 | 297.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.52 | 46.38 | 8.67 | 37.48 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7163 | 36.0127 | 6.9438 | 33.9152 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19019
Auxin Solar | AXN6P612T325 | 325 W Polycrystalline Module | UL 1703 | 325 | 293.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.44 | 45.79 | 8.81 | 36.88 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7516 | 35.7204 | 7.0689 | 33.4705 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19251 |  | 2018-09-04
Auxin Solar | AXN6M612T330 | 330 W Monocrystalline Module | UL 1703 | 330 | 302.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.57 | 46.76 | 8.75 | 37.71 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7322 | 36.2337 | 7.0079 | 34.1233 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19019 |  | 2018-09-04
Auxin Solar | AXN6P612T330 | 330 W Polycrystalline Module | UL 1703 | 330 | 298 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.5 | 46.08 | 8.87 | 37.22 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7635 | 36.0497 | 7.117 | 33.7791 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19265 |  | 2018-09-04
Auxin Solar | AXN6M612T335 | 335 W Monocrystalline Module | UL 1703 | 335 | 307.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.61 | 47.04 | 8.82 | 37.98 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.746 | 36.4931 | 7.064 | 34.3676 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1902 |  | 2018-09-04
Auxin Solar | AXN6P612T335 | 335 W Polycrystalline Module | UL 1703 | 335 | 302.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.56 | 46.37 | 8.94 | 37.55 | 47.69 | -0.42 | 0.05 | -0.32 | -0.01 | -0.42 | 1.7774 | 36.3693 | 7.1732 | 34.0786 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19297 |  | 2018-09-04
Auxin Solar | AXN6M612B340 | 340 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 340 | 315.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 9.64 | 47.18 | 8.96 | 38.32 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.6941 | 37.7785 | 6.8544 | 35.7551 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M612T340 | 340 W Monocrystalline Module | UL 1703 | 340 | 311.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.64 | 47.18 | 8.96 | 38.32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7738 | 36.8198 | 7.1761 | 34.6753 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19209 |  | 2018-09-04
Auxin Solar | AXN6M612B345 | 345 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 345 | 320.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 9.72 | 47.28 | 8.98 | 38.4 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.6979 | 37.8574 | 6.8697 | 35.8297 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M612T345 | 345 W Monocrystalline Module | UL 1703 | 345 | 315.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.72 | 47.28 | 8.98 | 38.4 | 44.6 | -0.43 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7777 | 36.8967 | 7.1921 | 34.7477 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19012 |  | 2018-09-04
Auxin Solar | AXN6M612B350 | 350 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 350 | 325.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 9.81 | 47.37 | 9.1 | 38.48 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7206 | 37.9363 | 6.9615 | 35.9044 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M612T350 | 350 W Monocrystalline Module | UL 1703 | 350 | 320.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.81 | 47.37 | 9.1 | 38.48 | 44.6 | -0.43 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8015 | 36.9736 | 7.2882 | 34.8201 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19031 |  | 2018-09-04
Auxin Solar | AXN6M612B355 | 355 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 355 | 329.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 9.9 | 47.47 | 9.21 | 38.55 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7414 | 38.0053 | 7.0457 | 35.9697 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M612T355 | 355 W Monocrystalline Module | UL 1703 | 355 | 325.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.8985 | 47.4657 | 9.2082 | 38.5524 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8182 | 37.5082 | 7.381 | 35.3921 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211 |  | 2018-09-04
Auxin Solar | AXN6M612B360 | 360 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 360 | 334.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 9.99 | 47.56 | 9.32 | 38.63 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7622 | 38.0841 | 7.1298 | 36.0444 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M612T360 | 360 W Monocrystalline Module | UL 1703 | 360 | 330.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.9876 | 47.5606 | 9.3193 | 38.6295 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8401 | 37.5832 | 7.47 | 35.4629 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211 |  | 2018-09-04
Auxin Solar | AXN6M612B365 | 365 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 365 | 339.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.08 | 47.66 | 9.43 | 38.71 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.783 | 38.163 | 7.214 | 36.119 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M612T365 | 365 W Monocrystalline Module | UL 1703 | 365 | 334.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 10.0775 | 47.6557 | 9.4299 | 38.7068 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.862 | 37.6584 | 7.5586 | 35.5338 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211 |  | 2018-09-04
Auxin Solar | AXN6M612B370 | 370 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 370 | 344.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.17 | 47.75 | 9.54 | 38.78 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.8038 | 38.232 | 7.2982 | 36.1843 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M612T370 | 370 W Monocrystalline Module | UL 1703 | 370 | 339.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 10.1682 | 47.751 | 9.54 | 38.7842 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8837 | 37.7337 | 7.6468 | 35.6049 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211 |  | 2018-09-04
Auxin Solar | AXN6M612B375 | 375 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 375 | 349 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.26 | 47.85 | 9.65 | 38.86 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.8246 | 38.3109 | 7.3823 | 36.259 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M612T375 | 375 W Monocrystalline Module | UL 1703 | 375 | 344.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 10.2597 | 47.8465 | 9.6496 | 38.8617 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.9053 | 37.8092 | 7.7347 | 35.6761 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
Auxin Solar | AXN6M612B380 | 380 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 380 | 353.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.35 | 47.94 | 9.76 | 38.94 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.8454 | 38.3897 | 7.4665 | 36.3336 | [6 empty] | 2019-06-03
Auxin Solar | AXN6M612T380 | 380 W Monocrystalline Module | UL 1703 | 380 | 349.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 10.352 | 47.9422 | 9.7587 | 38.9395 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.9269 | 37.8848 | 7.8222 | 35.7474 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
Auxin Solar | AXN6M612T385 | 385 W Monocrystalline Module | UL 1703 | 385 | 353.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 10.4452 | 48.0381 | 9.8674 | 39.0173 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.9484 | 37.9605 | 7.9093 | 35.8189 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
AXITEC | AC-190M/125-72S | 190 W Monocrystalline Module | UL 1703 | 190 | 170.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.51 | 45.23 | 5.21 | 36.5 | 45.8 | -0.4669 | 0.0823 | -0.403 | -0.0389 | -0.4352 | 1.0741 | 34.9771 | 4.2122 | 33.4041 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19774
AXITEC | AC-195M/125-72S | 195 W Monocrystalline Module | UL 1703 | 195 | 175.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.62 | 45.44 | 5.28 | 36.94 | 45.8 | -0.4669 | 0.0823 | -0.403 | -0.0389 | -0.4352 | 1.0516 | 36.9797 | 4.385 | 33.1447 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19943
AXITEC | AC-200M/125-72S | 200 W Monocrystalline Module | UL 1703 | 200 | 179.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.65 | 45.87 | 5.35 | 37.39 | 45.8 | -0.4669 | 0.0823 | -0.403 | -0.0389 | -0.4352 | 1.0656 | 37.4302 | 4.4432 | 33.5484 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19942
AXITEC | AC-225P/156-60S | 225 W Polycrystalline Module | UL 1703 | 225 | 202.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.08 | 36.95 | 7.7 | 29.22 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.5133 | 28.4215 | 6.273 | 25.7847 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19116
AXITEC | AC-230M/156-60S | 230 W Monocrystalline Module | UL 1703 | 230 | 207.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6229 | 60 | 1 | N | 8.39 | 37.06 | 7.8 | 29.49 | 45.7 | -0.4395 | 0.0688 | -0.3617 | -0.0451 | -0.3445 | 1.5542 | 29.49 | 6.3604 | 27.0537 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19927
AXITEC | AC-230P/156-60S | 230 W Polycrystalline Module | UL 1703 | 230 | 206.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.23 | 37.05 | 7.84 | 29.34 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.5406 | 28.5382 | 6.3862 | 25.8906 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19116
AXITEC | AC-235M/156-60S | 235 W Monocrystalline Module | UL 1703 | 235 | 212.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6229 | 60 | 1 | N | 8.46 | 37.26 | 7.87 | 29.86 | 45.7 | -0.4395 | 0.0688 | -0.3617 | -0.0451 | -0.3445 | 1.5681 | 29.86 | 6.4175 | 27.3931 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19925
AXITEC | AC-235P/156-60B | 235 W Polycrystalline Module | UL 1703 | 235 | 210.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.4 | 37.3 | 7.95 | 29.55 | 47.9 | -0.4324 | 0.0841 | -0.385 | 0.03 | -0.4459 | 1.5936 | 29.2591 | 6.5025 | 26.611 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19841
AXITEC | AC-235P/156-60S | 235 W Polycrystalline Module | UL 1703 | 235 | 211.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.32 | 37.16 | 7.97 | 29.49 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.5661 | 28.6841 | 6.4918 | 26.023 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19116
AXITEC | AC-240M/156-60S | 240 W Monocrystalline Module | UL 1703 | 240 | 217 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6229 | 60 | 1 | N | 8.53 | 37.47 | 7.94 | 30.23 | 45.7 | -0.4395 | 0.0688 | -0.3617 | -0.0451 | -0.3445 | 1.5821 | 30.23 | 6.4745 | 27.7326 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19928
AXITEC | AC-240P/156-60B | 240 W Polycrystalline Module | UL 1703 | 240 | 214.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.45 | 37.4 | 8 | 30 | 47.9 | -0.4324 | 0.0841 | -0.385 | 0.03 | -0.4459 | 1.6036 | 29.7047 | 6.5433 | 27.0163 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19848
AXITEC | AC-240P/156-60S | 240 W Polycrystalline Module | UL 1703 | 240 | 216.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.48 | 37.25 | 8.09 | 29.67 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.6118 | 29.0793 | 6.5657 | 26.9007 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19529
AXITEC | AC-245M/156-60S | 245 W Monocrystalline Module | UL 1703 | 245 | 221.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6229 | 60 | 1 | N | 8.6 | 37.67 | 8.01 | 30.59 | 45.7 | -0.4395 | 0.0688 | -0.3617 | -0.0451 | -0.3445 | 1.6357 | 30.207 | 6.5518 | 27.9594 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.20167
AXITEC | AC-245P/156-60S | 245 W Polycrystalline Module | UL 1703 | 245 | 220.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.63 | 37.34 | 8.2 | 29.88 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.6338 | 29.2851 | 6.6554 | 27.0911 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19529
AXITEC | AC-250M/156-60S | 250 W Monocrystalline Module | UL 1703 | 250 | 225.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6229 | 60 | 1 | N | 8.88 | 37.51 | 8.22 | 30.4 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.5773 | 29.7818 | 6.5782 | 27.1479 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1879
AXITEC | AC-250P/156-60S | 250 W Polycrystalline Module | UL 1703 | 250 | 225.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.79 | 37.41 | 8.34 | 29.98 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.6616 | 29.3831 | 6.7686 | 27.1818 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19529
AXITEC | AC-255M/156-60S | 255 W Monocrystalline Module | UL 1703 | 255 | 229.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6229 | 60 | 1 | N | 9.03 | 37.59 | 8.36 | 30.5 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.6036 | 29.8798 | 6.6877 | 27.2372 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1879
AXITEC | AC-255P/156-60S | 255 W Polycrystalline Module | UL 1703 | 255 | 230 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.94 | 37.54 | 8.43 | 30.25 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.6797 | 29.6477 | 6.8423 | 27.4266 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19529
AXITEC | AC-260M/156-60S | 260 W Monocrystalline Module | UL 1703 | 260 | 234.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6229 | 60 | 1 | N | 9.18 | 37.73 | 8.5 | 30.6 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.6297 | 29.9777 | 6.7966 | 27.3265 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1879
AXITEC | AC-260P/156-60S | 260 W Polycrystalline Module | UL 1703 | 260 | 231.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 9.09 | 37.65 | 8.52 | 30.51 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6403 | 29.8933 | 6.8296 | 27.5882 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1886
AXITEC | AC-265M/156-60S | 265 W Monocrystalline Module | UL 1703 | 265 | 239.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6229 | 60 | 1 | N | 9.31 | 37.91 | 8.63 | 30.7 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.6556 | 30.0757 | 6.9047 | 27.4158 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1879
AXITEC | AC-265P/156-60S | 265 W Polycrystalline Module | UL 1703 | 265 | 236.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 9.24 | 37.77 | 8.61 | 30.78 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6573 | 30.1579 | 6.9003 | 27.8323 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.18861
AXITEC | AC-265P/60S | 265 W, 60 cell polycrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 265 | 244.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.1 | 38.14 | 8.56 | 30.96 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.6875 | 29.6698 | 6.8088 | 28.3885 | [6 empty] | 2018-12-17
AXITEC | AC-265P/60V | 265 W, 60 cell polycrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 265 | 244.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.1 | 38.14 | 8.56 | 30.96 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.6875 | 29.6698 | 6.8088 | 28.3885 | [6 empty] | 2018-12-17
AXITEC | AC-270M/156-60S | 270 W Monocrystalline Module | UL 1703 | 270 | 243.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6229 | 60 | 1 | N | 9.39 | 38.09 | 8.77 | 30.79 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.6821 | 30.1639 | 7.0152 | 27.4961 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.18792
AXITEC | AC-270P/156-60S | 270 W Polycrystalline Module | UL 1703 | 270 | 244.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.31 | 38.5 | 8.57 | 31.11 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.74 | 30.3 | 6.8 | 27.96 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19527
AXITEC | AC-270P/156-72S | 270 W Polycrystalline Module | UL 1703 | 270 | 242.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.2 | 44.18 | 7.7 | 35.06 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.5265 | 33.9593 | 6.164 | 31.8935 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.192
AXITEC | AC-270P/60S | 270 W, 60 cell polycrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 270 | 248.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.15 | 38.31 | 8.64 | 31.26 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7033 | 29.9573 | 6.8725 | 28.6636 | [6 empty] | 2018-12-17
AXITEC | AC-270P/60V | 270 W, 60 cell polycrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 270 | 248.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.15 | 38.31 | 8.64 | 31.26 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7033 | 29.9573 | 6.8725 | 28.6636 | [6 empty] | 2018-12-17
AXITEC | AC-275P/156-72S | 275 W Polycrystalline Module | UL 1703 | 275 | 247.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.29 | 44.34 | 7.81 | 35.21 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.5484 | 34.0988 | 6.2525 | 32.0245 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.192
AXITEC | AC-275P/60S | 275 W, 60 cell polycrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 275 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.24 | 38.5 | 8.74 | 31.46 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.723 | 30.149 | 6.952 | 28.847 | [6 empty] | 2018-12-17
AXITEC | AC-275P/60V | 275 W, 60 cell polycrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 275 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.24 | 38.5 | 8.74 | 31.46 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.723 | 30.149 | 6.952 | 28.847 | [6 empty] | 2018-12-17
AXITEC | AC-280M/156-60S | 280 W Monocrystalline Module | UL 1703 | 280 | 250.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.28 | 39.1 | 8.91 | 31.43 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.71 | 30.63 | 7.1 | 28.22 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18706
AXITEC | AC-280M/60S | 280 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 280 | 254.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.36 | 39.05 | 8.84 | 31.68 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8014 | 31.4118 | 7.0472 | 29.3263 | [6 empty] | 2018-11-15
AXITEC | AC-280M/60V | 280 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 280 | 254.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.36 | 39.05 | 8.84 | 31.68 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8014 | 31.4118 | 7.0472 | 29.3263 | [6 empty] | 2018-11-15
AXITEC | AC-280P/156-72S | 280 W Polycrystalline Module | UL 1703 | 280 | 252 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.4 | 44.46 | 7.91 | 35.39 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.5686 | 34.2731 | 6.3338 | 32.1882 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.192
AXITEC | AC-285M/156-60S | 285 W Monocrystalline Module | UL 1703 | 285 | 260.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.56 | 38.9 | 9.05 | 31.5 | 45.3 | -0.417 | 0.056 | -0.312 | 0.027 | -0.419 | 1.8427 | 31.187 | 7.6464 | 28.5752 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20165
AXITEC | AC-285M/156-72S | 285 W Monocrystalline Module | UL 1703 | 285 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.48 | 44.78 | 7.91 | 36.03 | 45.8 | -0.4316 | 0.0675 | -0.3562 | -0.0061 | -0.365 | 1.5779 | 36.1716 | 6.4682 | 32.8244 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20026
AXITEC | AC-285M/60S | 285 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 285 | 259.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.43 | 39.24 | 8.96 | 31.81 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8258 | 31.5407 | 7.1429 | 29.4466 | [6 empty] | 2018-11-15
AXITEC | AC-285M/60V | 285 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 285 | 259.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.43 | 39.24 | 8.96 | 31.81 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8258 | 31.5407 | 7.1429 | 29.4466 | [6 empty] | 2018-11-15
AXITEC | AC-285P/156-72S | 285 W Polycrystalline Module | UL 1703 | 285 | 256.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.52 | 44.51 | 8 | 35.6 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.5869 | 34.4823 | 6.4078 | 32.3847 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.192
AXITEC | AC-290M/156-60S | 290 W Monocrystalline Module | UL 1703 | 290 | 265.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.65 | 39.2 | 9.12 | 31.8 | 45.3 | -0.417 | 0.056 | -0.312 | 0.027 | -0.419 | 1.857 | 31.4841 | 7.7055 | 28.8474 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20161
AXITEC | AC-290M/156-72S | 290 W Monocrystalline Module | UL 1703 | 290 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.55 | 44.98 | 7.97 | 36.4 | 45.8 | -0.4316 | 0.0675 | -0.3562 | -0.0061 | -0.365 | 1.6253 | 35.4229 | 6.5092 | 32.9554 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19852
AXITEC | AC-290M/60S | 290 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 290 | 264.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.54 | 39.42 | 9.06 | 32.01 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8462 | 31.739 | 7.2226 | 29.6317 | [6 empty] | 2018-11-15
AXITEC | AC-290M/60V | 290 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 290 | 264.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.54 | 39.42 | 9.06 | 32.01 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8462 | 31.739 | 7.2226 | 29.6317 | [6 empty] | 2018-11-15
AXITEC | AC-290P/156-72S | 290 W Polycrystalline Module | UL 1703 | 290 | 261.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.64 | 44.65 | 8.09 | 35.86 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.5678 | 35.3075 | 6.5181 | 32.2669 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.19089
AXITEC | AC-295M/156-72S | 295 W Monocrystalline Module | UL 1703 | 295 | 265.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.71 | 45.01 | 8.09 | 36.48 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.5462 | 36.0506 | 6.4774 | 33.6489 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.18896
AXITEC | AC-295M/60S | 295 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 295 | 268.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.67 | 39.56 | 9.15 | 32.25 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8645 | 31.977 | 7.2943 | 29.8539 | [6 empty] | 2018-11-15
AXITEC | AC-295M/60V | 295 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 295 | 268.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.67 | 39.56 | 9.15 | 32.25 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8645 | 31.977 | 7.2943 | 29.8539 | [6 empty] | 2018-11-15
AXITEC | AC-295P/156-72S | 295 W Polycrystalline Module | UL 1703 | 295 | 265.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.76 | 44.74 | 8.2 | 35.98 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.5896 | 35.4257 | 6.6084 | 32.3749 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.19089
AXITEC | AC-300M/156-72S | 300 W Monocrystalline Module | UL 1703 | 300 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.81 | 45.11 | 8.2 | 36.6 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.5673 | 36.1692 | 6.5656 | 33.7596 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.18896
AXITEC | AC-300M/60S | 300 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 300 | 273.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.74 | 39.72 | 9.27 | 32.37 | 47 | -0.404 | 0.05 | -0.303 | 1.889 | 32.096 | 1.889 | 32.096 | 7.39 | 29.965 | [6 empty] | 2018-11-15 | 2019-08-15
AXITEC | AC-300M/60V | 300 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 300 | 273.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.74 | 39.72 | 9.27 | 32.37 | 47.07 | -0.404 | 0.05 | -0.303 | 1.889 | 32.096 | 1.889 | 32.096 | 7.39 | 29.965 | [6 empty] | 2018-11-15 | 2019-08-15
AXITEC | AC-300P/156-72S | 300 W Polycrystalline Module | UL 1703 | 300 | 270.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.88 | 44.82 | 8.26 | 36.3 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.6021 | 35.7447 | 6.6604 | 32.6665 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.19089
AXITEC | AC-305M/156-72S | 305 W Monocrystalline Module | UL 1703 | 305 | 275 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.92 | 45.28 | 8.31 | 36.72 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.5882 | 36.2878 | 6.6532 | 33.8703 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.18896
AXITEC | AC-305M/60S | 305 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 305 | 278.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.83 | 39.81 | 9.41 | 32.41 | 47.07 | -0.404 | 0.05 | -0.303 | 1.9175 | 32.1357 | 1.9175 | 32.1357 | 7.5016 | 30.002 | [6 empty] | 2019-08-15
AXITEC | AC-305M/60V | 305 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 305 | 278.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.83 | 39.81 | 9.41 | 32.41 | 47.07 | -0.404 | 0.05 | -0.303 | 1.9175 | 32.1357 | 1.9175 | 32.1357 | 7.5016 | 30.002 | [6 empty] | 2019-08-15
AXITEC | AC-305MH/120S | 305W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 305 | 283.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.86 | 39.42 | 9.42 | 32.37 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.8251 | 31.1903 | 7.3525 | 30.0639 | [6 empty] | 2019-08-15
AXITEC | AC-305MH/120V | 305W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 305 | 283.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.86 | 39.42 | 9.42 | 32.37 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.8251 | 31.1903 | 7.3525 | 30.0639 | [6 empty] | 2019-08-15
AXITEC | AC-305P/156-72S | 305 W Polycrystalline Module | UL 1703 | 305 | 275.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.99 | 44.91 | 8.33 | 36.61 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.6149 | 36.052 | 6.7137 | 32.9472 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.19089
AXITEC | AC-310M/156-72S | 310 W Monocrystalline Module | UL 1703 | 310 | 279.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 9.01 | 45.49 | 8.41 | 36.84 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.609 | 36.4064 | 6.7403 | 33.981 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.18896
AXITEC | AC-310M/60S | 310 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 310 | 282.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.92 | 39.9 | 9.55 | 32.46 | 47.07 | -0.404 | 0.05 | -0.303 | 1.9461 | 32.1852 | 1.9461 | 32.1852 | 7.6132 | 30.0483 | [6 empty] | 2019-08-15
AXITEC | AC-310M/60V | 310 W, 60 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 310 | 282.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.92 | 39.9 | 9.55 | 32.46 | 47.07 | -0.404 | 0.05 | -0.303 | 1.9461 | 32.1852 | 1.9461 | 32.1852 | 7.6132 | 30.0483 | [6 empty] | 2019-08-15
AXITEC | AC-310MH/120S | 310W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 310 | 288 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.95 | 39.58 | 9.51 | 32.58 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.8426 | 31.3927 | 7.4228 | 30.259 | [6 empty] | 2019-08-15
AXITEC | AC-310MH/120V | 310W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 310 | 288 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.95 | 39.58 | 9.51 | 32.58 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.8426 | 31.3927 | 7.4228 | 30.259 | [6 empty] | 2019-08-15
AXITEC | AC-310P/156-72S | 310 W Polycrystalline Module | UL 1703 | 310 | 276 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 9.1 | 45.05 | 8.42 | 36.82 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6147 | 35.8422 | 6.8032 | 32.6667 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.18669
AXITEC | AC-315M/156-72S | 315 W Monocrystalline Module | UL 1703 | 315 | 284.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 9.12 | 45.62 | 8.53 | 36.91 | 47 | -0.43 | 0.065 | -0.323 | 0.057 | -0.466 | 1.6318 | 36.4756 | 6.836 | 34.0455 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.18896
AXITEC | AC-315MH/120S | 315W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 315 | 292.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 10.04 | 39.74 | 9.6 | 32.79 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.86 | 31.595 | 7.493 | 30.454 | [6 empty] | 2019-08-15
AXITEC | AC-315MH/120V | 315W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 315 | 292.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 10.04 | 39.74 | 9.6 | 32.79 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.86 | 31.595 | 7.493 | 30.454 | [6 empty] | 2019-08-15
AXITEC | AC-315P/156-72S | 315 W Polycrystalline Module | UL 1703 | 315 | 280.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 9.21 | 45.16 | 8.49 | 37.11 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6281 | 36.1245 | 6.8598 | 32.924 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.18671
AXITEC | AC-315P/72S | 315 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 315 | 290.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 8.91 | 45.6 | 8.45 | 37.28 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7017 | 35.7922 | 6.8325 | 34.2736 | [6 empty] | 2018-12-17
AXITEC | AC-315P/72V | 315 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 315 | 290.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 8.91 | 45.6 | 8.45 | 37.28 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7017 | 35.7922 | 6.8325 | 34.2736 | [6 empty] | 2018-12-17
AXITEC | AC-320MH/120S | 320W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 320 | 297.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 10.13 | 39.92 | 9.69 | 33.01 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.8774 | 31.807 | 7.5632 | 30.6583 | [6 empty] | 2019-08-15
AXITEC | AC-320MH/120V | 320W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 320 | 297.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 10.13 | 39.92 | 9.69 | 33.01 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.8774 | 31.807 | 7.5632 | 30.6583 | [6 empty] | 2019-08-15
AXITEC | AC-320P/156-72S | 320 W Polycrystalline Module | UL 1703 | 320 | 285.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 9.32 | 45.27 | 8.57 | 37.34 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6435 | 36.3484 | 6.9244 | 33.1281 | Rack | Flat Plate | 0.992 | 1.952 | 1 | 0.18668
AXITEC | AC-320P/72S | 320 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 320 | 295 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.03 | 45.82 | 8.52 | 37.56 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7158 | 36.061 | 6.8891 | 34.5311 | [6 empty] | 2018-12-17
AXITEC | AC-320P/72V | 320 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 320 | 295 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.03 | 45.82 | 8.52 | 37.56 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7158 | 36.061 | 6.8891 | 34.5311 | [6 empty] | 2018-12-17
AXITEC | AC-320P/72X | 320 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 320 | 290.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.03 | 45.82 | 8.52 | 37.56 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.8406 | 35.4892 | 6.7555 | 35.2289 | [6 empty] | 2018-11-15
AXITEC | AC-320P/72XV | 320 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 320 | 290.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.03 | 45.82 | 8.52 | 37.56 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.8406 | 35.4892 | 6.7555 | 35.2289 | [6 empty] | 2018-11-15
AXITEC | AC-325MH/120S | 325 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 325 | 303.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.43 | 40.1 | 9.93 | 32.71 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9285 | 32.4337 | 7.7983 | 31.1654 | [6 empty] | 2020-01-13
AXITEC | AC-325MH/120V | 325 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 325 | 303.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.43 | 40.1 | 9.93 | 32.71 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9285 | 32.4337 | 7.7983 | 31.1654 | [6 empty] | 2020-01-13
AXITEC | AC-325P/156-72S | 325 W Polycrystalline Module | UL 1703 | 325 | 295.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.22 | 45.7 | 8.7 | 37.4 | 43.2 | -0.4877 | 0.0584 | -0.3572 | -0.0193 | -0.4729 | 1.736 | 36.1292 | 6.9951 | 34.5903 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19298
AXITEC | AC-325P/72S | 325 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 325 | 299.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.15 | 45.92 | 8.63 | 37.66 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.738 | 36.157 | 6.978 | 34.623 | [6 empty] | 2018-12-17
AXITEC | AC-325P/72V | 325 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 325 | 299.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.15 | 45.92 | 8.63 | 37.66 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.738 | 36.157 | 6.978 | 34.623 | [6 empty] | 2018-12-17
AXITEC | AC-325P/72X | 325 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 325 | 294.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.15 | 45.92 | 8.63 | 37.66 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.8644 | 35.5837 | 6.8427 | 35.3227 | [6 empty] | 2018-11-15
AXITEC | AC-325P/72XV | 325 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 325 | 294.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.15 | 45.92 | 8.63 | 37.66 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.8644 | 35.5837 | 6.8427 | 35.3227 | [6 empty] | 2018-11-15
AXITEC | AC-330MH/120S | 330 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 330 | 308.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.51 | 40.27 | 10.02 | 32.91 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.946 | 32.632 | 7.869 | 31.356 | [6 empty] | 2020-01-13
AXITEC | AC-330MH/120V | 330 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 330 | 308.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.51 | 40.27 | 10.02 | 32.91 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.946 | 32.632 | 7.869 | 31.356 | [6 empty] | 2020-01-13
AXITEC | AC-330P/156-72S | 330 W Polycrystalline Module | UL 1703 | 330 | 300.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.27 | 45.9 | 8.76 | 37.7 | 43.2 | -0.4877 | 0.0584 | -0.3572 | -0.0193 | -0.4729 | 1.748 | 36.419 | 7.0433 | 34.8677 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19291
AXITEC | AC-330P/72S | 330 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 330 | 304.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.28 | 45.97 | 8.73 | 37.8 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7581 | 36.2914 | 7.0589 | 34.7517 | [6 empty] | 2018-12-17
AXITEC | AC-330P/72V | 330 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 330 | 304.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.28 | 45.97 | 8.73 | 37.8 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7581 | 36.2914 | 7.0589 | 34.7517 | [6 empty] | 2018-12-17
AXITEC | AC-330P/72X | 330 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 330 | 299.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.28 | 45.97 | 8.73 | 37.8 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.886 | 35.716 | 6.922 | 35.454 | [6 empty] | 2018-11-15
AXITEC | AC-330P/72XV | 330 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 330 | 299.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.28 | 45.97 | 8.73 | 37.8 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.886 | 35.716 | 6.922 | 35.454 | [6 empty] | 2018-11-15
AXITEC | AC-335M/72S | 335 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 335 | 304.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.41 | 46.04 | 8.95 | 37.44 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.7696 | 36.0215 | 7.4393 | 33.5108 | [6 empty] | 2018-11-15
AXITEC | AC-335M/72V | 335 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 335 | 304.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.41 | 46.04 | 8.95 | 37.44 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.7696 | 36.0215 | 7.4393 | 33.5108 | [6 empty] | 2018-11-15
AXITEC | AC-335MH/120S | 335 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 335 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.6 | 40.44 | 10.11 | 33.11 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9635 | 32.8303 | 7.9397 | 31.5466 | [6 empty] | 2020-01-13
AXITEC | AC-335MH/120V | 335 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 335 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.6 | 40.44 | 10.11 | 33.11 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9635 | 32.8303 | 7.9397 | 31.5466 | [6 empty] | 2020-01-13
AXITEC | AC-335P/156-72S | 335 W Polycrystalline Module | UL 1703 | 335 | 304.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.34 | 46.2 | 8.82 | 38 | 43.2 | -0.4877 | 0.0584 | -0.3572 | -0.0193 | -0.4729 | 1.7599 | 36.7088 | 7.0915 | 35.1452 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19285
AXITEC | AC-335P/72S | 335 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 335 | 309.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.3 | 46.45 | 8.82 | 37.98 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7763 | 36.4642 | 7.1316 | 34.9172 | [6 empty] | 2018-12-17
AXITEC | AC-335P/72V | 335 W, 72 cell polycrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 335 | 309.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.3 | 46.45 | 8.82 | 37.98 | 44.88 | -0.383 | 0.052 | -0.299 | 0.012 | -0.394 | 1.7763 | 36.4642 | 7.1316 | 34.9172 | [6 empty] | 2018-12-17
AXITEC | AC-335P/72X | 335 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 335 | 304.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.3 | 46.45 | 8.82 | 37.98 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.9054 | 35.8861 | 6.9934 | 35.6228 | [6 empty] | 2018-11-15
AXITEC | AC-335P/72XV | 335 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 335 | 304.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.3 | 46.45 | 8.82 | 37.98 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.9054 | 35.8861 | 6.9934 | 35.6228 | [6 empty] | 2018-11-15
AXITEC | AC-340M/156-72S | 340 W Monocrystalline Module | UL 1703 | 340 | 310.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.45 | 46.6 | 8.93 | 38.1 | 45.2 | -0.425 | 0.049 | -0.317 | -0.021 | -0.434 | 1.8796 | 37.4154 | 7.5907 | 34.6861 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20684
AXITEC | AC-340M/72S | 340 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 340 | 309.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.48 | 46.16 | 9.05 | 37.57 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.7894 | 36.1466 | 7.5224 | 33.6271 | [6 empty] | 2018-11-15
AXITEC | AC-340M/72V | 340 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 340 | 309.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.48 | 46.16 | 9.05 | 37.57 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.7894 | 36.1466 | 7.5224 | 33.6271 | [6 empty] | 2018-11-15
AXITEC | AC-340MH/120S | 340 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 340 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.69 | 40.62 | 10.21 | 33.31 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9829 | 33.0286 | 8.0182 | 31.7371 | [6 empty] | 2020-01-13
AXITEC | AC-340MH/120V | 340 W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 340 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.69 | 40.62 | 10.21 | 33.31 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9829 | 33.0286 | 8.0182 | 31.7371 | [6 empty] | 2020-01-13
AXITEC | AC-340P/156-72S | 340 W Polycrystalline Module | UL 1703 | 340 | 309.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.4 | 46.4 | 8.89 | 38.3 | 43.2 | -0.4877 | 0.0584 | -0.3572 | -0.0193 | -0.4729 | 1.7739 | 36.9986 | 7.1478 | 35.4227 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19304
AXITEC | AC-340P/72X | 340 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 340 | 308.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.4 | 46.61 | 8.91 | 38.16 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.9249 | 36.0562 | 7.0647 | 35.7917 | [6 empty] | 2018-11-15
AXITEC | AC-340P/72XV | 340 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 340 | 308.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.4 | 46.61 | 8.91 | 38.16 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.9249 | 36.0562 | 7.0647 | 35.7917 | [6 empty] | 2018-11-15
AXITEC | AC-345M/156-72S | 345 W Monocrystalline Module | UL 1703 | 345 | 315.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.5 | 47 | 8.99 | 38.4 | 45.2 | -0.425 | 0.049 | -0.317 | -0.021 | -0.434 | 1.8922 | 37.7101 | 7.6417 | 34.9592 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20682
AXITEC | AC-345M/72S | 345 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 345 | 314.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.51 | 46.61 | 9.09 | 37.96 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.7973 | 36.5218 | 7.5556 | 33.9762 | [6 empty] | 2018-11-15
AXITEC | AC-345M/72V | 345 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 345 | 314.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.51 | 46.61 | 9.09 | 37.96 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.7973 | 36.5218 | 7.5556 | 33.9762 | [6 empty] | 2018-11-15
AXITEC | AC-345P/156-72S | 345 W Polycrystalline Module | UL 1703 | 345 | 314.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.46 | 46.6 | 8.95 | 38.6 | 43.2 | -0.4877 | 0.0584 | -0.3572 | -0.0193 | -0.4729 | 1.7859 | 37.2884 | 7.1961 | 35.7001 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19302
AXITEC | AC-345P/72X | 345 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 345 | 313.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.5 | 46.76 | 8.98 | 38.42 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.94 | 36.3018 | 7.1202 | 36.0355 | [6 empty] | 2018-11-15
AXITEC | AC-345P/72XV | 345 W, 72 cell polycrystalline module, 7 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 345 | 313.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.5 | 46.76 | 8.98 | 38.42 | 47.07 | -0.412 | 0.051 | -0.32 | -0.04 | -0.381 | 1.94 | 36.3018 | 7.1202 | 36.0355 | [6 empty] | 2018-11-15
AXITEC | AC-350M/156-72S | 350 W Monocrystalline Module | UL 1703 | 350 | 320 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.59 | 47.2 | 9.1 | 38.5 | 45.2 | -0.425 | 0.049 | -0.317 | -0.021 | -0.434 | 1.9153 | 37.8083 | 7.7352 | 35.0502 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.2069
AXITEC | AC-350M/72S | 350 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 350 | 319 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.58 | 46.89 | 9.13 | 38.34 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8052 | 36.8874 | 7.5889 | 34.3163 | [6 empty] | 2018-11-15
AXITEC | AC-350M/72V | 350 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 350 | 319 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.58 | 46.89 | 9.13 | 38.34 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8052 | 36.8874 | 7.5889 | 34.3163 | [6 empty] | 2018-11-15
AXITEC | AC-350MH/120V | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 322.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.15 | 40.1 | 10.42 | 33.6 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1006 | 32.2472 | 8.4131 | 31.2264 | [6 empty] | 2021-09-13
AXITEC | AC-350MH/120VB | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 350 | 326.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.15 | 40.1 | 10.42 | 33.6 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.1421 | 32.0519 | 7.3211 | 35.3073 | [6 empty] | 2021-09-13
AXITEC | AC-355M/156-72S | 355 W Monocrystalline Module | UL 1703 | 355 | 324.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.67 | 47.4 | 9.2 | 38.6 | 45.2 | -0.425 | 0.049 | -0.317 | -0.021 | -0.434 | 1.9364 | 37.9065 | 7.8202 | 35.1413 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20676
AXITEC | AC-355M/72S | 355 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 355 | 323.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.66 | 47.16 | 9.19 | 38.63 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8171 | 37.1664 | 7.6388 | 34.5759 | [6 empty] | 2018-11-15
AXITEC | AC-355M/72V | 355 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 355 | 323.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.66 | 47.16 | 9.19 | 38.63 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8171 | 37.1664 | 7.6388 | 34.5759 | [6 empty] | 2018-11-15
AXITEC | AC-355MH/120V | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 327.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.25 | 40.3 | 10.51 | 33.8 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1187 | 32.4391 | 8.4857 | 31.4123 | [6 empty] | 2021-09-13
AXITEC | AC-355MH/120VB | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 355 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.25 | 40.3 | 10.51 | 33.8 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.1606 | 32.2426 | 7.3843 | 35.5175 | [6 empty] | 2021-09-13
AXITEC | AC-355MH/144S | 355W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 355 | 328.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.6 | 46.82 | 9.1 | 39.01 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.7849 | 37.124 | 7.1613 | 35.8318 | [6 empty] | 2019-08-15
AXITEC | AC-355MH/144V | 355W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 355 | 328.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.6 | 46.82 | 9.1 | 39.01 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.7849 | 37.124 | 7.1613 | 35.8318 | [6 empty] | 2019-08-15
AXITEC | AC-360M/72S | 360 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 360 | 328.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.73 | 47.44 | 9.23 | 39.01 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8329 | 37.888 | 7.7052 | 35.2472 | [6 empty] | 2018-11-15 | 2019-08-15
AXITEC | AC-360M/72V | 360 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 360 | 328.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.73 | 47.44 | 9.23 | 39.01 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8329 | 37.888 | 7.7052 | 35.2472 | [6 empty] | 2018-11-15 | 2019-08-15
AXITEC | AC-360MH/120V | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 332.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.35 | 40.5 | 10.59 | 34 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1349 | 32.6311 | 8.5503 | 31.5981 | [6 empty] | 2021-09-13
AXITEC | AC-360MH/120VB | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 360 | 336 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.35 | 40.5 | 10.59 | 34 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.1771 | 32.4334 | 7.4406 | 35.7277 | [6 empty] | 2021-09-13
AXITEC | AC-360MH/144S | 360W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 360 | 333.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.69 | 47.01 | 9.18 | 39.2 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8005 | 37.3048 | 7.2242 | 36.0063 | [6 empty] | 2019-08-15
AXITEC | AC-360MH/144V | 360W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 360 | 333.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.69 | 47.01 | 9.18 | 39.2 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8005 | 37.3048 | 7.2242 | 36.0063 | [6 empty] | 2019-08-15
AXITEC | AC-365M/72S | 365 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 365 | 333.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.81 | 47.67 | 9.27 | 39.38 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8329 | 37.888 | 7.7052 | 35.2472 | [6 empty] | 2018-11-15
AXITEC | AC-365M/72V | 365 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 365 | 333.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.81 | 47.67 | 9.27 | 39.38 | 47 | -0.404 | 0.05 | -0.303 | -0.01 | -0.4 | 1.8329 | 37.888 | 7.7052 | 35.2472 | [6 empty] | 2018-11-15
AXITEC | AC-365MH/120V | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 337 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.43 | 40.7 | 10.68 | 34.2 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.153 | 32.823 | 8.623 | 31.784 | [6 empty] | 2021-09-13
AXITEC | AC-365MH/120VB | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 365 | 340.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.43 | 40.7 | 10.68 | 34.2 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.1956 | 32.6242 | 7.5038 | 35.9378 | [6 empty] | 2021-09-13
AXITEC | AC-365MH/144S | 365W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 365 | 338.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.77 | 47.21 | 9.27 | 39.39 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8182 | 37.4856 | 7.295 | 36.1808 | [6 empty] | 2019-08-15
AXITEC | AC-365MH/144V | 365W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 365 | 338.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.77 | 47.21 | 9.27 | 39.39 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8182 | 37.4856 | 7.295 | 36.1808 | [6 empty] | 2019-08-15
AXITEC | AC-370M/72S | 370 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 370 | 337.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.89 | 47.91 | 9.29 | 39.84 | 47 | -0.404 | 0.05 | -0.303 |  |  | 1.8359 | 38.2376 | 7.7219 | 35.6589 | [6 empty] | 2019-08-15
AXITEC | AC-370M/72V | 370 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 370 | 337.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.89 | 47.91 | 9.29 | 39.84 | 47 | -0.404 | 0.05 | -0.303 |  |  | 1.8359 | 38.2376 | 7.7219 | 35.6589 | [6 empty] | 2019-08-15
AXITEC | AC-370MH/120V | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 341.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.52 | 40.9 | 10.76 | 34.4 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1691 | 33.0149 | 8.6876 | 31.9699 | [6 empty] | 2021-09-13
AXITEC | AC-370MH/120VB | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 370 | 345.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.52 | 40.9 | 10.76 | 34.4 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.212 | 32.815 | 7.56 | 36.148 | [6 empty] | 2021-09-13
AXITEC | AC-370MH/144S | 370W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 370 | 343.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.85 | 47.4 | 9.35 | 39.6 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8339 | 37.6855 | 7.358 | 36.3737 | [6 empty] | 2019-08-15
AXITEC | AC-370MH/144V | 370W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 370 | 343.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.85 | 47.4 | 9.35 | 39.6 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8339 | 37.6855 | 7.358 | 36.3737 | [6 empty] | 2019-08-15
AXITEC | AC-375M/72S | 375 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 375 | 342.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.95 | 48.16 | 9.33 | 40.21 | 47 | -0.404 | 0.05 | -0.303 |  |  | 1.8438 | 38.5927 | 7.7551 | 35.9901 | [6 empty] | 2019-08-15
AXITEC | AC-375M/72V | 375 W, 72 cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 375 | 342.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.95 | 48.16 | 9.33 | 40.21 | 47 | -0.404 | 0.05 | -0.303 |  |  | 1.8438 | 38.5927 | 7.7551 | 35.9901 | [6 empty] | 2019-08-15
AXITEC | AC-375MH/120V | 375 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 346.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.6 | 41.1 | 10.84 | 34.6 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1853 | 33.2069 | 8.7522 | 32.1557 | [6 empty] | 2021-09-13
AXITEC | AC-375MH/120VB | 375 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 375 | 350.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.6 | 41.1 | 10.84 | 34.6 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.2284 | 33.0058 | 7.6162 | 36.3582 | [6 empty] | 2021-09-13
AXITEC | AC-375MH/144S | 375W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 375 | 348 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.93 | 47.61 | 9.43 | 39.81 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8496 | 37.8853 | 7.421 | 36.5666 | [6 empty] | 2019-08-15
AXITEC | AC-375MH/144V | 375W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 375 | 348 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.93 | 47.61 | 9.43 | 39.81 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8496 | 37.8853 | 7.421 | 36.5666 | [6 empty] | 2019-08-15
AXITEC | AC-380MH/144S | 380W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 380 | 352.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 10.01 | 47.8 | 9.5 | 40.02 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8633 | 38.0852 | 7.476 | 36.7595 | [6 empty] | 2019-08-15
AXITEC | AC-380MH/144V | 380W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 380 | 352.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 10.01 | 47.8 | 9.5 | 40.02 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.8633 | 38.0852 | 7.476 | 36.7595 | [6 empty] | 2019-08-15
AXITEC | AC-385MH/144S | 385W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 385 | 357.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 10.08 | 48 | 9.58 | 40.21 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.879 | 38.266 | 7.539 | 36.934 | [6 empty] | 2019-08-15
AXITEC | AC-385MH/144V | 385W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 385 | 357.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 10.08 | 48 | 9.58 | 40.21 | 45.81 | -0.352 | 0.042 | -0.275 |  |  | 1.879 | 38.266 | 7.539 | 36.934 | [6 empty] | 2019-08-15
AXITEC | AC-390MH/144S | 390 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 390 | 364.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.48 | 48.18 | 9.66 | 40.37 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.9379 | 38.7253 | 7.8452 | 37.3321 | [6 empty] | 2020-01-13
AXITEC | AC-390MH/144V | 390 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 390 | 364.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.48 | 48.18 | 9.66 | 40.37 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.9379 | 38.7253 | 7.8452 | 37.3321 | [6 empty] | 2020-01-13
AXITEC | AC-395MH/144S | 395 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 395 | 369 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.56 | 48.37 | 9.74 | 40.55 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.954 | 38.898 | 7.9102 | 37.4986 | [6 empty] | 2020-01-13
AXITEC | AC-395MH/144V | 395 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 395 | 369 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.56 | 48.37 | 9.74 | 40.55 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.954 | 38.898 | 7.9102 | 37.4986 | [6 empty] | 2020-01-13
AXITEC | AC-400MH/144S | 400 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 400 | 373.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.64 | 48.55 | 9.81 | 40.77 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.968 | 39.109 | 7.967 | 37.702 | [6 empty] | 2020-01-13
AXITEC | AC-400MH/144V | 400 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 400 | 373.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.64 | 48.55 | 9.81 | 40.77 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.968 | 39.109 | 7.967 | 37.702 | [6 empty] | 2020-01-13
AXITEC | AC-405MH/144S | 405 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 405 | 378.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.71 | 48.73 | 9.89 | 40.95 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.984 | 39.2817 | 8.032 | 37.8685 | [6 empty] | 2020-01-13
AXITEC | AC-405MH/144V | 405 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 405 | 378.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.71 | 48.73 | 9.89 | 40.95 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.984 | 39.2817 | 8.032 | 37.8685 | [6 empty] | 2020-01-13
AXITEC | AC-410MB/144V | 410 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 381.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.41 | 49.3 | 9.91 | 41.4 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.9638 | 39.9419 | 7.8846 | 39.0773 | [6 empty] | 2021-09-13
AXITEC | AC-410MH/144S | 410 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 410 | 383.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.79 | 48.91 | 9.97 | 41.12 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 2.0001 | 39.4447 | 8.0969 | 38.0257 | [6 empty] | 2020-01-13
AXITEC | AC-410MH/144V | 410 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 410 | 383.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.79 | 48.91 | 9.97 | 41.12 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 2.0001 | 39.4447 | 8.0969 | 38.0257 | [6 empty] | 2020-01-13
AXITEC | AC-415MH/144V | 415 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 384.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 2 | N | 10.66 | 49.6 | 10.15 | 40.9 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.9686 | 39.9574 | 7.9025 | 39.05 | [6 empty] | 2021-09-13
AXITEC | AC-420MH/144V | 420 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 420 | 389.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 2 | N | 10.76 | 49.7 | 10.25 | 41 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.988 | 40.0551 | 7.9804 | 39.1454 | [6 empty] | 2021-09-13
AXITEC | AC-425MB/144V | 425 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 393.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.22 | 48.7 | 10.52 | 40.4 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1216 | 38.92 | 8.4532 | 37.7572 | [6 empty] | 2021-09-13
AXITEC | AC-425MH/144V | 425 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 392.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.23 | 48.3 | 10.5 | 40.5 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1156 | 38.9956 | 8.4411 | 37.7756 | [6 empty] | 2021-09-13
AXITEC | AC-430MB/144V | 430 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 397.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.3 | 48.9 | 10.6 | 40.6 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1378 | 39.1127 | 8.5175 | 37.9442 | [6 empty] | 2021-09-13
AXITEC | AC-430MH/144V | 430 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 397 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.19 | 49.2 | 10.6 | 40.6 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1358 | 39.0919 | 8.5215 | 37.8689 | [6 empty] | 2021-09-13
AXITEC | AC-435MB/144V | 435 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 402.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.36 | 49.1 | 10.67 | 40.8 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1519 | 39.3053 | 8.5738 | 38.1311 | [6 empty] | 2021-09-13
AXITEC | AC-435MH/144V | 435 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 401.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.26 | 49.4 | 10.67 | 40.8 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1499 | 39.2844 | 8.5777 | 38.0555 | [6 empty] | 2021-09-13
AXITEC | AC-440MB/144V | 440 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 407.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.45 | 49.3 | 10.74 | 41 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.166 | 39.498 | 8.63 | 38.318 | [6 empty] | 2021-09-13
AXITEC | AC-440MH/144V | 440 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 406.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.33 | 49.6 | 10.74 | 41 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.164 | 39.477 | 8.634 | 38.242 | [6 empty] | 2021-09-13
AXITEC | AC-445MB/144V | 445 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 412.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.52 | 49.5 | 10.81 | 41.2 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1801 | 39.6907 | 8.6862 | 38.5049 | [6 empty] | 2021-09-13
AXITEC | AC-445MH/144V | 445 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 411.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.4 | 49.8 | 10.81 | 41.2 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1781 | 39.6696 | 8.6903 | 38.4285 | [6 empty] | 2021-09-13
AXITEC | AC-450MB/144V | 450 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 416.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.58 | 49.6 | 10.87 | 41.4 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1922 | 39.8833 | 8.7345 | 38.6918 | [6 empty] | 2021-09-13
AXITEC | AC-450MH/144V | 450 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 416.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.47 | 50 | 10.88 | 41.4 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1922 | 39.8621 | 8.7465 | 38.6151 | [6 empty] | 2021-09-13
Bluesun Solar Co.,Ltd | BSM360M-60HPH | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 334 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.15 | 40.7 | 10.5 | 34.3 | 45.5 | -0.3637 | 0.0335 | -0.2942 |  |  | 2.1089 | 32.5305 | 8.047 | 31.6888 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM365M-60HPH | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 338.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.2 | 40.9 | 10.56 | 34.6 | 45.5 | -0.3637 | 0.0335 | -0.2942 |  |  | 2.121 | 32.815 | 8.093 | 31.966 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM370M-60HPH | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 343.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.26 | 41.1 | 10.61 | 34.9 | 45.5 | -0.3637 | 0.0335 | -0.2942 |  |  | 2.131 | 33.0995 | 8.1313 | 32.2432 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM430M-72HPH | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 398.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.26 | 48.8 | 10.73 | 40.1 | 45.2 | -0.377 | 0.0592 | -0.3023 |  |  | 2.0848 | 38.9218 | 8.4616 | 37.9019 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM435M-72HBD | 435 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 402.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.16 | 49.8 | 10.51 | 41.4 | 45.3 | -0.3766 | 0.075 | -0.2982 |  |  | 2.1119 | 39.2673 | 8.7189 | 37.1724 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM435M-72HPH | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 403 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.33 | 49 | 10.8 | 40.3 | 45.2 | -0.377 | 0.0592 | -0.3023 |  |  | 2.0984 | 39.1159 | 8.5168 | 38.091 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM440M-72HBD | 440 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 407.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.22 | 50 | 10.58 | 41.6 | 45.3 | -0.3766 | 0.075 | -0.2982 |  |  | 2.126 | 39.457 | 8.777 | 37.352 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM440M-72HPH | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 407.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.4 | 49.2 | 10.87 | 40.5 | 45.2 | -0.377 | 0.0592 | -0.3023 |  |  | 2.112 | 39.31 | 8.572 | 38.28 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM445M-72HBD | 445 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 412.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.29 | 50.2 | 10.65 | 41.8 | 45.3 | -0.3766 | 0.075 | -0.2982 |  |  | 2.1401 | 39.6467 | 8.8351 | 37.5316 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM445M-72HPH | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 412.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.47 | 49.4 | 10.94 | 40.7 | 45.2 | -0.377 | 0.0592 | -0.3023 |  |  | 2.1256 | 39.5041 | 8.6272 | 38.469 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM450M-72HBD | 450 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 417.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.36 | 50.4 | 10.72 | 42 | 45.3 | -0.3766 | 0.075 | -0.2982 |  |  | 2.1541 | 39.8364 | 8.8931 | 37.7112 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM450M-72HPH | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 417.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.54 | 49.6 | 11.01 | 40.9 | 45.2 | -0.377 | 0.0592 | -0.3023 |  |  | 2.1392 | 39.6982 | 8.6824 | 38.6581 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM455M-72HBD | 455 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 422 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.43 | 50.6 | 10.79 | 42.2 | 45.3 | -0.3766 | 0.075 | -0.2982 |  |  | 2.1682 | 40.0261 | 8.9512 | 37.8907 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM455M-72HPH | 455 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 422.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.61 | 49.8 | 11.08 | 41.1 | 45.2 | -0.377 | 0.0592 | -0.3023 |  |  | 2.1528 | 39.8924 | 8.7376 | 38.8471 | [6 empty] | 2021-07-21
Bluesun Solar Co.,Ltd | BSM460M-72HBD | 460 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 426.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.5 | 50.8 | 10.86 | 42.4 | 45.3 | -0.3766 | 0.075 | -0.2982 |  |  | 2.1823 | 40.2158 | 9.0093 | 38.0703 | [6 empty] | 2021-07-21
Bluesun Solar Energy Tech. Co.,Ltd | BSM265M-60 | 265 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 265 | 238.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.05 | 38.26 | 8.52 | 31.11 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.5432 | 30.4901 | 6.6044 | 27.901 | [6 empty] | 2018-03-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM270M-60 | 270 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 270 | 242.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.17 | 38.46 | 8.62 | 31.33 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.5613 | 30.7057 | 6.6819 | 28.0983 | [6 empty] | 2018-03-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM275M-60 | 275 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 275 | 247.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.25 | 38.86 | 8.73 | 31.51 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.5812 | 30.8822 | 6.7672 | 28.2598 | [6 empty] | 2018-03-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM280M-60 | 280 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 280 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.37 | 39.05 | 8.84 | 31.68 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.6012 | 31.0488 | 6.8525 | 28.4122 | [6 empty] | 2018-03-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM285M-60 | 285 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 285 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.49 | 39.25 | 8.95 | 31.85 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.6211 | 31.2154 | 6.9377 | 28.5647 | [6 empty] | 2018-03-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM290M-60 | 290 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 290 | 261.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.56 | 39.46 | 9.06 | 32.07 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.641 | 31.431 | 7.023 | 28.762 | [6 empty] | 2018-03-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM295M-60 | 295 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 295 | 266 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.72 | 39.64 | 9.14 | 32.29 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.6555 | 31.6466 | 7.085 | 28.9593 | [6 empty] | 2018-03-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM300M-60 | 300 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 300 | 270.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.84 | 39.82 | 9.23 | 32.51 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.6718 | 31.8622 | 7.1548 | 29.1566 | [6 empty] | 2018-03-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM305M-60 | 305 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 305 | 280.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.96 | 40 | 9.32 | 32.73 | 44.9 | -0.4131 | 0.0654 | -0.3339 | 0.0288 | -0.4812 | 1.837 | 32.101 | 7.383 | 30.727 | [6 empty] | 2018-03-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM310M-60 | 310 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 310 | 285 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.08 | 40.18 | 9.41 | 32.95 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.8547 | 32.3168 | 7.4543 | 30.9335 | [6 empty] | 2019-05-15 | 2019-06-17
Bluesun Solar Energy Tech. Co.,Ltd | BSM315M-60 | 315 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 289.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.04 | 40.7 | 9.49 | 33.2 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.8705 | 32.562 | 7.5177 | 31.1682 | [6 empty] | 2019-05-15 | 2019-06-17
Bluesun Solar Energy Tech. Co.,Ltd | BSM320M-60 | 320 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 320 | 294.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.15 | 40.9 | 9.59 | 33.4 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.8902 | 32.7581 | 7.5969 | 31.356 | [6 empty] | 2019-05-15 | 2019-06-17
Bluesun Solar Energy Tech. Co.,Ltd | BSM320P-72 | 320W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 320 | 292.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.05 | 46.19 | 8.66 | 36.95 | 45.1 | -0.4211 | 0.0564 | -0.3342 |  |  | 1.6992 | 36.9432 | 6.8683 | 34.2024 | [6 empty] | 2019-07-15
Bluesun Solar Energy Tech. Co.,Ltd | BSM325P-72 | 325W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 325 | 296.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.16 | 46.38 | 8.74 | 37.17 | 45.1 | -0.4211 | 0.0564 | -0.3342 |  |  | 1.7149 | 37.1631 | 6.9317 | 34.4061 | [6 empty] | 2019-07-15
Bluesun Solar Energy Tech. Co.,Ltd | BSM330P-72 | 330W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 330 | 301.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.26 | 46.57 | 8.83 | 37.39 | 45.1 | -0.4211 | 0.0564 | -0.3342 |  |  | 1.7326 | 37.3831 | 7.0031 | 34.6097 | [6 empty] | 2019-07-15
Bluesun Solar Energy Tech. Co.,Ltd | BSM335P-72 | 335W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 335 | 306.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.36 | 46.76 | 8.91 | 37.61 | 45.1 | -0.4211 | 0.0564 | -0.3342 |  |  | 1.7483 | 37.603 | 7.0666 | 34.8134 | [6 empty] | 2019-07-15
Bluesun Solar Energy Tech. Co.,Ltd | BSM340P-72 | 340W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 340 | 311 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.46 | 46.95 | 8.99 | 37.83 | 45.1 | -0.4211 | 0.0564 | -0.3342 |  |  | 1.764 | 37.823 | 7.13 | 35.017 | [6 empty] | 2019-07-15
Bluesun Solar Energy Tech. Co.,Ltd | BSM345P-72 | 345W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 345 | 315.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.56 | 47.14 | 9.07 | 38.05 | 45.1 | -0.4211 | 0.0564 | -0.3342 |  |  | 1.7797 | 38.043 | 7.1934 | 35.2206 | [6 empty] | 2019-07-15
Bluesun Solar Energy Tech. Co.,Ltd | BSM350P-72 | 350W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 350 | 320.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.66 | 47.33 | 9.15 | 38.27 | 45.1 | -0.4211 | 0.0564 | -0.3342 |  |  | 1.7954 | 38.2629 | 7.2569 | 35.4243 | [6 empty] | 2019-07-15
Bluesun Solar Energy Tech. Co.,Ltd | BSM355P-72 | 355W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 355 | 325.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.76 | 47.52 | 9.22 | 38.49 | 45.1 | -0.4211 | 0.0564 | -0.3342 |  |  | 1.8091 | 38.4829 | 7.3124 | 35.6279 | [6 empty] | 2019-07-15
Bluesun Solar Energy Tech. Co.,Ltd | BSM365M-72 | 365 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 365 | 335.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.93 | 48.01 | 9.29 | 39.29 | 44.9 | -0.4131 | 0.0654 | -0.3339 | 0.061 | -0.465 | 1.7628 | 39.4272 | 7.2466 | 36.8546 | [6 empty] | 2019-02-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM370M-72 | 370 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 370 | 340.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.03 | 48.23 | 9.37 | 39.51 | 44.9 | -0.4131 | 0.0654 | -0.3339 | 0.061 | -0.465 | 1.778 | 39.648 | 7.309 | 37.061 | [6 empty] | 2019-02-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM375M-72 | 375 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 375 | 344.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.12 | 48.45 | 9.44 | 39.73 | 44.9 | -0.4131 | 0.0654 | -0.3339 | 0.061 | -0.465 | 1.7913 | 39.8688 | 7.3636 | 37.2674 | [6 empty] | 2019-02-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM380M-72 | 380 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 380 | 349.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.22 | 48.67 | 9.52 | 39.95 | 44.9 | -0.4131 | 0.0654 | -0.3339 | 0.061 | -0.465 | 1.8065 | 40.0895 | 7.426 | 37.4737 | [6 empty] | 2019-02-15 | 2019-06-03
Bluesun Solar Energy Tech. Co.,Ltd | BSM385M-72 | 385 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 385 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.31 | 48.89 | 9.59 | 40.17 | 44.9 | -0.4131 | 0.0654 | -0.3339 | 0.061 | -0.465 | 1.8197 | 40.3103 | 7.4806 | 37.6801 | [6 empty] | 2019-02-15 | 2019-06-03
Boviet Solar Technology Co., Ltd. | BVM6610P-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 225.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.85 | 37.5 | 8.31 | 30.1 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.69 | 29.31 | 6.59 | 27.05 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19814 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610P-255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 9 | 37.4 | 8.45 | 30.2 | 45.5 | -0.4426 | 0.0726 | -0.3224 | 0.0324 | -0.4703 | 1.6822 | 29.7113 | 6.8261 | 27.3675 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.196 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-260 | 260 W Monocrystalline Module | UL 1703 | 260 | 235.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.14 | 38.1 | 8.47 | 30.7 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.6 | 30.3 | 6.71 | 27.89 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18646 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610P-260 | 260 W Polycrystalline Module | UL 1703 | 260 | 235.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 9.12 | 37.5 | 8.56 | 30.4 | 45.5 | -0.4426 | 0.0726 | -0.3224 | 0.0324 | -0.4703 | 1.7041 | 29.9081 | 6.915 | 27.5487 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.19603 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-265 | 265 W Monocrystalline Module, white backsheet | UL 1703 | 265 | 242.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 8.98 | 38.2 | 8.5 | 31.2 | 44.9 | -0.41 | 0.056 | -0.312 | 0.027 | -0.407 | 1.666 | 31.2 | 6.913 | 29.31 | [7 empty] | 2018-02-01
Boviet Solar Technology Co., Ltd. | BVM6610P-265 | 265 W, 60 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 265 | 244.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.627 | 60 | 1 | N | 9.07 | 38.1 | 8.61 | 30.8 | 43.7 | -0.3958 | 0.0708 | -0.3064 | 0.0012 | -0.3968 | 1.5769 | 30.1509 | 6.7591 | 28.9452 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.17942 |  | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-270 | 270 W Monocrystalline Module, white backsheet | UL 1703 | 270 | 247.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 9.09 | 38.4 | 8.6 | 31.4 | 44.9 | -0.41 | 0.056 | -0.312 | 0.027 | -0.407 | 1.666 | 31.4 | 6.913 | 29.31 | [7 empty] | 2018-02-01
Boviet Solar Technology Co., Ltd. | BVM6610P-270 | 270 W, 60 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 270 | 249.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.627 | 60 | 1 | N | 9.16 | 38.3 | 8.71 | 31 | 43.7 | -0.3958 | 0.0708 | -0.3064 | 0.0012 | -0.3968 | 1.5952 | 30.3466 | 6.8376 | 29.1331 |  | Flat Plate | 0.992 | 1.64 | 1 | 0.1793 |  | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-275 | 275W Monocrystalline Module, can have black backsheet or white backsheet | UL 1703 | 275 | 252.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 9.21 | 38.6 | 8.71 | 31.6 | 44.9 | -0.4064 | 0.03 | -0.44 | 0.10225 | -0.34194 | 1.665 | 31.922 | 7.125 | 29.754 | [7 empty] | 2018-02-01
Boviet Solar Technology Co., Ltd. | BVM6610P-275 | 275 W, 60 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 275 | 254.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.627 | 60 | 1 | N | 9.25 | 38.5 | 8.82 | 31.2 | 43.7 | -0.3958 | 0.0708 | -0.3064 | 0.0012 | -0.3968 | 1.6154 | 30.5424 | 6.924 | 29.3211 |  | Flat Plate | 0.992 | 1.64 | 1 | 0.17941 |  | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-280 | 280W Monocrystalline Module, can have black backsheet or white backsheet | UL 1703 | 280 | 257 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 9.33 | 38.8 | 8.81 | 31.8 | 44.9 | -0.4064 | 0.03 | -0.44 | 0.10225 | -0.34194 | 1.665 | 31.922 | 7.125 | 29.754 | [7 empty] | 2018-02-01
Boviet Solar Technology Co., Ltd. | BVM6610P-280 | 280 W, 60 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 280 | 259 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.627 | 60 | 1 | N | 9.34 | 38.7 | 8.92 | 31.4 | 43.7 | -0.3958 | 0.0708 | -0.3064 | 0.0012 | -0.3968 | 1.6337 | 30.7382 | 7.0025 | 29.509 |  | Flat Plate | 0.992 | 1.64 | 1 | 0.17934 | 2017-06-01 | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-285 | 285 W, 60 cell monocrystalline module, white or black backsheet, 1000V max system Vdc | UL 1703 | 285 | 262.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 9.56 | 38.9 | 8.94 | 31.9 | 44.8 | -0.4016 | 0.0888 | -0.2962 | 0.0277 | -0.4251 | 1.6537 | 31.4007 | 7.012 | 29.3084 | [7 empty] | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610P-285 | 285 W, 60 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 285 | 263.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.627 | 60 | 1 | N | 9.45 | 39 | 9.02 | 31.6 | 43.7 | -0.3958 | 0.0708 | -0.3064 | 0.0012 | -0.3968 | 1.652 | 30.934 | 7.081 | 29.697 |  | Flat Plate | 0.992 | 1.64 | 1 | 0.17931 | 2017-06-01 | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-290 | 290 W, 60 cell monocrystalline module, white or black backsheet, 1000V max system Vdc | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 9.65 | 39.2 | 9.07 | 32 | 44.8 | -0.4016 | 0.0888 | -0.2962 | 0.0277 | -0.4251 | 1.6778 | 31.4991 | 7.1139 | 29.4002 | [7 empty] | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610P-290 | 290 W, 60 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 290 | 268.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.627 | 60 |  | N | 9.56 | 39.2 | 9.12 | 31.8 | 43.7 | -0.3958 | 0.0708 | -0.3064 | 0.0012 | -0.3968 | 1.6703 | 31.1298 | 7.1595 | 29.885 | [6 empty] | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-295 | 295 W, 60 cell monocrystalline module, white or black backsheet, 1000V max system Vdc | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 9.73 | 39.4 | 9.2 | 32.1 | 44.8 | -0.4016 | 0.0888 | -0.2962 | 0.0277 | -0.4251 | 1.7018 | 31.5976 | 7.2159 | 29.4921 | [6 empty] | 2018-01-16 | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610P-295 | 295 W, 60 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 295 | 273.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.627 | 60 |  | N | 9.66 | 39.5 | 9.22 | 32 | 43.7 | -0.3958 | 0.0708 | -0.3064 | 0.0012 | -0.3968 | 1.6886 | 31.3256 | 7.238 | 30.0729 | [6 empty] | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-300 | 300 W, 60 cell monocrystalline module, white or black backsheet, 1000V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 9.84 | 39.5 | 9.32 | 32.2 | 44.8 | -0.4016 | 0.0888 | -0.2962 | 0.0277 | -0.4251 | 1.724 | 31.696 | 7.31 | 29.584 | [6 empty] | 2018-01-16 | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-300-H | 300 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 300 | 279.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.69 | 39.5 | 9.33 | 32.21 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.8411 | 31.994 | 7.4051 | 29.9439 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6610M-W5-300-H | 300 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 300 | 279.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 9.69 | 39.5 | 9.33 | 32.21 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.8427 | 32.0931 | 7.4116 | 30.0366 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612P-300 | 300 W Polycrystalline Module | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.79 | 45.3 | 8.12 | 36.5 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.53 | 35.71 | 6.48 | 32.96 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18212 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-305 | 305 W, 60 cell monocrystalline module, white or black backsheet, 1000V max system Vdc | UL 1703 | 305 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 9.94 | 39.9 | 9.42 | 32.4 | 44.8 | -0.4016 | 0.0888 | -0.2962 | 0.0277 | -0.4251 | 1.7425 | 31.8929 | 7.3884 | 29.7678 | [6 empty] | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-305-H | 305 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 305 | 283.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.79 | 39.9 | 9.43 | 32.4 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.8601 | 32.318 | 7.4815 | 30.2471 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6610M-W5-305-H | 305 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 305 | 283.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 9.79 | 39.9 | 9.43 | 32.4 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.8625 | 32.2824 | 7.4911 | 30.2138 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612P-305 | 305 W Polycrystalline Module | UL 1703 | 305 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 45.6 | 8.16 | 37.4 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.54 | 36.59 | 6.52 | 33.77 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18475 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-310 | 310 W, 60 cell monocrystalline module, white or black backsheet, 1000V max system Vdc | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 10.04 | 40.1 | 9.51 | 32.6 | 44.8 | -0.4016 | 0.0888 | -0.2962 | 0.0277 | -0.4251 | 1.7591 | 32.0897 | 7.459 | 29.9515 | [6 empty] | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-310-H | 310 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 310 | 288.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.89 | 40.1 | 9.52 | 32.62 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.8791 | 32.48 | 7.5579 | 30.3987 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6610M-W5-310-H | 310 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 310 | 288.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 9.89 | 40.1 | 9.52 | 32.62 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.8802 | 32.5016 | 7.5626 | 30.4189 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-310 | 310 W Monocrystalline Module | UL 1703 | 310 | 280.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9 | 46.1 | 8.33 | 37.2 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.56 | 36.59 | 6.55 | 34.06 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18413 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6612P-310 | 310 W Polycrystalline Module | UL 1703 | 310 | 280 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.08 | 45.8 | 8.22 | 37.7 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.55 | 36.89 | 6.56 | 34.04 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18445 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-315 | 315 W, 60 cell monocrystalline module, white or black backsheet, 1000V max system Vdc | UL 1703 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 |  | N | 10.12 | 40.5 | 9.58 | 32.9 | 44.8 | -0.4016 | 0.0888 | -0.2962 | 0.0277 | -0.4251 | 1.7721 | 32.385 | 7.5139 | 30.2271 | [6 empty] | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-315-H | 315 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 315 | 293.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.97 | 40.5 | 9.59 | 32.91 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.8943 | 32.804 | 7.6191 | 30.702 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6610M-315L-H | 315 W, 60 cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 315 | 294.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.12 | 40.45 | 9.59 | 32.91 | 43.1 | -0.3627 | 0.0607 | -0.2833 |  |  | 1.8672 | 32.3531 | 7.4936 | 31.579 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6610M-W5-315-H | 315 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 315 | 293.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 9.97 | 40.5 | 9.59 | 32.91 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.8941 | 32.7905 | 7.6182 | 30.6893 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-315 | 315 W Monocrystalline Module | UL 1703 | 315 | 285.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 46.1 | 8.38 | 37.6 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.57 | 36.99 | 6.59 | 34.42 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18436 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6612P-315 | 315 W Polycrystalline Module | UL 1703 | 315 | 288.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.09 | 45.3 | 8.56 | 36.8 | 45.1 | -0.4123 | 0.0682 | -0.3449 | 0.0682 | -0.4717 | 1.6774 | 35.7288 | 6.9537 | 33.2748 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19026 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6610M-320-H | 320 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 298.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10 | 41 | 9.62 | 33.33 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.9 | 33.209 | 7.642 | 31.081 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6610M-320L-H | 320 W, 60 cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 320 | 299.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.15 | 40.95 | 9.62 | 33.33 | 43.1 | -0.3627 | 0.0607 | -0.2833 |  |  | 1.873 | 32.766 | 7.517 | 31.982 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6610M-W5-320-H | 320 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 320 | 298.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 10 | 41 | 9.62 | 33.33 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.9 | 33.209 | 7.642 | 31.081 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-320 | 320 W Monocrystalline Module | UL 1703 | 320 | 289.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.08 | 46.3 | 8.46 | 37.8 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.59 | 37.18 | 6.65 | 34.61 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18474 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6612P-320 | 320 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 320 | 295.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.17 | 45.5 | 8.65 | 37 | 43.6 | -0.3986 | 0.0674 | -0.3113 | 0.0398 | -0.4326 | 1.583 | 36.6554 | 6.8056 | 34.7536 |  | Flat Plate | 0.992 | 1.956 | 1 | 0.18132 |  | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-325-H | 325 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 325 | 302.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.05 | 41.5 | 9.71 | 33.53 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.9095 | 33.614 | 7.6802 | 31.46 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6610M-325L-H | 325 W, 60 cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 325 | 304.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.2 | 41.45 | 9.71 | 33.53 | 43.1 | -0.3627 | 0.0607 | -0.2833 |  |  | 1.8905 | 32.9626 | 7.5873 | 32.1739 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6610M-W5-325-H | 325 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 325 | 303 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 10.05 | 41.5 | 9.71 | 33.53 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.9178 | 33.4083 | 7.7135 | 31.2675 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-325 | 325 W Monocrystalline Module | UL 1703 | 325 | 296.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.16 | 46 | 8.65 | 37.6 | 45.2 | -0.425 | 0.049 | -0.317 | -0.021 | -0.434 | 1.8206 | 36.9244 | 7.3527 | 34.2309 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20685 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6612P-325 | 325 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 325 | 300.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.25 | 45.7 | 8.74 | 37.2 | 43.6 | -0.3986 | 0.0674 | -0.3113 | 0.0398 | -0.4326 | 1.5994 | 36.8536 | 6.8764 | 34.9414 |  | Flat Plate | 0.992 | 1.956 | 1 | 0.18137 |  | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-330-H | 330 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 330 | 307.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.11 | 41.95 | 9.8 | 33.74 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.9209 | 33.9785 | 7.7261 | 31.8012 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6610M-330L-H | 330 W, 60 cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 330 | 309 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.26 | 41.9 | 9.8 | 33.74 | 43.1 | -0.3627 | 0.0607 | -0.2833 |  |  | 1.908 | 33.1691 | 7.6577 | 32.3754 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6610M-W5-330-H | 330 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 330 | 307.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 10.11 | 41.95 | 9.8 | 33.74 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.9356 | 33.6175 | 7.785 | 31.4633 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-330 | 330 W Monocrystalline Module | UL 1703 | 330 | 301.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.26 | 46.2 | 8.76 | 37.7 | 45.2 | -0.425 | 0.049 | -0.317 | -0.021 | -0.434 | 1.8438 | 37.0226 | 7.4462 | 34.3219 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20685 |  | 2018-07-02
Boviet Solar Technology Co., Ltd. | BVM6612P-330 | 330 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 330 | 305.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.33 | 45.8 | 8.83 | 37.4 | 43.6 | -0.3986 | 0.0674 | -0.3113 | 0.0398 | -0.4326 | 1.6159 | 37.0517 | 6.9472 | 35.1293 |  | Flat Plate | 0.992 | 1.956 | 1 | 0.18143 |  | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-335L-H | 335 W, 60 cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 335 | 313.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.32 | 42.35 | 9.89 | 33.94 | 43.1 | -0.3627 | 0.0607 | -0.2833 |  |  | 1.9256 | 33.3657 | 7.728 | 32.5673 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6610M-W5-335-H | 335 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 335 | 312.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 10.17 | 42.4 | 9.89 | 33.94 | 43.5 | -0.3798 | 0.0521 | -0.3017 |  |  | 1.9533 | 33.8168 | 7.8565 | 31.6498 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-335 | 335 W Monocrystalline Module, white backsheet | UL 1703 | 335 | 307.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.35 | 46.4 | 8.84 | 37.9 | 45.1 | -0.407 | 0.058 | -0.336 | 0.014 | -0.404 | 1.755 | 37.633 | 7.35 | 34.679 | [7 empty] | 2018-02-01
Boviet Solar Technology Co., Ltd. | BVM6612P-335 | 335 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 335 | 309.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.41 | 46.1 | 8.92 | 37.6 | 43.6 | -0.3986 | 0.0674 | -0.3113 | 0.0398 | -0.4326 | 1.6324 | 37.2499 | 7.0181 | 35.3171 |  | Flat Plate | 0.992 | 1.956 | 1 | 0.18151 | 2017-06-01 | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6612M-340 | 340W Monocrystalline Module, White Backsheet, 1500V max system Vdc | UL 1703 | 340 | 313.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.45 | 46.6 | 8.93 | 38.1 | 44.9 | -0.3924 | 0.07 | -0.3035 | 0.0242 | -0.413 | 1.6755 | 37.2653 | 7.0959 | 34.9469 | [7 empty] | 2018-10-01
Boviet Solar Technology Co., Ltd. | BVM6612P-340 | 340 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 340 | 314.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.49 | 46.5 | 9 | 37.8 | 43.6 | -0.3986 | 0.0674 | -0.3113 | 0.0398 | -0.4326 | 1.647 | 37.448 | 7.081 | 35.505 |  | Flat Plate | 0.992 | 1.956 | 1 | 0.1814 | 2017-06-01 | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6612M-345 | 345W Monocrystalline Module, White Backsheet, 1500V max system Vdc | UL 1703 | 345 | 318 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.5 | 47 | 8.99 | 38.4 | 44.9 | -0.3924 | 0.07 | -0.3035 | 0.0242 | -0.413 | 1.6867 | 37.5588 | 7.1436 | 35.2221 | [7 empty] | 2018-10-01
Boviet Solar Technology Co., Ltd. | BVM6612P-345 | 345 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 345 | 319.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.57 | 46.8 | 9.09 | 38 | 43.6 | -0.3986 | 0.0674 | -0.3113 | 0.0398 | -0.4326 | 1.6635 | 37.6461 | 7.1518 | 35.6929 |  | Flat Plate | 0.992 | 1.956 | 1 | 0.18152 | 2017-06-01 | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6612M-350 | 350W Monocrystalline Module, White Backsheet, 1500V max system Vdc | UL 1703 | 350 | 322.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.59 | 47.2 | 9.1 | 38.5 | 44.9 | -0.3924 | 0.07 | -0.3035 | 0.0242 | -0.413 | 1.7074 | 37.6566 | 7.231 | 35.3138 | [7 empty] | 2018-10-01
Boviet Solar Technology Co., Ltd. | BVM6612P-350 | 350 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 350 | 324.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.65 | 47 | 9.17 | 38.2 | 43.6 | -0.3986 | 0.0674 | -0.3113 | 0.0398 | -0.4326 | 1.6781 | 37.8443 | 7.2148 | 35.8807 | [6 empty] | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-355S-H-HC | 355 W, 120 half-cut cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 355 | 333.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 60 | 2 | N | 11.29 | 40.02 | 10.7 | 33.23 | 42.8 | -0.3406 | 0.0487 | -0.308 | 2.1097 | 32.1056 | 2.1097 | 32.1056 | 8.4516 | 31.4334 | [6 empty] | 2021-05-21
Boviet Solar Technology Co., Ltd. | BVM6610M-355S-H-HC-BF | 355 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 355 | 333.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.29 | 40.02 | 10.7 | 33.23 | 42.8 | -0.3486 | 0.0504 | -0.2979 |  |  | 2.097 | 33.0177 | 8.4829 | 31.05 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6610M-355S-H-HC-BF-DG | 355 W, 120 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 355 | 334.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.29 | 40.02 | 10.7 | 33.23 | 42.7 | -0.3335 | 0.055 | -0.2596 |  |  | 2.1263 | 33.4492 | 8.5532 | 30.9557 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6612M-355 | 355W Monocrystalline Module, White Backsheet, 1500V max system Vdc | UL 1703 | 355 | 327.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.67 | 47.4 | 9.2 | 38.6 | 44.9 | -0.3924 | 0.07 | -0.3035 | 0.0242 | -0.413 | 1.7261 | 37.7544 | 7.3105 | 35.4056 | [7 empty] | 2018-10-01
Boviet Solar Technology Co., Ltd. | BVM6612P-355 | 355 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 355 | 328.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.73 | 47.3 | 9.25 | 38.4 | 43.6 | -0.3986 | 0.0674 | -0.3113 | 0.0398 | -0.4326 | 1.6927 | 38.0424 | 7.2777 | 36.0686 | [6 empty] | 2018-09-04
Boviet Solar Technology Co., Ltd. | BVM6610M-360S-H-HC | 360 W, 120 half-cut cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 360 | 338.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 60 | 2 | N | 11.37 | 40.21 | 10.78 | 33.45 | 42.8 | -0.3406 | 0.0487 | -0.308 | 2.1255 | 32.3182 | 2.1255 | 32.3182 | 8.5148 | 31.6415 | [6 empty] | 2021-05-21
Boviet Solar Technology Co., Ltd. | BVM6610M-360S-H-HC-BF | 360 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 360 | 338.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.37 | 40.21 | 10.78 | 33.45 | 42.8 | -0.3486 | 0.0504 | -0.2979 |  |  | 2.1127 | 33.2363 | 8.5463 | 31.2556 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6610M-360S-H-HC-BF-DG | 360 W, 120 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 360 | 339.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.37 | 40.21 | 10.78 | 33.45 | 42.7 | -0.3335 | 0.055 | -0.2596 |  |  | 2.1422 | 33.6706 | 8.6171 | 31.1606 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6612M-360 | 360W Monocrystalline Module, White Backsheet, 1500V max system Vdc | UL 1703 | 360 | 332.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.83 | 47.5 | 9.29 | 38.8 | 44.9 | -0.3924 | 0.07 | -0.3035 | 0.0242 | -0.413 | 1.743 | 37.95 | 7.382 | 35.589 | [6 empty] | 2017-11-01 | 2018-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-360-H | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 334.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.68 | 47.5 | 9.29 | 38.82 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8192 | 38.7424 | 7.3064 | 36.4359 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6612M-W5-360-H | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 334.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.68 | 47.5 | 9.29 | 38.82 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8122 | 38.7788 | 7.2784 | 36.4702 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6610M-365S-H-HC | 365 W, 120 half-cut cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 365 | 343.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 60 | 2 | N | 11.46 | 40.38 | 10.87 | 33.63 | 42.8 | -0.3406 | 0.0487 | -0.308 | 2.1433 | 32.4921 | 2.1433 | 32.4921 | 8.5859 | 31.8117 | [6 empty] | 2021-05-21
Boviet Solar Technology Co., Ltd. | BVM6610M-365S-H-HC-BF | 365 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 343 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.46 | 40.38 | 10.87 | 33.63 | 42.8 | -0.3486 | 0.0504 | -0.2979 |  |  | 2.1304 | 33.4151 | 8.6176 | 31.4238 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6610M-365S-H-HC-BF-DG | 365 W, 120 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 344 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.46 | 40.38 | 10.87 | 33.63 | 42.7 | -0.3335 | 0.055 | -0.2596 |  |  | 2.1601 | 33.8518 | 8.6891 | 31.3283 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6612M-365 | 365W Monocrystalline Module, White Backsheet, 1500V max system Vdc | UL 1703 | 365 | 336.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.94 | 47.6 | 9.39 | 38.9 | 44.9 | -0.3924 | 0.07 | -0.3035 | 0.0242 | -0.413 | 1.7618 | 38.0478 | 7.4615 | 35.6807 | [6 empty] | 2017-11-01 | 2018-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-365-H | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 339.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.79 | 47.6 | 9.4 | 38.9 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8399 | 38.8239 | 7.3895 | 36.5126 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6612M-W5-365-H | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 339.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.79 | 47.6 | 9.4 | 38.9 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8337 | 38.8587 | 7.3646 | 36.5454 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6610M-370S-H-HC | 370 W, 120 half-cut cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 370 | 348.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 60 | 2 | N | 11.54 | 40.56 | 10.96 | 33.81 | 42.8 | -0.3406 | 0.0487 | -0.308 | 2.161 | 32.666 | 2.161 | 32.666 | 8.657 | 31.982 | [6 empty] | 2021-05-21
Boviet Solar Technology Co., Ltd. | BVM6610M-370S-H-HC-BF | 370 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 347.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.54 | 40.56 | 10.96 | 33.81 | 42.8 | -0.3486 | 0.0504 | -0.2979 |  |  | 2.148 | 33.594 | 8.689 | 31.592 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6610M-370S-H-HC-BF-DG | 370 W, 120 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 348.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.54 | 40.56 | 10.96 | 33.81 | 42.7 | -0.3335 | 0.055 | -0.2596 |  |  | 2.178 | 34.033 | 8.761 | 31.496 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6612M-370 | 370W Monocrystalline Module, White Backsheet, 1500V max system Vdc | UL 1703 | 370 | 341.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 10.04 | 47.7 | 9.49 | 39 | 44.9 | -0.3924 | 0.07 | -0.3035 | 0.0242 | -0.413 | 1.7805 | 38.1456 | 7.5409 | 35.7724 | [6 empty] | 2018-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-370-H | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 344.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.89 | 47.7 | 9.5 | 39.02 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8587 | 38.9055 | 7.4649 | 36.5893 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6612M-W5-370-H | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 344.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.89 | 47.7 | 9.5 | 39.02 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8532 | 38.9786 | 7.443 | 36.6581 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6610M-375S-H-HC | 375 W, 120 half-cut cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 375 | 353.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 60 | 2 | N | 11.62 | 40.75 | 11.06 | 33.96 | 42.8 | -0.3406 | 0.0487 | -0.308 | 2.1807 | 32.8109 | 2.1807 | 32.8109 | 8.736 | 32.1239 | [6 empty] | 2021-05-21
Boviet Solar Technology Co., Ltd. | BVM6610M-375S-H-HC-BF | 375 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 352.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.62 | 40.75 | 11.06 | 33.96 | 42.8 | -0.3486 | 0.0504 | -0.2979 |  |  | 2.1676 | 33.743 | 8.7683 | 31.7322 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6610M-375S-H-HC-BF-DG | 375 W, 120 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 353.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.62 | 40.75 | 11.06 | 33.96 | 42.7 | -0.3335 | 0.055 | -0.2596 |  |  | 2.1979 | 34.184 | 8.8409 | 31.6357 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6612M-375 | 375W Monocrystalline Module, White Backsheet, 1500V max system Vdc | UL 1703 | 375 | 346.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 10.11 | 48 | 9.57 | 39.2 | 44.9 | -0.3924 | 0.07 | -0.3035 | 0.0242 | -0.413 | 1.7955 | 38.3412 | 7.6045 | 35.9559 | [6 empty] | 2018-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-375-H | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 349.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.96 | 48 | 9.58 | 39.22 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8718 | 39.1502 | 7.5178 | 36.8195 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6612M-375L-H | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 349.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 1 | N | 10.11 | 47.95 | 9.58 | 39.22 | 43.3 | -0.3825 | 0.0524 | -0.2837 |  |  | 1.8502 | 39.9932 | 7.5082 | 36.8268 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-375L-H-BF | 375 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 349.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.11 | 47.95 | 9.58 | 39.22 | 43.3 | -0.3777 | 0.0507 | -0.2921 | 1.9063 |  | 1.9063 | 39.3103 | 7.5682 | 36.8228 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-375L-H-BF-DG | 375 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 350.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 1 | N | 10.11 | 47.95 | 9.58 | 39.22 | 42.7 | -0.3673 | 0.0172 | -0.2936 |  |  | 1.8126 | 39.5009 | 7.345 | 38.0865 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-375L-H-HC | 375 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 350.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.03 | 72 | 2 | N | 10.11 | 47.95 | 9.58 | 39.22 | 43.1 | -0.3662 | 0.0353 | -0.2961 |  |  | 1.7225 | 39.3525 | 7.3921 | 37.701 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-375L-H-HC-BF | 375 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 350.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.11 | 47.95 | 9.58 | 39.22 | 42.9 | -0.3645 | 0.0318 | -0.292 |  |  | 1.8212 | 39.9334 | 7.6427 | 36.1242 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-375L-H-HC-BF-DG | 375 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 350.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.11 | 47.95 | 9.58 | 39.22 | 42.8 | -0.3629 | 0.0166 | -0.2757 | 1.6992 |  | 1.6992 | 39.2936 | 7.2837 | 37.8551 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-W5-375-H | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 349.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.96 | 48 | 9.58 | 39.22 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8688 | 39.1784 | 7.5056 | 36.846 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6610M-380S-H-HC | 380 W, 120 half-cut cell monocrystalline module, black or white backsheet, 1500V max system Vdc | UL 61730 | 380 | 358 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 60 | 2 | N | 11.73 | 40.94 | 11.14 | 34.17 | 42.8 | -0.3406 | 0.0487 | -0.308 | 2.1965 | 33.0138 | 2.1965 | 33.0138 | 8.7992 | 32.3225 | [6 empty] | 2021-05-21
Boviet Solar Technology Co., Ltd. | BVM6610M-380S-H-HC-BF | 380 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 357.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.73 | 40.94 | 11.14 | 34.17 | 42.8 | -0.3486 | 0.0504 | -0.2979 |  |  | 2.1833 | 33.9517 | 8.8317 | 31.9284 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6610M-380S-H-HC-BF-DG | 380 W, 120 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 358.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 60 | 2 | N | 11.73 | 40.94 | 11.14 | 34.17 | 42.7 | -0.3335 | 0.055 | -0.2596 |  |  | 2.2138 | 34.3954 | 8.9049 | 31.8314 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM6612M-380-H | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 353.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.04 | 48.3 | 9.66 | 39.41 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8868 | 39.3949 | 7.5782 | 37.0496 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6612M-380L-H | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 353.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 1 | N | 10.19 | 48.25 | 9.66 | 39.41 | 43.3 | -0.3825 | 0.0524 | -0.2837 |  |  | 1.8656 | 40.187 | 7.5709 | 37.0052 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-380L-H-BF | 380 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 354.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.19 | 48.25 | 9.66 | 39.41 | 43.3 | -0.3777 | 0.0507 | -0.2921 | 1.9222 |  | 1.9222 | 39.5007 | 7.6314 | 37.0012 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-380L-H-BF-DG | 380 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 355.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 1 | N | 10.19 | 48.25 | 9.66 | 39.41 | 42.7 | -0.3673 | 0.0172 | -0.2936 |  |  | 1.8277 | 39.6923 | 7.4063 | 38.271 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-380L-H-HC | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 355.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.03 | 72 | 2 | N | 10.19 | 48.25 | 9.66 | 39.41 | 43.1 | -0.3662 | 0.0353 | -0.2961 |  |  | 1.7368 | 39.5431 | 7.4538 | 37.8837 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-380L-H-HC-BF | 380 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 355.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.19 | 48.25 | 9.66 | 39.41 | 42.9 | -0.3645 | 0.0318 | -0.292 |  |  | 1.8364 | 40.1268 | 7.7065 | 36.2992 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-380L-H-HC-BF-DG | 380 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 355.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.19 | 48.25 | 9.66 | 39.41 | 42.8 | -0.3629 | 0.0166 | -0.2757 | 1.7134 |  | 1.7134 | 39.4839 | 7.3445 | 38.0385 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-W5-380-H | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 353.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.04 | 48.3 | 9.66 | 39.41 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.8844 | 39.3682 | 7.5683 | 37.0245 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-385-H | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 358.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.11 | 48.5 | 9.74 | 39.6 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.9 | 39.558 | 7.631 | 37.203 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6612M-385L-H | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 358.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 1 | N | 10.26 | 48.45 | 9.74 | 39.6 | 43.3 | -0.3825 | 0.0524 | -0.2837 |  |  | 1.8811 | 40.3807 | 7.6336 | 37.1836 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-385L-H-BF | 385 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 358.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.26 | 48.45 | 9.74 | 39.6 | 43.3 | -0.3777 | 0.0507 | -0.2921 | 1.9382 |  | 1.9382 | 39.6911 | 7.6946 | 37.1796 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-385L-H-BF-DG | 385 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 360.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 1 | N | 10.26 | 48.45 | 9.74 | 39.6 | 42.7 | -0.3673 | 0.0172 | -0.2936 |  |  | 1.8429 | 39.8836 | 7.4677 | 38.4555 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-385L-H-HC | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 359.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.03 | 72 | 2 | N | 10.26 | 48.45 | 9.74 | 39.6 | 43.1 | -0.3662 | 0.0353 | -0.2961 |  |  | 1.7512 | 39.7338 | 7.5155 | 38.0663 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-385L-H-HC-BF | 385 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 360.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.26 | 48.45 | 9.74 | 39.6 | 42.9 | -0.3645 | 0.0318 | -0.292 |  |  | 1.8516 | 40.3203 | 7.7704 | 36.4742 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-385L-H-HC-BF-DG | 385 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 360.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.26 | 48.45 | 9.74 | 39.6 | 42.8 | -0.3629 | 0.0166 | -0.2757 | 1.7276 |  | 1.7276 | 39.6743 | 7.4054 | 38.2219 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-W5-385-H | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 358.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.11 | 48.5 | 9.74 | 39.6 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.9 | 39.558 | 7.631 | 37.203 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-390-H | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 363.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.18 | 48.7 | 9.82 | 39.79 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.9132 | 39.7211 | 7.6838 | 37.3564 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6612M-390L-H | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 363.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 1 | N | 10.33 | 48.65 | 9.82 | 39.79 | 43.3 | -0.3825 | 0.0524 | -0.2837 |  |  | 1.8965 | 40.5745 | 7.6963 | 37.362 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-390L-H-BF | 390 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 363.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.33 | 48.65 | 9.82 | 39.79 | 43.3 | -0.3777 | 0.0507 | -0.2921 | 1.9541 |  | 1.9541 | 39.8816 | 7.7578 | 37.358 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-390L-H-BF-DG | 390 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 365.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 1 | N | 10.33 | 48.65 | 9.82 | 39.79 | 42.7 | -0.3673 | 0.0172 | -0.2936 |  |  | 1.858 | 40.075 | 7.529 | 38.64 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-390L-H-HC | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 364.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.03 | 72 | 2 | N | 10.33 | 48.65 | 9.82 | 39.79 | 43.1 | -0.3662 | 0.0353 | -0.2961 |  |  | 1.7656 | 39.9244 | 7.5773 | 38.249 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-390L-H-HC-BF | 390 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 365 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.33 | 48.65 | 9.82 | 39.79 | 42.9 | -0.3645 | 0.0318 | -0.292 |  |  | 1.8668 | 40.5137 | 7.8342 | 36.6492 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-390L-H-HC-BF-DG | 390 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 365.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.33 | 48.65 | 9.82 | 39.79 | 42.8 | -0.3629 | 0.0166 | -0.2757 | 1.7418 |  | 1.7418 | 39.8647 | 7.4662 | 38.4053 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-W5-390-H | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 363.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.18 | 48.7 | 9.82 | 39.79 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.9156 | 39.7478 | 7.6937 | 37.3815 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-395-H | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 368.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.27 | 48.9 | 9.9 | 39.98 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.9301 | 39.8843 | 7.7518 | 37.5098 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6612M-395L-H | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 368.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 1 | N | 10.42 | 48.85 | 9.9 | 39.97 | 43.3 | -0.3825 | 0.0524 | -0.2837 |  |  | 1.912 | 40.758 | 7.759 | 37.531 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-395L-H-BF | 395 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 368.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.42 | 48.85 | 9.9 | 39.97 | 43.3 | -0.3777 | 0.0507 | -0.2921 | 1.97 |  | 1.97 | 40.062 | 7.821 | 37.527 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-395L-H-BF-DG | 395 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 370 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 1 | N | 10.42 | 48.85 | 9.9 | 39.97 | 42.7 | -0.3673 | 0.0172 | -0.2936 |  |  | 1.8731 | 40.2563 | 7.5903 | 38.8148 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-395L-H-HC | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 369.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.03 | 72 | 2 | N | 10.42 | 48.85 | 9.9 | 39.97 | 43.1 | -0.3662 | 0.0353 | -0.2961 |  |  | 1.78 | 40.105 | 7.639 | 38.422 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-395L-H-HC-BF | 395 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 369.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.42 | 48.85 | 9.9 | 39.97 | 42.9 | -0.3645 | 0.0318 | -0.292 |  |  | 1.882 | 40.697 | 7.898 | 36.815 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-395L-H-HC-BF-DG | 395 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 370.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.42 | 48.85 | 9.9 | 39.97 | 42.8 | -0.3629 | 0.0166 | -0.2757 | 1.756 |  | 1.756 | 40.045 | 7.527 | 38.579 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-W5-395-H | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 368.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.27 | 48.9 | 9.9 | 39.98 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.9312 | 39.9376 | 7.7564 | 37.56 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-400-H | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 373 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.3 | 49.2 | 9.98 | 40.16 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.9357 | 40.1289 | 7.7744 | 37.74 | [6 empty] | 2020-02-11
Boviet Solar Technology Co., Ltd. | BVM6612M-400L-H | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 373 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 1 | N | 10.45 | 49.15 | 9.98 | 40.16 | 43.3 | -0.3825 | 0.0524 | -0.2837 |  |  | 1.9275 | 40.9517 | 7.8217 | 37.7094 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-400L-H-BF | 400 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 373.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.45 | 49.15 | 9.98 | 40.16 | 43.3 | -0.3777 | 0.0507 | -0.2921 | 1.9859 |  | 1.9859 | 40.2524 | 7.8842 | 37.7054 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-400L-H-BF-DG | 400 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 374.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 1 | N | 10.45 | 49.15 | 9.98 | 40.16 | 42.7 | -0.3673 | 0.0172 | -0.2936 |  |  | 1.8883 | 40.4477 | 7.6517 | 38.9993 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-400L-H-HC | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 374.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.03 | 72 | 2 | N | 10.45 | 49.15 | 9.98 | 40.16 | 43.1 | -0.3662 | 0.0353 | -0.2961 |  |  | 1.7944 | 40.2956 | 7.7007 | 38.6046 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-400L-H-HC-BF | 400 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 374.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.45 | 49.15 | 9.98 | 40.16 | 42.9 | -0.3645 | 0.0318 | -0.292 |  |  | 1.8972 | 40.8905 | 7.9618 | 36.99 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-400L-H-HC-BF-DG | 400 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 374.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.45 | 49.15 | 9.98 | 40.16 | 42.8 | -0.3629 | 0.0166 | -0.2757 | 1.7702 |  | 1.7702 | 40.2354 | 7.5878 | 38.7624 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-W5-400-H | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 373 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.3 | 49.2 | 9.98 | 40.16 | 43.5 | -0.3824 | 0.0389 | -0.3003 |  |  | 1.9468 | 40.1174 | 7.819 | 37.7291 | [6 empty] | 2019-12-02
Boviet Solar Technology Co., Ltd. | BVM6612M-405L-H | 405 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 377.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 1 | N | 10.49 | 49.45 | 10.06 | 40.33 | 43.3 | -0.3825 | 0.0524 | -0.2837 |  |  | 1.9429 | 41.1251 | 7.8844 | 37.869 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-405L-H-BF | 405 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 378.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.49 | 49.45 | 10.06 | 40.33 | 43.3 | -0.3777 | 0.0507 | -0.2921 | 2.0018 |  | 2.0018 | 40.4228 | 7.9474 | 37.865 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-405L-H-BF-DG | 405 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 379.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 1 | N | 10.49 | 49.45 | 10.06 | 40.33 | 42.7 | -0.3673 | 0.0172 | -0.2936 |  |  | 1.9034 | 40.6189 | 7.713 | 39.1644 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-405L-H-HC | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 379.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.03 | 72 | 2 | N | 10.49 | 49.45 | 10.06 | 40.33 | 43.1 | -0.3662 | 0.0353 | -0.2961 |  |  | 1.8088 | 40.4662 | 7.7625 | 38.7681 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-405L-H-HC-BF | 405 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 379.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.49 | 49.45 | 10.06 | 40.33 | 42.9 | -0.3645 | 0.0318 | -0.292 |  |  | 1.9124 | 41.0635 | 8.0256 | 37.1466 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-405L-H-HC-BF-DG | 405 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 379.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.49 | 49.45 | 10.06 | 40.33 | 42.8 | -0.3629 | 0.0166 | -0.2757 | 1.7844 |  | 1.7844 | 40.4057 | 7.6486 | 38.9265 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-410L-H | 410 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 410 | 382.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 1 | N | 10.51 | 49.75 | 10.14 | 40.5 | 43.3 | -0.3825 | 0.0524 | -0.2837 |  |  | 1.9584 | 41.2984 | 7.9471 | 38.0287 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-410L-H-BF | 410 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 382.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.51 | 49.75 | 10.14 | 40.5 | 43.3 | -0.3777 | 0.0507 | -0.2921 | 2.0178 |  | 2.0178 | 40.5932 | 8.0106 | 38.0246 | [6 empty] | 2020-05-21
Boviet Solar Technology Co., Ltd. | BVM6612M-410L-H-BF-DG | 410 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 384.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 1 | N | 10.51 | 49.75 | 10.14 | 40.5 | 42.7 | -0.3673 | 0.0172 | -0.2936 |  |  | 1.9185 | 40.7901 | 7.7743 | 39.3295 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-410L-H-HC | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 410 | 383.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.03 | 72 | 2 | N | 10.51 | 49.75 | 10.14 | 40.5 | 43.1 | -0.3662 | 0.0353 | -0.2961 |  |  | 1.8232 | 40.6368 | 7.8242 | 38.9315 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-410L-H-HC-BF | 410 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 384.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.51 | 49.75 | 10.14 | 40.5 | 42.9 | -0.3645 | 0.0318 | -0.292 |  |  | 1.9276 | 41.2366 | 8.0895 | 37.3032 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-410L-H-HC-BF-DG | 410 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 384.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 72 | 2 | N | 10.51 | 49.75 | 10.14 | 40.5 | 42.8 | -0.3629 | 0.0166 | -0.2757 | 1.7986 |  | 1.7986 | 40.576 | 7.7095 | 39.0906 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-425S-H-HC | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 397.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.28 | 48.1 | 10.71 | 39.76 | 42.9 | -0.3642 | 0.0256 | -0.2911 |  |  | 2.1114 | 39.1533 | 8.6055 | 36.7293 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-425S-H-HC-BF | 425 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 397.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.28 | 48.1 | 10.71 | 39.76 | 42.8 | -0.3656 | 0.0221 | -0.3027 |  |  | 2.0887 | 39.1602 | 8.2867 | 37.9833 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-425S-H-HC-BF-DG | 425 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 398.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.28 | 48.1 | 10.71 | 39.76 | 42.8 | -0.3625 | 0.0252 | -0.3066 |  |  | 2.1015 | 39.0572 | 8.4308 | 37.7151 | [6 empty] | 2020-09-21
Boviet Solar Technology Co., Ltd. | BVM6612M-430S-H-HC | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 402.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.34 | 48.25 | 10.78 | 39.96 | 42.9 | -0.3642 | 0.0256 | -0.2911 |  |  | 2.1252 | 39.3502 | 8.6618 | 36.914 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-430S-H-HC-BF | 430 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 402.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.34 | 48.25 | 10.78 | 39.96 | 42.8 | -0.3656 | 0.0221 | -0.3027 |  |  | 2.1023 | 39.3572 | 8.3408 | 38.1744 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-430S-H-HC-BF-DG | 430 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 402.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.34 | 48.25 | 10.78 | 39.96 | 42.8 | -0.3625 | 0.0252 | -0.3066 |  |  | 2.1153 | 39.2537 | 8.4859 | 37.9048 | [6 empty] | 2020-09-21
Boviet Solar Technology Co., Ltd. | BVM6612M-435S-H-HC | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 407.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.42 | 48.45 | 10.85 | 40.17 | 42.9 | -0.3642 | 0.0256 | -0.2911 |  |  | 2.139 | 39.557 | 8.718 | 37.108 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-435S-H-HC-BF | 435 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 407.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.42 | 48.45 | 10.85 | 40.17 | 42.8 | -0.3656 | 0.0221 | -0.3027 |  |  | 2.116 | 39.564 | 8.395 | 38.375 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-435S-H-HC-BF-DG | 435 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 407.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.42 | 48.45 | 10.85 | 40.17 | 42.8 | -0.3625 | 0.0252 | -0.3066 |  |  | 2.129 | 39.46 | 8.541 | 38.104 | [6 empty] | 2020-09-21
Boviet Solar Technology Co., Ltd. | BVM6612M-440S-H-HC | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 412.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.48 | 48.6 | 10.92 | 40.37 | 42.9 | -0.3642 | 0.0256 | -0.2911 |  |  | 2.1528 | 39.7539 | 8.7742 | 37.2928 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-440S-H-HC-BF | 440 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 412.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.48 | 48.6 | 10.92 | 40.37 | 42.8 | -0.3656 | 0.0221 | -0.3027 |  |  | 2.1297 | 39.761 | 8.4492 | 38.5661 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-440S-H-HC-BF-DG | 440 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 412.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.48 | 48.6 | 10.92 | 40.37 | 42.8 | -0.3625 | 0.0252 | -0.3066 |  |  | 2.1427 | 39.6565 | 8.5961 | 38.2937 | [6 empty] | 2020-09-21
Boviet Solar Technology Co., Ltd. | BVM6612M-445S-H-HC | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 417.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.55 | 48.8 | 10.99 | 40.57 | 42.9 | -0.3642 | 0.0256 | -0.2911 |  |  | 2.1666 | 39.9509 | 8.8305 | 37.4775 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-445S-H-HC-BF | 445 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 417 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.55 | 48.8 | 10.99 | 40.57 | 42.8 | -0.3656 | 0.0221 | -0.3027 |  |  | 2.1433 | 39.958 | 8.5033 | 38.7571 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-445S-H-HC-BF-DG | 445 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 417.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.55 | 48.8 | 10.99 | 40.57 | 42.8 | -0.3625 | 0.0252 | -0.3066 |  |  | 2.1565 | 39.8529 | 8.6512 | 38.4834 | [6 empty] | 2020-09-21
Boviet Solar Technology Co., Ltd. | BVM6612M-450S-H-HC | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 421.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.6 | 49.05 | 11.06 | 40.76 | 42.9 | -0.3642 | 0.0256 | -0.2911 |  |  | 2.1804 | 40.138 | 8.8867 | 37.653 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-450S-H-HC-BF | 450 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 421.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.6 | 49.05 | 11.06 | 40.76 | 42.8 | -0.3656 | 0.0221 | -0.3027 |  |  | 2.157 | 40.1451 | 8.5575 | 38.9386 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-450S-H-HC-BF-DG | 450 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 422.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.6 | 49.05 | 11.06 | 40.76 | 42.8 | -0.3625 | 0.0252 | -0.3066 |  |  | 2.1702 | 40.0396 | 8.7063 | 38.6637 | [6 empty] | 2020-09-21
Boviet Solar Technology Co., Ltd. | BVM6612M-455S-H-HC | 455 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 426.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.71 | 49.25 | 11.15 | 40.88 | 42.9 | -0.3642 | 0.0256 | -0.2911 |  |  | 2.1981 | 40.2562 | 8.9591 | 37.7639 | [6 empty] | 2020-10-12
Boviet Solar Technology Co., Ltd. | BVM6612M-455S-H-HC-BF | 455 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 426.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.71 | 49.25 | 11.15 | 40.88 | 42.8 | -0.3656 | 0.0221 | -0.3027 |  |  | 2.1745 | 40.2633 | 8.6271 | 39.0533 | [6 empty] | 2020-10-01
Boviet Solar Technology Co., Ltd. | BVM6612M-455S-H-HC-BF-DG | 455 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 426.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.23 | 72 | 2 | N | 11.71 | 49.25 | 11.15 | 40.88 | 42.8 | -0.3625 | 0.0252 | -0.3066 |  |  | 2.1879 | 40.1575 | 8.7772 | 38.7775 | [6 empty] | 2020-09-21
Boviet Solar Technology Co., Ltd. | BVM7612M-520-H-HC | 520 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 520 | 487.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.595 | 72 | 2 | N | 13.32 | 49.39 | 12.55 | 41.51 | 43.9 | -0.34 | 0.0236 | -0.2952 |  |  | 2.5554 | 38.8355 | 10.2572 | 38.5461 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-520-H-HC-BF | 520 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 520 | 488.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.32 | 49.39 | 12.55 | 41.51 | 43 | -0.3455 | 0.0324 | -0.2396 |  |  | 2.5228 | 38.9349 | 10.2878 | 38.5343 | [6 empty] | 2021-06-01
Boviet Solar Technology Co., Ltd. | BVM7612M-520-H-HC-BF-DG | 520 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 520 | 488.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.32 | 49.39 | 12.55 | 41.51 | 43.5 | -0.3368 | 0.0301 | -0.2685 |  |  | 2.6463 | 38.7883 | 10.4745 | 38.5944 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-525-H-HC | 525 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 525 | 492.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.595 | 72 | 2 | N | 13.37 | 49.52 | 12.6 | 41.74 | 43.9 | -0.34 | 0.0236 | -0.2952 |  |  | 2.5656 | 39.0507 | 10.2981 | 38.7597 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-525-H-HC-BF | 525 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 525 | 493.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.37 | 49.52 | 12.6 | 41.74 | 43 | -0.3455 | 0.0324 | -0.2396 |  |  | 2.5329 | 39.1507 | 10.3288 | 38.7478 | [6 empty] | 2021-06-01
Boviet Solar Technology Co., Ltd. | BVM7612M-525-H-HC-BF-DG | 525 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 525 | 493.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.37 | 49.52 | 12.6 | 41.74 | 43.5 | -0.3368 | 0.0301 | -0.2685 |  |  | 2.6568 | 39.0032 | 10.5162 | 38.8082 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-530-H-HC | 530 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 530 | 497.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.595 | 72 | 2 | N | 13.43 | 49.71 | 12.66 | 41.94 | 43.9 | -0.34 | 0.0236 | -0.2952 |  |  | 2.5778 | 39.2378 | 10.3471 | 38.9454 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-530-H-HC-BF | 530 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 530 | 498.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.43 | 49.71 | 12.66 | 41.94 | 43 | -0.3455 | 0.0324 | -0.2396 |  |  | 2.5449 | 39.3383 | 10.378 | 38.9335 | [6 empty] | 2021-06-01
Boviet Solar Technology Co., Ltd. | BVM7612M-530-H-HC-BF-DG | 530 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 530 | 498.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.43 | 49.71 | 12.66 | 41.94 | 43.5 | -0.3368 | 0.0301 | -0.2685 |  |  | 2.6695 | 39.1901 | 10.5663 | 38.9942 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-535-H-HC | 535 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 535 | 502.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.595 | 72 | 2 | N | 13.48 | 49.8 | 12.71 | 42.17 | 43.9 | -0.34 | 0.0236 | -0.2952 |  |  | 2.588 | 39.453 | 10.388 | 39.159 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-535-H-HC-BF | 535 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 503.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.48 | 49.8 | 12.71 | 42.17 | 43 | -0.3455 | 0.0324 | -0.2396 |  |  | 2.555 | 39.554 | 10.419 | 39.147 | [6 empty] | 2021-06-01
Boviet Solar Technology Co., Ltd. | BVM7612M-535-H-HC-BF-DG | 535 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 503.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.48 | 49.8 | 12.71 | 42.17 | 43.5 | -0.3368 | 0.0301 | -0.2685 |  |  | 2.68 | 39.405 | 10.608 | 39.208 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-540-H-HC | 540 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 540 | 507 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.595 | 72 | 2 | N | 13.55 | 49.89 | 12.76 | 42.4 | 43.9 | -0.34 | 0.0236 | -0.2952 |  |  | 2.5982 | 39.6682 | 10.4289 | 39.3726 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-540-H-HC-BF | 540 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 508.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.55 | 49.89 | 12.76 | 42.4 | 43 | -0.3455 | 0.0324 | -0.2396 |  |  | 2.5651 | 39.7697 | 10.46 | 39.3605 | [6 empty] | 2021-06-01
Boviet Solar Technology Co., Ltd. | BVM7612M-540-H-HC-BF-DG | 540 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 508 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.55 | 49.89 | 12.76 | 42.4 | 43.5 | -0.3368 | 0.0301 | -0.2685 |  |  | 2.6905 | 39.6199 | 10.6497 | 39.4218 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-545-H-HC | 545 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 545 | 511.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.595 | 72 | 2 | N | 13.72 | 49.98 | 12.82 | 42.58 | 43.9 | -0.34 | 0.0236 | -0.2952 |  |  | 2.6104 | 39.8366 | 10.4779 | 39.5397 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-545-H-HC-BF | 545 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 545 | 512.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.72 | 49.98 | 12.82 | 42.58 | 43 | -0.3455 | 0.0324 | -0.2396 |  |  | 2.5771 | 39.9386 | 10.5092 | 39.5276 | [6 empty] | 2021-06-01
Boviet Solar Technology Co., Ltd. | BVM7612M-545-H-HC-BF-DG | 545 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 545 | 512.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.72 | 49.98 | 12.82 | 42.58 | 43.5 | -0.3368 | 0.0301 | -0.2685 |  |  | 2.7032 | 39.7881 | 10.6998 | 39.5892 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-550-H-HC | 550 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 550 | 516.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.595 | 72 | 2 | N | 13.84 | 50.13 | 12.88 | 42.76 | 43.9 | -0.34 | 0.0236 | -0.2952 |  |  | 2.6226 | 40.005 | 10.5269 | 39.7069 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-550-H-HC-BF | 550 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 550 | 517.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.84 | 50.13 | 12.88 | 42.76 | 43 | -0.3455 | 0.0324 | -0.2396 |  |  | 2.5892 | 40.1074 | 10.5584 | 39.6947 | [6 empty] | 2021-06-01
Boviet Solar Technology Co., Ltd. | BVM7612M-550-H-HC-BF-DG | 550 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 550 | 517.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 13.84 | 50.13 | 12.88 | 42.76 | 43.5 | -0.3368 | 0.0301 | -0.2685 |  |  | 2.7158 | 39.9563 | 10.7499 | 39.7566 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-555-H-HC | 555 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 555 | 521.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.595 | 72 | 2 | N | 14.08 | 50.2 | 12.95 | 42.93 | 43.9 | -0.34 | 0.0236 | -0.2952 |  |  | 2.6369 | 40.164 | 10.5842 | 39.8647 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-555-H-HC-BF | 555 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 555 | 522.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 14.08 | 50.2 | 12.95 | 42.93 | 43 | -0.3455 | 0.0324 | -0.2396 |  |  | 2.6032 | 40.2669 | 10.6157 | 39.8525 | [6 empty] | 2021-06-01
Boviet Solar Technology Co., Ltd. | BVM7612M-555-H-HC-BF-DG | 555 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 555 | 522.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 14.08 | 50.2 | 12.95 | 42.93 | 43.5 | -0.3368 | 0.0301 | -0.2685 |  |  | 2.7306 | 40.1152 | 10.8083 | 39.9146 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-560-H-HC | 560 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 560 | 526.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.595 | 72 | 2 | N | 14.2 | 50.24 | 13.04 | 43.01 | 43.9 | -0.34 | 0.0236 | -0.2952 |  |  | 2.6552 | 40.2389 | 10.6577 | 39.939 | [6 empty] | 2021-07-01
Boviet Solar Technology Co., Ltd. | BVM7612M-560-H-HC-BF | 560 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 560 | 527.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 14.2 | 50.24 | 13.04 | 43.01 | 43 | -0.3455 | 0.0324 | -0.2396 |  |  | 2.6213 | 40.3419 | 10.6895 | 39.9268 | [6 empty] | 2021-06-01
Boviet Solar Technology Co., Ltd. | BVM7612M-560-H-HC-BF-DG | 560 W, 144 half-cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 560 | 527.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.6 | 72 | 2 | N | 14.2 | 50.24 | 13.04 | 43.01 | 43.5 | -0.3368 | 0.0301 | -0.2685 |  |  | 2.7496 | 40.1899 | 10.8834 | 39.989 | [6 empty] | 2021-07-01
BYD Company Limited | BYD 225P6C-30 | 225 W Polycrystalline Module | UL 1703 | 225 | 202.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.41 | 36.21 | 7.85 | 28.66 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.508 | 27.7111 | 6.229 | 25.8708 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18573 |  | 2018-01-16
BYD Company Limited | BYD 230P6C-30 | 230 W Polycrystalline Module | UL 1703 | 230 | 207.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.49 | 36.52 | 7.94 | 28.97 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.5253 | 28.0109 | 6.3004 | 26.1506 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18576 |  | 2018-01-16
BYD Company Limited | BYD 235P6C-30 | 235 W Polycrystalline Module | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.57 | 36.83 | 8.03 | 29.27 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.5426 | 28.3009 | 6.3718 | 26.4214 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18577 |  | 2018-01-16
BYD Company Limited | BYD 240P6C-30 | 240 W Polycrystalline Module | UL 1703 | 240 | 216.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.65 | 37.14 | 8.12 | 29.57 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.5599 | 28.591 | 6.4432 | 26.6922 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18583 |  | 2018-01-16
BYD Company Limited | BYD 245P6C-30 | 245 W Polycrystalline Module | UL 1703 | 245 | 221.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.73 | 37.45 | 8.21 | 29.85 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.5772 | 28.8617 | 6.5147 | 26.945 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18579 |  | 2018-01-16
BYD Company Limited | BYD245P6K-30 | 245 W Polycrystalline Module | UL 1703 | 245 | 224.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.73 | 37.45 | 8.21 | 29.85 | 45.1 | -0.3983 | 0.0386 | -0.3115 | -0.4114 | -0.0169 | 1.76 | 30.076 | 7.042 | 28.742 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 250P6C-30 | 250 W Polycrystalline Module | UL 1703 | 250 | 225.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.81 | 37.76 | 8.3 | 30.13 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.635 | 29.1743 | 6.6095 | 27.5203 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1908 |  | 2018-01-16
BYD Company Limited | BYD250P6K-30 | 250 W Polycrystalline Module | UL 1703 | 250 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.81 | 37.76 | 8.3 | 30.13 | 45.1 | -0.3983 | 0.0386 | -0.3115 | -0.4114 | -0.0169 | 1.76 | 30.076 | 7.042 | 28.742 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 255P6C-30 | 255 W Polycrystalline Module | UL 1703 | 255 | 230.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.89 | 38.07 | 8.39 | 30.4 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.6527 | 29.4358 | 6.6812 | 27.7669 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19078 |  | 2018-01-16
BYD Company Limited | BYD255P6K-30 | 255 W Polycrystalline Module | UL 1703 | 255 | 233.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.89 | 38.07 | 8.39 | 30.4 | 45.1 | -0.3983 | 0.0386 | -0.3115 | -0.4114 | -0.0169 | 1.76 | 30.076 | 7.042 | 28.742 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 260P6C-30 | 260 W Polycrystalline Module | UL 1703 | 260 | 235.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.97 | 38.38 | 8.48 | 30.67 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.6704 | 29.6972 | 6.7529 | 28.0136 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1908 |  | 2018-01-16
BYD Company Limited | BYD 260P6C-36 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.24 | 42.81 | 7.62 | 34.12 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.4962 | 33.09 | 6.1053 | 30.8922 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19042 |  | 2018-01-16
BYD Company Limited | BYD260P6K-30 | 260 W Polycrystalline Module | UL 1703 | 260 | 238.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.97 | 38.38 | 8.48 | 30.67 | 45.1 | -0.3983 | 0.0386 | -0.3115 | -0.4114 | -0.0169 | 1.76 | 30.076 | 7.042 | 28.742 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 265P6C-30 | 265 W Polycrystalline Module | UL 1703 | 265 | 239.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.05 | 38.69 | 8.57 | 30.93 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.6882 | 29.949 | 6.8245 | 28.251 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19079 |  | 2018-01-16
BYD Company Limited | BYD 265P6C-36 | 265 W Polycrystalline Module | UL 1703 | 265 | 240.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.31 | 43.11 | 7.71 | 34.37 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.5138 | 33.3325 | 6.1774 | 31.1185 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19042 |  | 2018-01-16
BYD Company Limited | BYD265P6K-30 | 265 W Polycrystalline Module | UL 1703 | 265 | 243.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.05 | 38.69 | 8.57 | 30.92 | 45.1 | -0.3983 | 0.0386 | -0.3115 | -0.4114 | -0.0169 | 1.76 | 30.076 | 7.042 | 28.742 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 270P6C-36 | 270 W Polycrystalline Module | UL 1703 | 270 | 245.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.38 | 43.41 | 7.8 | 34.62 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.5315 | 33.5749 | 6.2496 | 31.3449 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19045 |  | 2018-01-16
BYD Company Limited | BYD270P6K-30 | 270 W Polycrystalline Module | UL 1703 | 270 | 247.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.13 | 39 | 8.66 | 31.18 | 45.1 | -0.3983 | 0.0386 | -0.3115 | -0.4114 | -0.0169 | 1.76 | 30.076 | 7.042 | 28.742 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 275P6C-36 | 275 W Polycrystalline Module | UL 1703 | 275 | 250.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.45 | 43.7 | 7.89 | 34.85 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.5492 | 33.798 | 6.3217 | 31.5531 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1904 |  | 2018-01-16
BYD Company Limited | BYD275P6K-30 | 275 W Polycrystalline Module | UL 1703 | 275 | 252.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.21 | 39.31 | 8.75 | 31.43 | 45.1 | -0.3983 | 0.0386 | -0.3115 | -0.4114 | -0.0169 | 1.76 | 30.076 | 7.042 | 28.742 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 280P6C-36 | 280 W Polycrystalline Module | UL 1703 | 280 | 254.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.52 | 44 | 7.98 | 35.09 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.5669 | 34.0308 | 6.3938 | 31.7704 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19043 |  | 2018-01-16
BYD Company Limited | BYD280P6K-30 | 280 W Polycrystalline Module | UL 1703 | 280 | 257.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.29 | 39.62 | 8.84 | 31.68 | 45.1 | -0.3983 | 0.0386 | -0.3115 | -0.4114 | -0.0169 | 1.76 | 30.076 | 7.042 | 28.742 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 285P6C-36 | 285 W Polycrystalline Module | UL 1703 | 285 | 259.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.6 | 44.3 | 8.07 | 35.4 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.588 | 34.4225 | 6.4419 | 32.0849 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1918 |  | 2018-01-16
BYD Company Limited | BYD 290P6C-36 | 290 W Polycrystalline Module | UL 1703 | 290 | 264.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.67 | 44.6 | 8.16 | 35.65 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.6057 | 34.6656 | 6.5138 | 32.3115 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19195 |  | 2018-01-16
BYD Company Limited | BYD 295P6C-36 | 295 W Polycrystalline Module | UL 1703 | 295 | 268.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.75 | 44.9 | 8.25 | 35.76 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.6235 | 34.7726 | 6.5856 | 32.4112 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19136 |  | 2018-01-16
BYD Company Limited | BYD295P6K-36 | 295 W Polycrystalline Module | UL 1703 | 295 | 270 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 8.75 | 44.9 | 8.25 | 35.76 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [7 empty] | 2018-02-01
BYD Company Limited | BYD 300P6C-36 | 300 W Polycrystalline Module | UL 1703 | 300 | 273.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.83 | 45.19 | 8.34 | 35.97 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.6412 | 34.9768 | 6.6575 | 32.6016 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19134 |  | 2018-01-16
BYD Company Limited | BYD300P6K-36 | 300 W Polycrystalline Module | UL 1703 | 300 | 274.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 8.83 | 45.19 | 8.34 | 35.97 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 305P6C-36 | 305 W Polycrystalline Module | UL 1703 | 305 | 278.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.91 | 45.49 | 8.43 | 36.18 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.6589 | 35.181 | 6.7293 | 32.7919 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19135 |  | 2018-01-16
BYD Company Limited | BYD305P6K-36 | 305 W Polycrystalline Module | UL 1703 | 305 | 279.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 8.91 | 45.49 | 8.43 | 36.18 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 310P6C-36 | 310 W Polycrystalline Module | UL 1703 | 310 | 282.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.99 | 45.79 | 8.52 | 36.38 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.6766 | 35.1755 | 6.8012 | 32.9732 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19024 |  | 2018-01-16
BYD Company Limited | BYD310P6K-36 | 310 W Polycrystalline Module | UL 1703 | 310 | 284.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 8.99 | 45.79 | 8.52 | 36.38 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD 315P6C-36 | 315 W Polycrystalline Module | UL 1703 | 315 | 287.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.07 | 46.09 | 8.61 | 36.59 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.6943 | 35.5797 | 6.873 | 33.1635 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19137 |  | 2018-01-16
BYD Company Limited | BYD315P6K-36 | 315 W Polycrystalline Module | UL 1703 | 315 | 288.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.07 | 46.09 | 8.61 | 36.58 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD320P6K-36 | 320 W Polycrystalline Module | UL 1703 | 320 | 293.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.15 | 46.39 | 8.7 | 36.78 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD325P6K-36 | 325 W Polycrystalline Module | UL 1703 | 325 | 298.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.23 | 46.69 | 8.79 | 36.98 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD330P6K-36 | 330 W Polycrystalline Module | UL 1703 | 330 | 302.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.31 | 46.98 | 8.88 | 37.16 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD335P6K-36 | 335 W Polycrystalline Module | UL 1703 | 335 | 307.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.39 | 47.28 | 8.97 | 37.35 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD340P6K-36 | 340 W Polycrystalline Module | UL 1703 | 340 | 312.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.47 | 47.58 | 9.06 | 37.53 | 46.1 | -0.3827 | 0.0401 | -0.3015 | -0.3907 | -0.0114 | 1.727 | 36.501 | 6.981 | 34.477 | [6 empty] | 2018-01-16 | 2018-02-01
BYD Company Limited | BYD420MIK-36 | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 366 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 24 | 6 | N | 10.57 | 50.34 | 10.07 | 41.78 | 44.1 | -0.3309 | 0.0446 | -0.2641 |  |  | 2.0708 | 40.237 | 8.1858 | 39.3209 | [6 empty] | 2020-12-11
BYD Company Limited | BYD415MIK-36 | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 370.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 24 | 6 | N | 10.5 | 50.06 | 10 | 41.55 | 44.1 | -0.3309 | 0.0446 | -0.2641 |  |  | 2.0564 | 40.0155 | 8.1289 | 39.1045 | [6 empty] | 2020-12-11
BYD Company Limited | BYD410MIK-36 | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 375.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 24 | 6 | N | 10.43 | 49.78 | 9.93 | 41.32 | 44.1 | -0.3309 | 0.0446 | -0.2641 |  |  | 2.042 | 39.794 | 8.072 | 38.888 | [6 empty] | 2020-12-11
BYD Company Limited | BYD405MIK-36 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 380.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 24 | 6 | N | 10.36 | 49.49 | 9.86 | 41.1 | 44.1 | -0.3309 | 0.0446 | -0.2641 |  |  | 2.0276 | 39.5821 | 8.0151 | 38.6809 | [6 empty] | 2020-12-11
BYD Company Limited | BYD400MIK-36 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 410 | 385.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 24 | 6 | N | 10.29 | 49.21 | 9.79 | 40.87 | 44.1 | -0.3309 | 0.0446 | -0.2641 |  |  | 2.0132 | 39.3606 | 7.9582 | 38.4645 | [6 empty] | 2020-12-11
BYD Company Limited | BYD395MIK-36 | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 415 | 390 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 24 | 6 | N | 10.22 | 48.92 | 9.72 | 40.65 | 44.1 | -0.3309 | 0.0446 | -0.2641 |  |  | 1.9988 | 39.1487 | 7.9013 | 38.2574 | [6 empty] | 2020-12-11
BYD Company Limited | BYD390MIK-36 | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 394.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 24 | 6 | N | 10.15 | 48.64 | 9.65 | 40.42 | 44.1 | -0.3309 | 0.0446 | -0.2641 |  |  | 1.9844 | 38.9272 | 7.8444 | 38.041 | [6 empty] | 2020-12-11
Caterpillar Inc. | PVT105 | 105 W Thin Film CdTe Module | UL 1703 | 105 | 97.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.74 | 86 | 1.55 | 67.8 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.3 | 68.28 | 1.13 | 59.13 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19509
Caterpillar Inc. | PVT105 ARC | 105 W Thin Film CdTe Module | UL 1703 | 105 | 97.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.74 | 86 | 1.55 | 67.8 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.3 | 68.28 | 1.13 | 59.13 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19509
Caterpillar Inc. | PVT107 | 107.5 W Thin Film CdTe Module | UL 1703 | 107.5 | 99.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 86.6 | 1.57 | 68.6 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 69.09 | 1.15 | 59.83 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19924
Caterpillar Inc. | PVT107 ARC | 107.5 W Thin Film CdTe Module | UL 1703 | 107.5 | 99.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 86.6 | 1.57 | 68.6 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 69.09 | 1.15 | 59.83 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19924
Caterpillar Inc. | PVT110 | 110 W Thin Film CdTe Module | UL 1703 | 110 | 102.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 87.2 | 1.59 | 69.4 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 69.89 | 1.16 | 60.53 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19696
Caterpillar Inc. | PVT110 ARC | 110 W Thin Film CdTe Module | UL 1703 | 110 | 102.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 87.2 | 1.59 | 69.4 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 69.89 | 1.16 | 60.53 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19696
Caterpillar Inc. | PVT112 | 112.5 W Thin Film CdTe Module | UL 1703 | 112.5 | 104.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 87.7 | 1.6 | 70.2 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 70.7 | 1.17 | 61.23 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19482
Caterpillar Inc. | PVT112 ARC | 112.5 W Thin Film CdTe Module | UL 1703 | 112.5 | 104.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 87.7 | 1.6 | 70.2 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 70.7 | 1.17 | 61.23 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19482
Caterpillar Inc. | PVT115 | 115 W Thin Film CdTe Module | UL 1703 | 115 | 105.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.78 | 87.8 | 1.63 | 70.5 | 46.3 | -0.3878 | 0.0454 | -0.3548 | 0.0168 | -0.4244 | 0.1 | 71.04 | 1.26 | 65.8 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.061774
Caterpillar Inc. | PVT115 ARC | 115 W Thin Film CdTe Module | UL 1703 | 115 | 105.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.78 | 87.8 | 1.63 | 70.5 | 46.3 | -0.3878 | 0.0454 | -0.3548 | 0.0168 | -0.4244 | 0.1 | 71.04 | 1.26 | 65.8 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.061774
Caterpillar Inc. | PVT117 | 117.5 W Thin Film CdTe Module | UL 1703 | 117.5 | 107.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.79 | 88.2 | 1.65 | 71.2 | 46.3 | -0.3878 | 0.0454 | -0.3548 | 0.0168 | -0.4244 | 0.11 | 71.74 | 1.28 | 66.45 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.067161
Caterpillar Inc. | PVT117 ARC | 117.5 W Thin Film CdTe Module | UL 1703 | 117.5 | 107.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.79 | 88.2 | 1.65 | 71.2 | 46.3 | -0.3878 | 0.0454 | -0.3548 | 0.0168 | -0.4244 | 0.11 | 71.74 | 1.28 | 66.45 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.067161
Caterpillar Inc. | PVC345MP03HA | 345 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 345 | 322 |  | 2020-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.06 | 40.2 | 10.09 | 34.2 | 45.2 | -0.339 | 0.04 | -0.266 |  |  | 1.99 | 32.54 | 8.06 | 31.5 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC350MP03HA | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 350 | 326.8 |  | 2020-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.16 | 40.4 | 10.18 | 34.4 | 45.2 | -0.339 | 0.04 | -0.266 |  |  | 2.01 | 32.73 | 8.13 | 31.6 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC355MP03HA | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 355 | 331.6 |  | 2020-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.25 | 40.6 | 10.27 | 34.6 | 45.2 | -0.339 | 0.04 | -0.266 |  |  | 2.02 | 32.92 | 8.2 | 31.8 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC360MP03 | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 336 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 9.87 | 47.84 | 9.23 | 39.01 | 44.48 | -0.349 | 0.038 | -0.263 |  |  | 1.7961 | 38.2664 | 7.3029 | 36.5972 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC360MP03HA | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 360 | 336.3 |  | 2020-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.33 | 40.8 | 10.35 | 34.8 | 45.2 | -0.339 | 0.04 | -0.266 |  |  | 2.04 | 33.11 | 8.26 | 32 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC365MP03 | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 340.8 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 9.9 | 48.13 | 9.28 | 39.34 | 44.48 | -0.349 | 0.038 | -0.263 |  |  | 1.8058 | 38.5901 | 7.3421 | 36.9068 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC365MP03H | 365 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 343.3 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 9.71 | 48.4 | 9.13 | 40 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.785 | 38.1754 | 7.2357 | 37.2207 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC365MP03HA | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 365 | 341.1 |  | 2020-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.41 | 41 | 10.43 | 35 | 45.2 | -0.339 | 0.04 | -0.266 |  |  | 2.05 | 33.3 | 8.33 | 32.2 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC370MP03 | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 345.6 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 9.93 | 48.4 | 9.32 | 39.69 | 44.48 | -0.349 | 0.038 | -0.263 |  |  | 1.8144 | 38.9334 | 7.3771 | 37.2351 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC370MP03H | 370 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 348.1 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 9.79 | 48.6 | 9.21 | 40.2 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.8007 | 38.3662 | 7.2991 | 37.4068 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC370MP03HA | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 370 | 345.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.5 | 41.2 | 10.52 | 35.2 | 45.2 | -0.339 | 0.04 | -0.266 |  |  | 2.07 | 33.49 | 8.4 | 32.4 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC375MP03 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 350.4 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 9.96 | 48.71 | 9.36 | 40.08 | 44.48 | -0.349 | 0.038 | -0.263 |  |  | 1.821 | 39.316 | 7.404 | 37.601 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC375MP03H | 375 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 352.9 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 9.87 | 48.8 | 9.28 | 40.4 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.8144 | 38.5571 | 7.3546 | 37.5929 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC380MP03 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 355.2 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 10 | 49.03 | 9.4 | 40.41 | 44.48 | -0.349 | 0.038 | -0.263 |  |  | 1.8293 | 39.6397 | 7.4378 | 37.9106 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC380MP03H | 380 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 357.7 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 9.96 | 49 | 9.36 | 40.6 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.83 | 38.748 | 7.418 | 37.779 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC385MP03H | 385 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 362.6 |  | 2019-10-31 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 10.03 | 49.2 | 9.43 | 40.8 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.8437 | 38.9389 | 7.4735 | 37.9651 | [6 empty] | 2020-02-11
Caterpillar Inc. | PVC425MB03H | 425 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 398.2 |  | 2020-04-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.22 | 48.7 | 10.52 | 40.4 | 44.8 | -0.331 | 0.041 | -0.259 |  |  | 2.06 | 39.26 | 8.35 | 37.9 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC425MP03H | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 397.5 |  | 2020-04-24 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.23 | 48.3 | 10.5 | 40.5 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.04 | 39.02 | 8.29 | 37.7 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC430MB03H | 430 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 403 |  | 2020-04-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.3 | 48.9 | 10.6 | 40.6 | 44.8 | -0.331 | 0.041 | -0.259 |  |  | 2.08 | 39.46 | 8.42 | 38.1 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC430MP03H | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 402.3 |  | 2020-04-24 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.31 | 48.5 | 10.57 | 40.7 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.06 | 39.21 | 8.35 | 37.9 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC435MB03H | 435 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 407.8 |  | 2020-04-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.36 | 49.1 | 10.66 | 40.8 | 44.8 | -0.331 | 0.041 | -0.259 |  |  | 2.09 | 39.65 | 8.46 | 38.3 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC435MP03H | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 407.1 |  | 2020-04-24 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.39 | 48.7 | 10.64 | 40.9 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.07 | 39.4 | 8.4 | 38 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC440MB03H | 440 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 412.6 |  | 2020-04-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.45 | 49.2 | 10.73 | 41 | 44.8 | -0.331 | 0.041 | -0.259 |  |  | 2.1 | 39.85 | 8.52 | 38.5 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC440MP03H | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 411.9 |  | 2020-04-24 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.46 | 48.9 | 10.71 | 41.1 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.08 | 39.6 | 8.46 | 38.2 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC445MB03H | 445 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 417.4 |  | 2020-04-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.52 | 49.4 | 10.8 | 41.2 | 44.8 | -0.331 | 0.041 | -0.259 |  |  | 2.11 | 40.04 | 8.57 | 38.7 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC445MP03H | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 416.7 |  | 2020-04-24 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.53 | 49.1 | 10.78 | 41.3 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.1 | 39.79 | 8.52 | 38.4 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC450MB03H | 450 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 422.2 |  | 2020-04-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.58 | 49.6 | 10.87 | 41.4 | 44.8 | -0.331 | 0.041 | -0.259 |  |  | 2.13 | 40.24 | 8.63 | 38.9 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC450MP03H | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 421.5 |  | 2020-04-24 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.6 | 49.3 | 10.85 | 41.5 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.11 | 39.98 | 8.57 | 38.6 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC455MB03H | 455 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 427 |  | 2020-04-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.65 | 49.8 | 10.93 | 41.6 | 44.8 | -0.331 | 0.041 | -0.259 |  |  | 2.14 | 40.43 | 8.68 | 39.1 | [6 empty] | 2020-09-21
Caterpillar Inc. | PVC455MP03H | 455 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 426.3 |  | 2020-04-24 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.66 | 49.5 | 10.92 | 41.7 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.13 | 40.18 | 8.63 | 38.8 | [6 empty] | 2020-09-21
Centrosolar America | DP36 130 | 130 W Polycrystalline Module | UL 1703 | 130 | 114.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.0108 | 36 | 1 | N | 8.42 | 21.69 | 7.92 | 16.41 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.56 | 16.23 | 6.46 | 14.65 | Rack | Flat Plate | 0.992 | 1.019 | 1 | 0.19476
Centrosolar America | DP36 135 | 135 W Polycrystalline Module | UL 1703 | 135 | 119.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.0108 | 36 | 1 | N | 8.48 | 21.9 | 7.98 | 16.92 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.57 | 16.73 | 6.51 | 15.1 | Rack | Flat Plate | 0.992 | 1.019 | 1 | 0.19456
Centrosolar America | VS-135C1 | 135 W Thin Film CIGS Module | UL 1703 | 135 | 125 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 100 | 1 | N | 3.43 | 59.5 | 3.02 | 44.7 | 47 | -0.306 | 0.00651 | -0.286 | 0.00228 | -0.264 | 0.56894 | 41.9127 | 2.3379 | 40.7026 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.17664
Centrosolar America | VS-135C2 | 135 W Thin Film CIGS Module | UL 1703 | 135 | 125.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 133 | 1 | N | 2.51 | 79.8 | 2.19 | 61.64 | 46.9 | -0.298 | 0.00792 | -0.291 | 0.00343 | -0.302 | 0.40581 | 57.6653 | 1.721 | 57.592 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.17334
Centrosolar America | DP36 140 | 140 W Polycrystalline Module | UL 1703 | 140 | 123.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.0108 | 36 | 1 | N | 8.53 | 22.15 | 8.03 | 17.43 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.59 | 17.39 | 6.45 | 15.83 | Rack | Flat Plate | 0.992 | 1.019 | 1 | 0.1975
Centrosolar America | VS-140C1 | 140 W Thin Film CIGS Module | UL 1703 | 140 | 129.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 100 | 1 | N | 3.44 | 60.6 | 3.05 | 46 | 47 | -0.306 | 0.00651 | -0.286 | 0.00228 | -0.264 | 0.57459 | 43.1317 | 2.3611 | 41.8863 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.17702
Centrosolar America | VS-140C2 | 140 W Thin Film CIGS Module | UL 1703 | 140 | 130.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 133 | 1 | N | 2.51 | 79.95 | 2.23 | 62.78 | 46.9 | -0.298 | 0.00792 | -0.291 | 0.00343 | -0.302 | 0.41322 | 58.7318 | 1.7524 | 58.6572 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.17335
Centrosolar America | DP36 145 | 145 W Polycrystalline Module | UL 1703 | 145 | 128.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.0108 | 36 | 1 | N | 8.6 | 22.37 | 8.1 | 17.9 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.6 | 17.85 | 6.51 | 16.26 | Rack | Flat Plate | 0.992 | 1.019 | 1 | 0.19697
Centrosolar America | VS-145C1 | 145 W Thin Film CIGS Module | UL 1703 | 145 | 134.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 100 | 1 | N | 3.44 | 61.5 | 3.09 | 46.9 | 47 | -0.306 | 0.00651 | -0.286 | 0.00228 | -0.264 | 0.58213 | 43.9756 | 2.3921 | 42.7058 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.17655
Centrosolar America | VS-145C2 | 145 W Thin Film CIGS Module | UL 1703 | 145 | 134.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 133 | 1 | N | 2.52 | 80.45 | 2.27 | 63.87 | 46.9 | -0.298 | 0.00792 | -0.291 | 0.00343 | -0.302 | 0.417 | 59.3449 | 1.7835 | 57.6199 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.17067
Centrosolar America | DP36 150 | 150 W Polycrystalline Module | UL 1703 | 150 | 132.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.0108 | 36 | 1 | N | 8.63 | 22.51 | 8.13 | 18.45 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.61 | 18.4 | 6.53 | 16.76 | Rack | Flat Plate | 0.992 | 1.019 | 1 | 0.19749
Centrosolar America | VS-150C1 | 150 W Thin Film CIGS Module | UL 1703 | 150 | 139.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 100 | 1 | N | 3.45 | 62.5 | 3.12 | 48.1 | 47 | -0.306 | 0.00651 | -0.286 | 0.00228 | -0.264 | 0.58264 | 46.3836 | 2.4559 | 43.5413 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.18017
Centrosolar America | VS-150C2 | 150 W Thin Film CIGS Module | UL 1703 | 150 | 139.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 133 | 1 | N | 2.52 | 81.35 | 2.3 | 65.22 | 46.9 | -0.298 | 0.00792 | -0.291 | 0.00343 | -0.302 | 0.42251 | 60.5993 | 1.8071 | 58.8378 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.17069
Centrosolar America | VS-155C1 | 155 W Thin Film CIGS Module | UL 1703 | 155 | 143.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 100 | 1 | N | 3.46 | 63.4 | 3.15 | 49.2 | 47 | -0.306 | 0.00651 | -0.286 | 0.00228 | -0.264 | 0.58825 | 47.4443 | 2.4795 | 44.537 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.18006
Centrosolar America | VS-155C2 | 155 W Thin Film CIGS Module | UL 1703 | 155 | 144.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 133 | 1 | N | 2.52 | 82.85 | 2.33 | 66.52 | 46.9 | -0.298 | 0.00792 | -0.291 | 0.00343 | -0.302 | 0.42802 | 61.8072 | 1.8306 | 60.0106 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.17068
Centrosolar America | VS-160C1 | 160 W Thin Film CIGS Module | UL 1703 | 160 | 148.6 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 100 | 1 | N | 3.47 | 64.5 | 3.18 | 50.3 | 47 | -0.306 | 0.00651 | -0.286 | 0.00228 | -0.264 | 0.59385 | 48.5051 | 2.5031 | 45.5328 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.18003
Centrosolar America | E165 | 165 W Monocrystalline Module | UL 1703 | 165 | 146.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.19 | 44.12 | 4.6 | 35.8 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.91423 | 34.7887 | 3.5703 | 31.9571 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19276
Centrosolar America | E170 | 170 W Monocrystalline Module | UL 1703 | 170 | 151.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.3 | 44.16 | 4.71 | 36.13 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.93609 | 35.1094 | 3.6557 | 32.2516 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19333
Centrosolar America | DP48 175 | 175 W Polycrystalline Module | UL 1703 | 175 | 154.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3253 | 48 | 1 | N | 8.42 | 29.01 | 7.92 | 22.1 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.53 | 21.8 | 6.37 | 19.99 | Rack | Flat Plate | 0.992 | 1.336 | 1 | 0.19059
Centrosolar America | E175 | 175 W Monocrystalline Module | UL 1703 | 175 | 155.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.5 | 44.25 | 4.83 | 36.24 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.95994 | 35.2163 | 3.7488 | 32.3498 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19317
Centrosolar America | DP48 180 | 180 W Polycrystalline Module | UL 1703 | 180 | 159 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3253 | 48 | 1 | N | 8.48 | 29.2 | 7.98 | 22.56 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.55 | 22.25 | 6.41 | 20.41 | Rack | Flat Plate | 0.992 | 1.336 | 1 | 0.1916
Centrosolar America | E180 | 180 W Monocrystalline Module | UL 1703 | 180 | 157.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.61 | 44.6 | 4.95 | 36.3 | 47.6 | -0.53283 | 0.041933 | -0.39096 | -0.015774 | -0.51517 | 0.98531 | 35.9867 | 3.9603 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19699
Centrosolar America | DP48 185 | 185 W Polycrystalline Module | UL 1703 | 185 | 163.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3253 | 48 | 1 | N | 8.53 | 29.49 | 8.03 | 23.04 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.56 | 22.73 | 6.45 | 20.84 | Rack | Flat Plate | 0.992 | 1.336 | 1 | 0.19167
Centrosolar America | E185 | 185 W Monocrystalline Module | UL 1703 | 185 | 162.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.8 | 44.6 | 5.09 | 36.3 | 47.6 | -0.53283 | 0.041933 | -0.39096 | -0.015774 | -0.51517 | 1.0132 | 35.9867 | 4.0723 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19709
Centrosolar America | DP48 190 | 190 W Polycrystalline Module | UL 1703 | 190 | 168.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3253 | 48 | 1 | N | 8.57 | 29.73 | 8.07 | 23.54 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.58 | 23.59 | 6.52 | 21.09 | Rack | Flat Plate | 0.992 | 1.336 | 1 | 0.19617
Centrosolar America | DP48 195 | 195 W Polycrystalline Module | UL 1703 | 195 | 172.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3253 | 48 | 1 | N | 8.6 | 29.92 | 8.1 | 24.07 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.59 | 24.12 | 6.54 | 21.57 | Rack | Flat Plate | 0.992 | 1.336 | 1 | 0.19667
Centrosolar America | E195 | 195 W Polycrystalline Module | UL 1703 | 195 | 172.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.98 | 32.75 | 7.22 | 27 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4268 | 26.8958 | 5.5921 | 24.1124 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19679
Centrosolar America | D200 | 200 W Polycrystalline Module | UL 1703 | 200 | 183 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 7.68 | 36.2 | 6.93 | 28.9 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4244 | 28.0704 | 5.7178 | 26.8796 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19992
Centrosolar America | DP48 200 | 200 W Polycrystalline Module | UL 1703 | 200 | 177.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3253 | 48 | 1 | N | 8.63 | 30.12 | 8.13 | 24.6 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.6 | 24.65 | 6.56 | 22.04 | Rack | Flat Plate | 0.992 | 1.336 | 1 | 0.1972
Centrosolar America | DP54 200 | 200 W Polycrystalline Module | UL 1703 | 200 | 176.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.483 | 54 | 1 | N | 8.42 | 32.8 | 7.92 | 25.25 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.58 | 24.55 | 6.45 | 22.79 | Rack | Flat Plate | 0.992 | 1.495 | 1 | 0.19395
Centrosolar America | E200 | 200 W Polycrystalline Module | UL 1703 | 200 | 176.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.86 | 32.72 | 7.36 | 27.21 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4544 | 27.1049 | 5.7006 | 24.2999 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19711
Centrosolar America | DP54 205 | 205 W Polycrystalline Module | UL 1703 | 205 | 181.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.483 | 54 | 1 | N | 8.47 | 33.01 | 7.97 | 25.72 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.59 | 25.01 | 6.49 | 23.21 | Rack | Flat Plate | 0.992 | 1.495 | 1 | 0.19398
Centrosolar America | E205 | 205 W Polycrystalline Module | UL 1703 | 205 | 181.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.1 | 32.8 | 7.5 | 27.3 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4821 | 27.1946 | 5.809 | 24.3803 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19661
Centrosolar America | D210 | 210 W Polycrystalline Module | UL 1703 | 210 | 192.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 7.91 | 36.4 | 7.26 | 28.9 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4922 | 28.0704 | 5.99 | 26.8796 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19946
Centrosolar America | DP54 210 | 210 W Polycrystalline Module | UL 1703 | 210 | 185.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.483 | 54 | 1 | N | 8.5 | 33.23 | 8 | 26.25 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.6 | 25.52 | 6.52 | 23.69 | Rack | Flat Plate | 0.992 | 1.495 | 1 | 0.19444
Centrosolar America | E210 | 210 W Polycrystalline Module | UL 1703 | 210 | 186.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.3 | 32.83 | 7.63 | 27.54 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.5078 | 27.4337 | 5.9097 | 24.5946 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19697
Centrosolar America | DP54 215 | 215 W Polycrystalline Module | UL 1703 | 215 | 190.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.483 | 54 | 1 | N | 8.52 | 33.44 | 8.02 | 26.81 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.59 | 26.47 | 6.42 | 24.63 | Rack | Flat Plate | 0.992 | 1.495 | 1 | 0.19575
Centrosolar America | D220 | 220 W Polycrystalline Module | UL 1703 | 220 | 201.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.09 | 36.6 | 7.52 | 29.3 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4962 | 28.5107 | 5.9847 | 26.9322 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.1939
Centrosolar America | DP54 220 | 220 W Polycrystalline Module | UL 1703 | 220 | 194.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.483 | 54 | 1 | N | 8.55 | 33.66 | 8.05 | 27.33 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.6 | 26.99 | 6.44 | 25.11 | Rack | Flat Plate | 0.992 | 1.495 | 1 | 0.19629
Centrosolar America | DP60 220 | 220 W Polycrystalline Module | UL 1703 | 220 | 197.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.46 | 36.26 | 7.96 | 27.64 | 45.9 | -0.452 | 0.051 | -0.331 | -0.071 | -0.389 | 1.56 | 27.32 | 6.29 | 25.7 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19372
Centrosolar America | E220 | 220 W Polycrystalline Module | UL 1703 | 220 | 198.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.1 | 36.3 | 7.58 | 29 | 45.6 | -0.446 | 0.065 | -0.34 | 0.105 | -0.534 | 1.6579 | 28.474 | 6.3477 | 25.576 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21457
Centrosolar America | E220B | 220 W Polycrystalline Module, Black Frame | UL 1703 | 220 | 198.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.1 | 36.3 | 7.58 | 29 | 45.6 | -0.446 | 0.065 | -0.34 | 0.105 | -0.534 | 1.6579 | 28.474 | 6.3477 | 25.576 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21457
Centrosolar America | DP54 225 | 225 W Polycrystalline Module | UL 1703 | 225 | 199.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.483 | 54 | 1 | N | 8.6 | 33.8 | 8.1 | 27.78 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.61 | 27.43 | 6.48 | 25.52 | Rack | Flat Plate | 0.992 | 1.495 | 1 | 0.19628
Centrosolar America | DP60 225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.48 | 36.4 | 7.98 | 28.2 | 45.9 | -0.452 | 0.051 | -0.331 | -0.071 | -0.389 | 1.57 | 27.87 | 6.3 | 26.22 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19447
Centrosolar America | E225 | 225 W Polycrystalline Module | UL 1703 | 225 | 202.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.1 | 36.3 | 7.75 | 29 | 45.6 | -0.446 | 0.065 | -0.34 | 0.105 | -0.534 | 1.695 | 28.474 | 6.4901 | 25.576 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21451
Centrosolar America | E225B | 225 W Polycrystalline Module, Black Frame | UL 1703 | 225 | 202.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.1 | 36.3 | 7.75 | 29 | 45.6 | -0.446 | 0.065 | -0.34 | 0.105 | -0.534 | 1.695 | 28.474 | 6.4901 | 25.576 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21451
Centrosolar America | K225 | 225 W Polycrystalline Module | UL 1703 | 225 | 200.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.25 | 36.7 | 7.65 | 29.4 | 46.6 | -0.4634 | 0.0738 | -0.3525 | 0.0263 | -0.4011 | 1.5397 | 28.9017 | 5.0773 | 26.6095 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19778
Centrosolar America | K225B | 225 W Monocrystalline Module | UL 1703 | 225 | 202.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.08 | 37 | 7.57 | 29.7 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.5155 | 29.7894 | 6.197 | 26.582 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20065
Centrosolar America | D230 | 230 W Polycrystalline Module | UL 1703 | 230 | 211 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.34 | 36.8 | 7.71 | 29.8 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.534 | 28.9973 | 6.1359 | 27.3918 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.1934
Centrosolar America | DM60 230 | 230 W Monocrystalline Module | UL 1703 | 230 | 208.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 8.5 | 36.2 | 8 | 28.8 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.6 | 28.1 | 6.43 | 26.25 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19548
Centrosolar America | DP54 230 | 230 W Polycrystalline Module | UL 1703 | 230 | 204 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.483 | 54 | 1 | N | 8.66 | 34.02 | 8.16 | 28.19 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.62 | 27.83 | 6.53 | 25.9 | Rack | Flat Plate | 0.992 | 1.495 | 1 | 0.19602
Centrosolar America | DP60 230 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.5 | 36.68 | 8 | 28.75 | 45.9 | -0.452 | 0.051 | -0.331 | -0.071 | -0.389 | 1.57 | 28.42 | 6.32 | 26.73 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.194
Centrosolar America | E230 | 230 W Polycrystalline Module | UL 1703 | 230 | 207.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.82 | 29.4 | 45.6 | -0.446 | 0.065 | -0.34 | 0.105 | -0.534 | 1.7104 | 28.8667 | 6.5487 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
Centrosolar America | E230B | 230 W Polycrystalline Module, Black Frame | UL 1703 | 230 | 207.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.82 | 29.4 | 45.6 | -0.446 | 0.065 | -0.34 | 0.105 | -0.534 | 1.7104 | 28.8667 | 6.5487 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
Centrosolar America | K230 | 230 W Polycrystalline Module | UL 1703 | 230 | 205.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.35 | 36.8 | 7.78 | 29.6 | 46.6 | -0.4634 | 0.0738 | -0.3525 | 0.0263 | -0.4011 | 1.5659 | 29.0983 | 5.1635 | 26.7905 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19811
Centrosolar America | K230B | 230 W Monocrystalline Module | UL 1703 | 230 | 206.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.2 | 37.1 | 7.69 | 29.9 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.5396 | 29.99 | 6.2953 | 26.761 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20074
Centrosolar America | DM60 235 | 235 W Monocrystalline Module | UL 1703 | 235 | 212.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 8.6 | 36.5 | 8 | 29.4 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.6 | 28.69 | 6.43 | 26.8 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19534
Centrosolar America | DP60 235 | 235 W Polycrystalline Module | UL 1703 | 235 | 211.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.52 | 36.98 | 8.02 | 29.3 | 45.9 | -0.452 | 0.051 | -0.331 | -0.071 | -0.389 | 1.58 | 29.11 | 6.46 | 26.66 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19572
Centrosolar America | E235 | 235 W Polycrystalline Module | UL 1703 | 235 | 212.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5695 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.6 | -0.446 | 0.065 | -0.34 | 0.105 | -0.534 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.97 | 1.618 | 1 | 0.21466
Centrosolar America | E235B | 235 W Polycrystalline Module, Black Frame | UL 1703 | 235 | 212.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5695 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.6 | -0.446 | 0.065 | -0.34 | 0.105 | -0.534 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.97 | 1.618 | 1 | 0.21466
Centrosolar America | EP6 235 BW | 235 W Polycrystalline Module | UL 1703 | 235 | 208.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6348 | 60 | 1 | N | 8.69 | 37.44 | 8.07 | 29.74 | 47.5 | -0.4793 | 0.0656 | -0.334 | -0.0174 | -0.4579 | 1.6942 | 29.8059 | 8.0887 | 25.7961 | Rack | Flat Plate | 0.986 | 1.658 | 1 | 0.21489
Centrosolar America | EP6 235 SW | 235 W Polycrystalline Module | UL 1703 | 235 | 208.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6348 | 60 | 1 | N | 8.69 | 37.44 | 8.07 | 29.74 | 47.5 | -0.4793 | 0.0656 | -0.334 | -0.0174 | -0.4579 | 1.6942 | 29.8059 | 8.0887 | 25.7961 | Rack | Flat Plate | 0.986 | 1.658 | 1 | 0.21489
Centrosolar America | K235 | 235 W Polycrystalline Module | UL 1703 | 235 | 210 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.47 | 36.9 | 7.89 | 29.8 | 46.6 | -0.4634 | 0.0738 | -0.3525 | 0.0263 | -0.4011 | 1.5881 | 29.2949 | 5.2365 | 26.9715 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19797
Centrosolar America | K235B | 235 W Monocrystalline Module | UL 1703 | 235 | 211.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.31 | 37.2 | 7.83 | 30 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.5676 | 30.0903 | 6.4099 | 26.8506 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20072
Centrosolar America | DM60 240 | 240 W Monocrystalline Module | UL 1703 | 240 | 217.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 8.6 | 36.8 | 8.1 | 29.7 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.62 | 28.98 | 6.51 | 27.07 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19562
Centrosolar America | DP60 240 | 240 W Polycrystalline Module | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.55 | 37.16 | 8.05 | 29.81 | 45.9 | -0.452 | 0.051 | -0.331 | -0.071 | -0.389 | 1.58 | 29.61 | 6.49 | 27.13 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19493
Centrosolar America | E240 | 240 W Polycrystalline Module | UL 1703 | 240 | 214.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 46.6 | -0.459 | 0.023 | -0.308 | -0.043 | -0.425 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
Centrosolar America | E240B | 240 W Polycrystalline Module, Black Frame | UL 1703 | 240 | 214.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 46.6 | -0.459 | 0.023 | -0.308 | -0.043 | -0.425 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
Centrosolar America | EP6 240 BW | 240 W Polycrystalline Module | UL 1703 | 240 | 212.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6348 | 60 | 1 | N | 8.82 | 37.64 | 8.2 | 29.9 | 47.5 | -0.4793 | 0.0656 | -0.334 | -0.0174 | -0.4579 | 1.7204 | 29.9643 | 8.2136 | 25.9332 | Rack | Flat Plate | 0.986 | 1.658 | 1 | 0.21479
Centrosolar America | EP6 240 SW | 240 W Polycrystalline Module | UL 1703 | 240 | 212.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6348 | 60 | 1 | N | 8.82 | 37.64 | 8.2 | 29.9 | 47.5 | -0.4793 | 0.0656 | -0.334 | -0.0174 | -0.4579 | 1.7204 | 29.9643 | 8.2136 | 25.9332 | Rack | Flat Plate | 0.986 | 1.658 | 1 | 0.21479
Centrosolar America | DM60 245 | 245 W Monocrystalline Module | UL 1703 | 245 | 222 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 8.7 | 37.1 | 8.1 | 30.3 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.62 | 29.57 | 6.51 | 27.62 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19552
Centrosolar America | DP60 245 | 245 W Polycrystalline Module | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.58 | 37.4 | 8.08 | 30.32 | 45.9 | -0.452 | 0.051 | -0.331 | -0.071 | -0.389 | 1.59 | 30.12 | 6.51 | 27.59 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19547
Centrosolar America | E245 | 245 W Polycrystalline Module | UL 1703 | 245 | 219 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
Centrosolar America | E245B | 245 W Polycrystalline Module, Black frame | UL 1703 | 245 | 219 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
Centrosolar America | EP6 245 BW | 245 W Polycrystalline Module | UL 1703 | 245 | 217.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6348 | 60 | 1 | N | 8.82 | 37.64 | 8.2 | 29.9 | 47.5 | -0.4793 | 0.0656 | -0.334 | -0.0174 | -0.4579 | 1.7204 | 29.9643 | 8.2136 | 25.9332 | Rack | Flat Plate | 0.986 | 1.658 | 1 | 0.21041
Centrosolar America | EP6 245 SW | 245 W Polycrystalline Module | UL 1703 | 245 | 217.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6348 | 60 | 1 | N | 8.82 | 37.64 | 8.2 | 29.9 | 47.5 | -0.4793 | 0.0656 | -0.334 | -0.0174 | -0.4579 | 1.7204 | 29.9643 | 8.2136 | 25.9332 | Rack | Flat Plate | 0.986 | 1.658 | 1 | 0.21041
Centrosolar America | TP6 245xx | 245 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 245 | 220.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.64 | 37.3 | 8.13 | 30.3 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.63 | 29.68 | 6.52 | 27.52 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19746
Centrosolar America | TP6S 245xx | 245 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 245 | 220.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.64 | 37.3 | 8.13 | 30.3 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.63 | 29.68 | 6.52 | 27.52 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19746
Centrosolar America | DM60 250 | 250 W Monocrystalline Module | UL 1703 | 250 | 226.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 8.7 | 37.4 | 8.2 | 30.6 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.64 | 29.86 | 6.59 | 27.89 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19588
Centrosolar America | DP60 250 | 250 W Polycrystalline Module | UL 1703 | 250 | 225.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.61 | 37.65 | 8.11 | 30.83 | 45.9 | -0.452 | 0.051 | -0.331 | -0.071 | -0.389 | 1.6 | 30.62 | 6.53 | 28.05 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19597
Centrosolar America | E250 | 250 W Polycrystalline Module | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
Centrosolar America | E250B | 250 W Polycrystalline Module, Black Frame | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
Centrosolar America | EP6 250BW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.79 | 37.41 | 8.34 | 29.98 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6051 | 29.3741 | 6.683 | 27.1089 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1886
Centrosolar America | EP6 250SW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.79 | 37.41 | 8.34 | 29.98 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6051 | 29.3741 | 6.683 | 27.1089 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1886
Centrosolar America | TP6 250xx | 250 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 250 | 225 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.76 | 37.5 | 8.24 | 30.5 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.65 | 29.88 | 6.61 | 27.7 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19721
Centrosolar America | TP6S 250xx | 250 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 250 | 225 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.76 | 37.5 | 8.24 | 30.5 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.65 | 29.88 | 6.61 | 27.7 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19721
Centrosolar America | DM60 255 | 255 W Monocrystalline Module | UL 1703 | 255 | 231.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 8.8 | 37.9 | 8.2 | 31.1 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.65 | 30.36 | 6.61 | 28.46 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19645
Centrosolar America | DP60 255 | 255 W Polycrystalline Module | UL 1703 | 255 | 226.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.66 | 37.9 | 8.16 | 31.25 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.61 | 31.04 | 6.57 | 28.44 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19598
Centrosolar America | E255B | 255 W Polycrystalline Module, Black Frame | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.01 | 6.57 | 27.41 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19536
Centrosolar America | EP6 255BW | 255 W Polycrystalline Module | UL 1703 | 255 | 226.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.94 | 37.54 | 8.43 | 30.25 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6226 | 29.6386 | 6.7559 | 27.3531 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1886
Centrosolar America | EP6 255SW | 255 W Polycrystalline Module | UL 1703 | 255 | 226.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.94 | 37.54 | 8.43 | 30.25 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6226 | 29.6386 | 6.7559 | 27.3531 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1886
Centrosolar America | EP60 255BW | 255 W Polycrystalline Module, Black Frame | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
Centrosolar America | EP60 255SW | 255 W Polycrystalline Module | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
Centrosolar America | TP6 255xx | 255 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 255 | 229.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.89 | 38.1 | 8.34 | 30.6 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.67 | 29.97 | 6.69 | 27.79 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19627
Centrosolar America | TP6S 255xx | 255 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 255 | 229.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.89 | 38.1 | 8.34 | 30.6 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.67 | 29.97 | 6.69 | 27.79 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19627
Centrosolar America | CM60 260-C1 | 260 W Monocrystalline Module | UL 1703 | 260 | 235.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.14 | 38.1 | 8.47 | 30.7 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.6 | 30.3 | 6.71 | 27.89 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18646
Centrosolar America | CP60 260-C1 | 260 W Monocrystalline Module | UL 1703 | 260 | 235.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.16 | 38.3 | 8.56 | 30.95 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.61 | 30.55 | 6.78 | 28.12 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18918
Centrosolar America | CP60 260SW | 260 W Polycrystalline Module | UL 1703 | 260 | 236.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.83 | 37.67 | 8.43 | 30.93 | 43.2 | -0.48 | 0.07 | -0.35 | 0.004 | -0.48 | 1.69 | 30.59 | 6.82 | 28.39 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19883
Centrosolar America | DM60 260 | 260 W Monocrystalline Module | UL 1703 | 260 | 236 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 8.8 | 38.2 | 8.3 | 31.4 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.67 | 30.65 | 6.69 | 28.73 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19687
Centrosolar America | DP60 260 | 260 W Polycrystalline Module | UL 1703 | 260 | 234.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.7 | 38.28 | 8.2 | 31.71 | 46.5 | -0.4411 | 0.07403 | -0.339 | 0.009095 | -0.4456 | 1.64 | 30.72 | 6.61 | 28.9 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19377
Centrosolar America | E260 | 260 W Polycrystalline Module | UL 1703 | 260 | 231.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7389 | 72 | 1 | N | 7.79 | 43.49 | 7.23 | 36 | 45.3 | -0.5185 | 0.061617 | -0.37273 | -0.0082988 | -0.48972 | 1.75 | 33.8 | 5.879 | 31.01 | Rack | Flat Plate | 0.922 | 1.886 | 1 | 0.2275
Centrosolar America | E260B | 260 W Polycrystalline Module, Black Frame | UL 1703 | 260 | 235.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.56 | 6.57 | 27.92 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19511
Centrosolar America | EM60 260BB | 260 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 260 | 236.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.22 | 8.49 | 30.63 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.6357 | 30.3035 | 6.8251 | 28.1047 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19064
Centrosolar America | EP6 260BW | 260 W Polycrystalline Module | UL 1703 | 260 | 231.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 9.09 | 37.65 | 8.52 | 30.51 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6403 | 29.8933 | 6.8296 | 27.5882 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1886
Centrosolar America | EP6 260SW | 260 W Polycrystalline Module | UL 1703 | 260 | 231.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 9.09 | 37.65 | 8.52 | 30.51 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6403 | 29.8933 | 6.8296 | 27.5882 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.1886
Centrosolar America | EP60 260BW | 260 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 260 | 237 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.07 | 38.16 | 8.5 | 30.59 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6624 | 30.2766 | 6.7782 | 28.0531 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19358
Centrosolar America | EP60 260SW | 260 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 260 | 237 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.07 | 38.16 | 8.5 | 30.59 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6624 | 30.2766 | 6.7782 | 28.0531 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19358
Centrosolar America | TM6 260xx | 260 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 260 | 236.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.04 | 37.8 | 8.49 | 30.8 | 46.9 | -0.404 | 0.055 | -0.305 | 0.002 | -0.406 | 1.7 | 29.93 | 6.82 | 28.11 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.1957
Centrosolar America | TM6S 260xx | 260 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 260 | 236.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.04 | 37.8 | 8.49 | 30.8 | 46.9 | -0.404 | 0.055 | -0.305 | 0.002 | -0.406 | 1.7 | 29.93 | 6.82 | 28.11 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.1957
Centrosolar America | TP6 260xx | 260 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 260 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.99 | 37.9 | 8.46 | 30.9 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.7 | 30.27 | 6.78 | 28.06 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19792
Centrosolar America | TP6S 260xx | 260 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 260 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.99 | 37.9 | 8.46 | 30.9 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.7 | 30.27 | 6.78 | 28.06 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19792
Centrosolar America | CM60 265-C1 | 265 W Polycrystalline Module | UL 1703 | 265 | 239.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.01 | 38 | 8.42 | 30.7 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.71 | 29.9 | 6.68 | 27.59 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19294
Centrosolar America | CP60 265-C1 | 265 W Polycrystalline Module | UL 1703 | 265 | 239.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.2 | 38.3 | 8.47 | 30.89 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.72 | 30.08 | 6.72 | 27.76 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19524
Centrosolar America | DM60 265 | 265 W Monocrystalline Module | UL 1703 | 265 | 240.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 8.9 | 38.5 | 8.3 | 32 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.67 | 31.24 | 6.69 | 29.28 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19687
Centrosolar America | DP60 265 | 265 W Polycrystalline Module | UL 1703 | 265 | 239.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.73 | 38.4 | 8.23 | 32.2 | 46.5 | -0.4411 | 0.07403 | -0.339 | 0.009095 | -0.4456 | 1.65 | 31.19 | 6.63 | 29.34 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.1942
Centrosolar America | E265 | 265 W Polycrystalline Module | UL 1703 | 265 | 235.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7389 | 72 | 1 | N | 7.9 | 43.63 | 7.28 | 36.4 | 45.3 | -0.5185 | 0.061617 | -0.37273 | -0.0082988 | -0.48972 | 1.7621 | 34.1756 | 5.9197 | 31.3546 | Rack | Flat Plate | 0.922 | 1.886 | 1 | 0.22725
Centrosolar America | E265B | 265 W Polycrystalline Module, Black Frame | UL 1703 | 265 | 235.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7389 | 72 | 1 | N | 7.9 | 43.63 | 7.28 | 36.4 | 45.3 | -0.5185 | 0.061617 | -0.37273 | -0.0082988 | -0.48972 | 1.7621 | 34.1756 | 5.9197 | 31.3546 | Rack | Flat Plate | 0.922 | 1.886 | 1 | 0.22725
Centrosolar America | EM60 265BB | 265 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 265 | 241.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.1 | 38.29 | 8.65 | 30.64 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.6665 | 30.3134 | 6.9537 | 28.1139 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19063
Centrosolar America | EM60 265SW | 265 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 265 | 241.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.1 | 38.29 | 8.65 | 30.64 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6665 | 30.3134 | 6.9537 | 28.1139 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19063
Centrosolar America | EP6 265BW | 265 W Polycrystalline Module | UL 1703 | 265 | 236.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 9.24 | 37.77 | 8.61 | 30.78 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6573 | 30.1579 | 6.9003 | 27.8323 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.18861
Centrosolar America | EP6 265SW | 265 W Polycrystalline Module | UL 1703 | 265 | 236.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 9.24 | 37.77 | 8.61 | 30.78 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.6573 | 30.1579 | 6.9003 | 27.8323 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.18861
Centrosolar America | EP60 265BW | 265 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 265 | 241.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.24 | 38.29 | 8.62 | 30.74 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6859 | 30.425 | 6.8739 | 28.1906 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
Centrosolar America | EP60 265SW | 265 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 265 | 241.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.24 | 38.29 | 8.62 | 30.74 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6859 | 30.425 | 6.8739 | 28.1906 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
Centrosolar America | TM6 265xx | 265 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 265 | 240.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.16 | 38 | 8.6 | 31 | 46.9 | -0.404 | 0.055 | -0.305 | 0.002 | -0.406 | 1.72 | 30.13 | 6.91 | 28.29 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19556
Centrosolar America | TM6S 265xx | 265 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 265 | 240.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.16 | 38 | 8.6 | 31 | 46.9 | -0.404 | 0.055 | -0.305 | 0.002 | -0.406 | 1.72 | 30.13 | 6.91 | 28.29 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19556
Centrosolar America | TP6 265xx | 265 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 265 | 238.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 9.12 | 38.5 | 8.55 | 31 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.71 | 30.37 | 6.85 | 28.15 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19597
Centrosolar America | TP6S 265xx | 265 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 265 | 238.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 9.12 | 38.5 | 8.55 | 31 | 48.2 | -0.412 | 0.051 | -0.305 | -0.01 | -0.404 | 1.71 | 30.37 | 6.85 | 28.15 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19597
Centrosolar America | CP60 270SW | 270 W Monocrystalline Module | UL 1703 | 270 | 243.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.26 | 38.79 | 8.69 | 31.07 | 43.6 | -0.51 | 0.07 | -0.38 | 0.0007 | -0.52 | 1.78 | 30.34 | 6.92 | 28.6 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20002
Centrosolar America | DM60 270 | 270 W Monocrystalline Module | UL 1703 | 270 | 245.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 8.9 | 38.8 | 8.4 | 32.2 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.69 | 31.44 | 6.77 | 29.46 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19679
Centrosolar America | DP60 270 | 270 W Polycrystalline Module | UL 1703 | 270 | 243.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6398 | 60 | 1 | N | 8.8 | 38.6 | 8.32 | 32.46 | 46.5 | -0.4411 | 0.07403 | -0.339 | 0.009095 | -0.4456 | 1.66 | 31.45 | 6.71 | 29.58 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19336
Centrosolar America | DP72 270 | 270 W Polycrystalline Module | UL 1703 | 270 | 238.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.09 | 43.85 | 7.59 | 35.55 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.49 | 34.86 | 6.06 | 33.03 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19238
Centrosolar America | E270 | 270 W Polycrystalline Module | UL 1703 | 270 | 237.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7389 | 72 | 1 | N | 7.9 | 43.63 | 7.42 | 36.4 | 47 | -0.53025 | 0.064818 | -0.38025 | -0.020571 | -0.50998 | 1.5416 | 36.7634 | 5.8087 | 32.6728 | Rack | Flat Plate | 0.922 | 1.886 | 1 | 0.20991
Centrosolar America | E270B | 270 W Polycrystalline Module, Black Frame | UL 1703 | 270 | 237.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7389 | 72 | 1 | N | 7.9 | 43.63 | 7.42 | 36.4 | 47 | -0.53025 | 0.064818 | -0.38025 | -0.020571 | -0.50998 | 1.5416 | 36.7634 | 5.8087 | 32.6728 | Rack | Flat Plate | 0.922 | 1.886 | 1 | 0.20991
Centrosolar America | EM60 270BB | 270 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 270 | 245.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.12 | 38.68 | 8.76 | 30.83 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.6877 | 30.5014 | 7.0422 | 28.2882 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19066
Centrosolar America | EM60 270SW | 270 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 270 | 246.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.12 | 38.68 | 8.76 | 30.83 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6877 | 30.5014 | 7.0422 | 28.2882 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19066
Centrosolar America | EP60 270BW | 270 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 270 | 246.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.31 | 38.72 | 8.72 | 30.97 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7054 | 30.6527 | 6.9537 | 28.4016 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
Centrosolar America | EP60 270SW | 270 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 270 | 246.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.31 | 38.72 | 8.72 | 30.97 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7054 | 30.6527 | 6.9537 | 28.4016 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
Centrosolar America | TM6 270xx | 270 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 270 | 244.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.28 | 38.2 | 8.71 | 31.2 | 47.8 | -0.404 | 0.042 | -0.278 | -0.013 | -0.369 | 1.76 | 30.57 | 6.98 | 28.53 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19927
Centrosolar America | TM6S 270xx | 270 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 270 | 244.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.28 | 38.2 | 8.71 | 31.2 | 47.8 | -0.404 | 0.042 | -0.278 | -0.013 | -0.369 | 1.76 | 30.57 | 6.98 | 28.53 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19927
Centrosolar America | CM60 275SW | 275 W Monocrystalline Module | UL 1703 | 275 | 248.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.37 | 38.99 | 8.8 | 31.27 | 43.6 | -0.51 | 0.07 | -0.38 | 0.0007 | -0.52 | 1.8 | 30.53 | 7.01 | 28.78 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19983
Centrosolar America | DM60 275 | 275 W Monocrystalline Module | UL 1703 | 275 | 250 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6398 | 60 | 1 | N | 9 | 39.1 | 8.4 | 32.8 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.69 | 32.02 | 6.77 | 30.01 | Rack | Flat Plate | 0.992 | 1.653 | 1 | 0.19678
Centrosolar America | DP72 275 | 275 W Polycrystalline Module | UL 1703 | 275 | 243.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.2 | 44 | 7.7 | 35.7 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.52 | 35.01 | 6.15 | 33.17 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19351
Centrosolar America | E275 | 275 W Polycrystalline Module | UL 1703 | 275 | 241.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7389 | 72 | 1 | N | 7.96 | 43.78 | 7.49 | 36.72 | 47 | -0.53025 | 0.064818 | -0.38025 | -0.020571 | -0.50998 | 1.5562 | 37.0866 | 5.8635 | 32.96 | Rack | Flat Plate | 0.922 | 1.886 | 1 | 0.20986
Centrosolar America | E275B | 275 W Polycrystalline Module, Black Frame | UL 1703 | 275 | 241.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7389 | 72 | 1 | N | 7.96 | 43.78 | 7.49 | 36.72 | 47 | -0.53025 | 0.064818 | -0.38025 | -0.020571 | -0.50998 | 1.5562 | 37.0866 | 5.8635 | 32.96 | Rack | Flat Plate | 0.922 | 1.886 | 1 | 0.20986
Centrosolar America | EM60 275BB | 275 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 275 | 250.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.14 | 39.08 | 8.88 | 30.97 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.7108 | 30.6399 | 7.1386 | 28.4167 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
Centrosolar America | EM60 275BW | 275 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 275 | 251.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.14 | 39.08 | 8.88 | 30.97 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7108 | 30.6399 | 7.1386 | 28.4167 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
Centrosolar America | EM60 275SW | 275 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 275 | 251.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.14 | 39.08 | 8.88 | 30.97 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7108 | 30.6399 | 7.1386 | 28.4167 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
Centrosolar America | EP60 275BW | 275 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 275 | 251.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.35 | 38.92 | 8.78 | 31.32 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7172 | 30.9991 | 7.0015 | 28.7225 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
Centrosolar America | EP60 275SW | 275 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 275 | 251.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.35 | 38.92 | 8.78 | 31.32 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7172 | 30.9991 | 7.0015 | 28.7225 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
Centrosolar America | SM60 275SW | 275 W Monocrystalline Module | UL 1703 | 275 | 245.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.45 | 38.1 | 8.81 | 31.2 | 50.1 | -0.418 | 0.0497 | -0.3135 | -0.006 | -0.413 | 1.76 | 31.12 | 6.99 | 28.12 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19917
Centrosolar America | TM6 275xx | 275 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 275 | 249.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.36 | 38.4 | 8.8 | 31.4 | 47.8 | -0.404 | 0.042 | -0.278 | -0.013 | -0.369 | 1.78 | 30.77 | 7.05 | 28.71 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19917
Centrosolar America | TM6S 275xx | 275 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 275 | 249.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.36 | 38.4 | 8.8 | 31.4 | 47.8 | -0.404 | 0.042 | -0.278 | -0.013 | -0.369 | 1.78 | 30.77 | 7.05 | 28.71 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19917
Centrosolar America | CM60 280SW | 280 W Monocrystalline Module | UL 1703 | 280 | 253.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.53 | 39.04 | 8.95 | 31.33 | 43.6 | -0.51 | 0.07 | -0.38 | 0.0007 | -0.52 | 1.83 | 30.59 | 7.13 | 28.84 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19993
Centrosolar America | DP72 280 | 280 W Polycrystalline Module | UL 1703 | 280 | 247.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.31 | 44.15 | 7.81 | 35.85 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.54 | 35.16 | 6.23 | 33.31 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19338
Centrosolar America | E280 | 280 W Polycrystalline Module | UL 1703 | 280 | 250.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.876 | 72 | 1 | N | 7.98 | 43.78 | 7.63 | 36.72 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5853 | 37.0866 | 5.9731 | 32.96 | Rack | Flat Plate | 0.97 | 1.934 | 1 | 0.20997
Centrosolar America | E280B | 280 W Polycrystalline Module, Black Frame | UL 1703 | 280 | 250.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.876 | 72 | 1 | N | 7.98 | 43.78 | 7.63 | 36.72 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5853 | 37.0866 | 5.9731 | 32.96 | Rack | Flat Plate | 0.97 | 1.934 | 1 | 0.20997
Centrosolar America | EM60 280BB | 280 W Monocrystalline Module, Black backsheet, Black Frame | UL 1703 | 280 | 255.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
Centrosolar America | EM60 280BW | 280 W Monocrystalline Module, White backsheet, Black Frame | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
Centrosolar America | EM60 280SW | 280 W Monocrystalline Module, White backsheet, White Frame | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
Centrosolar America | EP60 280BW | 280 W Polycrystalline Module, White backsheet, Black Frame | UL 1703 | 280 | 255.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.47 | 39.16 | 8.84 | 31.68 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7289 | 31.3554 | 7.0494 | 29.0527 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
Centrosolar America | EP60 280SW | 280 W Polycrystalline Module, White backsheet, White Frame | UL 1703 | 280 | 255.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.47 | 39.16 | 8.84 | 31.68 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7289 | 31.3554 | 7.0494 | 29.0527 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
Centrosolar America | SM60 280SW | 280 W Monocrystalline Module | UL 1703 | 280 | 250.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.5 | 38.2 | 8.95 | 31.3 | 50.1 | -0.418 | 0.0497 | -0.3135 | -0.006 | -0.413 | 1.78 | 31.22 | 7.1 | 28.21 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19847
Centrosolar America | TM6 280xx | 280 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 280 | 253.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.43 | 38.7 | 8.86 | 31.7 | 47.8 | -0.404 | 0.042 | -0.278 | -0.013 | -0.369 | 1.79 | 31.06 | 7.1 | 28.99 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19856
Centrosolar America | TM6S 280xx | 280 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 280 | 253.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.43 | 38.7 | 8.86 | 31.7 | 47.8 | -0.404 | 0.042 | -0.278 | -0.013 | -0.369 | 1.79 | 31.06 | 7.1 | 28.99 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19856
Centrosolar America | DM72 285 | 285 W Monocrystalline Module | UL 1703 | 285 | 258.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 8.6 | 44.1 | 8 | 35.7 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.59 | 34.66 | 6.44 | 32.4 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19337
Centrosolar America | DP72 285 | 285 W Polycrystalline Module | UL 1703 | 285 | 252.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.41 | 44.32 | 7.91 | 36.02 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.53 | 35.44 | 6.33 | 32.3 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19026
Centrosolar America | E285 | 285 W Polycrystalline Module | UL 1703 | 285 | 254.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.876 | 72 | 1 | N | 8.52 | 44.35 | 7.91 | 36.03 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5287 | 35.7661 | 6.3872 | 32.9263 | Rack | Flat Plate | 0.97 | 1.934 | 1 | 0.19185
Centrosolar America | E285B | 285 W Polycrystalline Module, Black Frame | UL 1703 | 285 | 254.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.876 | 72 | 1 | N | 8.52 | 44.35 | 7.91 | 36.03 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5287 | 35.7661 | 6.3872 | 32.9263 | Rack | Flat Plate | 0.97 | 1.934 | 1 | 0.19185
Centrosolar America | EM60 285BB | 285 W Monocrystalline Module, Black backsheet, Black Frame | UL 1703 | 285 | 259.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065
Centrosolar America | EM60 285BW | 285 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065
Centrosolar America | EM60 285SW | 285 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065
Centrosolar America | TM6 285xx | 285 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 285 | 258.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.47 | 39.1 | 8.91 | 32 | 47.8 | -0.404 | 0.042 | -0.278 | -0.013 | -0.369 | 1.8 | 31.35 | 7.14 | 29.26 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.198
Centrosolar America | TM6S 285xx | 285 W Monocrystalline Module, where xx is a wildcard | UL 1703 | 285 | 258.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.47 | 39.1 | 8.91 | 32 | 47.8 | -0.404 | 0.042 | -0.278 | -0.013 | -0.369 | 1.8 | 31.35 | 7.14 | 29.26 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.198
Centrosolar America | DM72 290 | 290 W Monocrystalline Module | UL 1703 | 290 | 262.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 8.6 | 44.4 | 8 | 36.3 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.59 | 35.24 | 6.44 | 32.94 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19321
Centrosolar America | DP72 290 | 290 W Polycrystalline Module | UL 1703 | 290 | 256.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.52 | 44.46 | 8.02 | 36.16 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.55 | 35.58 | 6.42 | 32.42 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19017
Centrosolar America | E290 | 290 W Polycrystalline Module | UL 1703 | 290 | 259.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.61 | 44.5 | 8 | 36.25 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5461 | 35.9845 | 6.4599 | 33.1274 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
Centrosolar America | E290B | 290 W Polycrystalline Module, Black Frame | UL 1703 | 290 | 259.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.61 | 44.5 | 8 | 36.25 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5461 | 35.9845 | 6.4599 | 33.1274 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
Centrosolar America | EM60 290BW | 290 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 290 | 265.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.59 | 39.68 | 9.03 | 32.12 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 31.7777 | 7.2592 | 29.4719 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19064
Centrosolar America | EM60 290SW | 290 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 290 | 265.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.59 | 39.68 | 9.03 | 32.12 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 31.7777 | 7.2592 | 29.4719 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19064
Centrosolar America | TP7 290xx | 290 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 290 | 262 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.52 | 44.9 | 8.03 | 36.3 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.6 | 35.21 | 6.46 | 32.77 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19426
Centrosolar America | TP7S 290xx | 290 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 290 | 262 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.52 | 44.9 | 8.03 | 36.3 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.6 | 35.21 | 6.46 | 32.77 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19426
Centrosolar America | DM72 295 | 295 W Monocrystalline Module | UL 1703 | 295 | 267.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 8.7 | 44.7 | 8.1 | 36.5 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.61 | 35.44 | 6.52 | 33.12 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19342
Centrosolar America | DP72 295 | 295 W Polycrystalline Module | UL 1703 | 295 | 261.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.58 | 44.68 | 8.1 | 36.38 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.57 | 35.8 | 6.48 | 32.62 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19053
Centrosolar America | E295 | 295 W Polycrystalline Module | UL 1703 | 295 | 263.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6945 | 32.7533 | 6.7469 | 30.0578 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18814
Centrosolar America | E295B | 295 W Polycrystalline Module, Black Frame | UL 1703 | 295 | 263.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6945 | 32.7533 | 6.7469 | 30.0578 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18814
Centrosolar America | TP7 295xx | 295 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 295 | 266.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.62 | 45.1 | 8.12 | 36.5 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.62 | 35.4 | 6.53 | 32.95 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.1944
Centrosolar America | TP7S 295xx | 295 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 295 | 266.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.62 | 45.1 | 8.12 | 36.5 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.62 | 35.4 | 6.53 | 32.95 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.1944
Centrosolar America | CP72 300-C1 | 300 W Polycrystalline Module | UL 1703 | 300 | 271.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.79 | 45.3 | 8.12 | 36.5 | 45.4 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.53 | 35.71 | 6.48 | 32.96 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18212
Centrosolar America | CP72 300SW | 300 W Polycrystalline Module | UL 1703 | 300 | 273.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.52 | 46.47 | 8.12 | 36.97 | 43.2 | -0.47 | 0.08 | -0.35 | 0.005 | -0.47 | 1.62 | 36.42 | 6.51 | 33.53 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19667
Centrosolar America | DM72 300 | 300 W Monocrystalline Module | UL 1703 | 300 | 272.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 8.7 | 45 | 8.1 | 37.1 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.61 | 36.02 | 6.52 | 33.67 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19331
Centrosolar America | DP72 300 | 300 W Polycrystalline Module | UL 1703 | 300 | 266 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.63 | 44.82 | 8.21 | 36.52 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.59 | 35.94 | 6.57 | 32.74 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19048
Centrosolar America | E300 | 300 W Polycrystalline Module | UL 1703 | 300 | 268.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6986 | 33.2151 | 6.7634 | 30.4816 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18807
Centrosolar America | E300B | 300 W Polycrystalline Module, Black Frame | UL 1703 | 300 | 268.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6986 | 33.2151 | 6.7634 | 30.4816 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18807
Centrosolar America | TP7 300xx | 300 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 300 | 271.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.72 | 45.3 | 8.21 | 36.7 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.64 | 35.59 | 6.6 | 33.13 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19456
Centrosolar America | TP7S 300xx | 300 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 300 | 271.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.72 | 45.3 | 8.21 | 36.7 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.64 | 35.59 | 6.6 | 33.13 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19456
Centrosolar America | CP72 305-C1 | 305 W Polycrystalline Module | UL 1703 | 305 | 276.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 45.6 | 8.16 | 37.4 | 45.4 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.54 | 36.59 | 6.52 | 33.77 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18475
Centrosolar America | CP72 305SW | 305 W Polycrystalline Module | UL 1703 | 305 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.56 | 46.87 | 8.2 | 37.27 | 43.2 | -0.47 | 0.08 | -0.35 | 0.005 | -0.47 | 1.64 | 36.71 | 6.57 | 33.8 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19739
Centrosolar America | DM72 305 | 305 W Monocrystalline Module | UL 1703 | 305 | 276.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 8.8 | 45.4 | 8.2 | 37.2 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.64 | 36.12 | 6.61 | 34.06 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19422
Centrosolar America | DP72 305 | 305 W Polycrystalline Module | UL 1703 | 305 | 270.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.66 | 44.96 | 8.27 | 36.85 | 46.7 | -0.5 | 0.06 | -0.36 | 0.01 | -0.49 | 1.6 | 36.26 | 6.62 | 33.04 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19022
Centrosolar America | E305 | 305 W Polycrystalline Module | UL 1703 | 305 | 272.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.78 | 45.12 | 8.21 | 37.18 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.7049 | 33.6679 | 6.7882 | 30.8972 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18819
Centrosolar America | E305B | 305 W Polycrystalline Module, Black Frame | UL 1703 | 305 | 272.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.78 | 45.12 | 8.21 | 37.18 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.7049 | 33.6679 | 6.7882 | 30.8972 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18819
Centrosolar America | EP72 305BW | 305 W Polycrystalline Module, Black Frame | UL 1703 | 305 | 272.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.78 | 45.12 | 8.21 | 37.18 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.7049 | 33.6679 | 6.7882 | 30.8972 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18819
Centrosolar America | EP72 305SW | 305 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 305 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.04 | 45.18 | 8.42 | 36.23 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6234 | 35.9571 | 6.7282 | 33.7152 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138
Centrosolar America | TP7 305xx | 305 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 305 | 275.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.82 | 45.5 | 8.3 | 36.9 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.66 | 35.79 | 6.67 | 33.31 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19479
Centrosolar America | TP7S 305xx | 305 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 305 | 275.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.82 | 45.5 | 8.3 | 36.9 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.66 | 35.79 | 6.67 | 33.31 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19479
Centrosolar America | CM72 310-C1 | 310 W Monocrystalline Module | UL 1703 | 310 | 280.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9 | 46.1 | 8.33 | 37.2 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.56 | 36.59 | 6.55 | 34.06 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18413
Centrosolar America | CP72 310-C1 | 310 W Polycrystalline Module | UL 1703 | 310 | 280 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.08 | 45.8 | 8.22 | 37.7 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.55 | 36.89 | 6.56 | 34.04 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18445
Centrosolar America | CP72 310SW | 310 W Polycrystalline Module | UL 1703 | 310 | 282.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.6 | 47.27 | 8.27 | 37.56 | 43.2 | -0.47 | 0.08 | -0.35 | 0.005 | -0.47 | 1.65 | 37 | 6.63 | 34.06 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19694
Centrosolar America | DM72 310 | 310 W Monocrystalline Module | UL 1703 | 310 | 281.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 8.8 | 45.7 | 8.2 | 37.9 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.64 | 36.8 | 6.61 | 34.7 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19468
Centrosolar America | DP72 310 | 310 W Polycrystalline Module | UL 1703 | 310 | 279.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.7 | 45.18 | 8.31 | 37.3 | 46.5 | -0.4411 | 0.07403 | -0.339 | 0.009095 | -0.4456 | 1.65 | 35.96 | 6.73 | 34.02 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.1914
Centrosolar America | EP72 310BW | 310 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 310 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 45.65 | 8.49 | 36.54 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6369 | 36.2647 | 6.7841 | 34.0037 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19149
Centrosolar America | EP72 310SW | 310 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 310 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 45.65 | 8.49 | 36.54 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6369 | 36.2647 | 6.7841 | 34.0037 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19149
Centrosolar America | TP7 310xx | 310 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 310 | 280.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.9 | 45.7 | 8.39 | 37.1 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.67 | 35.98 | 6.74 | 33.49 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19383
Centrosolar America | TP7S 310xx | 310 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 310 | 280.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.9 | 45.7 | 8.39 | 37.1 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.67 | 35.98 | 6.74 | 33.49 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19383
Centrosolar America | CM72 315-C1 | 315 W Monocrystalline Module | UL 1703 | 315 | 284.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 46.1 | 8.38 | 37.6 | 45.7 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.57 | 36.99 | 6.59 | 34.42 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18436
Centrosolar America | CP72 315-C1 | 315 W Polycrystalline Module | UL 1703 | 315 | 284.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.17 | 45.9 | 8.31 | 37.9 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.56 | 37.08 | 6.64 | 34.22 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18363
Centrosolar America | CP72 315SW | 315 W Polycrystalline Module | UL 1703 | 315 | 287.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.01 | 45.91 | 8.49 | 37.18 | 43.2 | -0.47 | 0.08 | -0.35 | 0.005 | -0.47 | 1.69 | 36.62 | 6.81 | 33.72 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19647
Centrosolar America | DM72 315 | 315 W Monocrystalline Module | UL 1703 | 315 | 286.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 8.9 | 46 | 8.3 | 38 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.66 | 36.9 | 6.69 | 34.79 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19446
Centrosolar America | DP72 315 | 315 W Polycrystalline Module | UL 1703 | 315 | 284.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.72 | 45.32 | 8.38 | 37.58 | 46.5 | -0.4411 | 0.07403 | -0.339 | 0.009095 | -0.4456 | 1.67 | 36.23 | 6.79 | 34.27 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19208
Centrosolar America | EP72 315BW | 315 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 315 | 287.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.12 | 45.75 | 8.56 | 36.81 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6504 | 36.5327 | 6.84 | 34.255 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1914
Centrosolar America | EP72 315SW | 315 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 315 | 287.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.12 | 45.75 | 8.56 | 36.81 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6504 | 36.5327 | 6.84 | 34.255 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1914
Centrosolar America | SP72 315SW | 315 W Polycrystalline Module | UL 1703 | 315 | 282.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.25 | 44.8 | 8.66 | 36.4 | 48.6 | -0.4192 | 0.0557 | -0.3164 | -0.0035 | -0.4152 | 1.71 | 36.21 | 6.81 | 33.09 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19657
Centrosolar America | TM7 315SW | 315 W Monocrystalline Module | UL 1703 | 315 | 286.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.05 | 45.5 | 8.49 | 37.1 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.72 | 36.35 | 6.81 | 33.97 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19848
Centrosolar America | TM7S 315SW | 315 W Monocrystalline Module | UL 1703 | 315 | 286.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.05 | 45.5 | 8.49 | 37.1 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.72 | 36.35 | 6.81 | 33.97 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19848
Centrosolar America | TP7 315xx | 315 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 315 | 285.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.98 | 45.9 | 8.48 | 37.3 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.69 | 36.18 | 6.82 | 33.67 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19411
Centrosolar America | TP7S 315xx | 315 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 315 | 285.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.98 | 45.9 | 8.48 | 37.3 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.69 | 36.18 | 6.82 | 33.67 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19411
Centrosolar America | CM72 320-C1 | 320 W Monocrystalline Module | UL 1703 | 320 | 288.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.08 | 46.3 | 8.46 | 37.8 | 45.7 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.59 | 37.18 | 6.65 | 34.61 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18474
Centrosolar America | CM72 320SW | 320 W Monocrystalline Module | UL 1703 | 320 | 288.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.99 | 46.46 | 8.61 | 37.27 | 43.6 | -0.52 | 0.07 | -0.37 | -0.02 | -0.5 | 1.74 | 36.35 | 6.96 | 34.01 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19765
Centrosolar America | CP72 320-C1 | 320 W Polycrystalline Module | UL 1703 | 320 | 289.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.2 | 46.2 | 8.33 | 38.4 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.57 | 37.57 | 6.65 | 34.67 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18433
Centrosolar America | CP72 320SW | 320 W Polycrystalline Module | UL 1703 | 320 | 291.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.1 | 46.15 | 8.58 | 37.36 | 43.2 | -0.47 | 0.08 | -0.35 | 0.005 | -0.47 | 1.71 | 36.8 | 6.88 | 33.88 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19665
Centrosolar America | DM72 320 | 320 W Monocrystalline Module | UL 1703 | 320 | 290.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 8.9 | 46.3 | 8.3 | 38.6 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.66 | 37.48 | 6.69 | 35.34 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19443
Centrosolar America | DP72 320 | 320 W Polycrystalline Module | UL 1703 | 320 | 288.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.76 | 45.5 | 8.42 | 38 | 46.5 | -0.4411 | 0.07403 | -0.339 | 0.009095 | -0.4456 | 1.68 | 36.64 | 6.82 | 34.66 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19236
Centrosolar America | EM72 320BW | 320 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 320 | 292.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 46.31 | 8.65 | 37 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6892 | 36.1108 | 6.9511 | 33.994 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
Centrosolar America | EM72 320SW | 320 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 320 | 292.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 46.31 | 8.65 | 37 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6892 | 36.1108 | 6.9511 | 33.994 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
Centrosolar America | EP72 320BW | 320 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 320 | 291.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.24 | 45.94 | 8.62 | 37.13 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6619 | 36.8503 | 6.888 | 34.5528 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138
Centrosolar America | EP72 320SW | 320 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 320 | 291.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.24 | 45.94 | 8.62 | 37.13 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6619 | 36.8503 | 6.888 | 34.5528 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138
Centrosolar America | SP72 320SW | 320 W Polycrystalline Module | UL 1703 | 320 | 287.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.38 | 44.9 | 8.78 | 36.4 | 48.6 | -0.4192 | 0.0557 | -0.3164 | -0.0035 | -0.4152 | 1.73 | 36.21 | 6.91 | 33.09 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19576
Centrosolar America | TM7 320SW | 320 W Monocrystalline Module | UL 1703 | 320 | 291 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.15 | 45.6 | 8.58 | 37.3 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.74 | 36.54 | 6.89 | 34.15 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19869
Centrosolar America | TM7S 320SW | 320 W Monocrystalline Module | UL 1703 | 320 | 291 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.15 | 45.6 | 8.58 | 37.3 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.74 | 36.54 | 6.89 | 34.15 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19869
Centrosolar America | TP7 320xx | 320 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 320 | 289.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 9.06 | 46.1 | 8.57 | 37.5 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.71 | 36.37 | 6.89 | 33.85 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19435
Centrosolar America | TP7S 320xx | 320 W Polycrystalline Module, where xx is a wildcard | UL 1703 | 320 | 289.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 9.06 | 46.1 | 8.57 | 37.5 | 47.5 | -0.408 | 0.055 | -0.31 | -0.0003 | -0.407 | 1.71 | 36.37 | 6.89 | 33.85 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19435
Centrosolar America | CM72 325SW | 325 W Monocrystalline Module | UL 1703 | 325 | 292.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.24 | 45.65 | 8.74 | 37.22 | 43.6 | -0.52 | 0.07 | -0.37 | -0.02 | -0.5 | 1.77 | 36.3 | 7.06 | 33.96 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1977
Centrosolar America | CP72 325SW | 325 W Polycrystalline Module | UL 1703 | 325 | 296.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.19 | 46.38 | 8.68 | 37.52 | 43.2 | -0.47 | 0.08 | -0.35 | 0.005 | -0.47 | 1.73 | 36.96 | 6.96 | 34.03 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19674
Centrosolar America | DM72 325 | 325 W Monocrystalline Module | UL 1703 | 325 | 295.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 9 | 46.6 | 8.4 | 38.7 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.68 | 37.58 | 6.77 | 35.43 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19426
Centrosolar America | DP72 325 | 325 W Polycrystalline Module | UL 1703 | 325 | 293.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.78 | 45.65 | 8.48 | 38.32 | 46.5 | -0.4411 | 0.07403 | -0.339 | 0.009095 | -0.4456 | 1.69 | 36.95 | 6.87 | 34.95 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19214
Centrosolar America | EM72 325BW | 325 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 325 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.11 | 46.54 | 8.76 | 37.11 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7107 | 36.2181 | 7.0395 | 34.0951 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19064
Centrosolar America | EM72 325SW | 325 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 325 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.11 | 46.54 | 8.76 | 37.11 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7107 | 36.2181 | 7.0395 | 34.0951 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19064
Centrosolar America | EP72 325BW | 325 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 325 | 296.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.28 | 46.31 | 8.72 | 37.28 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6812 | 36.9992 | 6.9679 | 34.6924 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19139
Centrosolar America | EP72 325SW | 325 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 325 | 296.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.28 | 46.31 | 8.72 | 37.28 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6812 | 36.9992 | 6.9679 | 34.6924 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19139
Centrosolar America | TM7 325SW | 325 W Monocrystalline Module | UL 1703 | 325 | 295.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.25 | 45.8 | 8.67 | 37.5 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.76 | 36.74 | 6.96 | 34.34 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19896
Centrosolar America | TM7S 325SW | 325 W Monocrystalline Module | UL 1703 | 325 | 295.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.25 | 45.8 | 8.67 | 37.5 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.76 | 36.74 | 6.96 | 34.34 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19896
Centrosolar America | CM72 330SW | 330 W Monocrystalline Module | UL 1703 | 330 | 297.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.32 | 45.92 | 8.85 | 37.38 | 43.6 | -0.52 | 0.07 | -0.37 | -0.02 | -0.5 | 1.79 | 36.46 | 7.15 | 34.11 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19777
Centrosolar America | CP72 330SW | 330 W Polycrystalline Module | UL 1703 | 330 | 301.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.28 | 46.62 | 8.78 | 37.68 | 43.2 | -0.47 | 0.08 | -0.35 | 0.005 | -0.47 | 1.75 | 37.12 | 7.04 | 34.17 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19685
Centrosolar America | DM72 330 | 330 W Monocrystalline Module | UL 1703 | 330 | 300.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 9 | 46.9 | 8.4 | 39.3 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.68 | 38.16 | 6.77 | 35.98 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19427
Centrosolar America | DP72 330 | 330 W Polycrystalline Module | UL 1703 | 330 | 298.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.82 | 45.8 | 8.54 | 38.62 | 46.5 | -0.4411 | 0.07403 | -0.339 | 0.009095 | -0.4456 | 1.7 | 37.24 | 6.92 | 35.22 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19184
Centrosolar America | EM72 330BW | 330 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 330 | 301.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.29 | 46.64 | 8.79 | 37.55 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7166 | 36.6475 | 7.0636 | 34.4993 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19063
Centrosolar America | EM72 330SW | 330 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 330 | 301.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.29 | 46.64 | 8.79 | 37.55 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7166 | 36.6475 | 7.0636 | 34.4993 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19063
Centrosolar America | EP72 330BW | 330 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 330 | 301.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.35 | 46.65 | 8.78 | 37.58 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6928 | 37.2969 | 7.0158 | 34.9715 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19132
Centrosolar America | EP72 330SW | 330 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 330 | 301.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.35 | 46.65 | 8.78 | 37.58 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6928 | 37.2969 | 7.0158 | 34.9715 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19132
Centrosolar America | SM72 330SW | 330 W Monocrystalline Module | UL 1703 | 330 | 297.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.48 | 45.6 | 8.62 | 38.3 | 48.5 | -0.4146 | 0.0498 | -0.3113 | -0.0047 | -0.4109 | 1.73 | 38.23 | 6.88 | 34.97 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20042
Centrosolar America | TM7 330SW | 330 W Monocrystalline Module | UL 1703 | 330 | 300.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.32 | 46.1 | 8.73 | 37.8 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.77 | 37.03 | 7.01 | 34.61 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19862
Centrosolar America | TM7S 330SW | 330 W Monocrystalline Module | UL 1703 | 330 | 300.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.32 | 46.1 | 8.73 | 37.8 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.77 | 37.03 | 7.01 | 34.61 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19862
Centrosolar America | CM72 335SW | 335 W Monocrystalline Module | UL 1703 | 335 | 302.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.41 | 46.04 | 8.96 | 37.47 | 43.6 | -0.52 | 0.07 | -0.37 | -0.02 | -0.5 | 1.82 | 36.55 | 7.24 | 34.19 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19857
Centrosolar America | DM72 335 | 335 W Monocrystalline Module | UL 1703 | 335 | 304.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9443 | 72 | 1 | N | 9.1 | 47.2 | 8.5 | 39.5 | 45.6 | -0.4319 | 0.07499 | -0.324 | 0.009659 | -0.4242 | 1.7 | 38.36 | 6.85 | 36.16 | Rack | Flat Plate | 0.992 | 1.96 | 1 | 0.19466
Centrosolar America | EM72 335BW | 335 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.33 | 46.75 | 8.83 | 37.94 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7244 | 37.0282 | 7.0957 | 34.8576 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1906
Centrosolar America | EM72 335SW | 335 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.33 | 46.75 | 8.83 | 37.94 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7244 | 37.0282 | 7.0957 | 34.8576 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1906
Centrosolar America | EP72 335BW | 335 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 335 | 306 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.47 | 46.83 | 8.84 | 37.9 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7043 | 37.6145 | 7.0638 | 35.2693 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19137
Centrosolar America | EP72 335SW | 335 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 335 | 306 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.47 | 46.83 | 8.84 | 37.9 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7043 | 37.6145 | 7.0638 | 35.2693 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19137
Centrosolar America | SM72 335SW | 335 W Monocrystalline Module | UL 1703 | 335 | 302 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.6 | 45.7 | 8.73 | 38.4 | 48.5 | -0.4146 | 0.0498 | -0.3113 | -0.0047 | -0.4109 | 1.75 | 38.33 | 6.97 | 35.06 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20023
Centrosolar America | TM7 335SW | 335 W Monocrystalline Module | UL 1703 | 335 | 305.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.37 | 46.4 | 8.79 | 38.1 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.79 | 37.33 | 7.05 | 34.88 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19946
Centrosolar America | TM7S 335SW | 335 W Monocrystalline Module | UL 1703 | 335 | 305.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.37 | 46.4 | 8.79 | 38.1 | 46.5 | -0.41 | 0.04 | -0.29 | -0.02 | -0.38 | 1.79 | 37.33 | 7.05 | 34.88 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19946
Centrosolar America | EM72 340BW | 340 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 340 | 310.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.41 | 46.91 | 8.91 | 38.17 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.74 | 37.2526 | 7.16 | 35.0689 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19065
Centrosolar America | EM72 340SW | 340 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 340 | 310.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.41 | 46.91 | 8.91 | 38.17 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.74 | 37.2526 | 7.16 | 35.0689 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19065
Centrosolar America | SM72 340SW | 340 W Monocrystalline Module | UL 1703 | 340 | 306.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.72 | 45.8 | 8.84 | 38.5 | 48.5 | -0.4146 | 0.0498 | -0.3113 | -0.0047 | -0.4109 | 1.77 | 38.43 | 7.06 | 35.15 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20006
Centrosolar America | EM72 345BW | 345 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.48 | 47.13 | 8.99 | 38.38 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7556 | 37.4576 | 7.2243 | 35.2619 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19061
Centrosolar America | EM72 345SW | 345 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.48 | 47.13 | 8.99 | 38.38 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7556 | 37.4576 | 7.2243 | 35.2619 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19061
Centrosolar America | EM72 350BW | 350 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.59 | 47.64 | 9.09 | 38.51 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7752 | 37.5845 | 7.3046 | 35.3813 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
Centrosolar America | EM72 350SW | 350 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.59 | 47.64 | 9.09 | 38.51 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7752 | 37.5845 | 7.3046 | 35.3813 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
CertainTeed | Apollo II - 67 | 67 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 67 | 60.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.42 | 14 | 1 | Y | 9.34 | 9.35 | 8.9 | 7.56 | 48.52 | -0.373 | 0.048 | -0.275 |  |  | 1.768 | 7.502 | 7.139 | 6.916 | [6 empty] | 2019-11-01
CertainTeed | Apollo Tile II - 67 | 67 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 67 | 61.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.42 | 14 | 1 | Y | 9.34 | 9.35 | 8.9 | 7.56 | 47.74 | -0.373 | 0.048 | -0.275 |  |  | 1.768 | 7.502 | 7.139 | 6.916 | [6 empty] | 2019-11-01
CertainTeed | Apollo II - 70x | 70 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 70 | 59.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.53 | 14 | 1 | Y | 9.417 | 9.571 | 9.028 | 7.767 | 61.75 | -0.371 | 0.046 | -0.273 |  |  | 1.7588 | 7.3592 | 7.1339 | 6.5329 | [6 empty] | 2020-03-11
CertainTeed | Apollo Tile II - 70x | 70 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 70 | 61 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.54 | 14 | 1 | Y | 9.417 | 9.571 | 9.028 | 7.767 | 57.03 | -0.371 | 0.046 | -0.273 |  |  | 1.7588 | 7.3592 | 7.1358 | 6.6531 | [6 empty] | 2020-03-11
CertainTeed | Apollo II - 71x | 71 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 71 | 60.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.53 | 14 | 1 | Y | 9.455 | 9.641 | 9.085 | 7.82 | 61.75 | -0.371 | 0.046 | -0.273 |  |  | 1.7699 | 7.4095 | 7.1789 | 6.5775 | [6 empty] | 2020-03-11
CertainTeed | Apollo Tile II - 71x | 71 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 71 | 61.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.54 | 14 | 1 | Y | 9.455 | 9.641 | 9.085 | 7.82 | 57.03 | -0.371 | 0.046 | -0.273 |  |  | 1.7699 | 7.4095 | 7.1809 | 6.6985 | [6 empty] | 2020-03-11
CertainTeed | Apollo II - 72x | 72 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 72 | 61.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.53 | 14 | 1 | Y | 9.493 | 9.71 | 9.137 | 7.886 | 61.75 | -0.371 | 0.046 | -0.273 |  |  | 1.78 | 7.472 | 7.22 | 6.633 | [6 empty] | 2020-03-11
CertainTeed | Apollo Tile II - 72x | 72 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 72 | 62.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.54 | 14 | 1 | Y | 9.493 | 9.71 | 9.137 | 7.886 | 57.03 | -0.371 | 0.046 | -0.273 |  |  | 1.78 | 7.472 | 7.222 | 6.755 | [6 empty] | 2020-03-11
CertainTeed | Apollo II - 73x | 73 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 73 | 62.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.53 | 14 | 1 | Y | 9.531 | 9.766 | 9.192 | 7.939 | 61.75 | -0.371 | 0.046 | -0.273 |  |  | 1.7907 | 7.5222 | 7.2635 | 6.6776 | [6 empty] | 2020-03-11
CertainTeed | Apollo Tile II - 73x | 73 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 73 | 63.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.54 | 14 | 1 | Y | 9.531 | 9.766 | 9.192 | 7.939 | 57.03 | -0.371 | 0.046 | -0.273 |  |  | 1.7907 | 7.5222 | 7.2655 | 6.8004 | [6 empty] | 2020-03-11
CertainTeed | Apollo II - 74x | 74 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 74 | 63.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.53 | 14 | 1 | Y | 9.579 | 9.863 | 9.268 | 8.005 | 61.75 | -0.371 | 0.046 | -0.273 |  |  | 1.8055 | 7.5848 | 7.3235 | 6.7331 | [6 empty] | 2020-03-11
CertainTeed | Apollo Tile II - 74x | 74 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 74 | 64.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.54 | 14 | 1 | Y | 9.579 | 9.863 | 9.268 | 8.005 | 57.03 | -0.371 | 0.046 | -0.273 |  |  | 1.8055 | 7.5848 | 7.3255 | 6.8569 | [6 empty] | 2020-03-11
CertainTeed | Apollo II - 75x | 75 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 75 | 64.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.53 | 14 | 1 | Y | 9.616 | 9.919 | 9.328 | 8.058 | 61.75 | -0.371 | 0.046 | -0.273 |  |  | 1.8172 | 7.635 | 7.3709 | 6.7777 | [6 empty] | 2020-03-11
CertainTeed | Apollo Tile II - 75x | 75 W, 14 cell monocrystalline module, black backsheet, 600V max system Vdc | UL 1703 | 75 | 65.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.54 | 14 | 1 | Y | 9.616 | 9.919 | 9.328 | 8.058 | 57.03 | -0.371 | 0.046 | -0.273 |  |  | 1.8172 | 7.635 | 7.373 | 6.9023 | [6 empty] | 2020-03-11
CertainTeed | CT280M10-02 | 280 W Monocrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.34 | 39.1 | 8.88 | 31.53 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.768 | 30.2676 | 7.112 | 28.4983 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19111
CertainTeed | CT280M11-02 | 280 W Monocrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.34 | 39.1 | 8.88 | 31.53 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.768 | 30.2676 | 7.112 | 28.4983 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19111
CertainTeed | CT285M10-01 | 285 W Monocrystalline Module | UL 1703 | 285 | 258.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.5 | 38.7 | 8.9 | 31.8 | 46.04 | -0.4316 | 0.034895 | -0.2928 | -0.02734 | -0.40682 | 1.7033 | 32.0065 | 7.1312 | 29.5286 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19128
CertainTeed | CT285M10-02 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.48 | 39.43 | 8.97 | 31.76 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7859 | 30.4884 | 7.1841 | 28.7062 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19105
CertainTeed | CT285M11-01 | 285 W Monocrystalline Module | UL 1703 | 285 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.5 | 38.7 | 8.9 | 31.8 | 46.48 | -0.43723 | 0.048604 | -0.30206 | -0.029573 | -0.40958 | 1.6864 | 31.4952 | 7.1648 | 28.6505 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18637
CertainTeed | CT290M10-01 | 290 W Monocrystalline Module | UL 1703 | 290 | 263.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.7 | 38.8 | 9.1 | 32 | 46.04 | -0.4316 | 0.034895 | -0.2928 | -0.02734 | -0.40682 | 1.7415 | 32.2078 | 7.2915 | 29.7143 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19342
CertainTeed | CT290M10-02 | 290 W Monocrystalline Module | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.62 | 39.77 | 9.06 | 32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8038 | 30.7188 | 7.2562 | 28.9231 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19107
CertainTeed | CT290M11-01 | 290 W Monocrystalline Module | UL 1703 | 290 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.7 | 38.8 | 9.1 | 32 | 46.48 | -0.43723 | 0.048604 | -0.30206 | -0.029573 | -0.40958 | 1.7243 | 31.6933 | 7.3258 | 28.8307 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18845
CertainTeed | CT290M11-02 | 290 W Monocrystalline Module | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.62 | 39.77 | 9.06 | 32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8038 | 30.7188 | 7.2562 | 28.9231 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19107
CertainTeed | CT295M10-01 | 295 W Monocrystalline Module | UL 1703 | 295 | 268.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.8 | 39 | 9.2 | 32.1 | 46.04 | -0.43043 | 0.034722 | -0.2928 | -0.027282 | -0.40682 | 1.757 | 32.3084 | 7.3561 | 29.8071 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19242
CertainTeed | CT295M10-02 | 295 W Monocrystalline Module | UL 1703 | 295 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.814 | 31.2838 | 7.323 | 29.5803 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
CertainTeed | CT295M11-01 | 295 W Monocrystalline Module | UL 1703 | 295 | 267.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.8 | 39 | 9.2 | 32.1 | 46.48 | -0.43723 | 0.048604 | -0.30206 | -0.029573 | -0.40958 | 1.7433 | 31.7923 | 7.4064 | 28.9208 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18787
CertainTeed | CT295M11-02 | 295 W Monocrystalline Module | UL 1703 | 295 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.814 | 31.2838 | 7.323 | 29.5803 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
CertainTeed | CT300M10-01 | 300 W Monocrystalline Module | UL 1703 | 300 | 272.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.9 | 39.1 | 9.3 | 32.3 | 46.04 | -0.4316 | 0.034895 | -0.2928 | -0.02734 | -0.40682 | 1.7798 | 32.5097 | 7.4517 | 29.9929 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19287
CertainTeed | CT300M10-02 | 300 W Monocrystalline Module | UL 1703 | 300 | 275.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8319 | 31.5167 | 7.395 | 29.8005 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19245
CertainTeed | CT300M10-03 | 300W 60 cell monocrystalline module, black frame, white backsheet | UL 1703 | 300 | 277.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 |  | N | 9.75 | 40.3 | 9.24 | 32.5 | 45.6 | -0.373 | 0.045 | -0.279 | 0.007 | -0.381 | 1.8249 | 32.2985 | 7.385 | 30.5024 | [6 empty] | 2018-04-02
CertainTeed | CT300M11-01 | 300 W Monocrystalline Module | UL 1703 | 300 | 270.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.9 | 39.1 | 9.3 | 32.3 | 46.59 | -0.46109 | 0.044103 | -0.32861 | -0.025027 | -0.44381 | 1.7001 | 31.9924 | 7.4785 | 28.8137 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1813
CertainTeed | CT300M11-02 | 300 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 300 | 274 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.575 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 48.62 | -0.374 | 0.042 | -0.281 | -0.005 | -0.381 | 1.79 | 31.682 | 7.123 | 29.819 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18904 |  | 2019-08-01
CertainTeed | CT300M11-03 | 300 W, 60 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.606 | 60 |  | N | 9.75 | 40.3 | 9.24 | 32.5 | 46.06 | -0.379 | 0.043 | -0.282 | -0.002 | -0.378 | 1.8221 | 31.3907 | 7.2586 | 29.7123 | [6 empty] | 2018-08-01
CertainTeed | CT305M10-02 | 305 W Monocrystalline Module | UL 1703 | 305 | 279.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 10.0618 | 40.792 | 9.3191 | 32.7286 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8475 | 31.7578 | 7.4583 | 30.0285 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
CertainTeed | CT305M11-02 | 305 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 305 | 278.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.575 | 60 | 1 | N | 10.06 | 40.79 | 9.3 | 32.7 | 48.62 | -0.374 | 0.042 | -0.281 | -0.005 | -0.381 | 1.8016 | 31.8966 | 7.1693 | 30.021 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18841 |  | 2019-08-01
CertainTeed | CT310HC11-04 | 310 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 285.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.609 | 60 | 2 | N | 9.95 | 39.58 | 9.51 | 32.58 | 47.62 | -0.354 | 0.043 | -0.275 | 1.795 | 31.8775 | 1.795 | 31.8775 | 7.2643 | 30.4795 | [6 empty] | 2019-09-03
CertainTeed | CT310M11-02 | 310 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 310 | 283.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.575 | 60 | 1 | N | 10.21 | 41.14 | 9.4 | 33 | 48.62 | -0.374 | 0.042 | -0.281 |  |  | 1.821 | 32.1892 | 7.2463 | 30.2964 | [6 empty] | 2019-08-01
CertainTeed | CT315HC11-04 | 315 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 315 | 290.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.609 | 60 | 2 | N | 10.04 | 39.74 | 9.6 | 32.79 | 47.62 | -0.354 | 0.043 | -0.275 | 1.812 | 32.083 | 1.812 | 32.083 | 7.333 | 30.676 | [6 empty] | 2019-09-03
CertainTeed | CT315M11-02 | 315 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 315 | 288.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.575 | 60 | 1 | N | 10.37 | 41.49 | 9.5 | 33.2 | 48.62 | -0.374 | 0.042 | -0.281 |  |  | 1.8404 | 32.3843 | 7.3234 | 30.48 | [6 empty] | 2019-08-01
CertainTeed | CT320HC11-04 | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 295.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.609 | 60 | 2 | N | 10.13 | 39.92 | 9.69 | 33.01 | 47.62 | -0.354 | 0.043 | -0.275 | 1.829 | 32.2983 | 1.829 | 32.2983 | 7.4017 | 30.8818 | [6 empty] | 2019-09-03
CertainTeed | CT320P00-01 |  | UL 1703 | 320 | 293.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.81 | 72 |  |  | 9.0 | 45.7 | 8.8 | 36.4 | 45.5 | -0.4 | 0.04 | -0.29 | -0.001 | -0.16 | 1.58 | 36.5 | 7.01 | 32.4 | [6 empty] | 2017-09-01 | 2018-04-02
CertainTeed | CT325HC11-04 | 325 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 325 | 294.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 60 | 2 | N | 10.43 | 40.1 | 9.93 | 32.71 | 48.5 | -0.4034 | 0.0686 | -0.3162 |  |  | 2.39 | 32.6 | 7.47 | 29.95 | [6 empty] | 2020-01-21
CertainTeed | CT325P00-01 |  | UL 1703 | 325 | 298.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.81 | 72 |  |  | 9.1 | 45.9 | 8.8 | 36.6 | 45.5 | -0.4 | 0.04 | -0.29 | -0.001 | -0.16 | 1.58 | 36.5 | 7.01 | 32.4 | [6 empty] | 2017-09-01 | 2018-04-02
CertainTeed | CT330HC11-04 | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 330 | 299.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 60 | 2 | N | 10.51 | 40.27 | 10.02 | 32.91 | 48.5 | -0.4034 | 0.0686 | -0.3162 |  |  | 2.4117 | 32.7993 | 7.5377 | 30.1331 | [6 empty] | 2020-01-21
CertainTeed | CT335HC11-04 | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 335 | 304.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 60 | 2 | N | 10.6 | 40.44 | 10.11 | 33.11 | 48.5 | -0.4034 | 0.0686 | -0.3162 |  |  | 2.4333 | 32.9987 | 7.6054 | 30.3162 | [6 empty] | 2020-01-21
CertainTeed | CT350M00-01 |  | UL 1703 | 350 | 321.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 72 |  |  | 9.6 | 47.1 | 9.0 | 38.7 | 45.6 | -0.4 | 0.039 | -0.29 | -0.0023 | -0.164 | 1.78 | 37.1 | 7.45 | 34.1 | [6 empty] | 2017-09-01 | 2018-04-02
CertainTeed | CT350M10-01 |  | UL 1703 | 350 | 321.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 72 |  |  | 9.6 | 47.1 | 9.0 | 38.7 | 45.6 | -0.4 | 0.039 | -0.29 | -0.0023 | -0.164 | 1.78 | 37.1 | 7.45 | 34.1 | [6 empty] | 2017-09-01 | 2018-04-02
CertainTeed | CT355M00-01 |  | UL 1703 | 355 | 326.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 72 |  |  | 9.7 | 47.3 | 9.1 | 38.9 | 45.6 | -0.4 | 0.039 | -0.29 | -0.0023 | -0.164 | 1.78 | 37.1 | 7.45 | 34.1 | [6 empty] | 2017-09-01 | 2018-04-02
CertainTeed | CT355M10-01 |  | UL 1703 | 355 | 326.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 72 |  |  | 9.7 | 47.3 | 9.1 | 38.9 | 45.6 | -0.4 | 0.039 | -0.29 | -0.0023 | -0.164 | 1.78 | 37.1 | 7.45 | 34.1 | [6 empty] | 2017-09-01 | 2018-04-02
CertainTeed | CT355M10-02 | 355 W Monocrystalline Module | UL 1703 | 355 | 325.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.8985 | 47.4657 | 9.2082 | 38.5524 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8182 | 37.5082 | 7.381 | 35.3921 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
CertainTeed | CT355M10-03 | 355 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 324.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 | 1 | N | 9.64 | 47 | 9.04 | 39.3 | 47.21 | -0.385 | 0.043 | -0.288 | -0.006 | -0.38 | 1.7813 | 36.4364 | 7.2132 | 34.4219 | [6 empty] | 2018-04-02 | 2019-12-02
CertainTeed | CT355M11-02 | 355 W Monocrystalline Module | UL 1703 | 355 | 325.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.8985 | 47.4657 | 9.2082 | 38.5524 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8182 | 37.5082 | 7.381 | 35.3921 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
CertainTeed | CT355M11-03 | 355 W, 72 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 1703 | 355 | 327.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 |  | N | 9.64 | 47 | 9.04 | 39.3 | 45.73 | -0.376 | 0.044 | -0.281 | 0.006 | -0.382 | 1.8239 | 37.8389 | 7.2968 | 35.7412 | [6 empty] | 2018-08-01
CertainTeed | CT360M00-01 |  | UL 1703 | 360 | 331.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 72 |  |  | 9.8 | 47.4 | 9.2 | 39.1 | 45.6 | -0.4 | 0.039 | -0.29 | -0.0023 | -0.164 | 1.78 | 37.1 | 7.45 | 34.1 | [6 empty] | 2017-09-01 | 2018-04-02
CertainTeed | CT360M10-01 |  | UL 1703 | 360 | 331.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 72 |  |  | 9.8 | 47.4 | 9.2 | 39.1 | 45.6 | -0.4 | 0.039 | -0.29 | -0.0023 | -0.164 | 1.78 | 37.1 | 7.45 | 34.1 | [6 empty] | 2017-09-01 | 2018-04-02
CertainTeed | CT360M10-02 | 360 W Monocrystalline Module | UL 1703 | 360 | 330.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.9876 | 47.5606 | 9.3193 | 38.6295 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8401 | 37.5832 | 7.47 | 35.4629 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
CertainTeed | CT360M10-03 | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 329.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 | 1 | N | 9.67 | 47.4 | 9.07 | 39.7 | 47.21 | -0.385 | 0.043 | -0.288 | -0.006 | -0.38 | 1.7872 | 36.8073 | 7.2371 | 34.7723 | [6 empty] | 2018-04-02 | 2019-12-02
CertainTeed | CT360M11-02 | 360 W, 72 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 360 | 328.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 9.99 | 47.56 | 9.32 | 38.63 | 48.62 | -0.374 | 0.042 | -0.281 | -0.005 | -0.381 | 1.771 | 37.843 | 7.092 | 35.551 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18617 |  | 2019-08-01
CertainTeed | CT360M11-03 | 360 W, 72 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 1703 | 360 | 332.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 |  | N | 9.67 | 47.4 | 9.07 | 39.7 | 45.73 | -0.376 | 0.044 | -0.281 | 0.006 | -0.382 | 1.83 | 38.224 | 7.321 | 36.105 | [6 empty] | 2018-08-01
CertainTeed | CT365M10-02 | 365 W, 72 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 365 | 335.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 10.08 | 47.66 | 9.43 | 38.71 | 47.39 | -0.371 | 0.039 | -0.281 | -0.005 | -0.381 | 1.801 | 38.045 | 7.209 | 35.807 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18772 |  | 2019-08-01
CertainTeed | CT365M10-03 | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 334.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 | 1 | N | 9.71 | 47.8 | 9.11 | 40.1 | 47.21 | -0.385 | 0.043 | -0.288 |  |  | 1.7951 | 37.1781 | 7.2691 | 35.1226 | [6 empty] | 2019-12-02
CertainTeed | CT365M11-02 | 365 W, 72 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 365 | 333.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 10.08 | 47.66 | 9.43 | 38.71 | 48.62 | -0.374 | 0.042 | -0.281 | -0.005 | -0.381 | 1.7862 | 37.9116 | 7.1529 | 35.6154 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18553 |  | 2019-08-01
CertainTeed | CT370M00-04 | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 345 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 9.9 | 47.9 | 9.3 | 39.8 | 43.54 | -0.376 | 0.042 | -0.276 | 1.849 | 37.8288 | 1.849 | 37.8288 | 7.456 | 36.1853 | [6 empty] | 2019-09-03
CertainTeed | CT370M10-02 | 370 W, 72 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 370 | 340.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 10.17 | 47.75 | 9.5 | 38.8 | 47.39 | -0.371 | 0.039 | -0.281 |  |  | 1.8144 | 38.1335 | 7.2625 | 35.8903 | [6 empty] | 2019-08-01
CertainTeed | CT370M10-03 | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 339 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.923 | 72 | 1 | N | 9.74 | 48.2 | 9.14 | 40.5 | 47.21 | -0.385 | 0.043 | -0.288 |  |  | 1.801 | 37.549 | 7.293 | 35.473 | [6 empty] | 2019-12-02
CertainTeed | CT370M11-02 | 370 W, 72 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 370 | 338.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 10.17 | 47.75 | 9.5 | 38.8 | 48.62 | -0.374 | 0.042 | -0.281 |  |  | 1.8052 | 38.0095 | 7.229 | 35.7075 | [6 empty] | 2019-08-01
CertainTeed | CT375M00-04 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 349.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 9.9 | 48.2 | 9.3 | 40.2 | 43.54 | -0.376 | 0.042 | -0.276 | 1.849 | 38.209 | 1.849 | 38.209 | 7.456 | 36.549 | [6 empty] | 2019-09-03
CertainTeed | CT375M10-02 | 375 W, 72 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 375 | 344.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 10.26 | 47.85 | 9.7 | 38.9 | 47.39 | -0.371 | 0.039 | -0.281 |  |  | 1.8526 | 38.2317 | 7.4154 | 35.9828 | [6 empty] | 2019-08-01
CertainTeed | CT375M11-02 | 375 W, 72 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 375 | 342.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 10.26 | 47.85 | 9.7 | 38.9 | 48.62 | -0.374 | 0.042 | -0.281 |  |  | 1.8432 | 38.1075 | 7.3812 | 35.7995 | [6 empty] | 2019-08-01
CertainTeed | CT380M10-02 | 380 W, 72 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 380 | 349.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.882 | 72 | 1 | N | 10.35 | 47.94 | 9.8 | 38.9 | 47.39 | -0.371 | 0.039 | -0.281 |  |  | 1.8717 | 38.2317 | 7.4919 | 35.9828 | [6 empty] | 2019-08-01
CertainTeed | CT390HC00-04 | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 390 | 364.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.48 | 48.18 | 9.66 | 40.37 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.9379 | 38.7253 | 7.8452 | 37.3321 | [6 empty] | 2020-01-21
CertainTeed | CT390HC11-04 | 390 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 390 | 354.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.48 | 48.18 | 9.66 | 40.37 | 48.1 | -0.4125 | 0.0489 | -0.3182 |  |  | 2.38 | 36.21 | 7.45 | 36.29 | [6 empty] | 2020-01-21
CertainTeed | CT395HC00-04 | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 395 | 369.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.56 | 48.37 | 9.74 | 40.55 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.954 | 38.898 | 7.9102 | 37.4986 | [6 empty] | 2020-01-21
CertainTeed | CT395HC11-04 | 395 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 395 | 358.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.56 | 48.37 | 9.74 | 40.55 | 48.1 | -0.4125 | 0.0489 | -0.3182 |  |  | 2.3997 | 36.3715 | 7.5117 | 36.4518 | [6 empty] | 2020-01-21
CertainTeed | CT400HC00-04 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 400 | 373.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.64 | 48.55 | 9.81 | 40.77 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.968 | 39.109 | 7.967 | 37.702 | [6 empty] | 2020-01-21
CertainTeed | CT400HC11-04 | 400 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 400 | 363.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.64 | 48.55 | 9.81 | 40.77 | 48.1 | -0.4125 | 0.0489 | -0.3182 |  |  | 2.417 | 36.5688 | 7.5657 | 36.6496 | [6 empty] | 2020-01-21
CertainTeed | CT405HC00-04 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 405 | 378.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.71 | 48.73 | 9.89 | 40.95 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.984 | 39.2817 | 8.032 | 37.8685 | [6 empty] | 2020-01-21
CertainTeed | CT405HC11-04 | 405 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 405 | 368.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.71 | 48.73 | 9.89 | 40.95 | 48.1 | -0.4125 | 0.0489 | -0.3182 |  |  | 2.4367 | 36.7302 | 7.6274 | 36.8114 | [6 empty] | 2020-01-21
Changzhou Eging Photovoltaic Technology | EG-170P48-C | 170 W Polycrystalline Module | UL 1703 | 170 | 151.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3216 | 48 | 1 | N | 7.8 | 29 | 7.4 | 23 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.4685 | 22.4162 | 5.9603 | 21.1379 | Rack | Flat Plate | 0.99 | 1.335 | 1 | 0.19363
Changzhou Eging Photovoltaic Technology | EG-175P48-C | 175 W Polycrystalline Module | UL 1703 | 175 | 156.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3216 | 48 | 1 | N | 8.2 | 29.2 | 7.56 | 23.2 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5002 | 22.6111 | 6.0892 | 21.3217 | Rack | Flat Plate | 0.99 | 1.335 | 1 | 0.19384
Changzhou Eging Photovoltaic Technology | EG-180M48-C | 180 W Monocrystalline Module | UL 1703 | 180 | 159.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3216 | 48 | 1 | N | 8.62 | 29.4 | 7.69 | 23.4 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.5165 | 22.7625 | 5.9974 | 22.0851 | Rack | Flat Plate | 0.99 | 1.335 | 1 | 0.19177
Changzhou Eging Photovoltaic Technology | EG-180P48-C | 180 W Polycrystalline Module | UL 1703 | 180 | 160.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3216 | 48 | 1 | N | 8.62 | 29.4 | 7.69 | 23.4 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.526 | 22.806 | 6.1939 | 21.5055 | Rack | Flat Plate | 0.99 | 1.335 | 1 | 0.19335
Changzhou Eging Photovoltaic Technology | EG-185M48-C | 185 W Monocrystalline Module | UL 1703 | 185 | 164.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3216 | 48 | 1 | N | 8.8 | 29.6 | 7.83 | 23.62 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.5441 | 22.9765 | 6.1066 | 22.2927 | Rack | Flat Plate | 0.99 | 1.335 | 1 | 0.19177
Changzhou Eging Photovoltaic Technology | EG-190M48-C | 190 W Monocrystalline Module | UL 1703 | 190 | 168.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3216 | 48 | 1 | N | 8.91 | 29.6 | 8.04 | 23.62 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.5855 | 22.9765 | 6.2704 | 22.2927 | Rack | Flat Plate | 0.99 | 1.335 | 1 | 0.19173
Changzhou Eging Photovoltaic Technology | EG-190P54-C | 190 W Polycrystalline Module | UL 1703 | 190 | 169.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4751 | 54 | 1 | N | 8.2 | 32.6 | 7.34 | 25.87 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.4566 | 25.1346 | 5.9215 | 23.7142 | Rack | Flat Plate | 0.99 | 1.49 | 1 | 0.19269
Changzhou Eging Photovoltaic Technology | EG-195P54-C | 195 W Polycrystalline Module | UL 1703 | 195 | 173.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4751 | 54 | 1 | N | 8.37 | 32.8 | 7.47 | 26.1 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.4824 | 25.3581 | 6.0264 | 23.925 | Rack | Flat Plate | 0.99 | 1.49 | 1 | 0.19277
Changzhou Eging Photovoltaic Technology | EG-200P54-C | 200 W Polycrystalline Module | UL 1703 | 200 | 178.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4751 | 54 | 1 | N | 8.58 | 32.8 | 7.66 | 26.1 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5201 | 25.3581 | 6.1797 | 23.925 | Rack | Flat Plate | 0.99 | 1.49 | 1 | 0.19273
Changzhou Eging Photovoltaic Technology | EG-205M54-C | 205 W Monocrystalline Module | UL 1703 | 205 | 182 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4751 | 54 | 1 | N | 8.73 | 33.1 | 7.79 | 26.33 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.558 | 25.2713 | 6.1918 | 24.2224 | Rack | Flat Plate | 0.99 | 1.49 | 1 | 0.19206
Changzhou Eging Photovoltaic Technology | EG-205P54-C | 205 W Polycrystalline Module | UL 1703 | 205 | 183.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4751 | 54 | 1 | N | 8.73 | 33.1 | 7.79 | 26.33 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5459 | 25.5815 | 6.2845 | 24.1358 | Rack | Flat Plate | 0.99 | 1.49 | 1 | 0.19291
Changzhou Eging Photovoltaic Technology | EG-210M54-C | 210 W Monocrystalline Module | UL 1703 | 210 | 186.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4751 | 54 | 1 | N | 8.88 | 33.3 | 7.9 | 26.57 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.58 | 25.5017 | 6.2792 | 24.4432 | Rack | Flat Plate | 0.99 | 1.49 | 1 | 0.19187
Changzhou Eging Photovoltaic Technology | EG-210P54-C | 210 W Polycrystalline Module | UL 1703 | 210 | 187.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4751 | 54 | 1 | N | 8.88 | 33.3 | 7.9 | 26.57 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5677 | 25.8147 | 6.3733 | 24.3558 | Rack | Flat Plate | 0.99 | 1.49 | 1 | 0.19271
Changzhou Eging Photovoltaic Technology | EG-210P60-C | 210 W Polycrystalline Module | UL 1703 | 210 | 187.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.04 | 36.61 | 7.39 | 28.41 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.4627 | 27.8223 | 6.0038 | 25.8798 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19379
Changzhou Eging Photovoltaic Technology | EG-215M54-C | 215 W Monocrystalline Module | UL 1703 | 215 | 191.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4751 | 54 | 1 | N | 8.96 | 33.3 | 8.09 | 26.57 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.618 | 25.5017 | 6.4302 | 24.4432 | Rack | Flat Plate | 0.99 | 1.49 | 1 | 0.19191
Changzhou Eging Photovoltaic Technology | EG-215P60-C | 215 W Polycrystalline Module | UL 1703 | 215 | 191.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.26 | 36.67 | 7.6 | 28.28 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5043 | 27.695 | 6.1744 | 25.7614 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19377
Changzhou Eging Photovoltaic Technology | EG-220P60-C | 220 W Polycrystalline Module | UL 1703 | 220 | 196.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.48 | 36.69 | 7.8 | 28.22 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5439 | 27.6362 | 6.3369 | 25.7067 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19394
Changzhou Eging Photovoltaic Technology | EG-225M60-C | 225 W Monocrystalline Module | UL 1703 | 225 | 199.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 8.68 | 36.74 | 7.99 | 28.18 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.5818 | 27.2958 | 6.3677 | 25.8602 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19189
Changzhou Eging Photovoltaic Technology | EG-225P60-C | 225 W Polycrystalline Module | UL 1703 | 225 | 200.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.68 | 36.74 | 7.99 | 28.18 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5815 | 27.597 | 6.4912 | 25.6703 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19397
Changzhou Eging Photovoltaic Technology | EG-230M60-C | 230 W Monocrystalline Module | UL 1703 | 230 | 204.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 8.9 | 36.76 | 8.15 | 28.22 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.6135 | 27.3346 | 6.4952 | 25.8969 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19175
Changzhou Eging Photovoltaic Technology | EG-230P60-C | 230 W Polycrystalline Module | UL 1703 | 230 | 205.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.9 | 36.76 | 8.15 | 28.22 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.6131 | 27.6362 | 6.6212 | 25.7067 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19383
Changzhou Eging Photovoltaic Technology | EG-235M60-C | 235 W Monocrystalline Module | UL 1703 | 235 | 208.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 9.01 | 36.76 | 8.33 | 28.22 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.6491 | 27.3346 | 6.6386 | 25.8969 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19182
Changzhou Eging Photovoltaic Technology | EG-245M72-C | 245 W Monocrystalline Module | UL 1703 | 245 | 217 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9483 | 72 | 1 | N | 7.93 | 43.5 | 7.1 | 34.5 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.4056 | 33.4175 | 5.6584 | 31.6599 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.19172
Changzhou Eging Photovoltaic Technology | EG-255P72-C | 255 W Polycrystalline Module | UL 1703 | 255 | 227.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9483 | 72 | 1 | N | 8.37 | 43.5 | 7.39 | 34.5 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.4703 | 33.518 | 5.9389 | 31.4428 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.19326
Changzhou Eging Photovoltaic Technology | EG-260P72-C | 260 W Polycrystalline Module | UL 1703 | 260 | 232 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9483 | 72 | 1 | N | 8.47 | 43.8 | 7.47 | 34.8 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.4862 | 33.8095 | 6.0032 | 31.7162 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.19326
Changzhou Eging Photovoltaic Technology | EG-265M72-C | 265 W Monocrystalline Module | UL 1703 | 265 | 235.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9483 | 72 | 1 | N | 8.52 | 43.8 | 7.61 | 34.8 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.4908 | 33.2093 | 6.1094 | 31.6283 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.18683
Changzhou Eging Photovoltaic Technology | EG-265P72-C | 265 W Polycrystalline Module | UL 1703 | 265 | 236.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9483 | 72 | 1 | N | 8.52 | 43.8 | 7.61 | 34.8 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5141 | 33.8095 | 6.1157 | 31.7162 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.19317
Changzhou Eging Photovoltaic Technology | EG-270M72-C | 270 W Monocrystalline Module | UL 1703 | 270 | 239.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9483 | 72 | 1 | N | 8.62 | 44.1 | 7.69 | 35.1 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.5065 | 33.4955 | 6.1737 | 31.901 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.18689
Changzhou Eging Photovoltaic Technology | EG-270P72-C | 270 W Polycrystalline Module | UL 1703 | 270 | 241.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9483 | 72 | 1 | N | 8.62 | 44.1 | 7.69 | 35.1 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5005 | 34.4959 | 6.1402 | 32.267 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.19171
Changzhou Eging Photovoltaic Technology | EG-275M72-C | 275 W Monocrystalline Module | UL 1703 | 275 | 244.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9483 | 72 | 1 | N | 8.72 | 44.4 | 7.76 | 35.42 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.5202 | 33.8009 | 6.2299 | 32.1918 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.18685
Changzhou Eging Photovoltaic Technology | EG-275P72-C | 275 W Polycrystalline Module | UL 1703 | 275 | 245.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9483 | 72 | 1 | N | 8.72 | 44.4 | 7.76 | 35.42 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5141 | 34.8104 | 6.196 | 32.5612 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.19167
Changzhou Eging Photovoltaic Technology | EG-280M72-C | 280 W Monocrystalline Module | UL 1703 | 280 | 248.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9483 | 72 | 1 | N | 8.89 | 44.4 | 7.91 | 35.42 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.5799 | 34.0717 | 6.4942 | 31.6211 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.19226
Changzhou Eging Photovoltaic Technology | EG-280P72-C | 280 W Polycrystalline Module | UL 1703 | 280 | 250.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9483 | 72 | 1 | N | 8.89 | 44.4 | 7.91 | 35.42 | 46.7 | -0.46 | 0.06 | -0.35 | -0.001 | -0.47 | 1.5434 | 34.8104 | 6.3158 | 32.5612 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.19188
Changzhou Eging Photovoltaic Technology | EG-285M72-C | 285 W Monocrystalline Module | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9483 | 72 | 1 | N | 8.92 | 44.4 | 8.05 | 35.42 | 46.8 | -0.48 | 0.03 | -0.36 | -0.04 | -0.45 | 1.6079 | 34.0717 | 6.6091 | 31.6211 | Rack | Flat Plate | 0.99 | 1.968 | 1 | 0.19223
Changzhou Nesl Solartech | DJ-230P-ST15 | 230 W DC, Polycrystalline, ACPV Module | UL 1741 | 230 | 203.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.78 | 37.48 | 7.81 | 30.73 | 47.3 | -0.49253 | 0.05345 | -0.34989 | -0.05324 | -0.49797 | 1.5385 | 32.2894 | 6.1884 | 27.8192 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.21598
Changzhou Nesl Solartech | DJ-235P-ST15 | 235 W DC, Polycrystalline, ACPV Module | UL 1741 | 235 | 212.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.8 | 36.2 | 7.91 | 29.7 | 45.7 | -0.44096 | 0.0826 | -0.378 | 0.0478 | -0.4786 | 1.5864 | 29.0685 | 6.3494 | 27.1333 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19623
Changzhou Nesl Solartech | DJ-240DA/C-ST15 | 240 W DC, Monocrystalline, ACPV Module | UL 1741 | 240 | 216.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 8.55 | 37.57 | 7.92 | 30.3 | 45.8 | -0.4416 | 0.0809 | -0.4154 | 0.0343 | -0.4975 | 1.625 | 30.1186 | 6.4399 | 27.7397 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.20392
Changzhou Nesl Solartech | DJ-240P-ST15 | 240 W DC, Polycrystalline, ACPV Module | UL 1741 | 240 | 215.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9374 | 72 | 1 | N | 8.32 | 39.64 | 7.18 | 34.21 | 46.5 | -0.4352 | 0.0897 | -0.3974 | 0.0208 | -0.4746 | 1.3879 | 35.0126 | 5.67 | 30.5482 | Rack | Flat Plate | 0.99 | 1.957 | 1 | 0.20248
Changzhou Nesl Solartech | DJ-245DA/C-ST15 | 245 W DC, Monocrystalline, ACPV Module | UL 1741 | 245 | 221.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 8.68 | 37.82 | 8.03 | 30.5 | 45.8 | -0.4416 | 0.0809 | -0.4154 | 0.0343 | -0.4975 | 1.6479 | 30.3174 | 6.5309 | 27.9228 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.20392
Changzhou Nesl Solartech | DJ-250DA/C-ST15 | 250 W DC, Monocrystalline, ACPV Module | UL 1741 | 250 | 226 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 8.79 | 38.07 | 8.14 | 30.7 | 45.8 | -0.4416 | 0.0809 | -0.4154 | 0.0343 | -0.4975 | 1.6706 | 30.5162 | 6.6208 | 28.1059 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.20392
Changzhou Nesl Solartech | DJ-255D/C-ST15 | 255 W DC, Monocrystalline, ACPV Module | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6335 | 60 | 1 | N | 8.94 | 38.19 | 8.28 | 30.8 | 45.8 | -0.4416 | 0.0809 | -0.4154 | 0.0343 | -0.4975 | 1.6985 | 30.6156 | 6.7313 | 28.1975 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.20392
China Sunergy (Nanjing) | CSUN170-72M | 170 W Monocrystalline Module | UL 1703 | 170 | 145.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.29 | 44.4 | 4.83 | 35.2 | 51 | -0.51944 | 0.027397 | -0.37562 | -0.034043 | -0.48966 | 0.97628 | 33.2335 | 3.7397 | 30.5198 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19085
China Sunergy (Nanjing) | CSUN175-72M | 175 W Monocrystalline Module | UL 1703 | 175 | 156.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.34 | 44.5 | 4.96 | 35.3 | 45.8 | -0.47437 | 0.027674 | -0.32958 | -0.065861 | -0.4342 | 1.0062 | 34.3409 | 4.0671 | 34.0601 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19746
China Sunergy (Nanjing) | SST175-72M | 175 W Monocrystalline Module | UL 1703 | 175 | 156.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.34 | 44.5 | 4.96 | 35.3 | 45.8 | -0.47437 | 0.027674 | -0.32958 | -0.065861 | -0.4342 | 1.0062 | 34.3409 | 4.0671 | 34.0601 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19746
China Sunergy (Nanjing) | CSUN180-72M | 180 W Monocrystalline Module | UL 1703 | 180 | 161 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.4 | 44.6 | 5.09 | 35.4 | 45.8 | -0.47437 | 0.027674 | -0.32958 | -0.065861 | -0.4342 | 1.0326 | 34.4381 | 4.1128 | 34.1366 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19756
China Sunergy (Nanjing) | SST180-72M | 180 W Monocrystalline Module | UL 1703 | 180 | 161 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.4 | 44.6 | 5.09 | 35.4 | 45.8 | -0.47437 | 0.027674 | -0.32958 | -0.065861 | -0.4342 | 1.0326 | 34.4381 | 4.1128 | 34.1366 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19756
China Sunergy (Nanjing) | CSUN185-72M | 185 W Monocrystalline Module | UL 1703 | 185 | 165.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.48 | 44.8 | 5.17 | 35.8 | 45.8 | -0.47437 | 0.027674 | -0.32958 | -0.065861 | -0.4342 | 1.0488 | 34.8273 | 4.1737 | 34.2897 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19745
China Sunergy (Nanjing) | SST185-72M | 185 W Monocrystalline Module | UL 1703 | 185 | 165.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.48 | 44.8 | 5.17 | 35.8 | 45.8 | -0.47437 | 0.027674 | -0.32958 | -0.065861 | -0.4342 | 1.0488 | 34.8273 | 4.1737 | 34.2897 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19745
China Sunergy (Nanjing) | CSUN190-72M | 190 W Monocrystalline Module | UL 1703 | 190 | 167.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.5 | 45 | 5.25 | 36.2 | 47.6 | -0.5 | 0.06 | -0.37 | -0.01 | -0.5 | 1.024 | 36.7018 | 4.2279 | 31.6639 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19781
China Sunergy (Nanjing) | SST190-72M | 190 W Monocrystalline Module | UL 1703 | 190 | 167.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.5 | 45 | 5.25 | 36.2 | 47.6 | -0.5 | 0.06 | -0.37 | -0.01 | -0.5 | 1.024 | 36.7018 | 4.2279 | 31.6639 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19781
China Sunergy (Nanjing) | SST215-54M | 215 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 215 | 185.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4652 | 54 | 1 | N | 8.62 | 33.4 | 7.99 | 26.9 | 48.8 | -0.54 | 0.05 | -0.39 | -0.03 | -0.51 | 1.6488 | 26.3759 | 6.3611 | 24.088 | Rack | Flat Plate | 0.99 | 1.48 | 1 | 0.20228
China Sunergy (Nanjing) | SST220-54M | 220 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 220 | 190.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4652 | 54 | 1 | N | 8.75 | 33.5 | 8.15 | 27 | 48.8 | -0.54 | 0.05 | -0.39 | -0.03 | -0.51 | 1.6819 | 26.474 | 6.4885 | 24.1776 | Rack | Flat Plate | 0.99 | 1.48 | 1 | 0.20239
China Sunergy (Nanjing) | SST220-60M | 220 W Monocrystalline Module | UL 1703 | 220 | 198.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.28 | 36.5 | 7.57 | 29.1 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.6215 | 28.8267 | 5.7447 | 26.4253 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.21246
China Sunergy (Nanjing) | SST220-60P | 220 W Polycrystalline Module | UL 1703 | 220 | 195.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.28 | 36.5 | 7.57 | 29.1 | 45.7 | -0.5 | 0.06 | -0.37 | -0.01 | -0.5 | 1.4243 | 28.9816 | 6.1165 | 26.4653 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.18762
China Sunergy (Nanjing) | SST225-54M | 225 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 225 | 194.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4652 | 54 | 1 | N | 8.84 | 33.6 | 8.3 | 27.1 | 48.8 | -0.54 | 0.05 | -0.39 | -0.03 | -0.51 | 1.7128 | 26.572 | 6.6079 | 24.2671 | Rack | Flat Plate | 0.99 | 1.48 | 1 | 0.20228
China Sunergy (Nanjing) | SST225-60M | 225 W Monocrystalline Module | UL 1703 | 225 | 203.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.36 | 36.7 | 7.68 | 29.3 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.645 | 29.0248 | 5.8282 | 26.6069 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.21221
China Sunergy (Nanjing) | SST225-60P | 225 W Polycrystalline Module | UL 1703 | 225 | 200.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.36 | 36.7 | 7.68 | 29.3 | 45.7 | -0.5 | 0.06 | -0.37 | -0.01 | -0.5 | 1.4449 | 29.1808 | 6.2054 | 26.6472 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.1874
China Sunergy (Nanjing) | SST230-60M | 230 W Monocrystalline Module | UL 1703 | 230 | 208 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.45 | 36.8 | 7.8 | 29.5 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.6707 | 29.2229 | 5.9192 | 26.7885 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.21228
China Sunergy (Nanjing) | SST230-60P | 230 W Polycrystalline Module | UL 1703 | 230 | 204.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.45 | 36.8 | 7.8 | 29.5 | 45.7 | -0.5 | 0.06 | -0.37 | -0.01 | -0.5 | 1.4675 | 29.38 | 6.3023 | 26.8291 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.18746
China Sunergy (Nanjing) | SST235-60M | 235 W Monocrystalline Module | UL 1703 | 235 | 212.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.54 | 36.8 | 7.94 | 29.6 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.5461 | 29.322 | 6.3839 | 26.8793 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19291
China Sunergy (Nanjing) | SST235-60P | 235 W Polycrystalline Module | UL 1703 | 235 | 209.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.54 | 36.8 | 7.94 | 29.6 | 45.7 | -0.5 | 0.06 | -0.37 | -0.01 | -0.5 | 1.4939 | 29.4796 | 6.4154 | 26.92 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.1874
China Sunergy (Nanjing) | CSUN240-54M | 240 W Monocrystalline Module | UL 1703 | 240 | 209.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4652 | 54 | 1 | N | 9.09 | 34 | 8.7 | 27.6 | 47.7 | -0.55 | 0.05 | -0.4 | -0.01 | -0.56 | 1.5915 | 29.2533 | 6.803 | 24.6548 | Rack | Flat Plate | 0.99 | 1.48 | 1 | 0.19399
China Sunergy (Nanjing) | SST240-54M | 240 W Monocrystalline Module | UL 1703 | 240 | 209.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4652 | 54 | 1 | N | 9.09 | 34 | 8.7 | 27.6 | 47.7 | -0.55 | 0.05 | -0.4 | -0.01 | -0.56 | 1.5915 | 29.2533 | 6.803 | 24.6548 | Rack | Flat Plate | 0.99 | 1.48 | 1 | 0.19399
China Sunergy (Nanjing) | SST240-60M | 240 W Monocrystalline Module | UL 1703 | 240 | 217.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.62 | 37 | 8.06 | 29.8 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.5695 | 29.5201 | 6.4804 | 27.0609 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19305
China Sunergy (Nanjing) | SST240-60P | 240 W Polycrystalline Module | UL 1703 | 240 | 213.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.62 | 37 | 8.06 | 29.8 | 45.7 | -0.5 | 0.06 | -0.37 | -0.01 | -0.5 | 1.5164 | 29.6787 | 6.5124 | 27.1019 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.18753
China Sunergy (Nanjing) | CSUN245-60M | 245 W Monocrystalline Module | UL 1703 | 245 | 218.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.69 | 37.2 | 8.17 | 30 | 46.7 | -0.47 | 0.05 | -0.34 | -0.01 | -0.47 | 1.6846 | 29.6089 | 6.6022 | 26.8905 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20359
China Sunergy (Nanjing) | CSUN245-60P | 245 W Polycrystalline Module | UL 1703 | 245 | 216.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.75 | 37.5 | 8.17 | 30 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.6614 | 29.2612 | 6.538 | 26.8552 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19842
China Sunergy (Nanjing) | SST245-60M | 245 W Polycrystalline Module | UL 1703 | 245 | 218.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.69 | 37.2 | 8.17 | 30 | 46.7 | -0.47 | 0.05 | -0.34 | -0.01 | -0.47 | 1.6846 | 29.6089 | 6.6022 | 26.8905 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20359
China Sunergy (Nanjing) | SST245-60P | 245 W Polycrystalline Module | UL 1703 | 245 | 216.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.75 | 37.5 | 8.17 | 30 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.6614 | 29.2612 | 6.538 | 26.8552 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19842
China Sunergy (Nanjing) | CSUN250-60M | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.78 | 37.3 | 8.31 | 30.1 | 46.7 | -0.47 | 0.05 | -0.34 | -0.01 | -0.47 | 1.7135 | 29.7076 | 6.7154 | 26.9801 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20362
China Sunergy (Nanjing) | CSUN250-60P | 250 W Polycrystalline Module | UL 1703 | 250 | 221 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.83 | 37.7 | 8.28 | 30.2 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.6837 | 29.4563 | 6.626 | 27.0343 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19839
China Sunergy (Nanjing) | SST250-60M | 250 W Polycrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.78 | 37.3 | 8.31 | 30.1 | 46.7 | -0.47 | 0.05 | -0.34 | -0.01 | -0.47 | 1.7135 | 29.7076 | 6.7154 | 26.9801 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20362
China Sunergy (Nanjing) | SST250-60P | 250 W Polycrystalline Module | UL 1703 | 250 | 221 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.83 | 37.7 | 8.28 | 30.2 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.6837 | 29.4563 | 6.626 | 27.0343 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19839
China Sunergy (Nanjing) | CSUN255-60M | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.85 | 37.4 | 8.44 | 30.2 | 46.7 | -0.47 | 0.05 | -0.34 | -0.01 | -0.47 | 1.7403 | 29.8063 | 6.8204 | 27.0698 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20342
China Sunergy (Nanjing) | CSUN255-60P | 255 W Polycrystalline Module | UL 1703 | 255 | 225.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.89 | 37.3 | 8.51 | 30 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.7305 | 29.2612 | 6.81 | 26.8552 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19858
China Sunergy (Nanjing) | SST255-60M | 255 W Polycrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.85 | 37.4 | 8.44 | 30.2 | 46.7 | -0.47 | 0.05 | -0.34 | -0.01 | -0.47 | 1.7403 | 29.8063 | 6.8204 | 27.0698 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20342
China Sunergy (Nanjing) | SST255-60P | 255 W Polycrystalline Module | UL 1703 | 255 | 225.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.89 | 37.3 | 8.51 | 30 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.7305 | 29.2612 | 6.81 | 26.8552 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19858
China Sunergy (Nanjing) | CSUN260-60M | 260 W Monocrystalline Module | UL 1703 | 260 | 232.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.9 | 38.1 | 8.44 | 30.8 | 46.7 | -0.47 | 0.05 | -0.34 | -0.01 | -0.47 | 1.7403 | 30.3984 | 6.8204 | 27.6076 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20347
China Sunergy (Nanjing) | CSUN260-60P | 260 W Polycrystalline Module | UL 1703 | 260 | 230.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 9.01 | 38 | 8.5 | 30.6 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.7285 | 29.8465 | 6.802 | 27.3923 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19842
China Sunergy (Nanjing) | SST260-60M | 260 W Polycrystalline Module | UL 1703 | 260 | 232.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.9 | 38.1 | 8.44 | 30.8 | 46.7 | -0.47 | 0.05 | -0.34 | -0.01 | -0.47 | 1.7403 | 30.3984 | 6.8204 | 27.6076 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20347
China Sunergy (Nanjing) | SST260-60P | 260 W Polycrystalline Module | UL 1703 | 260 | 230.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 9.01 | 38 | 8.5 | 30.6 | 46.8 | -0.51 | 0.07 | -0.37 | -0.03 | -0.48 | 1.7285 | 29.8465 | 6.802 | 27.3923 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19842
China Sunergy (Nanjing) | CSUN265-60M | 265 W Monocrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.99 | 37.7 | 8.67 | 30.6 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6403 | 29.8229 | 6.9482 | 27.6857 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18459
China Sunergy (Nanjing) | CSUN265-60P | 265 W Polycrystalline Module | UL 1703 | 265 | 238.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6131 | 60 | 1 | N | 9.01 | 37.7 | 8.69 | 30.5 | 46.9 | -0.4375 | 0.0489 | -0.3303 | 0.0082 | -0.4794 | 1.6438 | 30.2089 | 7.0061 | 27.6373 | Rack | Flat Plate | 0.986 | 1.636 | 1 | 0.18738
China Sunergy (Nanjing) | SST265-60M | 265 W Monocrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.99 | 37.7 | 8.67 | 30.6 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6403 | 29.8229 | 6.9482 | 27.6857 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18459
China Sunergy (Nanjing) | SST265-72M | 265 W Monocrystalline Module | UL 1703 | 265 | 239.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.31 | 43.8 | 7.58 | 35 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.4929 | 34.698 | 6.0293 | 32.3627 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19547
China Sunergy (Nanjing) | CSUN270-60M | 270 W Monocrystalline Module | UL 1703 | 270 | 242.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 9.07 | 37.9 | 8.77 | 30.8 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6592 | 30.0178 | 7.0284 | 27.8667 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18446
China Sunergy (Nanjing) | CSUN270-60P | 270 W Polycrystalline Module | UL 1703 | 270 | 243.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6131 | 60 | 1 | N | 9.08 | 37.9 | 8.8 | 30.7 | 46.9 | -0.4375 | 0.0489 | -0.3303 | 0.0082 | -0.4794 | 1.6646 | 30.407 | 7.0948 | 27.8185 | Rack | Flat Plate | 0.986 | 1.636 | 1 | 0.18746
China Sunergy (Nanjing) | SST270-60M | 270 W Monocrystalline Module | UL 1703 | 270 | 242.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 9.07 | 37.9 | 8.77 | 30.8 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6592 | 30.0178 | 7.0284 | 27.8667 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18446
China Sunergy (Nanjing) | SST270-72M | 270 W Monocrystalline Module | UL 1703 | 270 | 244.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.39 | 43.9 | 7.7 | 35.1 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.5165 | 34.7972 | 6.1248 | 32.4551 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19545
China Sunergy (Nanjing) | CSUN275-60M | 275 W Monocrystalline Module | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 9.14 | 38.1 | 8.88 | 31 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.68 | 30.2127 | 7.1165 | 28.0476 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18457
China Sunergy (Nanjing) | CSUN275-60P | 275 W Polycrystalline Module | UL 1703 | 275 | 248.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6131 | 60 | 1 | N | 9.15 | 38 | 8.91 | 38 | 46.9 | -0.4375 | 0.0489 | -0.3303 | 0.0082 | -0.4794 | 1.6854 | 37.6373 | 7.1835 | 34.4333 | Rack | Flat Plate | 0.986 | 1.636 | 1 | 0.23067
China Sunergy (Nanjing) | SST275-60M | 275 W Monocrystalline Module | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 9.14 | 38.1 | 8.88 | 31 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.68 | 30.2127 | 7.1165 | 28.0476 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18457
China Sunergy (Nanjing) | SST275-72M | 275 W Monocrystalline Module | UL 1703 | 275 | 248.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.46 | 44.1 | 7.8 | 35.3 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.5362 | 34.9954 | 6.2043 | 32.6401 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19549
China Sunergy (Nanjing) | SST275-72P | 275 W Polycrystalline Module | UL 1703 | 275 | 241.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.48 | 43.8 | 7.82 | 35.2 | 47.4 | -0.51 | 0.05 | -0.37 | -0.05 | -0.47 | 1.4669 | 36.5447 | 6.2124 | 31.8234 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19493
China Sunergy (Nanjing) | CSUN280-60M | 280 W Monocrystalline Module | UL 1703 | 280 | 251.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 9.21 | 38.7 | 8.97 | 31.2 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.697 | 30.4076 | 7.1886 | 28.2286 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18429
China Sunergy (Nanjing) | CSUN280-72P | 280 W Polycrystalline Module | UL 1703 | 280 | 246.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.58 | 44 | 7.94 | 35.3 | 47.4 | -0.51 | 0.05 | -0.37 | -0.05 | -0.47 | 1.5557 | 35.3405 | 6.3944 | 36.7392 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19635
China Sunergy (Nanjing) | SST280-60M | 280 W Monocrystalline Module | UL 1703 | 280 | 250.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 60 | 1 | N | 9.21 | 38.7 | 8.97 | 31.2 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.697 | 30.4076 | 7.1886 | 28.2286 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18429
China Sunergy (Nanjing) | SST280-72M | 280 W Monocrystalline Module | UL 1703 | 280 | 253.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.53 | 44.2 | 7.89 | 35.5 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.5539 | 35.1937 | 6.2759 | 32.825 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19532
China Sunergy (Nanjing) | SST280-72P | 280 W Polycrystalline Module | UL 1703 | 280 | 246.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.58 | 44 | 7.94 | 35.3 | 47.4 | -0.51 | 0.05 | -0.37 | -0.05 | -0.47 | 1.4894 | 36.6485 | 6.3077 | 31.9138 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19494
China Sunergy (Nanjing) | CSUN285-60M | 285 W Monocrystalline Module Black Back sheet Black Frame 60 Cell | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6131 | 60 | 1 | N | 9.28 | 38.8 | 9 | 31.7 | 46.3 | -0.4568 | 0.0551 | -0.3269 | 0.011 | -0.4514 | 1.7232 | 30.973 | 7.1193 | 29.1505 | Rack | Flat Plate | 0.986 | 1.636 | 1 | 0.18727
China Sunergy (Nanjing) | SST285-72M | 285 W Monocrystalline Module | UL 1703 | 285 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.59 | 44.4 | 7.99 | 35.7 | 46.2 | -0.423 | 0.039 | -0.307 | 0.0018 | -0.416 | 1.5736 | 35.392 | 6.3555 | 33.0099 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19542
China Sunergy (Nanjing) | SST285-72P | 285 W Polycrystalline Module | UL 1703 | 285 | 250.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.59 | 44.4 | 7.99 | 35.7 | 47.4 | -0.51 | 0.05 | -0.37 | -0.05 | -0.47 | 1.4988 | 37.0638 | 6.3474 | 32.2755 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19491
China Sunergy (Nanjing) | CSUN290-60M | 290 W Monocrystalline Module Black Back sheet Black Frame 60 Cell | UL 1703 | 290 | 261.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6131 | 60 | 1 | N | 9.36 | 38.9 | 9.1 | 31.9 | 46.3 | -0.4568 | 0.0551 | -0.3269 | 0.011 | -0.4514 | 1.7423 | 31.1684 | 7.1984 | 29.3344 | Rack | Flat Plate | 0.986 | 1.636 | 1 | 0.18726
China Sunergy (Nanjing) | CSUN290-72P | 290 W Polycrystalline Module | UL 1703 | 290 | 261.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5444 | 72 | 1 | N | 8.75 | 44.3 | 8.15 | 35.6 | 47.2 | -0.45 | 0.07 | -0.35 | 0.04 | -0.49 | 1.54 | 34.38 | 6.47 | 33.16 | Rack | Flat Plate | 0.99 | 1.56 | 1 | 0.18257
China Sunergy (Nanjing) | SST290-72M | 290 W Monocrystalline Module | UL 1703 | 290 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.68 | 44.5 | 8.11 | 35.8 | 48 | -0.52 | 0.04 | -0.39 | -0.05 | -0.48 | 1.5573 | 36.2157 | 6.564 | 31.5044 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19447
China Sunergy (Nanjing) | SST290-72P | 290 W Polycrystalline Module | UL 1703 | 290 | 255.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9364 | 72 | 1 | N | 8.68 | 44.5 | 8.11 | 35.8 | 47.4 | -0.51 | 0.05 | -0.37 | -0.05 | -0.47 | 1.5213 | 37.1676 | 6.4428 | 32.3659 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19497
China Sunergy (Nanjing) | CSUN295-72P | 295 W Polycrystalline Module | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5444 | 72 | 1 | N | 8.84 | 44.4 | 8.26 | 35.7 | 47.2 | -0.45 | 0.07 | -0.35 | 0.04 | -0.49 | 1.57 | 34.47 | 6.55 | 33.25 | Rack | Flat Plate | 0.99 | 1.56 | 1 | 0.18345
China Sunergy (Nanjing) | SST295-72M | 295 W Monocrystalline Module | UL 1703 | 295 | 258.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.73 | 44.6 | 8.22 | 35.9 | 48 | -0.52 | 0.04 | -0.39 | -0.05 | -0.48 | 1.5784 | 36.3169 | 6.653 | 31.5924 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19431
China Sunergy (Nanjing) | CSUN300-72P | 300 W Polycrystalline Module | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5444 | 72 | 1 | N | 8.93 | 44.5 | 8.37 | 35.8 | 47.2 | -0.45 | 0.07 | -0.35 | 0.04 | -0.49 | 1.59 | 34.57 | 6.64 | 33.34 | Rack | Flat Plate | 0.99 | 1.56 | 1 | 0.18322
China Sunergy (Nanjing) | SST300-72M | 300 W Monocrystalline Module | UL 1703 | 300 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.8 | 44.8 | 8.32 | 36.1 | 48 | -0.52 | 0.04 | -0.39 | -0.05 | -0.48 | 1.5976 | 36.5192 | 6.734 | 31.7684 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.19447
China Sunergy (Nanjing) | CSUN305-72M | 305 W Monocrystalline Module | UL 1703 | 305 | 273.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.87 | 45 | 8.41 | 36.3 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.5707 | 35.1415 | 6.7002 | 32.2452 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18097
China Sunergy (Nanjing) | CSUN305-72P | 305 W Polycrystalline Module | UL 1703 | 305 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5444 | 72 | 1 | N | 9.01 | 44.7 | 8.5 | 35.9 | 47.2 | -0.45 | 0.07 | -0.35 | 0.04 | -0.49 | 1.61 | 34.67 | 6.74 | 33.44 | Rack | Flat Plate | 0.99 | 1.56 | 1 | 0.18301
China Sunergy (Nanjing) | SST305-72M | 305 W Monocrystalline Module | UL 1703 | 305 | 273.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.87 | 45 | 8.41 | 36.3 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.5707 | 35.1415 | 6.7002 | 32.2452 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18097
China Sunergy (Nanjing) | CSUN310-72M | 310 W Monocrystalline Module | UL 1703 | 310 | 278.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.91 | 45.2 | 8.5 | 36.5 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.5875 | 35.3351 | 6.7719 | 32.4229 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18095
China Sunergy (Nanjing) | CSUN310-72P | 310 W Polycrystalline Module | UL 1703 | 310 | 280.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5444 | 72 | 1 | N | 9.03 | 44.8 | 8.61 | 36 | 47.2 | -0.45 | 0.07 | -0.35 | 0.04 | -0.49 | 1.63 | 34.76 | 6.83 | 33.53 | Rack | Flat Plate | 0.99 | 1.56 | 1 | 0.18277
China Sunergy (Nanjing) | SST310-72M | 310 W Monocrystalline Module | UL 1703 | 310 | 278.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.91 | 45.2 | 8.5 | 36.5 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.5875 | 35.3351 | 6.7719 | 32.4229 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18095
China Sunergy (Nanjing) | CSUN315-72M | 315 W Monocrystalline Module | UL 1703 | 315 | 282.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.99 | 45.5 | 8.59 | 36.7 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6043 | 35.5287 | 6.8436 | 32.6005 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18095
China Sunergy (Nanjing) | CSUN315-72P | 315 W Polycrystalline Module | UL 1703 | 315 | 284.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5444 | 72 | 1 | N | 9.11 | 44.9 | 8.7 | 36.2 | 47.2 | -0.45 | 0.07 | -0.35 | 0.04 | -0.49 | 1.65 | 34.96 | 6.9 | 33.72 | Rack | Flat Plate | 0.99 | 1.56 | 1 | 0.18312
China Sunergy (Nanjing) | SST315-72M | 315 W Monocrystalline Module | UL 1703 | 315 | 282.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 8.99 | 45.5 | 8.59 | 36.7 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6043 | 35.5287 | 6.8436 | 32.6005 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18095
China Sunergy (Nanjing) | CSUN320-72M | 320 W Monocrystalline Module | UL 1703 | 320 | 287.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 9.06 | 45.7 | 8.68 | 36.9 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6211 | 35.7223 | 6.9153 | 32.7782 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18097
China Sunergy (Nanjing) | CSUN320-72P | 320 W Polycrystalline Module | UL 1703 | 320 | 288.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9247 | 72 | 1 | N | 9.17 | 45 | 8.84 | 36.2 | 46.9 | -0.4375 | 0.0489 | -0.3303 | 0.0082 | -0.4794 | 1.7189 | 35.3996 | 7.1211 | 32.8744 | Rack | Flat Plate | 0.986 | 1.952 | 1 | 0.19015
China Sunergy (Nanjing) | SST320-72M | 320 W Monocrystalline Module | UL 1703 | 320 | 287.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 9.06 | 45.7 | 8.68 | 36.9 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6211 | 35.7223 | 6.9153 | 32.7782 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18097
China Sunergy (Nanjing) | CSUN325-72M | 325 W Monocrystalline Module | UL 1703 | 325 | 291.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 9.14 | 45.9 | 8.77 | 37.1 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6379 | 35.916 | 6.987 | 32.9559 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.181
China Sunergy (Nanjing) | SST325-72M | 325 W Monocrystalline Module | UL 1703 | 325 | 291.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 9.14 | 45.9 | 8.77 | 37.1 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6379 | 35.916 | 6.987 | 32.9559 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.181
China Sunergy (Nanjing) | CSUN330-72M | 330 W Monocrystalline Module | UL 1703 | 330 | 296.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 9.2 | 46.1 | 8.85 | 37.3 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6528 | 36.1096 | 7.0507 | 33.1335 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18086
China Sunergy (Nanjing) | SST330-72M | 330 W Monocrystalline Module | UL 1703 | 330 | 296.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9364 | 72 | 1 | N | 9.2 | 46.1 | 8.85 | 37.3 | 46.2 | -0.47 | 0.06 | -0.36 | 0.02 | -0.45 | 1.6528 | 36.1096 | 7.0507 | 33.1335 | Rack | Flat Plate | 0.99 | 1.956 | 1 | 0.18086
China Sunergy (Nanjing) | CSUN335-72M | 335 W Monocrystalline Module | UL 1703 | 335 | 302.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9247 | 72 | 1 | N | 9.26 | 46.3 | 8.93 | 37.6 | 46.3 | -0.4568 | 0.0551 | -0.3269 | 0.011 | -0.4514 | 1.7113 | 36.8088 | 7.1007 | 34.732 | Rack | Flat Plate | 0.986 | 1.952 | 1 | 0.18803
China Sunergy (Nanjing) | CSUN340-72M | 340 W Monocrystalline Module | UL 1703 | 340 | 306.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9247 | 72 | 1 | N | 9.32 | 46.5 | 9.01 | 37.8 | 46.3 | -0.4568 | 0.0551 | -0.3269 | 0.011 | -0.4514 | 1.7266 | 37.0046 | 7.1643 | 34.9168 | Rack | Flat Plate | 0.986 | 1.952 | 1 | 0.18792
China Sunergy (Nanjing) | CSUN345-72M | 345 W Monocrystalline Module | UL 1703 | 345 | 311.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9247 | 72 | 1 | N | 9.38 | 46.7 | 9.09 | 38 | 46.3 | -0.4568 | 0.0551 | -0.3269 | 0.011 | -0.4514 | 1.7419 | 37.2004 | 7.228 | 35.1015 | Rack | Flat Plate | 0.986 | 1.952 | 1 | 0.18783
China Sunergy (Nanjing) Co.,Ltd. | CSUN285-60MH5 | 285 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 285 | 262.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.31 | 38.7 | 8.99 | 31.7 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7158 | 31.3347 | 6.7958 | 29.0084 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN285-60MH5BB | 285 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 285 | 262.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.31 | 38.7 | 8.99 | 31.7 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7158 | 31.3347 | 6.7958 | 29.0084 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN285-60MH5BW | 285 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 285 | 262.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.31 | 38.7 | 8.99 | 31.7 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7158 | 31.3347 | 6.7958 | 29.0084 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN285-60MM5 | 285 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 285 | 262.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.31 | 38.7 | 8.99 | 31.7 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7158 | 31.3347 | 6.7958 | 29.0084 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN285-60MM5BB | 285 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 285 | 262.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.31 | 38.7 | 8.99 | 31.7 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7158 | 31.3347 | 6.7958 | 29.0084 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN285-60MM5BW | 285 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 285 | 262.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.31 | 38.7 | 8.99 | 31.7 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7158 | 31.3347 | 6.7958 | 29.0084 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN290-60MH5 | 290 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.39 | 38.8 | 9.11 | 31.9 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7387 | 31.5324 | 6.8865 | 29.1914 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN290-60MH5BB | 290 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.39 | 38.8 | 9.11 | 31.9 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7387 | 31.5324 | 6.8865 | 29.1914 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN290-60MH5BW | 290 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.39 | 38.8 | 9.11 | 31.9 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7387 | 31.5324 | 6.8865 | 29.1914 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN290-60MM5 | 290 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.39 | 38.8 | 9.11 | 31.9 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7387 | 31.5324 | 6.8865 | 29.1914 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN290-60MM5BB | 290 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.39 | 38.8 | 9.11 | 31.9 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7387 | 31.5324 | 6.8865 | 29.1914 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN290-60MM5BW | 290 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.39 | 38.8 | 9.11 | 31.9 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7387 | 31.5324 | 6.8865 | 29.1914 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN295-60MH5 | 295 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.47 | 39 | 9.23 | 32 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7616 | 31.6312 | 6.9772 | 29.2829 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN295-60MH5BB | 295 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.47 | 39 | 9.23 | 32 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7616 | 31.6312 | 6.9772 | 29.2829 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN295-60MH5BW | 295 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.47 | 39 | 9.23 | 32 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7616 | 31.6312 | 6.9772 | 29.2829 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN295-60MM5 | 295 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.47 | 39 | 9.23 | 32 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7616 | 31.6312 | 6.9772 | 29.2829 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN295-60MM5BB | 295 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.47 | 39 | 9.23 | 32 | 44.8 | -0.40227 | 0.05762 | -0.3095 | 0.048011 | -0.44057 | 1.7616 | 31.6312 | 6.9772 | 29.2829 | [6 empty] | 2018-12-17 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN295-60MM5BW | 295 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.47 | 39 | 9.23 | 32 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7616 | 31.6312 | 6.9772 | 29.2829 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN300-60MH5 | 300 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.63 | 39.7 | 9.33 | 32.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7807 | 31.8289 | 7.0528 | 29.4659 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN300-60MH5BB | 300 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.63 | 39.7 | 9.33 | 32.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7807 | 31.8289 | 7.0528 | 29.4659 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN300-60MH5BW | 300 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.63 | 39.7 | 9.33 | 32.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7807 | 31.8289 | 7.0528 | 29.4659 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN300-60MM5 | 300 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.63 | 39.7 | 9.33 | 32.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7807 | 31.8289 | 7.0528 | 29.4659 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN300-60MM5BB | 300 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.63 | 39.7 | 9.33 | 32.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 | 0.048011 | -0.44057 | 1.7807 | 31.8289 | 7.0528 | 29.4659 | [6 empty] | 2018-12-17 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN300-60MM5BW | 300 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.63 | 39.7 | 9.33 | 32.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7807 | 31.8289 | 7.0528 | 29.4659 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN305-60MH5 | 305 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 305 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.75 | 39.8 | 9.43 | 32.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7997 | 32.0266 | 7.1284 | 29.649 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN305-60MH5BB | 305 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 305 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.75 | 39.8 | 9.43 | 32.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7997 | 32.0266 | 7.1284 | 29.649 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN305-60MH5BW | 305 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 305 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.75 | 39.8 | 9.43 | 32.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7997 | 32.0266 | 7.1284 | 29.649 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN305-60MM5 | 305 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 305 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.75 | 39.8 | 9.43 | 32.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7997 | 32.0266 | 7.1284 | 29.649 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN305-60MM5BB | 305 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 305 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.75 | 39.8 | 9.43 | 32.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 | 0.048011 | -0.44057 | 1.7997 | 32.0266 | 7.1284 | 29.649 | [6 empty] | 2018-12-17 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN305-60MM5BW | 305 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 305 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.75 | 39.8 | 9.43 | 32.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.7997 | 32.0266 | 7.1284 | 29.649 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN310-60MH5 | 310 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.83 | 40.1 | 9.52 | 32.6 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8169 | 32.2243 | 7.1964 | 29.832 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN310-60MH5BB | 310 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.83 | 40.1 | 9.52 | 32.6 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8169 | 32.2243 | 7.1964 | 29.832 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN310-60MH5BW | 310 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.83 | 40.1 | 9.52 | 32.6 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8169 | 32.2243 | 7.1964 | 29.832 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN310-60MM5 | 310 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.83 | 40.1 | 9.52 | 32.6 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8169 | 32.2243 | 7.1964 | 29.832 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN310-60MM5BB | 310 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.83 | 40.1 | 9.52 | 32.6 | 44.8 | -0.40227 | 0.05762 | -0.3095 | 0.048011 | -0.44057 | 1.8169 | 32.2243 | 7.1964 | 29.832 | [6 empty] | 2018-12-17 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN310-60MM5BW | 310 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.83 | 40.1 | 9.52 | 32.6 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8169 | 32.2243 | 7.1964 | 29.832 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-60MH5 | 315 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.92 | 40.2 | 9.62 | 32.8 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.836 | 32.422 | 7.272 | 30.015 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-60MH5BB | 315 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.92 | 40.2 | 9.62 | 32.8 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.836 | 32.422 | 7.272 | 30.015 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-60MH5BW | 315 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.92 | 40.2 | 9.62 | 32.8 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.836 | 32.422 | 7.272 | 30.015 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-60MM5 | 315 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.92 | 40.2 | 9.62 | 32.8 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.836 | 32.422 | 7.272 | 30.015 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-60MM5BB | 315 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.92 | 40.2 | 9.62 | 32.8 | 44.8 | -0.40227 | 0.05762 | -0.3095 | 0.048011 | -0.44057 | 1.836 | 32.422 | 7.272 | 30.015 | [6 empty] | 2018-12-17 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-60MM5BW | 315 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.92 | 40.2 | 9.62 | 32.8 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.836 | 32.422 | 7.272 | 30.015 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-72PH5 | 315 W, 72 cell polycrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 315 | 288.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.04 | 45.6 | 8.51 | 37.1 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6408 | 35.9938 | 6.5632 | 33.1462 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-72PH5BB | 315 W, 72 cell polycrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 315 | 288.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.04 | 45.6 | 8.51 | 37.1 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6408 | 35.9938 | 6.5632 | 33.1462 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-72PH5BW | 315 W, 72 cell polycrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 315 | 288.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.04 | 45.6 | 8.51 | 37.1 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6408 | 35.9938 | 6.5632 | 33.1462 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-72PM5 | 315 W, 72 cell polycrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 315 | 288.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.04 | 45.6 | 8.51 | 37.1 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6408 | 35.9938 | 6.5632 | 33.1462 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-72PM5BB | 315 W, 72 cell polycrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 315 | 288.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.04 | 45.6 | 8.51 | 37.1 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6408 | 35.9938 | 6.5632 | 33.1462 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN315-72PM5BW | 315 W, 72 cell polycrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 315 | 288.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.04 | 45.6 | 8.51 | 37.1 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6408 | 35.9938 | 6.5632 | 33.1462 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-60MH5 | 320 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 320 | 295.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.03 | 40.4 | 9.7 | 33 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8513 | 32.6197 | 7.3325 | 30.198 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-60MH5BB | 320 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 320 | 295.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.03 | 40.4 | 9.7 | 33 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8513 | 32.6197 | 7.3325 | 30.198 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-60MH5BW | 320 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 320 | 295.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.03 | 40.4 | 9.7 | 33 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8513 | 32.6197 | 7.3325 | 30.198 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-60MM5 | 320 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 320 | 295.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.03 | 40.4 | 9.7 | 33 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8513 | 32.6197 | 7.3325 | 30.198 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-60MM5BB | 320 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 320 | 295.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.03 | 40.4 | 9.7 | 33 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8513 | 32.6197 | 7.3325 | 30.198 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-60MM5BW | 320 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 320 | 295.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.03 | 40.4 | 9.7 | 33 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8513 | 32.6197 | 7.3325 | 30.198 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-72PH5 | 320 W, 72 cell polycrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 320 | 292.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.13 | 45.8 | 8.58 | 37.3 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6543 | 36.1878 | 6.6172 | 33.3249 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-72PH5BB | 320 W, 72 cell polycrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 320 | 292.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.13 | 45.8 | 8.58 | 37.3 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6543 | 36.1878 | 6.6172 | 33.3249 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-72PH5BW | 320 W, 72 cell polycrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 320 | 292.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.13 | 45.8 | 8.58 | 37.3 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6543 | 36.1878 | 6.6172 | 33.3249 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-72PM5 | 320 W, 72 cell polycrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 320 | 292.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.13 | 45.8 | 8.58 | 37.3 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6543 | 36.1878 | 6.6172 | 33.3249 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-72PM5BB | 320 W, 72 cell polycrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 320 | 292.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.13 | 45.8 | 8.58 | 37.3 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6543 | 36.1878 | 6.6172 | 33.3249 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN320-72PM5BW | 320 W, 72 cell polycrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 320 | 292.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.13 | 45.8 | 8.58 | 37.3 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6543 | 36.1878 | 6.6172 | 33.3249 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-60MH5 | 325 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 325 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.12 | 40.6 | 9.79 | 33.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8684 | 32.8174 | 7.4005 | 30.381 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-60MH5BB | 325 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 325 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.12 | 40.6 | 9.79 | 33.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8684 | 32.8174 | 7.4005 | 30.381 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-60MH5BW | 325 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 325 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.12 | 40.6 | 9.79 | 33.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8684 | 32.8174 | 7.4005 | 30.381 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-60MM5 | 325 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 325 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.12 | 40.6 | 9.79 | 33.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8684 | 32.8174 | 7.4005 | 30.381 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-60MM5BB | 325 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 325 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.12 | 40.6 | 9.79 | 33.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8684 | 32.8174 | 7.4005 | 30.381 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-60MM5BW | 325 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 325 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.12 | 40.6 | 9.79 | 33.2 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8684 | 32.8174 | 7.4005 | 30.381 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-72PH5 | 325 W, 72 cell polycrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.22 | 45.9 | 8.65 | 37.6 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6678 | 36.4789 | 6.6712 | 33.5929 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-72PH5BB | 325 W, 72 cell polycrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.22 | 45.9 | 8.65 | 37.6 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6678 | 36.4789 | 6.6712 | 33.5929 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-72PH5BW | 325 W, 72 cell polycrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.22 | 45.9 | 8.65 | 37.6 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6678 | 36.4789 | 6.6712 | 33.5929 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-72PM5 | 325 W, 72 cell polycrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.22 | 45.9 | 8.65 | 37.6 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6678 | 36.4789 | 6.6712 | 33.5929 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-72PM5BB | 325 W, 72 cell polycrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.22 | 45.9 | 8.65 | 37.6 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6678 | 36.4789 | 6.6712 | 33.5929 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN325-72PM5BW | 325 W, 72 cell polycrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.22 | 45.9 | 8.65 | 37.6 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6678 | 36.4789 | 6.6712 | 33.5929 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-60MH5 | 330 W, 60 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 330 | 304.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.22 | 40.8 | 9.88 | 33.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8856 | 33.0151 | 7.4685 | 30.5641 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-60MH5BB | 330 W, 60 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 330 | 304.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.22 | 40.8 | 9.88 | 33.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8856 | 33.0151 | 7.4685 | 30.5641 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-60MH5BW | 330 W, 60 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 330 | 304.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.22 | 40.8 | 9.88 | 33.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8856 | 33.0151 | 7.4685 | 30.5641 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-60MM5 | 330 W, 60 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 330 | 304.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.22 | 40.8 | 9.88 | 33.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8856 | 33.0151 | 7.4685 | 30.5641 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-60MM5BB | 330 W, 60 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 330 | 304.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.22 | 40.8 | 9.88 | 33.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8856 | 33.0151 | 7.4685 | 30.5641 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-60MM5BW | 330 W, 60 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 330 | 304.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.22 | 40.8 | 9.88 | 33.4 | 44.8 | -0.40227 | 0.05762 | -0.3095 |  |  | 1.8856 | 33.0151 | 7.4685 | 30.5641 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-72PH5 | 330 W, 72 cell polycrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 330 | 302.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.3 | 46.1 | 8.74 | 37.8 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6852 | 36.6729 | 6.7406 | 33.7716 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-72PH5BB | 330 W, 72 cell polycrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 330 | 302.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.3 | 46.1 | 8.74 | 37.8 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6852 | 36.6729 | 6.7406 | 33.7716 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-72PH5BW | 330 W, 72 cell polycrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 330 | 302.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.3 | 46.1 | 8.74 | 37.8 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6852 | 36.6729 | 6.7406 | 33.7716 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-72PM5 | 330 W, 72 cell polycrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 330 | 302.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.3 | 46.1 | 8.74 | 37.8 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6852 | 36.6729 | 6.7406 | 33.7716 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-72PM5BB | 330 W, 72 cell polycrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 330 | 302.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.3 | 46.1 | 8.74 | 37.8 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6852 | 36.6729 | 6.7406 | 33.7716 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN330-72PM5BW | 330 W, 72 cell polycrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 330 | 302.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.3 | 46.1 | 8.74 | 37.8 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.6852 | 36.6729 | 6.7406 | 33.7716 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN335-72PH5 | 335 W, 72 cell polycrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 335 | 307 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.39 | 46.3 | 8.82 | 38 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7006 | 36.867 | 6.8023 | 33.9503 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN335-72PH5BB | 335 W, 72 cell polycrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 335 | 307 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.39 | 46.3 | 8.82 | 38 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7006 | 36.867 | 6.8023 | 33.9503 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN335-72PH5BW | 335 W, 72 cell polycrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 335 | 307 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.39 | 46.3 | 8.82 | 38 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7006 | 36.867 | 6.8023 | 33.9503 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN335-72PM5 | 335 W, 72 cell polycrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 335 | 307 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.39 | 46.3 | 8.82 | 38 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7006 | 36.867 | 6.8023 | 33.9503 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN335-72PM5BB | 335 W, 72 cell polycrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 335 | 307 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.39 | 46.3 | 8.82 | 38 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7006 | 36.867 | 6.8023 | 33.9503 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN335-72PM5BW | 335 W, 72 cell polycrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 335 | 307 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.39 | 46.3 | 8.82 | 38 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7006 | 36.867 | 6.8023 | 33.9503 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN340-72PH5 | 340 W, 72 cell polycrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 340 | 311.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.48 | 46.5 | 8.91 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7179 | 37.061 | 6.8717 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN340-72PH5BB | 340 W, 72 cell polycrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 340 | 311.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.48 | 46.5 | 8.91 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7179 | 37.061 | 6.8717 | 34.129 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN340-72PH5BW | 340 W, 72 cell polycrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 340 | 311.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.48 | 46.5 | 8.91 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7179 | 37.061 | 6.8717 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN340-72PM5 | 340 W, 72 cell polycrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 340 | 311.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.48 | 46.5 | 8.91 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7179 | 37.061 | 6.8717 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN340-72PM5BB | 340 W, 72 cell polycrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 340 | 311.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.48 | 46.5 | 8.91 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7179 | 37.061 | 6.8717 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN340-72PM5BW | 340 W, 72 cell polycrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 340 | 311.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.48 | 46.5 | 8.91 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.7179 | 37.061 | 6.8717 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN345-72PH5 | 345 W, 72 cell polycrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 345 | 316.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.57 | 46.7 | 9.04 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.743 | 37.061 | 6.972 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN345-72PH5BB | 345 W, 72 cell polycrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 345 | 316.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.57 | 46.7 | 9.04 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.743 | 37.061 | 6.972 | 34.129 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN345-72PH5BW | 345 W, 72 cell polycrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 345 | 316.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.57 | 46.7 | 9.04 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.743 | 37.061 | 6.972 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN345-72PM5 | 345 W, 72 cell polycrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 345 | 316.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.57 | 46.7 | 9.04 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.743 | 37.061 | 6.972 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN345-72PM5BB | 345 W, 72 cell polycrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 345 | 316.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.57 | 46.7 | 9.04 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.743 | 37.061 | 6.972 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN345-72PM5BW | 345 W, 72 cell polycrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 345 | 316.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.57 | 46.7 | 9.04 | 38.2 | 45.2 | -0.40858 | 0.0492 | -0.30037 |  |  | 1.743 | 37.061 | 6.972 | 34.129 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN360-72MH5 | 360 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 360 | 330.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.78 | 47.3 | 9.22 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7409 | 39.199 | 6.9183 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN360-72MH5BB | 360 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 360 | 330.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.78 | 47.3 | 9.22 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7409 | 39.199 | 6.9183 | 35.8562 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN360-72MH5BW | 360 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 360 | 330.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.78 | 47.3 | 9.22 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7409 | 39.199 | 6.9183 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN360-72MM5 | 360 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 360 | 330.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.78 | 47.3 | 9.22 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7409 | 39.199 | 6.9183 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN360-72MM5BB | 360 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 360 | 330.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.78 | 47.3 | 9.22 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7409 | 39.199 | 6.9183 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN360-72MM5BW | 360 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 360 | 330.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.78 | 47.3 | 9.22 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7409 | 39.199 | 6.9183 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN365-72MH5 | 365 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 365 | 335.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.89 | 47.5 | 9.32 | 39.2 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7598 | 39.2992 | 6.9933 | 35.9479 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN365-72MH5BB | 365 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 365 | 335.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.89 | 47.5 | 9.32 | 39.2 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7598 | 39.2992 | 6.9933 | 35.9479 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN365-72MH5BW | 365 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 365 | 335.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.89 | 47.5 | 9.32 | 39.2 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7598 | 39.2992 | 6.9933 | 35.9479 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN365-72MM5 | 365 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 365 | 335.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.89 | 47.5 | 9.32 | 39.2 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7598 | 39.2992 | 6.9933 | 35.9479 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN365-72MM5BB | 365 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 365 | 335.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.89 | 47.5 | 9.32 | 39.2 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7598 | 39.2992 | 6.9933 | 35.9479 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN365-72MM5BW | 365 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 365 | 335.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.89 | 47.5 | 9.32 | 39.2 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7598 | 39.2992 | 6.9933 | 35.9479 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN370-72MH5 | 370 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 370 | 340.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.99 | 47.6 | 9.4 | 39.4 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7749 | 39.4997 | 7.0534 | 36.1313 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN370-72MH5BB | 370 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 370 | 340.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.99 | 47.6 | 9.4 | 39.4 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7749 | 39.4997 | 7.0534 | 36.1313 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN370-72MH5BW | 370 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 370 | 340.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.99 | 47.6 | 9.4 | 39.4 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7749 | 39.4997 | 7.0534 | 36.1313 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN370-72MM5 | 370 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 370 | 340.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.99 | 47.6 | 9.4 | 39.4 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7749 | 39.4997 | 7.0534 | 36.1313 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN370-72MM5BB | 370 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 370 | 340.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.99 | 47.6 | 9.4 | 39.4 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7749 | 39.4997 | 7.0534 | 36.1313 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN370-72MM5BW | 370 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 370 | 340.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.99 | 47.6 | 9.4 | 39.4 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.7749 | 39.4997 | 7.0534 | 36.1313 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN375-72MH5 | 375 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 375 | 345.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.98 | 47.6 | 9.59 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8108 | 39.199 | 7.1959 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN375-72MH5BB | 375 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 375 | 345.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.98 | 47.6 | 9.59 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8108 | 39.199 | 7.1959 | 35.8562 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN375-72MH5BW | 375 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 375 | 345.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.98 | 47.6 | 9.59 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8108 | 39.199 | 7.1959 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN375-72MM5 | 375 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 375 | 345.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.98 | 47.6 | 9.59 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8108 | 39.199 | 7.1959 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN375-72MM5BB | 375 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 375 | 345.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.98 | 47.6 | 9.59 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8108 | 39.199 | 7.1959 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN375-72MM5BW | 375 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 375 | 345.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.98 | 47.6 | 9.59 | 39.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8108 | 39.199 | 7.1959 | 35.8562 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN380-72MH5 | 380 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 380 | 349.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.07 | 47.8 | 9.67 | 39.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8259 | 39.3995 | 7.256 | 36.0396 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN380-72MH5BB | 380 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 380 | 349.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.07 | 47.8 | 9.67 | 39.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8259 | 39.3995 | 7.256 | 36.0396 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN380-72MH5BW | 380 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 380 | 349.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.07 | 47.8 | 9.67 | 39.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8259 | 39.3995 | 7.256 | 36.0396 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN380-72MM5 | 380 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 380 | 349.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.07 | 47.8 | 9.67 | 39.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8259 | 39.3995 | 7.256 | 36.0396 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN380-72MM5BB | 380 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 380 | 349.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.07 | 47.8 | 9.67 | 39.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8259 | 39.3995 | 7.256 | 36.0396 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN380-72MM5BW | 380 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 380 | 349.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.07 | 47.8 | 9.67 | 39.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8259 | 39.3995 | 7.256 | 36.0396 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN385-72MH5 | 385 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 385 | 354.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.14 | 47.9 | 9.75 | 39.5 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.841 | 39.6 | 7.316 | 36.223 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN385-72MH5BB | 385 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 385 | 354.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.14 | 47.9 | 9.75 | 39.5 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.841 | 39.6 | 7.316 | 36.223 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN385-72MH5BW | 385 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 385 | 354.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.14 | 47.9 | 9.75 | 39.5 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.841 | 39.6 | 7.316 | 36.223 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN385-72MM5 | 385 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 385 | 354.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.14 | 47.9 | 9.75 | 39.5 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.841 | 39.6 | 7.316 | 36.223 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN385-72MM5BB | 385 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 385 | 354.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.14 | 47.9 | 9.75 | 39.5 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.841 | 39.6 | 7.316 | 36.223 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN385-72MM5BW | 385 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 385 | 354.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.14 | 47.9 | 9.75 | 39.5 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.841 | 39.6 | 7.316 | 36.223 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN390-72MH5 | 390 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 390 | 359.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.21 | 48.1 | 9.83 | 39.7 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8561 | 39.8005 | 7.376 | 36.4064 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN390-72MH5BB | 390 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 390 | 359.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.21 | 48.1 | 9.83 | 39.7 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8561 | 39.8005 | 7.376 | 36.4064 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN390-72MH5BW | 390 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 390 | 359.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.21 | 48.1 | 9.83 | 39.7 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8561 | 39.8005 | 7.376 | 36.4064 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN390-72MM5 | 390 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 390 | 359.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.21 | 48.1 | 9.83 | 39.7 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8561 | 39.8005 | 7.376 | 36.4064 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN390-72MM5BB | 390 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 390 | 359.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.21 | 48.1 | 9.83 | 39.7 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8561 | 39.8005 | 7.376 | 36.4064 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN390-72MM5BW | 390 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 390 | 359.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.21 | 48.1 | 9.83 | 39.7 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8561 | 39.8005 | 7.376 | 36.4064 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN395-72MH5 | 395 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 395 | 364.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.29 | 48.3 | 9.91 | 39.9 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8712 | 40.001 | 7.4361 | 36.5898 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN395-72MH5BB | 395 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 395 | 364.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.29 | 48.3 | 9.91 | 39.9 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8712 | 40.001 | 7.4361 | 36.5898 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN395-72MH5BW | 395 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 395 | 364.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.29 | 48.3 | 9.91 | 39.9 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8712 | 40.001 | 7.4361 | 36.5898 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN395-72MM5 | 395 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 395 | 364.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.29 | 48.3 | 9.91 | 39.9 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8712 | 40.001 | 7.4361 | 36.5898 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN395-72MM5BB | 395 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 395 | 364.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.29 | 48.3 | 9.91 | 39.9 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8712 | 40.001 | 7.4361 | 36.5898 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN395-72MM5BW | 395 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 395 | 364.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.29 | 48.3 | 9.91 | 39.9 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8712 | 40.001 | 7.4361 | 36.5898 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN400-72MH5 | 400 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 400 | 368.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.36 | 48.5 | 9.98 | 40.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8844 | 40.2015 | 7.4886 | 36.7732 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN400-72MH5BB | 400 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 400 | 368.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.36 | 48.5 | 9.98 | 40.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8844 | 40.2015 | 7.4886 | 36.7732 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN400-72MH5BW | 400 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 400 | 368.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.36 | 48.5 | 9.98 | 40.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8844 | 40.2015 | 7.4886 | 36.7732 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN400-72MM5 | 400 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 400 | 368.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.36 | 48.5 | 9.98 | 40.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8844 | 40.2015 | 7.4886 | 36.7732 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN400-72MM5BB | 400 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 400 | 368.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.36 | 48.5 | 9.98 | 40.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8844 | 40.2015 | 7.4886 | 36.7732 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN400-72MM5BW | 400 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 400 | 368.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.36 | 48.5 | 9.98 | 40.1 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8844 | 40.2015 | 7.4886 | 36.7732 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN405-72MH5 | 405 W, 72 cell monocrystalline module, white substrate, white frame, 1500V max system Vdc | UL 1703 | 405 | 373.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.44 | 48.7 | 10.05 | 40.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8976 | 40.402 | 7.5411 | 36.9566 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN405-72MH5BB | 405 W, 72 cell monocrystalline module, black substrate, black frame, 1500V max system Vdc | UL 1703 | 405 | 373.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.44 | 48.7 | 10.05 | 40.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8976 | 40.402 | 7.5411 | 36.9566 | [6 empty] | 2019-08-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN405-72MH5BW | 405 W, 72 cell monocrystalline module, white substrate, black frame,1500V max system Vdc | UL 1703 | 405 | 373.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.44 | 48.7 | 10.05 | 40.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8976 | 40.402 | 7.5411 | 36.9566 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN405-72MM5 | 405 W, 72 cell monocrystalline module, white substrate, white frame, 1000V max system Vdc | UL 1703 | 405 | 373.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.44 | 48.7 | 10.05 | 40.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8976 | 40.402 | 7.5411 | 36.9566 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN405-72MM5BB | 405 W, 72 cell monocrystalline module, black substrate, black frame,1000V max system Vdc | UL 1703 | 405 | 373.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.44 | 48.7 | 10.05 | 40.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8976 | 40.402 | 7.5411 | 36.9566 | [6 empty] | 2019-10-01 | 2019-11-01
China Sunergy (Nanjing) Co.,Ltd. | CSUN405-72MM5BW | 405 W, 72 cell monocrystalline module,white substrate, black frame,1000V max system Vdc | UL 1703 | 405 | 373.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.44 | 48.7 | 10.05 | 40.3 | 45.3 | -0.40187 | 0.05284 | -0.31524 |  |  | 1.8976 | 40.402 | 7.5411 | 36.9566 | [6 empty] | 2019-10-01 | 2019-11-01
Chinaland Solar Energy | HSE235-60P | 235 W Polycrystalline Module | UL 1703 | 235 | 207.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.43 | 35.6 | 7.88 | 29.8 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.6 | 29.24 | 6.22 | 26.21 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19908
Chinaland Solar Energy | HSE235-60P-B | 235 W Polycrystalline Module | UL 1703 | 235 | 208.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7095 | 60 | 1 | N | 8.43 | 35.6 | 7.88 | 29.8 | 48.1 | -0.4547 | 0.0282 | -0.358 | -0.0063 | -0.4617 | 1.6 | 29.23 | 6.19 | 26.34 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.19901
Chinaland Solar Energy | HSE240-60M | 240 W Monocrystalline Module | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.63 | 36.2 | 8.11 | 29.6 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.6493 | 29.3417 | 6.324 | 26.3568 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20164
Chinaland Solar Energy | HSE240-60M-B | 240 W Monocrystalline Module | UL 1703 | 240 | 216.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7095 | 60 | 1 | N | 8.63 | 36.2 | 8.11 | 29.6 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.65 | 29.29 | 6.38 | 26.54 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.20137
Chinaland Solar Energy | HSE240-60P | 240 W Polycrystalline Module | UL 1703 | 240 | 212.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.57 | 35.7 | 8 | 30 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.63 | 29.44 | 6.31 | 26.39 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19995
Chinaland Solar Energy | HSE240-60P-B | 240 W Polycrystalline Module | UL 1703 | 240 | 213.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7095 | 60 | 1 | N | 8.57 | 35.7 | 8 | 30 | 48.1 | -0.4547 | 0.0282 | -0.358 | -0.0063 | -0.4617 | 1.62 | 29.43 | 6.28 | 26.51 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.19865
Chinaland Solar Energy | HSE245-60M | 245 W Monocrystalline Module | UL 1703 | 245 | 221.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.65 | 36.8 | 8.13 | 30.1 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.6534 | 29.8373 | 6.3396 | 26.802 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20136
Chinaland Solar Energy | HSE245-60M-B | 245 W Monocrystalline Module | UL 1703 | 245 | 221.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7095 | 60 | 1 | N | 8.65 | 36.8 | 8.13 | 30.1 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.66 | 29.78 | 6.39 | 26.99 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.20177
Chinaland Solar Energy | HSE245-60P | 245 W Polycrystalline Module | UL 1703 | 245 | 216.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.63 | 36.1 | 8.05 | 30.4 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.64 | 29.83 | 6.35 | 26.74 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19968
Chinaland Solar Energy | HSE245-60P-B | 245 W Polycrystalline Module | UL 1703 | 245 | 217.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7095 | 60 | 1 | N | 8.63 | 36.1 | 8.05 | 30.4 | 48.1 | -0.4547 | 0.0282 | -0.358 | -0.0063 | -0.4617 | 1.63 | 29.82 | 6.32 | 26.87 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.19839
Chinaland Solar Energy | HSE250-60M | 250 W Monocrystalline Module | UL 1703 | 250 | 226 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.74 | 37.3 | 8.21 | 30.5 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.6697 | 30.2338 | 6.402 | 27.1582 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20192
Chinaland Solar Energy | HSE250-60M-B | 250 W Monocrystalline Module | UL 1703 | 250 | 225.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7095 | 60 | 1 | N | 8.74 | 37.3 | 8.21 | 30.5 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.67 | 30.18 | 6.46 | 27.34 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.2016
Chinaland Solar Energy | HSE250-60P | 250 W Polycrystalline Module | UL 1703 | 250 | 221.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.71 | 36.3 | 8.17 | 30.6 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.66 | 30.03 | 6.45 | 26.92 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.1994
Chinaland Solar Energy | HSE250-60P-B | 250 W Polycrystalline Module | UL 1703 | 250 | 222.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7095 | 60 | 1 | N | 8.71 | 36.3 | 8.17 | 30.6 | 48.1 | -0.4547 | 0.0282 | -0.358 | -0.0063 | -0.4617 | 1.66 | 30.02 | 6.41 | 27.04 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.19933
Chinaland Solar Energy | HSE255-60M | 255 W Monocrystalline Module | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.85 | 37.4 | 8.32 | 30.6 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.6863 | 30.3626 | 6.5829 | 27.4549 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20079
Chinaland Solar Energy | HSE255-60M-B | 255 W Monocrystalline Module | UL 1703 | 255 | 230.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7095 | 60 | 1 | N | 8.85 | 37.4 | 8.32 | 30.6 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.7 | 30.27 | 6.54 | 27.43 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.2018
Chinaland Solar Energy | HSE255-60P | 255 W Polycrystalline Module | UL 1703 | 255 | 225.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.8 | 36.4 | 8.3 | 30.7 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.69 | 30.13 | 6.55 | 27 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19969
Chinaland Solar Energy | HSE255-60P-B | 255 W Polycrystalline Module | UL 1703 | 255 | 226.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7095 | 60 | 1 | N | 8.8 | 36.4 | 8.3 | 30.7 | 48.1 | -0.4547 | 0.0282 | -0.358 | -0.0063 | -0.4617 | 1.68 | 30.12 | 6.52 | 27.13 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.19844
Chinaland Solar Energy | HSE260-60M | 260 W Monocrystalline Module | UL 1703 | 260 | 235.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.89 | 38 | 8.35 | 31.1 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.6924 | 30.8588 | 6.6066 | 27.9036 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20087
Chinaland Solar Energy | HSE260-60M-B | 260 W Monocrystalline Module | UL 1703 | 260 | 235 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7095 | 60 | 1 | N | 8.89 | 38 | 8.35 | 31.1 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.69 | 30.86 | 6.61 | 27.9 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.20059
Chinaland Solar Energy | HSE260-60P | 260 W Polycrystalline Module | UL 1703 | 260 | 230.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.89 | 36.7 | 8.42 | 30.9 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.71 | 30.48 | 6.62 | 27.07 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20046
Chinaland Solar Energy | HSE260-60P-B | 260 W Polycrystalline Module | UL 1703 | 260 | 231.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7095 | 60 | 1 | N | 8.89 | 36.7 | 8.42 | 30.9 | 48.1 | -0.4547 | 0.0282 | -0.358 | -0.0063 | -0.4617 | 1.71 | 30.65 | 6.62 | 27.59 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.20158
Chinaland Solar Energy | HSE265-60M | 265 W Monocrystalline Module | UL 1703 | 265 | 239.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 9.02 | 38.3 | 8.48 | 31.3 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.7188 | 31.0572 | 6.7095 | 28.083 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20144
Chinaland Solar Energy | HSE265-60M-B | 265 W Monocrystalline Module | UL 1703 | 265 | 239.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7095 | 60 | 1 | N | 9.02 | 38.3 | 8.48 | 31.3 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.72 | 31.06 | 6.71 | 28.08 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.2016
Chinaland Solar Energy | HSE265-60P | 265 W Polycrystalline Module | UL 1703 | 265 | 234.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.94 | 37 | 8.54 | 31 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.74 | 30.58 | 6.72 | 27.16 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20079
Chinaland Solar Energy | HSE265-60P-B | 265 W Polycrystalline Module | UL 1703 | 265 | 236 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7095 | 60 | 1 | N | 8.94 | 37 | 8.54 | 31 | 48.1 | -0.4547 | 0.0282 | -0.358 | -0.0063 | -0.4617 | 1.73 | 30.75 | 6.71 | 27.68 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.20075
Chinaland Solar Energy | HSE270-60M | 270 W Monocrystalline Module | UL 1703 | 270 | 244.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 9.07 | 37.8 | 8.51 | 31.7 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.7249 | 31.4541 | 6.7332 | 28.4419 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20094
Chinaland Solar Energy | HSE270-60M-B | 270 W Monocrystalline Module | UL 1703 | 270 | 244.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7095 | 60 | 1 | N | 9.07 | 37.8 | 8.51 | 31.7 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.72 | 31.45 | 6.73 | 28.44 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.20035
Chinaland Solar Energy | HSE270-60P | 270 W Polycrystalline Module | UL 1703 | 270 | 239.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 9.06 | 37.2 | 8.65 | 31.2 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.76 | 30.78 | 6.81 | 27.34 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20064
Chinaland Solar Energy | HSE270-60P-B | 270 W Polycrystalline Module | UL 1703 | 270 | 240.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7095 | 60 | 1 | N | 9.06 | 37.2 | 8.65 | 31.2 | 48.1 | -0.4547 | 0.0282 | -0.358 | -0.0063 | -0.4617 | 1.76 | 30.95 | 6.8 | 27.86 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.20175
Chinaland Solar Energy | HSE275-60M-B | 275 W Monocrystalline Module | UL 1703 | 275 | 248.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7095 | 60 | 1 | N | 9.21 | 38 | 8.63 | 31.9 | 45.5 | -0.4481 | 0.0431 | -0.3393 | -0.0081 | -0.4489 | 1.75 | 31.65 | 6.83 | 28.62 | Rack | Flat Plate | 1.02 | 1.676 | 1 | 0.20141
Chinaland Solar Energy | HSE290-72P | 290 W Polycrystalline Module | UL 1703 | 290 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9305 | 72 | 1 | N | 8.57 | 43.2 | 8 | 36.3 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.62 | 35.6 | 6.07 | 31.67 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.19887
Chinaland Solar Energy | HSE295-72M | 295 W Monocrystalline Module | UL 1703 | 295 | 266 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9305 | 72 | 1 | N | 8.65 | 44.4 | 8.13 | 36.3 | 46.1 | -0.445 | 0.0563 | -0.3447 | -0.0099 | -0.4566 | 1.66 | 35.8 | 6.47 | 31.98 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.20145
Chinaland Solar Energy | HSE295-72P | 295 W Polycrystalline Module | UL 1703 | 295 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9305 | 72 | 1 | N | 8.64 | 43.3 | 8.08 | 36.5 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.64 | 35.8 | 6.13 | 31.85 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.19902
Chinaland Solar Energy | HSE300-72M | 300 W Monocrystalline Module | UL 1703 | 300 | 270.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9305 | 72 | 1 | N | 8.74 | 44.6 | 8.21 | 36.5 | 46.1 | -0.445 | 0.0563 | -0.3447 | -0.0099 | -0.4566 | 1.67 | 35.99 | 6.54 | 32.16 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.20034
Chinaland Solar Energy | HSE300-72P | 300 W Polycrystalline Module | UL 1703 | 300 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9305 | 72 | 1 | N | 8.71 | 43.6 | 8.17 | 36.7 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.66 | 36 | 6.2 | 32.02 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.1992
Chinaland Solar Energy | HSE305-72M | 305 W Monocrystalline Module | UL 1703 | 305 | 275.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9305 | 72 | 1 | N | 8.79 | 45.1 | 8.26 | 36.9 | 46.1 | -0.445 | 0.0563 | -0.3447 | -0.0099 | -0.4566 | 1.68 | 36.39 | 6.58 | 32.51 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.20044
Chinaland Solar Energy | HSE305-72P | 305 W Polycrystalline Module | UL 1703 | 305 | 270.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9305 | 72 | 1 | N | 8.78 | 43.7 | 8.27 | 36.9 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.68 | 36.19 | 6.27 | 32.2 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.19934
Chinaland Solar Energy | HSE310-72M | 310 W Monocrystalline Module | UL 1703 | 310 | 279.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9305 | 72 | 1 | N | 8.89 | 45.4 | 8.35 | 37.1 | 46.1 | -0.445 | 0.0563 | -0.3447 | -0.0099 | -0.4566 | 1.7 | 36.58 | 6.65 | 32.69 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.2006
Chinaland Solar Energy | HSE310-72P | 310 W Polycrystalline Module | UL 1703 | 310 | 274.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9305 | 72 | 1 | N | 8.86 | 44 | 8.36 | 37.1 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.7 | 36.39 | 6.34 | 32.37 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.19956
Chinaland Solar Energy | HSE315-72M | 315 W Monocrystalline Module | UL 1703 | 315 | 284.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9305 | 72 | 1 | N | 8.95 | 45.9 | 8.41 | 37.5 | 46.1 | -0.445 | 0.0563 | -0.3447 | -0.0099 | -0.4566 | 1.71 | 36.98 | 6.7 | 33.04 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.20075
Chinaland Solar Energy | HSE315-72P | 315 W Polycrystalline Module | UL 1703 | 315 | 279.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9305 | 72 | 1 | N | 8.93 | 44.3 | 8.44 | 37.3 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.71 | 36.58 | 6.4 | 32.55 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.19858
Chinaland Solar Energy | HSE320-72M | 320 W Monocrystalline Module | UL 1703 | 320 | 289.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9305 | 72 | 1 | N | 9.04 | 45.1 | 8.48 | 37.7 | 46.1 | -0.445 | 0.0563 | -0.3447 | -0.0099 | -0.4566 | 1.73 | 37.18 | 6.75 | 33.22 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.201
Chinaland Solar Energy | HSE320-72P | 320 W Polycrystalline Module | UL 1703 | 320 | 283.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9305 | 72 | 1 | N | 9.03 | 44.6 | 8.53 | 37.5 | 48.3 | -0.4735 | 0.0323 | -0.3651 | -0.0163 | -0.4667 | 1.73 | 36.78 | 6.47 | 32.72 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.19884
Chinaland Solar Energy | HSE325-72M | 325 W Monocrystalline Module | UL 1703 | 325 | 293.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9305 | 72 | 1 | N | 9.14 | 45.9 | 8.58 | 37.9 | 46.1 | -0.445 | 0.0563 | -0.3447 | -0.0099 | -0.4566 | 1.75 | 37.37 | 6.83 | 33.39 | Rack | Flat Plate | 0.99 | 1.95 | 1 | 0.20122
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M-175 | 175 W Monocrystalline Module | UL 1703 | 175 | 153.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 44.3 | 4.68 | 36.33 | 48.6 | -0.4795 | 0.06248 | -0.35514 | -0.02165 | -0.46194 | 0.86446 | 35.4129 | 3.4876 | 32.3906 | Rack | Flat-Plate | 0.808 | 1.58 | 1 | 0.17493
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M-180 | 180 W Monocrystalline Module | UL 1703 | 180 | 158.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.31 | 44.88 | 5 | 36.02 | 48.6 | -0.4795 | 0.06248 | -0.35514 | -0.0011 | -0.46194 | 0.90249 | 34.0746 | 3.6411 | 31.1665 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17084
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M(BL)-185 | 185 W Monocrystalline Module | UL 1703 | 185 | 166.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.39 | 45.12 | 5.09 | 36.38 | 45.8 | -0.4613 | 0.0726 | -0.4023 | -0.0283 | -0.4373 | 1.0511 | 35.2453 | 4.1708 | 32.9062 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.20024
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M-185 | 185 W Monocrystalline Module | UL 1703 | 185 | 168.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 5.39 | 45.12 | 5.09 | 36.38 | 44.9 | -0.431 | 0.045 | -0.362 | 0.009 | -0.43 | 1.0096 | 34.5053 | 4.0238 | 32.8081 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18831
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M(BL)-190 | 190 W Monocrystalline Module | UL 1703 | 190 | 170.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.47 | 45.37 | 5.17 | 36.74 | 45.8 | -0.4613 | 0.0726 | -0.4023 | -0.0283 | -0.4373 | 1.0676 | 35.5941 | 4.2364 | 33.2319 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.2
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M-190 | 190 W Monocrystalline Module | UL 1703 | 190 | 171.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.47 | 45.37 | 5.17 | 36.74 | 45.9 | -0.4499 | 0.0722 | -0.3937 | 0.0113 | -0.4611 | 1.0557 | 35.8886 | 4.1923 | 33.6082 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.19941
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M(BL)-195 | 195 W Monocrystalline Module | UL 1703 | 195 | 175.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.55 | 45.62 | 5.25 | 37.1 | 45.8 | -0.4613 | 0.0726 | -0.4023 | -0.0283 | -0.4373 | 1.0841 | 35.9428 | 4.3019 | 33.5575 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.19983
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M-195 | 195 W Monocrystalline Module | UL 1703 | 195 | 175.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.55 | 45.62 | 5.25 | 37.1 | 45.9 | -0.4499 | 0.0722 | -0.3937 | 0.0113 | -0.4611 | 1.0721 | 36.2403 | 4.2572 | 33.9375 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.19924
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M(BL)-200 | 200 W Monocrystalline Module | UL 1703 | 200 | 180.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.63 | 45.87 | 5.34 | 37.46 | 45.8 | -0.4613 | 0.0726 | -0.4023 | -0.0283 | -0.4373 | 1.1027 | 36.2916 | 4.3757 | 33.8831 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.20009
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M-200 | 200 W Monocrystalline Module | UL 1703 | 200 | 180.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.63 | 45.87 | 5.34 | 37.46 | 45.9 | -0.4499 | 0.0722 | -0.3937 | 0.0113 | -0.4611 | 1.0904 | 36.592 | 4.3301 | 34.2669 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.19951
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M-205 | 205 W Monocrystalline Module | UL 1703 | 205 | 185.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.71 | 46.11 | 5.42 | 37.83 | 45.9 | -0.4499 | 0.0722 | -0.3937 | 0.0113 | -0.4611 | 1.1068 | 36.9534 | 4.395 | 34.6053 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.19951
Chint Solar (Zhejiang) Co., Ltd. | CHSM5612M-210 | 210 W Monocrystalline Module | UL 1703 | 210 | 189.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.79 | 46.36 | 5.5 | 38.19 | 45.9 | -0.4499 | 0.0722 | -0.3937 | 0.0113 | -0.4611 | 1.1231 | 37.305 | 4.4599 | 34.9346 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.19951
Chint Solar (Zhejiang) Co., Ltd. | CHSM6609M-215 | 215 W Monocrystalline Module | UL 1703 | 215 | 194.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4701 | 54 | 1 | N | 8.55 | 33.87 | 8.06 | 26.64 | 45.9 | -0.4302 | 0.0779 | -0.4031 | -0.0143 | -0.4175 | 1.6622 | 25.9912 | 6.613 | 24.2709 | Rack | Flat Plate | 0.988 | 1.488 | 1 | 0.20094
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-215 | 215 W Polycrystalline Module | UL 1703 | 215 | 194.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6421 | 60 | 1 | N | 7.96 | 36.65 | 7.23 | 29.65 | 43.4 | -0.46872 | 0.052 | -0.3441 | -0.00792 | -0.46319 | 1.5493 | 29.3423 | 6.0939 | 26.3842 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.21144
Chint Solar (Zhejiang) Co., Ltd. | CHSM6609M-220 | 220 W Monocrystalline Module | UL 1703 | 220 | 198.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.485 | 54 | 1 | N | 8.58 | 34 | 8.15 | 26.99 | 46 | -0.4451 | 0.0892 | -0.4138 | 0.0253 | -0.4658 | 1.6857 | 26.2967 | 6.6324 | 25.0105 | Rack | Flat Plate | 0.994 | 1.494 | 1 | 0.20149
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-220 | 220 W Monocrystalline Module | UL 1703 | 220 | 195.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6421 | 60 | 1 | N | 8.45 | 37.18 | 7.78 | 28.3 | 47.2 | -0.46868 | 0.03462 | -0.32806 | -0.04151 | -0.43259 | 1.5416 | 27.7531 | 6.3001 | 25.263 | Rack | Flat-Plate | 0.994 | 1.652 | 1 | 0.19448
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-220 | 220 W Polycrystalline Module | UL 1703 | 220 | 199.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6421 | 60 | 1 | N | 8.12 | 36.77 | 7.38 | 29.7 | 43.4 | -0.46872 | 0.052 | -0.3441 | -0.00792 | -0.46319 | 1.5814 | 29.3918 | 6.2203 | 26.4287 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.21128
Chint Solar (Zhejiang) Co., Ltd. | CHSM6609M-225 | 225 W Monocrystalline Module | UL 1703 | 225 | 202.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.485 | 54 | 1 | N | 8.61 | 34.15 | 8.23 | 27.42 | 46 | -0.4451 | 0.0892 | -0.4138 | 0.0253 | -0.4658 | 1.7022 | 26.7156 | 6.6975 | 25.4089 | Rack | Flat Plate | 0.994 | 1.494 | 1 | 0.20212
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-225 | 225 W Monocrystalline Module | UL 1703 | 225 | 199.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6421 | 60 | 1 | N | 8.48 | 37.33 | 7.86 | 28.66 | 47.2 | -0.46868 | 0.03462 | -0.32806 | -0.04151 | -0.43259 | 1.5575 | 28.1062 | 6.3648 | 25.5843 | Rack | Flat-Plate | 0.994 | 1.652 | 1 | 0.19455
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-225 | 225 W Polycrystalline Module | UL 1703 | 225 | 204.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6421 | 60 | 1 | N | 8.27 | 36.88 | 7.55 | 29.76 | 43.4 | -0.46872 | 0.052 | -0.3441 | -0.00792 | -0.46319 | 1.6179 | 29.4511 | 6.3636 | 26.4821 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.21177
Chint Solar (Zhejiang) Co., Ltd. | CHSM6609M-230 | 230 W Monocrystalline Module | UL 1703 | 230 | 207.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.485 | 54 | 1 | N | 8.64 | 34.28 | 8.31 | 27.74 | 46 | -0.4451 | 0.0892 | -0.4138 | 0.0253 | -0.4658 | 1.7188 | 27.0274 | 6.7626 | 25.7055 | Rack | Flat Plate | 0.994 | 1.494 | 1 | 0.20198
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-230 | 230 W Monocrystalline Module | UL 1703 | 230 | 204.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6421 | 60 | 1 | N | 8.52 | 37.48 | 7.93 | 29.03 | 47.2 | -0.46868 | 0.03462 | -0.32806 | -0.04151 | -0.43259 | 1.5713 | 28.469 | 6.4215 | 25.9146 | Rack | Flat-Plate | 0.994 | 1.652 | 1 | 0.1945
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-230 | 230 W Polycrystalline Module | UL 1703 | 230 | 208.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6421 | 60 | 1 | N | 8.43 | 37 | 7.69 | 29.81 | 43.4 | -0.46872 | 0.052 | -0.3441 | -0.00792 | -0.46319 | 1.6479 | 29.5006 | 6.4816 | 26.5266 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.21136
Chint Solar (Zhejiang) Co., Ltd. | CHSM6609M-235 | 235 W Monocrystalline Module | UL 1703 | 235 | 212.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.485 | 54 | 1 | N | 8.67 | 34.42 | 8.4 | 28.12 | 46 | -0.4451 | 0.0892 | -0.4138 | 0.0253 | -0.4658 | 1.7374 | 27.3976 | 6.8358 | 26.0576 | Rack | Flat Plate | 0.994 | 1.494 | 1 | 0.20256
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-235 | 235 W Monocrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6421 | 60 | 1 | N | 8.55 | 37.63 | 8.01 | 29.39 | 47.2 | -0.46868 | 0.03462 | -0.32806 | -0.0032 | -0.43259 | 1.5872 | 28.8221 | 6.4863 | 26.236 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.19466
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-235 | 235 W Polycrystalline Module | UL 1703 | 235 | 213.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6421 | 60 | 1 | N | 8.58 | 37.11 | 7.84 | 29.85 | 43.4 | -0.46872 | 0.052 | -0.3441 | -0.00792 | -0.46319 | 1.8 | 30.0738 | 6.49 | 27.042 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.23035
Chint Solar (Zhejiang) Co., Ltd. | CHSM6609M-240 | 240 W Monocrystalline Module | UL 1703 | 240 | 216.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.485 | 54 | 1 | N | 8.71 | 34.56 | 8.46 | 28.45 | 46 | -0.4451 | 0.0892 | -0.4138 | 0.0253 | -0.4658 | 1.7498 | 27.7192 | 6.8847 | 26.3634 | Rack | Flat Plate | 0.994 | 1.494 | 1 | 0.2021
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M(BL)-240 | 240 W Monocrystalline Module | UL 1703 | 240 | 216.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.58 | 37.78 | 8.08 | 29.75 | 46.2 | -0.4432 | 0.0899 | -0.4119 | 0.0465 | -0.483 | 1.6295 | 29.7204 | 6.5849 | 27.413 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20179
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-240 | 240 W Monocrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6421 | 60 | 1 | N | 8.61 | 37.78 | 8.08 | 29.75 | 47.2 | -0.46868 | 0.03462 | -0.32806 | -0.0032 | -0.43259 | 1.6011 | 29.1751 | 6.543 | 26.5574 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.19463
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-240 | 240 W Polycrystalline Module | UL 1703 | 240 | 218.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6421 | 60 | 1 | N | 8.59 | 37.77 | 8.13 | 29.54 | 43.4 | -0.46872 | 0.052 | -0.3441 | -0.00792 | -0.46319 | 1.6664 | 28.4376 | 6.5141 | 26.7206 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.19745
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M(BL)-245 | 245 W Monocrystalline Module | UL 1703 | 245 | 220.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.61 | 37.94 | 8.16 | 30.12 | 46.2 | -0.4432 | 0.0899 | -0.4119 | 0.0465 | -0.483 | 1.6457 | 30.09 | 6.6501 | 27.7539 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20212
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-245 | 245 W Monocrystalline Module | UL 1703 | 245 | 220.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6421 | 60 | 1 | N | 8.61 | 37.94 | 8.16 | 30.12 | 47.2 | -0.431 | 0.045 | -0.324 | -0.005 | -0.427 | 1.6667 | 27.5702 | 6.4085 | 26.7335 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.18756
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-245 | 245 W Polycrystalline Module | UL 1703 | 245 | 221.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6262 | 60 | 1 | N | 8.62 | 37.98 | 8.2 | 29.92 | 45.8 | -0.4369 | 0.0962 | -0.4137 | 0.0134 | -0.4484 | 1.6647 | 29.5499 | 6.7407 | 27.8893 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20078
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M(BL)-250 | 250 W Monocrystalline Module | UL 1703 | 250 | 225.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.64 | 38.09 | 8.23 | 30.48 | 46.2 | -0.4432 | 0.0899 | -0.4119 | 0.0465 | -0.483 | 1.6598 | 30.4497 | 6.7071 | 28.0856 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20216
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-250 | 250 W Monocrystalline Module | UL 1703 | 250 | 224.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6421 | 60 | 1 | N | 8.64 | 38.09 | 8.23 | 30.48 | 47.2 | -0.431 | 0.045 | -0.324 | -0.005 | -0.427 | 1.681 | 27.8997 | 6.4635 | 27.053 | Rack | Flat Plate | 0.994 | 1.652 | 1 | 0.1876
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-250 | 250 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 250 | 224.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 8.76 | 37.24 | 8.22 | 30.44 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.7157 | 29.7476 | 6.6511 | 27.3756 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20415
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 226.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6262 | 60 | 1 | N | 8.65 | 38.19 | 8.27 | 30.3 | 45.8 | -0.4369 | 0.0962 | -0.4137 | 0.0134 | -0.4484 | 1.6789 | 29.9252 | 6.7983 | 28.2435 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20097
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M(BL)-255 | 255 W Monocrystalline Module | UL 1703 | 255 | 230.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.67 | 38.24 | 8.31 | 30.84 | 46.2 | -0.4432 | 0.0899 | -0.4119 | 0.0465 | -0.483 | 1.6759 | 30.8093 | 6.7723 | 28.4174 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20249
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-255 | 255 W Monocrystalline Module | UL 1703 | 255 | 231.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.67 | 38.24 | 8.31 | 30.84 | 45.9 | -0.4302 | 0.0779 | -0.4031 | -0.0143 | -0.4175 | 1.7468 | 29.4571 | 6.7797 | 28.4403 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20179
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-255 | 255 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 255 | 228.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 8.85 | 37.48 | 8.33 | 30.66 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.7387 | 29.9625 | 6.7401 | 27.5734 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20429
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-255 | 255 W Polycrystalline Module | UL 1703 | 255 | 230.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6262 | 60 | 1 | N | 8.69 | 38.4 | 8.33 | 30.68 | 45.8 | -0.4369 | 0.0962 | -0.4137 | 0.0134 | -0.4484 | 1.6911 | 30.3005 | 6.8476 | 28.5977 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20094
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M(BL)-260 | 260 W Monocrystalline Module | UL 1703 | 260 | 234.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.7 | 38.39 | 8.38 | 31.19 | 46.2 | -0.4432 | 0.0899 | -0.4119 | 0.0465 | -0.483 | 1.69 | 31.159 | 6.8294 | 28.7399 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20254
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-260 | 260 W Monocrystalline Module | UL 1703 | 260 | 235.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.7 | 38.39 | 8.38 | 31.19 | 45.9 | -0.4302 | 0.0779 | -0.4031 | -0.0143 | -0.4175 | 1.7615 | 29.7914 | 6.8368 | 28.7631 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20184
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-260 | 260 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 260 | 233.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 8.95 | 37.72 | 8.43 | 30.88 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.7595 | 30.1775 | 6.821 | 27.7713 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20423
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-260 | 260 W Polycrystalline Module | UL 1703 | 260 | 235.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6262 | 60 | 1 | N | 8.72 | 38.53 | 8.39 | 31.05 | 45.8 | -0.4369 | 0.0962 | -0.4137 | 0.0134 | -0.4484 | 1.7033 | 30.6659 | 6.8969 | 28.9426 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20089
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-260 | 260 W Polycrystalline Module | UL 1703 | 260 | 232.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.12 | 44.12 | 7.34 | 35.51 | 46.8 | -0.45103 | 0.08739 | -0.33227 | 0.00691 | -0.44523 | 1.5927 | 33.7491 | 6.1215 | 31.0445 | Rack | Flat Plate | 0.994 | 1.956 | 1 | 0.20674
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-265 | 265 W Monocrystalline Module | UL 1703 | 265 | 240.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.74 | 38.55 | 8.44 | 31.49 | 45.9 | -0.4302 | 0.0779 | -0.4031 | -0.0143 | -0.4175 | 1.7741 | 30.078 | 6.8857 | 29.0397 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20136
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-265 | 265 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 265 | 238.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.04 | 37.97 | 8.53 | 31.1 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.7804 | 30.3925 | 6.9019 | 27.9691 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20419
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-265 | 265 W Polycrystalline Module | UL 1703 | 265 | 240.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6262 | 60 | 1 | N | 8.75 | 38.72 | 8.46 | 31.43 | 45.8 | -0.4369 | 0.0962 | -0.4137 | 0.0134 | -0.4484 | 1.7175 | 31.0412 | 6.9545 | 29.2968 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20118
Chint Solar (Zhejiang) Co., Ltd. | CHSM6611P-265 | 265 W Polycrystalline Module | UL 1703 | 265 | 238 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7872 | 66 | 1 | N | 8.59 | 41.55 | 8.14 | 32.56 | 47.2 | -0.4355 | 0.0935 | -0.4213 | 0.017 | -0.4521 | 1.6562 | 32.138 | 6.4229 | 29.7534 | Rack | Flat Plate | 0.994 | 1.798 | 1 | 0.20085
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-265 | 265 W Polycrystalline Module | UL 1703 | 265 | 237 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.27 | 44.24 | 7.48 | 35.54 | 46.8 | -0.45103 | 0.08739 | -0.33227 | 0.00691 | -0.44523 | 1.6231 | 33.7776 | 6.2382 | 31.0707 | Rack | Flat Plate | 0.994 | 1.956 | 1 | 0.20689
Chint Solar (Zhejiang) Co., Ltd. | CHSM60P-HC-270 | 270 W, 120 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 270 | 251.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.64 | 60 | 2 | N | 9.09 | 37.93 | 8.58 | 31.48 | 44.1 | -0.355 | 0.0415 | -0.2729 |  |  | 1.7397 | 30.0007 | 6.9473 | 29.3501 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-270 | 270 W Monocrystalline Module | UL 1703 | 270 | 245.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.77 | 38.7 | 8.51 | 31.82 | 45.9 | -0.4302 | 0.0779 | -0.4031 | -0.0143 | -0.4175 | 1.7888 | 30.3932 | 6.9429 | 29.3441 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20136
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-270 | 270 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 270 | 242.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.13 | 38.21 | 8.63 | 31.32 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.8013 | 30.6075 | 6.9828 | 28.167 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.2042
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-270 | 270 W Polycrystalline Module | UL 1703 | 270 | 242.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.13 | 38.21 | 8.63 | 31.32 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.8001 | 30.4452 | 7.0033 | 28.1135 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20298
Chint Solar (Zhejiang) Co., Ltd. | CHSM6611P-270 | 270 W Polycrystalline Module | UL 1703 | 270 | 242.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7872 | 66 | 1 | N | 8.62 | 41.78 | 8.21 | 32.91 | 47.2 | -0.4355 | 0.0935 | -0.4213 | 0.017 | -0.4521 | 1.6704 | 32.4835 | 6.4781 | 30.0733 | Rack | Flat Plate | 0.994 | 1.798 | 1 | 0.20097
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-270 | 270 W Polycrystalline Module | UL 1703 | 270 | 241.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.42 | 44.38 | 7.62 | 35.57 | 46.8 | -0.45103 | 0.08739 | -0.33227 | 0.00691 | -0.44523 | 1.6535 | 33.8061 | 6.355 | 31.097 | Rack | Flat Plate | 0.994 | 1.956 | 1 | 0.20703
Chint Solar (Zhejiang) Co., Ltd. | CHSM60P-HC-275 | 275 W, 120 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 275 | 255.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.64 | 60 | 2 | N | 9.18 | 38.17 | 8.68 | 31.68 | 44.1 | -0.355 | 0.0415 | -0.2729 |  |  | 1.76 | 30.1914 | 7.0283 | 29.5365 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M/HV-275 | 275 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 275 | 249.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.38 | 38.3565 | 8.8433 | 31.1 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8653 | 31.1346 | 7.0551 | 28.6461 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21118
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-275 | 275 W Monocrystalline Module | UL 1703 | 275 | 249.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6262 | 60 | 1 | N | 8.79 | 38.55 | 8.57 | 32.09 | 45.9 | -0.4302 | 0.0779 | -0.4031 | -0.0143 | -0.4175 | 1.8014 | 30.6511 | 6.9918 | 29.5931 | Rack | Flat Plate | 0.988 | 1.646 | 1 | 0.20079
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-275 | 275 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 275 | 247.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.22 | 38.45 | 8.73 | 31.54 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.8222 | 30.8225 | 7.0638 | 28.3648 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20423
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-275 | 275 W Polycrystalline Module | UL 1703 | 275 | 247.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.22 | 38.45 | 8.73 | 31.54 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.821 | 30.6591 | 7.0845 | 28.3109 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20302
Chint Solar (Zhejiang) Co., Ltd. | CHSM6611P-275 | 275 W Polycrystalline Module | UL 1703 | 275 | 247.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7872 | 66 | 1 | N | 8.65 | 42.01 | 8.27 | 33.33 | 47.2 | -0.4355 | 0.0935 | -0.4213 | 0.017 | -0.4521 | 1.6826 | 32.8981 | 6.5255 | 30.4571 | Rack | Flat Plate | 0.994 | 1.798 | 1 | 0.20129
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-275 | 275 W Polycrystalline Module | UL 1703 | 275 | 246.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.56 | 44.51 | 7.76 | 35.6 | 46.8 | -0.45103 | 0.08739 | -0.33227 | 0.00691 | -0.44523 | 1.6839 | 33.8346 | 6.4717 | 31.1232 | Rack | Flat Plate | 0.994 | 1.956 | 1 | 0.20717
Chint Solar (Zhejiang) Co., Ltd. | CHSM60P-HC-280 | 280 W, 120 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 280 | 260.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.64 | 60 | 2 | N | 9.27 | 38.41 | 8.77 | 31.9 | 44.1 | -0.355 | 0.0415 | -0.2729 |  |  | 1.7782 | 30.401 | 7.1012 | 29.7417 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M(BL)-280 | 280 W Monocrystalline Module | UL 1703 | 280 | 254.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.41 | 38.83 | 8.91 | 31.48 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8794 | 31.5151 | 7.1083 | 28.9961 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21153
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M/HV-280 | 280 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 280 | 254.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.41 | 38.83 | 8.91 | 31.48 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8794 | 31.5151 | 7.1083 | 28.9961 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21153
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-280 | 280 W Monocrystalline Module | UL 1703 | 280 | 254.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.41 | 38.83 | 8.91 | 31.48 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8794 | 31.5151 | 7.1083 | 28.9961 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21153
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-280 | 280 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 280 | 252.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.31 | 38.69 | 8.84 | 31.76 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.8451 | 31.0375 | 7.1528 | 28.5627 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20453
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-280 | 280 W Polycrystalline Module | UL 1703 | 280 | 252.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.31 | 38.69 | 8.84 | 31.76 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.844 | 30.8729 | 7.1737 | 28.5084 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20331
Chint Solar (Zhejiang) Co., Ltd. | CHSM6611P-280 | 280 W Polycrystalline Module | UL 1703 | 280 | 251.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7872 | 66 | 1 | N | 8.68 | 42.24 | 8.33 | 33.69 | 47.2 | -0.4355 | 0.0935 | -0.4213 | 0.017 | -0.4521 | 1.6948 | 33.2534 | 6.5728 | 30.786 | Rack | Flat Plate | 0.994 | 1.798 | 1 | 0.20128
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-280 | 280 W Polycrystalline Module | UL 1703 | 280 | 250.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9443 | 72 | 1 | N | 8.71 | 44.64 | 7.9 | 35.63 | 46.8 | -0.45103 | 0.08739 | -0.33227 | 0.00691 | -0.44523 | 1.7142 | 33.8631 | 6.5885 | 31.1494 | Rack | Flat Plate | 0.994 | 1.956 | 1 | 0.20732
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-285 | 285 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 285 | 265.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.43 | 38.79 | 8.93 | 31.92 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.7879 | 30.6371 | 7.2274 | 29.9851 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60P-HC-285 | 285 W, 120 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 285 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.64 | 60 | 2 | N | 9.34 | 38.65 | 8.87 | 32.12 | 44.1 | -0.355 | 0.0415 | -0.2729 |  |  | 1.7985 | 30.6107 | 7.1822 | 29.9468 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M(BL)-285 | 285 W Monocrystalline Module | UL 1703 | 285 | 259.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.46 | 39.15 | 8.97 | 31.8 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.892 | 31.8354 | 7.1562 | 29.2909 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21134
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M/HV-285 | 285 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 285 | 259.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.46 | 39.15 | 8.97 | 31.8 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.892 | 31.8354 | 7.1562 | 29.2909 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21134
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-285 | 285 W Monocrystalline Module | UL 1703 | 285 | 259.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.46 | 39.15 | 8.97 | 31.8 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.892 | 31.8354 | 7.1562 | 29.2909 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21134
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-285 | 285 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 285 | 256.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.4 | 38.94 | 8.94 | 31.98 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.866 | 31.2525 | 7.2337 | 28.7605 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20462
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-285 | 285 W Polycrystalline Module | UL 1703 | 285 | 256.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.4 | 38.94 | 8.94 | 31.98 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.8648 | 31.0868 | 7.2549 | 28.7059 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20341
Chint Solar (Zhejiang) Co., Ltd. | CHSM6611P-285 | 285 W Polycrystalline Module | UL 1703 | 285 | 256.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7872 | 66 | 1 | N | 8.72 | 42.48 | 8.39 | 34.06 | 47.2 | -0.4355 | 0.0935 | -0.4213 | 0.017 | -0.4521 | 1.707 | 33.6186 | 6.6202 | 31.1241 | Rack | Flat Plate | 0.994 | 1.798 | 1 | 0.20136
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-285 | 285 W Polycrystalline Module | UL 1703 | 285 | 257.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 8.86 | 44.77 | 8.04 | 35.66 | 46.3 | -0.4348 | 0.0899 | -0.4136 | 0.0211 | -0.4529 | 1.6366 | 35.2738 | 6.6669 | 32.5307 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20256
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-290 | 290 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 290 | 270.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.51 | 39.09 | 9.02 | 32.15 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.8059 | 30.8578 | 7.3003 | 30.2012 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60P-HC-290 | 290 W, 120 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 290 | 270.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.64 | 60 | 2 | N | 9.43 | 38.9 | 8.97 | 32.34 | 44.1 | -0.355 | 0.0415 | -0.2729 |  |  | 1.8188 | 30.8203 | 7.2631 | 30.1519 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M(BL)-290 | 290 W Monocrystalline Module | UL 1703 | 290 | 264 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.54 | 39.45 | 9.03 | 32.15 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.9047 | 32.1858 | 7.2041 | 29.6133 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21139
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M/HV-290 | 290 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 290 | 264 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.54 | 39.45 | 9.03 | 32.15 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.9047 | 32.1858 | 7.2041 | 29.6133 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21139
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-290 | 290 W Monocrystalline Module | UL 1703 | 290 | 264 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.54 | 39.45 | 9.03 | 32.15 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.9047 | 32.1858 | 7.2041 | 29.6133 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.21139
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-290 | 290 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 290 | 261.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.49 | 39.18 | 9.03 | 32.2 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.8848 | 31.4675 | 7.3065 | 28.9584 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20452
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-290 | 290 W Polycrystalline Module | UL 1703 | 290 | 261.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.49 | 39.18 | 9.03 | 32.2 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.8836 | 31.3006 | 7.3279 | 28.9034 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.2033
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-290 | 290 W Polycrystalline Module | UL 1703 | 290 | 261.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 8.94 | 44.9 | 8.15 | 36.68 | 46.3 | -0.4348 | 0.0899 | -0.4136 | 0.0211 | -0.4529 | 1.659 | 36.2827 | 6.7581 | 33.4612 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20756
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-295 | 295 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 295 | 275.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.59 | 39.39 | 9.08 | 32.5 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.8179 | 31.1938 | 7.3488 | 30.53 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60P-HC-295 | 295 W, 120 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 295 | 275 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.64 | 60 | 2 | N | 9.52 | 39.14 | 9.06 | 32.56 | 44.1 | -0.355 | 0.0415 | -0.2729 |  |  | 1.837 | 31.03 | 7.336 | 30.357 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M(BL)-295 | 295 W Monocrystalline Module | UL 1703 | 295 | 268.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.59 | 39.81 | 9.12 | 32.38 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8262 | 32.4161 | 7.2762 | 29.825 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20067
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M/HV-295 | 295 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 295 | 268.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.59 | 39.81 | 9.12 | 32.38 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8262 | 32.4161 | 7.2762 | 29.825 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20067
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M-295 | 295 W Monocrystalline Module | UL 1703 | 295 | 268.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.59 | 39.81 | 9.12 | 32.38 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8262 | 32.4161 | 7.2762 | 29.825 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20067
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P/HV-295 | 295 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 295 | 266 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.58 | 39.42 | 9.12 | 32.42 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.9036 | 31.6825 | 7.3793 | 29.1562 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20444
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610P-295 | 295 W Polycrystalline Module | UL 1703 | 295 | 266 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6315 | 60 | 1 | N | 9.58 | 39.42 | 9.12 | 32.42 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.9024 | 31.5145 | 7.401 | 29.1009 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20323
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-295 | 295 W Monocrystalline Module | UL 1703 | 295 | 265.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9266 | 72 | 1 | N | 8.49 | 45 | 8.13 | 36.29 | 46.8 | -0.4348 | 0.0923 | -0.4204 | 0.0133 | -0.4457 | 1.6651 | 35.5295 | 6.5898 | 33.4407 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20055
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-295 | 295 W Polycrystalline Module | UL 1703 | 295 | 266.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.16 | 45.03 | 8.3 | 35.72 | 46.3 | -0.4348 | 0.0899 | -0.4136 | 0.0211 | -0.4529 | 1.6895 | 35.3331 | 6.8825 | 32.5854 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20236
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-300 | 300 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 300 | 280.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.64 | 39.75 | 9.17 | 32.73 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.8359 | 31.4145 | 7.4217 | 30.746 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60P-HC-300 | 300 W, 120 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 300 | 279.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.64 | 60 | 2 | N | 9.6 | 39.39 | 9.16 | 32.78 | 44.1 | -0.355 | 0.0415 | -0.2729 |  |  | 1.8573 | 31.2397 | 7.417 | 30.5621 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M/HV-300 | 300 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 300 | 273.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.68 | 39.9 | 9.21 | 32.59 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8442 | 32.6264 | 7.348 | 30.0184 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20056
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-300 | 300 W Monocrystalline Module | UL 1703 | 300 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9266 | 72 | 1 | N | 8.51 | 45.11 | 8.2 | 36.59 | 46.8 | -0.4348 | 0.0923 | -0.4204 | 0.0133 | -0.4457 | 1.6795 | 35.8232 | 6.6465 | 33.7172 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20055
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-300 | 300 W Polycrystalline Module | UL 1703 | 300 | 271.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.27 | 45.16 | 8.4 | 35.74 | 46.3 | -0.4348 | 0.0899 | -0.4136 | 0.0211 | -0.4529 | 1.7099 | 35.3529 | 6.9654 | 32.6037 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20149
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-305 | 305 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 305 | 285 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.73 | 39.84 | 9.26 | 32.94 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.854 | 31.6161 | 7.4945 | 30.9433 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60P-HC-305 | 305 W, 120 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 305 | 284.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.64 | 60 | 2 | N | 9.68 | 39.63 | 9.26 | 33 | 44.1 | -0.355 | 0.0415 | -0.2729 |  |  | 1.8776 | 31.4493 | 7.4979 | 30.7672 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6610M/HV-305 | 305 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 305 | 278.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6315 | 60 | 1 | N | 9.72 | 40.05 | 9.3 | 32.8 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8622 | 32.8366 | 7.4198 | 30.2119 | Rack | Flat Plate | 0.99 | 1.648 | 1 | 0.20049
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-305 | 305 W Monocrystalline Module | UL 1703 | 305 | 275 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9266 | 72 | 1 | N | 8.53 | 45.32 | 8.24 | 37.02 | 46.8 | -0.4348 | 0.0923 | -0.4204 | 0.0133 | -0.4457 | 1.6877 | 36.2442 | 6.6789 | 34.1134 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20055
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-305 | 305 W Polycrystalline Module | UL 1703 | 305 | 275.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.42 | 45.29 | 8.53 | 35.77 | 46.3 | -0.4348 | 0.0899 | -0.4136 | 0.0211 | -0.4529 | 1.7363 | 35.3826 | 7.0732 | 32.6311 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20143
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-310 | 310 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 310 | 289.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.82 | 40.11 | 9.35 | 33.15 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.872 | 31.8177 | 7.5673 | 31.1406 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60P-HC-310 | 310 W, 120 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 310 | 289.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.64 | 60 | 2 | N | 9.77 | 39.87 | 9.34 | 33.22 | 44.1 | -0.355 | 0.0415 | -0.2729 |  |  | 1.8938 | 31.659 | 7.5627 | 30.9723 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-310 | 310 W Monocrystalline Module | UL 1703 | 310 | 279.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9266 | 72 | 1 | N | 8.55 | 45.44 | 8.3 | 37.36 | 46.8 | -0.4348 | 0.0923 | -0.4204 | 0.0133 | -0.4457 | 1.7 | 36.5771 | 6.7276 | 34.4267 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20058
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-310 | 310 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 310 | 279.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 8.9247 | 45.15 | 8.4037 | 36.914 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.7497 | 35.9664 | 6.8062 | 33.3716 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.203
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-310 | 310 W Polycrystalline Module | UL 1703 | 310 | 280.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.56 | 45.42 | 8.68 | 35.8 | 46.3 | -0.4348 | 0.0899 | -0.4136 | 0.0211 | -0.4529 | 1.7669 | 35.4123 | 7.1976 | 32.6584 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20183
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-315 | 315 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 315 | 294.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.9 | 40.42 | 9.42 | 33.44 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.886 | 32.096 | 7.624 | 31.413 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-315 | 315 W Monocrystalline Module | UL 1703 | 315 | 284.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9266 | 72 | 1 | N | 8.56 | 45.58 | 8.35 | 37.74 | 46.8 | -0.4348 | 0.0923 | -0.4204 | 0.0133 | -0.4457 | 1.7102 | 36.9491 | 6.7681 | 34.7769 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20061
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-315 | 315 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 315 | 284.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 9.0352 | 45.3 | 8.53 | 36.986 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.776 | 36.0366 | 6.9084 | 33.4367 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20318
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-315 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.02 | 45.55 | 8.8 | 35.83 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.71 | 35.57 | 6.81 | 32.88 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.19309
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-320 | 320 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 320 | 299.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.98 | 40.72 | 9.5 | 33.68 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.902 | 32.3264 | 7.6887 | 31.6385 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-320 | 320 W Monocrystalline Module | UL 1703 | 320 | 288.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9266 | 72 | 1 | N | 8.59 | 45.69 | 8.41 | 38.11 | 46.8 | -0.4348 | 0.0923 | -0.4204 | 0.0133 | -0.4457 | 1.7225 | 37.3114 | 6.8167 | 35.1178 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20084
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-320 | 320 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 320 | 288.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 9.14 | 45.45 | 8.65 | 37.058 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.801 | 36.1067 | 7.0056 | 33.5018 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20321
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-320 | 320 W Polycrystalline Module | UL 1703 | 320 | 290.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.06 | 45.68 | 8.93 | 35.86 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.74 | 35.6 | 6.91 | 32.9 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.19357
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-325 | 325 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 325 | 304.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 10.06 | 41.03 | 9.58 | 33.93 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.918 | 32.5663 | 7.7535 | 31.8733 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-325 | 325 W Monocrystalline Module | UL 1703 | 325 | 293.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9266 | 72 | 1 | N | 8.6 | 45.74 | 8.47 | 38.43 | 46.8 | -0.4348 | 0.0923 | -0.4204 | 0.0133 | -0.4457 | 1.7348 | 37.6247 | 6.8654 | 35.4127 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.20083
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-325 | 325 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 325 | 293.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 9.24 | 45.67 | 8.77 | 37.13 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.826 | 36.1769 | 7.1028 | 33.5669 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20325
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-325 | 325 W Polycrystalline Module | UL 1703 | 325 | 295.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.1 | 45.82 | 8.95 | 36.31 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.74 | 36.05 | 6.93 | 33.32 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.19301
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-325 | 325 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 325 | 302.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.18 | 45.38 | 8.7 | 37.35 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.6861 | 36.6714 | 6.7362 | 35.8469 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-330 | 330 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 330 | 308.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 10.14 | 41.32 | 9.66 | 34.17 | 44.3 | -0.3438 | 0.0353 | -0.2722 |  |  | 1.9341 | 32.7967 | 7.8182 | 32.0988 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M(BL)-330 | 330 W Monocrystalline Module | UL 1703 | 330 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.29 | 45.89 | 8.7958 | 37.555 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8473 | 35.8095 | 7.0152 | 34.6788 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20046
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-330 | 330 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 330 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.29 | 45.89 | 8.7958 | 37.555 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.7536 | 35.8095 | 7.0152 | 34.6788 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19028
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-330 | 330 W Monocrystalline Module | UL 1703 | 330 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.29 | 45.89 | 8.7958 | 37.555 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.7536 | 35.8095 | 7.0152 | 34.6788 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19028
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-330 | 330 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 330 | 298 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 9.35 | 45.86 | 8.9 | 37.19 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.853 | 36.2354 | 7.2081 | 33.6211 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20347
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-330 | 330 W Polycrystalline Module | UL 1703 | 330 | 300.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.13 | 45.95 | 8.97 | 36.79 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.74 | 36.53 | 6.94 | 33.76 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.19261
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-330 | 330 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 330 | 306.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.28 | 45.53 | 8.81 | 37.49 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.7075 | 36.8089 | 6.8214 | 35.9813 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-335 | 335 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 335 | 312.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 10.22 | 41.61 | 9.73 | 34.44 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.0059 | 33.245 | 7.8412 | 32.4028 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M(BL)-335 | 335 W Monocrystalline Module | UL 1703 | 335 | 304.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.38 | 45.98 | 8.87 | 37.818 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8629 | 36.0603 | 7.0744 | 34.9217 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20053
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-335 | 335 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 335 | 304.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.38 | 45.98 | 8.87 | 37.818 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.7683 | 36.0603 | 7.0744 | 34.9217 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19035
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-335 | 335 W Monocrystalline Module | UL 1703 | 335 | 304.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.38 | 45.98 | 8.87 | 37.818 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.7683 | 36.0603 | 7.0744 | 34.9217 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19035
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-335 | 335 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 335 | 302.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 9.45 | 45.98 | 9.01 | 37.26 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.8759 | 36.3036 | 7.2972 | 33.6844 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20329
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-335 | 335 W Polycrystalline Module | UL 1703 | 335 | 304.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.16 | 46.08 | 8.98 | 37.31 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.75 | 37.04 | 6.95 | 34.23 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.19349
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-335 | 335 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 335 | 311.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.37 | 45.74 | 8.92 | 37.57 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.7288 | 36.8875 | 6.9066 | 36.0581 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-340 | 340 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 340 | 316.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 10.3 | 41.88 | 9.8 | 34.69 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.0203 | 33.4864 | 7.8976 | 32.638 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M(BL)-340 | 340 W Monocrystalline Module | UL 1703 | 340 | 309.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.41 | 46.38 | 8.9338 | 38.081 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8763 | 36.311 | 7.1252 | 35.1645 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20038
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-340 | 340 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 340 | 309.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.41 | 46.38 | 8.9338 | 38.081 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.7811 | 36.311 | 7.1252 | 35.1645 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19021
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-340 | 340 W Monocrystalline Module | UL 1703 | 340 | 309.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.41 | 46.38 | 8.9338 | 38.081 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.7811 | 36.311 | 7.1252 | 35.1645 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19021
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-340 | 340 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 340 | 307.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 9.55 | 46.16 | 9.13 | 37.33 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.9009 | 36.3718 | 7.3944 | 33.7477 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20335
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-340 | 340 W Polycrystalline Module | UL 1703 | 340 | 309.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.2 | 46.2 | 8.99 | 37.82 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.75 | 37.55 | 6.96 | 34.7 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.19327
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-340 | 340 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 340 | 316.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.47 | 45.86 | 9.03 | 37.64 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.7501 | 36.9562 | 6.9917 | 36.1253 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-345 | 345 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 345 | 321.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 10.38 | 42.16 | 9.87 | 34.96 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.0347 | 33.747 | 7.954 | 32.892 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M(BL)-345 | 345 W Monocrystalline Module | UL 1703 | 345 | 314.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.48 | 46.7 | 9.011 | 38.34 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8925 | 36.558 | 7.1868 | 35.4037 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20054
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-345 | 345 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 345 | 314.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.48 | 46.7 | 9.011 | 38.34 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.7965 | 36.558 | 7.1868 | 35.4037 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19036
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-345 | 345 W Monocrystalline Module | UL 1703 | 345 | 314.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.48 | 46.7 | 9.011 | 38.34 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.7965 | 36.558 | 7.1868 | 35.4037 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19036
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-345 | 345 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 345 | 312 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 9.64 | 46.37 | 9.25 | 37.4 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.9259 | 36.44 | 7.4916 | 33.811 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20342
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P-345 | 345 W Polycrystalline Module | UL 1703 | 345 | 314.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9266 | 72 | 1 | N | 9.23 | 46.33 | 9.01 | 39.29 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.75 | 39.01 | 6.98 | 36.05 | Rack | Flat Plate | 0.988 | 1.95 | 1 | 0.19788
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-345 | 345 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 345 | 322.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.46 | 46.21 | 8.99 | 38.38 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.7568 | 36.6964 | 7.3021 | 35.9421 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-345 | 345 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 345 | 321.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.57 | 46.04 | 9.15 | 37.71 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.7734 | 37.0249 | 7.0847 | 36.1924 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-350 | 350 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 350 | 326.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 10.46 | 42.44 | 9.94 | 35.22 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.0492 | 33.998 | 8.0104 | 33.1367 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M(BL)-350 | 350 W Monocrystalline Module | UL 1703 | 350 | 318.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.53 | 47.01 | 9.0827 | 38.58 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.9076 | 36.7868 | 7.244 | 35.6253 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.2005
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-350 | 350 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 350 | 318.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.53 | 47.01 | 9.0827 | 38.58 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8107 | 36.7868 | 7.244 | 35.6253 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19032
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-350 | 350 W Monocrystalline Module | UL 1703 | 350 | 318.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.53 | 47.01 | 9.0827 | 38.58 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8107 | 36.7868 | 7.244 | 35.6253 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.19032
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-350 | 350 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 350 | 316.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 9.73 | 46.57 | 9.36 | 37.49 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.9488 | 36.5277 | 7.5807 | 33.8923 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20339
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-350 | 350 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 350 | 326.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.52 | 46.52 | 9.05 | 38.67 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.7686 | 36.9737 | 7.3508 | 36.2137 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-350 | 350 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 350 | 325.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.65 | 46.25 | 9.26 | 37.78 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.7947 | 37.0936 | 7.1698 | 36.2596 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-355 | 355 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 355 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 11.15 | 39.8 | 10.68 | 33.24 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.2017 | 32.0867 | 8.6068 | 31.2738 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M(BL)-355 | 355 W Monocrystalline Module | UL 1703 | 355 | 323.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.6 | 47.31 | 9.1543 | 38.82 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.9226 | 37.0157 | 7.3011 | 35.8469 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20047
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-355 | 355 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 355 | 323.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.6 | 47.31 | 9.1543 | 38.82 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.825 | 37.0157 | 7.3011 | 35.8469 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.1903
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-355 | 355 W Monocrystalline Module | UL 1703 | 355 | 323.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.6 | 47.31 | 9.1543 | 38.82 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.825 | 37.0157 | 7.3011 | 35.8469 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.1903
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612P/HV-355 | 355 W Polycrystalline Module with maximum system voltage of 1500 V | UL 1703 | 355 | 321.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 | 1 | N | 9.83 | 46.7 | 9.47 | 37.5478 | 47.1 | -0.4314 | 0.0525 | -0.3305 | 0.0057 | -0.438 | 1.9717 | 36.584 | 7.6698 | 33.9446 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.20319
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-355 | 355 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 331.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.57 | 46.83 | 9.12 | 38.91 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.7822 | 37.2032 | 7.4077 | 36.4384 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-355 | 355 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 330.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.74 | 46.45 | 9.37 | 37.87 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.816 | 37.182 | 7.255 | 36.346 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-360 | 360 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 360 | 336 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 11.21 | 40.14 | 10.75 | 33.49 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.2161 | 32.328 | 8.6632 | 31.509 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M(BL)-360 | 360 W Monocrystalline Module | UL 1703 | 360 | 328.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.66 | 47.62 | 9.2 | 39.14 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8422 | 40.471 | 7.3401 | 36.009 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.2071
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-360 | 360 W Monocrystalline Module with maximum system voltage of 1500 V | UL 1703 | 360 | 328.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.66 | 47.62 | 9.2 | 39.14 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8422 | 40.471 | 7.3401 | 36.009 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.2071
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-360 | 360 W Monocrystalline Module | UL 1703 | 360 | 328.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 | 1 | N | 9.66 | 47.62 | 9.2 | 39.14 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8422 | 40.471 | 7.3401 | 36.009 | Rack | Flat Plate | 0.99 | 1.954 | 1 | 0.2071
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-360 | 360 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 336.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.64 | 47.13 | 9.2 | 39.15 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.7979 | 37.4327 | 7.4727 | 36.6632 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-360 | 360 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 335.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.83 | 46.65 | 9.49 | 37.94 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.8393 | 37.2507 | 7.3479 | 36.4132 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-365 | 365 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 365 | 340.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 11.29 | 40.41 | 10.82 | 33.73 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.2306 | 32.5597 | 8.7196 | 31.7348 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-365 | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 338.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.75 | 47.82 | 9.27 | 39.38 | 44.3 | -0.3803 | 0.031 | -0.2807 | -0.0021 | -0.3792 | 1.889 | 37.891 | 7.607 | 36.31 | [6 empty] | 2019-02-15
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-365 | 365 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 365 | 338.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.75 | 47.82 | 9.27 | 39.38 | 44.3 | -0.3803 | 0.031 | -0.2807 | -0.0021 | -0.3792 | 1.889 | 37.891 | 7.607 | 36.31 | [6 empty] | 2019-02-15
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-365 | 365 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 341.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.71 | 47.44 | 9.25 | 39.47 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.8076 | 37.7386 | 7.5133 | 36.9629 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-365 | 365 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 340.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.92 | 46.84 | 9.6 | 38.02 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.8606 | 37.3293 | 7.4331 | 36.49 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-370 | 370 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 370 | 345.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 11.35 | 40.75 | 10.89 | 33.98 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.245 | 32.801 | 8.776 | 31.97 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-370 | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 343.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.91 | 48.36 | 9.36 | 39.56 | 44.3 | -0.3803 | 0.031 | -0.2807 | -0.0021 | -0.3792 | 1.9073 | 38.0642 | 7.6809 | 36.476 | [6 empty] | 2019-02-15
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-370 | 370 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 370 | 343.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.91 | 48.36 | 9.36 | 39.56 | 44.3 | -0.3803 | 0.031 | -0.2807 | -0.0021 | -0.3792 | 1.9073 | 38.0642 | 7.6809 | 36.476 | [6 empty] | 2019-02-15
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-370 | 370 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 346 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.8 | 47.64 | 9.32 | 39.71 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.8213 | 37.9681 | 7.5701 | 37.1876 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM72P-HC-370 | 370 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 345 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 10.01 | 47.04 | 9.71 | 38.11 | 44.1 | -0.3599 | 0.043 | -0.2765 |  |  | 1.8819 | 37.4176 | 7.5183 | 36.5763 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-375 | 375 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 375 | 350.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 11.42 | 41.05 | 10.94 | 34.28 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.2553 | 33.0906 | 8.8163 | 32.2523 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-375 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 348.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.94 | 48.45 | 9.45 | 39.76 | 44.3 | -0.3803 | 0.031 | -0.2807 | -0.0021 | -0.3792 | 1.9257 | 38.2566 | 7.7547 | 36.6604 | [6 empty] | 2019-02-15
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-375 | 375 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 375 | 348.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.94 | 48.45 | 9.45 | 39.76 | 44.3 | -0.3803 | 0.031 | -0.2807 | -0.0021 | -0.3792 | 1.9257 | 38.2566 | 7.7547 | 36.6604 | [6 empty] | 2019-02-15
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-375 | 375 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 350.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.88 | 47.89 | 9.39 | 39.94 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.835 | 38.188 | 7.627 | 37.403 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM60M-HC-380 | 380 W, 120 half-cut cell monocrystalline module, white backsheet, white or black frame, 1500V max system Vdc | UL 61730 | 380 | 355.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.788 | 60 | 2 | N | 11.49 | 41.34 | 11.01 | 34.51 | 44.8 | -0.3496 | 0.0392 | -0.2653 |  |  | 2.2697 | 33.3126 | 8.8727 | 32.4686 | [6 empty] | 2020-10-12
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M/HV-380 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 352.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.99 | 48.61 | 9.54 | 39.89 | 44.3 | -0.3803 | 0.031 | -0.2807 | -0.0021 | -0.3792 | 1.944 | 38.3817 | 7.8286 | 36.7802 | [6 empty] | 2019-02-15
Chint Solar (Zhejiang) Co., Ltd. | CHSM6612M-380 | 380 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 380 | 352.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.99 | 48.61 | 9.54 | 39.89 | 44.3 | -0.3803 | 0.031 | -0.2807 | -0.0021 | -0.3792 | 1.944 | 38.3817 | 7.8286 | 36.7802 | [6 empty] | 2019-02-15
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-380 | 380 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 355.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.95 | 48.18 | 9.44 | 40.26 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.8448 | 38.494 | 7.6676 | 37.7027 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-385 | 385 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 360.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.02 | 48.47 | 9.49 | 40.58 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.8545 | 38.7999 | 7.7082 | 38.0023 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-390 | 390 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 365.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.1 | 48.7 | 9.56 | 40.81 | 43.7 | -0.3528 | 0.04 | -0.2769 |  |  | 1.8682 | 39.0198 | 7.7651 | 38.2177 | [6 empty] | 2019-05-01
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-395 | 395 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 395 | 366.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 10.22 | 48.06 | 9.77 | 40.44 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 1.9604 | 38.2225 | 7.8747 | 36.9761 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-395 | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 366.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 2 | N | 10.17 | 48.98 | 9.62 | 41.07 | 46.4 | -0.3516 | 0.0359 | -0.2705 |  |  | 2.0212 | 38.3919 | 7.912 | 37.3192 | [6 empty] | 2020-01-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-400 | 400 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 400 | 371 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 10.3 | 48.24 | 9.84 | 40.67 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 1.9745 | 38.4399 | 7.9311 | 37.1864 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-400 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 370.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 2 | N | 10.24 | 49.25 | 9.68 | 41.32 | 46.4 | -0.3516 | 0.0359 | -0.2705 |  |  | 2.0338 | 38.6256 | 7.9613 | 37.5464 | [6 empty] | 2020-01-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-405 | 405 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 405 | 375.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 10.38 | 48.42 | 9.91 | 40.89 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 1.9885 | 38.6478 | 7.9876 | 37.3876 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-405 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 405 | 375.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 2 | N | 10.31 | 49.53 | 9.74 | 41.59 | 46.4 | -0.3516 | 0.0359 | -0.2705 |  |  | 2.0464 | 38.878 | 8.0107 | 37.7917 | [6 empty] | 2020-01-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-410 | 410 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 410 | 380.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 10.46 | 48.6 | 9.98 | 41.1 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 2.0026 | 38.8463 | 8.044 | 37.5796 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-410 | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 410 | 380.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 2 | N | 10.38 | 49.8 | 9.8 | 41.85 | 46.4 | -0.3516 | 0.0359 | -0.2705 |  |  | 2.059 | 39.121 | 8.06 | 38.028 | [6 empty] | 2020-01-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-415 | 415 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 415 | 385.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 10.54 | 48.78 | 10.05 | 41.31 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 2.0166 | 39.0448 | 8.1004 | 37.7716 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-415 | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 415 | 385.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 2 | N | 10.45 | 50.06 | 9.86 | 42.11 | 46.4 | -0.3516 | 0.0359 | -0.2705 |  |  | 2.0716 | 39.364 | 8.1093 | 38.2643 | [6 empty] | 2020-01-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-420 | 420 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 420 | 390 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 10.62 | 48.96 | 10.12 | 41.52 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 2.0307 | 39.2433 | 8.1568 | 37.9636 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-420 | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 420 | 390 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 2 | N | 10.95 | 47.48 | 10.48 | 40.08 | 46.4 | -0.3516 | 0.0359 | -0.2705 |  |  | 2.2019 | 37.4664 | 8.6193 | 36.4196 | [6 empty] | 2020-01-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-425 | 425 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 425 | 394.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 10.97 | 48.43 | 10.54 | 40.32 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 2.1149 | 38.1091 | 8.4953 | 36.8664 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-425 | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 425 | 394.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 2 | N | 11.03 | 47.73 | 10.56 | 40.25 | 46.4 | -0.3516 | 0.0359 | -0.2705 |  |  | 2.2187 | 37.6253 | 8.6851 | 36.5741 | [6 empty] | 2020-01-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-430 | 430 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 430 | 399.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 11.06 | 48.6 | 10.59 | 40.6 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 2.125 | 38.3737 | 8.5356 | 37.1224 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-430 | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 430 | 399.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 2 | N | 11.1 | 47.99 | 10.63 | 40.45 | 46.4 | -0.3516 | 0.0359 | -0.2705 |  |  | 2.2334 | 37.8123 | 8.7426 | 36.7559 | [6 empty] | 2020-01-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-435 | 435 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 435 | 404.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 11.12 | 48.9 | 10.65 | 40.85 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 2.137 | 38.61 | 8.584 | 37.351 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-435 | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 403 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.16 | 48.25 | 10.7 | 40.65 | 45.84 | -0.3697 | 0.0431 | -0.2725 |  |  | 2.2107 | 40.6589 | 8.5944 | 38.346 | [6 empty] | 2021-03-22
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-440 | 440 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 440 | 409.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 11.2 | 49.11 | 10.7 | 41.12 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 2.147 | 38.8652 | 8.6243 | 37.5979 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-440 | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 407.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.24 | 48.5 | 10.77 | 40.85 | 45.84 | -0.3697 | 0.0431 | -0.2725 |  |  | 2.2252 | 40.8589 | 8.6506 | 38.5346 | [6 empty] | 2021-03-22
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-445 | 445 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 445 | 413.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 11.25 | 49.44 | 10.76 | 41.36 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 2.1591 | 39.092 | 8.6727 | 37.8173 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-445 | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 412.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.3 | 48.8 | 10.84 | 41.05 | 45.84 | -0.3697 | 0.0431 | -0.2725 |  |  | 2.2397 | 41.0589 | 8.7068 | 38.7233 | [6 empty] | 2021-03-22
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-450 | 450 W, 144 half-cut cell, bifacial dual glass monocrystalline module, white or black frame , 1500V max system Vdc | UL 61730 | 450 | 418.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 48 | 3 | N | 11.3 | 49.78 | 10.82 | 41.59 | 46.1 | -0.3462 | 0.0504 | -0.267 |  |  | 2.1711 | 39.3094 | 8.721 | 38.0276 | [6 empty] | 2020-07-01 | 2020-07-13
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-450 | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 417.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.37 | 49.05 | 10.89 | 41.32 | 45.84 | -0.3697 | 0.0431 | -0.2725 |  |  | 2.25 | 41.329 | 8.747 | 38.978 | [6 empty] | 2021-03-22
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-455 | 455 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 422.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.44 | 49.35 | 10.96 | 41.51 | 45.84 | -0.3697 | 0.0431 | -0.2725 |  |  | 2.2645 | 41.519 | 8.8032 | 39.1572 | [6 empty] | 2021-03-22
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-515 | 515 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 515 | 477.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.2808 | 48.9 | 12.5327 | 41.0924 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.6083 | 39.8933 | 10.1985 | 37.8183 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-520 | 520 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 520 | 481.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.3215 | 49.1 | 12.6029 | 41.2605 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.6229 | 40.0565 | 10.2555 | 37.973 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-520 | 520 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 520 | 481.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.34 | 48.9 | 12.6544 | 41.0924 | 45.52 | -0.3829 | 0.0549 | -0.2927 |  |  | 2.6357 | 39.9307 | 10.3157 | 37.8665 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-525 | 525 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 525 | 486.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.3951 | 49.3 | 12.6724 | 41.4286 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.6374 | 40.2197 | 10.3122 | 38.1276 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-525 | 525 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 525 | 486 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.43 | 49.1 | 12.724 | 41.2605 | 45.52 | -0.3829 | 0.0549 | -0.2927 |  |  | 2.6502 | 40.0941 | 10.3724 | 38.0214 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-530 | 530 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 530 | 491.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.485 | 49.5 | 12.7414 | 41.5966 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.6518 | 40.3828 | 10.3683 | 38.2823 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-530 | 530 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 530 | 490.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.52 | 49.3 | 12.7931 | 41.4286 | 45.52 | -0.3829 | 0.0549 | -0.2927 |  |  | 2.6646 | 40.2574 | 10.4287 | 38.1763 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-535 | 535 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 535 | 496.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.5745 | 49.7 | 12.8099 | 41.7647 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.666 | 40.546 | 10.424 | 38.437 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-535 | 535 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 535 | 495.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.61 | 49.5 | 12.8616 | 41.5966 | 45.52 | -0.3829 | 0.0549 | -0.2927 |  |  | 2.6788 | 40.4207 | 10.4846 | 38.3311 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-540 | 540 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 540 | 501 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.6637 | 49.9 | 12.8778 | 41.9328 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.6801 | 40.7092 | 10.4793 | 38.5917 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-540 | 540 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 540 | 500.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.72 | 49.7 | 12.9296 | 41.7647 | 45.52 | -0.3829 | 0.0549 | -0.2927 |  |  | 2.693 | 40.584 | 10.54 | 38.486 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-545 | 545 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 545 | 505.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.7525 | 50.1 | 12.9451 | 42.1008 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.6941 | 40.8723 | 10.5341 | 38.7464 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-545 | 545 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 545 | 505.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.81 | 49.9 | 12.997 | 41.9328 | 45.52 | -0.3829 | 0.0549 | -0.2927 |  |  | 2.707 | 40.7473 | 10.595 | 38.6409 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-550 | 550 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 550 | 510.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.8235 | 50.3 | 13.0119 | 42.2689 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.7081 | 41.0355 | 10.5884 | 38.901 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M-HC-550 | 550 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 550 | 509.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.9 | 50.1 | 13.0639 | 42.1008 | 45.52 | -0.3829 | 0.0549 | -0.2927 |  |  | 2.721 | 40.9106 | 10.6495 | 38.7957 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-555 | 555 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 555 | 515.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.8939 | 50.5 | 13.0782 | 42.437 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.7219 | 41.1987 | 10.6424 | 39.0557 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM72M(DG)/F-BH-560 | 560 W, 144 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 560 | 520.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.48 | 72 | 2 | N | 13.9638 | 50.7 | 13.144 | 42.605 | 45.63 | -0.3745 | 0.0476 | -0.2838 |  |  | 2.7355 | 41.3618 | 10.6959 | 39.2104 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M(DG)/F-BH-635 | 635 W, 132 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 635 | 589 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.03 | 66 | 2 | N | 18.17 | 44.89 | 17.13 | 37.08 | 44.8 | -0.386 | 0.05 | -0.291 |  |  | 3.428 | 35.7526 | 13.7604 | 34.204 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M(DG)/F-BH-640 | 640 W, 132 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 640 | 593.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.03 | 66 | 2 | N | 18.22 | 45.09 | 17.17 | 37.28 | 44.8 | -0.386 | 0.05 | -0.291 |  |  | 3.436 | 35.9455 | 13.7926 | 34.3885 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M(DG)/F-BH-645 | 645 W, 132 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 645 | 598.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.03 | 66 | 2 | N | 18.27 | 45.29 | 17.21 | 37.48 | 44.8 | -0.386 | 0.05 | -0.291 |  |  | 3.444 | 36.1383 | 13.8247 | 34.573 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M-HC-645 | 645 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 645 | 597.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.02 | 66 | 2 | N | 18.38 | 45.08 | 17.32 | 37.25 | 45.4 | -0.386 | 0.05 | -0.291 |  |  | 3.4432 | 36.0572 | 13.7746 | 34.3487 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M(DG)/F-BH-650 | 650 W, 132 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 650 | 603.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.03 | 66 | 2 | N | 18.32 | 45.49 | 17.26 | 37.68 | 44.8 | -0.386 | 0.05 | -0.291 |  |  | 3.454 | 36.3312 | 13.8649 | 34.7575 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M-HC-650 | 650 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 650 | 601.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.02 | 66 | 2 | N | 18.43 | 45.28 | 17.36 | 37.45 | 45.4 | -0.386 | 0.05 | -0.291 |  |  | 3.4511 | 36.2508 | 13.8064 | 34.5332 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M(DG)/F-BH-655 | 655 W, 132 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 655 | 608.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.03 | 66 | 2 | N | 18.37 | 45.69 | 17.3 | 37.88 | 44.8 | -0.386 | 0.05 | -0.291 |  |  | 3.462 | 36.524 | 13.897 | 34.942 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M-HC-655 | 655 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 655 | 606.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.02 | 66 | 2 | N | 18.48 | 45.48 | 17.41 | 37.65 | 45.4 | -0.386 | 0.05 | -0.291 |  |  | 3.461 | 36.4444 | 13.8462 | 34.7176 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M(DG)/F-BH-660 | 660 W, 132 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 660 | 612.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.03 | 66 | 2 | N | 18.42 | 45.89 | 17.34 | 38.08 | 44.8 | -0.386 | 0.05 | -0.291 |  |  | 3.47 | 36.7168 | 13.9291 | 35.1265 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M-HC-660 | 660 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 660 | 611.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.02 | 66 | 2 | N | 18.53 | 45.68 | 17.45 | 37.85 | 45.4 | -0.386 | 0.05 | -0.291 |  |  | 3.469 | 36.638 | 13.878 | 34.902 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M(DG)/F-BH-665 | 665 W, 132 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 665 | 617.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.03 | 66 | 2 | N | 18.47 | 46.09 | 17.38 | 38.28 | 44.8 | -0.386 | 0.05 | -0.291 |  |  | 3.478 | 36.9097 | 13.9613 | 35.311 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M-HC-665 | 665 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 665 | 616.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.02 | 66 | 2 | N | 18.58 | 45.88 | 17.5 | 38.05 | 45.4 | -0.386 | 0.05 | -0.291 |  |  | 3.4789 | 36.8316 | 13.9178 | 35.0864 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M(DG)/F-BH-670 | 670 W, 132 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 670 | 622.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.03 | 66 | 2 | N | 18.52 | 46.29 | 17.42 | 38.48 | 44.8 | -0.386 | 0.05 | -0.291 |  |  | 3.486 | 37.1025 | 13.9934 | 35.4955 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M-HC-670 | 670 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 670 | 621.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.02 | 66 | 2 | N | 18.63 | 46.08 | 17.54 | 38.23 | 45.4 | -0.386 | 0.05 | -0.291 |  |  | 3.4869 | 37.0058 | 13.9496 | 35.2524 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M(DG)/F-BH-675 | 675 W, 132 half-cut cell bifacial monodrystalline module, 1500V max system Vdc | UL 61730 | 675 | 627.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.03 | 66 | 2 | N | 18.57 | 46.49 | 17.46 | 38.68 | 44.8 | -0.386 | 0.05 | -0.291 |  |  | 3.494 | 37.2954 | 14.0255 | 35.68 | [6 empty] | 2021-08-23
Chint Solar (Zhejiang) Co., Ltd. | CHSM66M-HC-675 | 675 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 675 | 625.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.02 | 66 | 2 | N | 18.68 | 46.28 | 17.58 | 38.42 | 45.4 | -0.386 | 0.05 | -0.291 |  |  | 3.4948 | 37.1897 | 13.9814 | 35.4276 | [6 empty] | 2021-08-23
CSI Solar Co., Ltd. | CS6P-200P | 200 W Polycrystalline Module | UL 1703 | 200 | 183 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 7.68 | 36.2 | 6.93 | 28.9 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4244 | 28.0704 | 5.7178 | 26.8796 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19992 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-200PX | 200 W Polycrystalline Module | UL 1703 | 200 | 183 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 7.68 | 36.2 | 6.93 | 28.9 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4244 | 28.0704 | 5.7178 | 26.8796 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19992 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-205M | 205 W Monocrystalline Module | UL 1703 | 205 | 184.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 7.66 | 36.5 | 7.02 | 29.2 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.385 | 28.8014 | 5.4927 | 25.0143 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19459 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-205P | 205 W Polycrystalline Module | UL 1703 | 205 | 187.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 7.6 | 36.2 | 7.1 | 28.9 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4593 | 28.0704 | 5.858 | 26.8796 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19982 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-205PX | 205 W Polycrystalline Module | UL 1703 | 205 | 187.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 7.6 | 36.2 | 7.1 | 28.9 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4593 | 28.0704 | 5.858 | 26.8796 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19982 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-210M | 210 W Monocrystalline Module | UL 1703 | 210 | 189.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 7.77 | 36.7 | 7.17 | 29.3 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.4146 | 28.9 | 5.61 | 25.1 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19468 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-210P | 210 W Polycrystalline Module | UL 1703 | 210 | 192.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 7.91 | 36.4 | 7.26 | 28.9 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4922 | 28.0704 | 5.99 | 26.8796 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19946 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-210PX | 210 W Polycrystalline Module | UL 1703 | 210 | 192.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 7.91 | 36.4 | 7.26 | 28.9 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4922 | 28.0704 | 5.99 | 26.8796 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19946 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-215M | 215 W Monocrystalline Module | UL 1703 | 215 | 193.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 7.89 | 36.8 | 7.33 | 29.3 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.4462 | 28.9 | 5.7352 | 25.1 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19439 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-215P | 215 W Polycrystalline Module | UL 1703 | 215 | 197 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.01 | 36.5 | 7.43 | 29 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4783 | 28.2188 | 5.9131 | 26.6565 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19402 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-215PX | 215 W Polycrystalline Module | UL 1703 | 215 | 197 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.01 | 36.5 | 7.43 | 29 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4783 | 28.2188 | 5.9131 | 26.6565 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19402 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-220M | 220 W Monocrystalline Module | UL 1703 | 220 | 198.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 7.97 | 36.9 | 7.45 | 29.5 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.4699 | 29.0973 | 5.8291 | 25.2713 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.1944 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-220P | 220 W Polycrystalline Module | UL 1703 | 220 | 201.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.09 | 36.6 | 7.52 | 29.3 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4962 | 28.5107 | 5.9847 | 26.9322 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.1939 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-220PX | 220 W Polycrystalline Module | UL 1703 | 220 | 201.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.09 | 36.6 | 7.52 | 29.3 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4962 | 28.5107 | 5.9847 | 26.9322 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.1939 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-225P | 225 W Polycrystalline Module | UL 1703 | 225 | 206.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.19 | 36.7 | 7.63 | 29.5 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.5181 | 28.7054 | 6.0722 | 27.1161 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19367 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-225PX | 225 W Polycrystalline Module | UL 1703 | 225 | 206.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.19 | 36.7 | 7.63 | 29.5 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.5181 | 28.7054 | 6.0722 | 27.1161 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19367 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-230M | 230 W Monocrystalline Module | UL 1703 | 230 | 207.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.22 | 37.1 | 7.7 | 29.9 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.4759 | 29.6075 | 6.1027 | 26.6114 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.18999 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-230MX | 230 W Monocrystalline Module, Zep Frame | UL 1703 | 230 | 202.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.22 | 37.1 | 7.7 | 29.9 | 48.3 | -0.48 | 0.04 | -0.35 | -0.01 | -0.4305 | 1.4759 | 29.6075 | 6.1027 | 26.6114 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.18999 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-230P | 230 W Polycrystalline Module | UL 1703 | 230 | 211 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.34 | 36.8 | 7.71 | 29.8 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.534 | 28.9973 | 6.1359 | 27.3918 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.1934 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-230PX | 230 W Polycrystalline Module | UL 1703 | 230 | 211 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.34 | 36.8 | 7.71 | 29.8 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.534 | 28.9973 | 6.1359 | 27.3918 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.1934 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-235M | 235 W Monocrystalline Module | UL 1703 | 235 | 212.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.34 | 37.2 | 7.82 | 30.1 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.4989 | 29.8055 | 6.1978 | 26.7894 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19011 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-235MX | 235 W Monocrystalline Module, Zep Frame | UL 1703 | 235 | 207.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.34 | 37.2 | 7.82 | 30.1 | 48.3 | -0.48 | 0.04 | -0.35 | -0.01 | -0.4305 | 1.4951 | 29.8055 | 6.182 | 26.7894 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.18962 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-235P | 235 W Polycrystalline Module | UL 1703 | 235 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 8.46 | 36.9 | 7.9 | 29.8 | 44.1 | -0.4538 | 0.0637 | -0.3654 | -0.0093 | -0.4108 | 1.5123 | 28.8186 | 6.2886 | 28.1224 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.18546 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-235PX | 235 W Polycrystalline Module | UL 1703 | 235 | 215.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.46 | 36.9 | 7.9 | 29.8 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.5718 | 28.9973 | 6.2871 | 27.3918 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.19395 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-240M | 240 W Monocrystalline Module | UL 1703 | 240 | 217.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.46 | 37.3 | 7.95 | 30.2 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.5238 | 29.9045 | 6.3009 | 26.8784 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.18987 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-240MX | 240 W Monocrystalline Module, Zep Frame | UL 1703 | 240 | 212 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.46 | 37.3 | 7.95 | 30.2 | 48.3 | -0.48 | 0.04 | -0.35 | -0.01 | -0.4305 | 1.5334 | 29.9045 | 6.3405 | 26.8784 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19107 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-240P | 240 W Polycrystalline Module | UL 1703 | 240 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 8.59 | 37 | 8.03 | 29.9 | 44.1 | -0.4538 | 0.0637 | -0.3654 | -0.0093 | -0.4108 | 1.5372 | 28.9153 | 6.3921 | 28.2168 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.1852 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-240PX | 240 W Polycrystalline Module | UL 1703 | 240 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 8.59 | 37 | 8.03 | 29.9 | 44.1 | -0.4538 | 0.0637 | -0.3654 | -0.0093 | -0.4108 | 1.5372 | 28.9153 | 6.3921 | 28.2168 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.1852 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-245M | 245 W Monocrystalline Module | UL 1703 | 245 | 223.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.61 | 37.4 | 8.09 | 30.3 | 44.3 | -0.442 | 0.0495 | -0.3416 | -0.0246 | -0.4204 | 1.6182 | 26.7227 | 6.5606 | 29.804 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.1765 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-245MX | 245 W Monocrystalline Module, ZEP frame | UL 1703 | 245 | 221.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.61 | 37.4 | 8.09 | 30.3 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.6162 | 26.7329 | 6.5526 | 29.8154 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.17635 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-245P | 245 W Polycrystalline Module | UL 1703 | 245 | 224.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 8.74 | 37.1 | 8.17 | 30 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.6562 | 29.4745 | 6.5755 | 28.2508 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19925 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-245PX | 245 W Polycrystalline Module, ZEP frame | UL 1703 | 245 | 224.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 8.74 | 37.1 | 8.17 | 30 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.66 | 29.47 | 6.58 | 28.25 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19967 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-250M | 250 W Monocrystalline Module | UL 1703 | 250 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.74 | 37.5 | 8.22 | 30.4 | 44.3 | -0.442 | 0.0495 | -0.3416 | -0.0246 | -0.4204 | 1.6442 | 26.8109 | 6.666 | 29.9024 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.17633 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-250MX | 250 W Monocrystalline Module, ZEP frame | UL 1703 | 250 | 226.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.74 | 37.5 | 8.22 | 30.4 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.6422 | 26.8211 | 6.6579 | 29.9138 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.17618 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-250P | 250 W Polycrystalline Module | UL 1703 | 250 | 229.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 8.87 | 37.2 | 8.3 | 30.1 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.6825 | 29.5728 | 6.6802 | 28.3449 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19903 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-250PX | 250 W Polycrystalline Module, ZEP frame | UL 1703 | 250 | 229.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 8.87 | 37.2 | 8.3 | 30.1 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.68 | 29.57 | 6.68 | 28.34 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19871 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-250P | 250 W, 108 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 250 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.55 | 54 | 2 | N | 9.55 | 34.2 | 8.75 | 28.6 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.8234 | 26.8937 | 7.1411 | 26.2869 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6P-255M | 255 W Monocrystalline Module | UL 1703 | 255 | 232.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.87 | 37.7 | 8.35 | 30.5 | 44.3 | -0.442 | 0.0495 | -0.3416 | -0.0246 | -0.4204 | 1.6702 | 26.8991 | 6.7714 | 30.0007 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.17618 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-255MX | 255 W Monocrystalline Module, ZEP frame | UL 1703 | 255 | 231 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.87 | 37.7 | 8.35 | 30.5 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.6682 | 26.9094 | 6.7632 | 30.0122 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.17604 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-255P | 255 W Polycrystalline Module | UL 1703 | 255 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 9 | 37.4 | 8.43 | 30.2 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.7089 | 29.671 | 6.7848 | 28.4391 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19884 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-255PX | 255 W Polycrystalline Module, ZEP frame | UL 1703 | 255 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 9 | 37.4 | 8.43 | 30.2 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.71 | 29.67 | 6.78 | 28.44 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19896 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-255P | 255 W, 108 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 255 | 236.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.55 | 54 | 2 | N | 9.62 | 34.4 | 8.86 | 28.8 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.8463 | 27.0817 | 7.2309 | 26.4707 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-255P | 255 W Polycrystalline Module | UL 1703 | 255 | 226.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8518 | 72 | 1 | N | 7.95 | 43.7 | 7.33 | 34.8 | 44.8 | -0.53 | 0.06 | -0.39 | -0.02 | -0.51 | 1.3862 | 33.5342 | 6.0767 | 31.319 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.1823 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-260M | 260 W Monocrystalline Module | UL 1703 | 260 | 237.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.99 | 37.8 | 8.48 | 30.7 | 44.3 | -0.442 | 0.0495 | -0.3416 | -0.0246 | -0.4204 | 1.6962 | 27.0754 | 6.8768 | 30.1975 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.17664 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-260MX | 260 W Monocrystalline Module, ZEP frame | UL 1703 | 260 | 235.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 8.99 | 37.8 | 8.48 | 30.7 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.6941 | 27.0858 | 6.8684 | 30.209 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.17649 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-260P | 260 W Polycrystalline Module | UL 1703 | 260 | 239.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 9.12 | 37.5 | 8.56 | 30.4 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.7352 | 29.8675 | 6.8894 | 28.6275 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19934 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-260PX | 260 W Polycrystalline Module, ZEP frame | UL 1703 | 260 | 239.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 9.12 | 37.5 | 8.56 | 30.4 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.74 | 29.87 | 6.89 | 28.63 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.1999 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-260P | 260 W, 108 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 260 | 241.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.55 | 54 | 2 | N | 9.69 | 34.6 | 8.97 | 29 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.8692 | 27.2698 | 7.3207 | 26.6545 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-260P | 260 W Polycrystalline Module | UL 1703 | 260 | 230.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8518 | 72 | 1 | N | 8.04 | 43.8 | 7.45 | 34.9 | 44.8 | -0.53 | 0.06 | -0.39 | -0.02 | -0.51 | 1.4089 | 33.6305 | 6.1762 | 31.409 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.18224 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-265M | 265 W Monocrystalline Module | UL 1703 | 265 | 242 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.11 | 37.9 | 8.61 | 30.9 | 44.3 | -0.442 | 0.0495 | -0.3416 | -0.0246 | -0.4204 | 1.7222 | 27.2518 | 6.9822 | 30.3942 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.17711 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-265MX | 265 W Monocrystalline Module, ZEP frame | UL 1703 | 265 | 240.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.11 | 37.9 | 8.61 | 30.9 | 46 | -0.436 | 0.0501 | -0.3647 | -0.0085 | -0.4853 | 1.7201 | 27.2623 | 6.9737 | 30.4058 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.17696 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-265P | 265 W Polycrystalline Module | UL 1703 | 265 | 243.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 9.23 | 37.7 | 8.66 | 30.6 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.7555 | 30.064 | 6.9699 | 28.8158 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19916 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-265PX | 265 W Polycrystalline Module, ZEP frame | UL 1703 | 265 | 243.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5488 | 60 | 1 | N | 9.23 | 37.7 | 8.66 | 30.6 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.76 | 30.06 | 6.97 | 28.82 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19964 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-265P | 265 W, 108 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 265 | 246.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.55 | 54 | 2 | N | 9.76 | 34.8 | 9.08 | 29.2 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.8922 | 27.4579 | 7.4105 | 26.8384 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-265P | 265 W Polycrystalline Module | UL 1703 | 265 | 235.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8518 | 72 | 1 | N | 8.1 | 43.9 | 7.55 | 35.1 | 44.8 | -0.53 | 0.06 | -0.39 | -0.02 | -0.51 | 1.4278 | 33.8233 | 6.2591 | 31.589 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.18224 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-270M | 270 W Monocrystalline Module | UL 1703 | 270 | 244.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.19 | 38.2 | 8.67 | 31.1 | 46.4 | -0.431 | 0.042 | -0.359 | -0.023 | -0.406 | 1.7311 | 30.9397 | 6.9321 | 28.345 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19837 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-270MX | 270 W Monocrystalline Module, ZEP frame | UL 1703 | 270 | 244.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.19 | 38.2 | 8.67 | 31.1 | 46.4 | -0.431 | 0.042 | -0.359 | -0.023 | -0.406 | 1.7311 | 30.9397 | 6.9321 | 28.345 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19837 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-270P | 270 W Polycrystalline Module | UL 1703 | 270 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5928 | 60 | 1 | N | 9.32 | 37.9 | 8.75 | 30.8 | 45.8 | -0.4002 | -0.0474 | -0.3071 | -0.4069 | 0.0084 | 1.7604 | 29.5689 | 7.0069 | 28.0876 | Rack | Flat Plate | 0.976 | 1.632 | 1 | 0.19279 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-270P | 270 W, 108 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 270 | 250.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.55 | 54 | 2 | N | 9.83 | 35 | 9.19 | 29.4 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.9151 | 27.6459 | 7.5002 | 27.0222 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-270P | 270 W Polycrystalline Module | UL 1703 | 270 | 240 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8518 | 72 | 1 | N | 8.19 | 44.1 | 7.65 | 35.3 | 44.8 | -0.53 | 0.06 | -0.39 | -0.02 | -0.51 | 1.4468 | 34.016 | 6.342 | 31.769 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.18227 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-275M | 275 W Monocrystalline Module | UL 1703 | 275 | 249.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.31 | 38.3 | 8.8 | 31.3 | 46.4 | -0.431 | 0.042 | -0.359 | -0.023 | -0.406 | 1.757 | 31.1387 | 7.036 | 28.5273 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19895 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-275MX | 275 W Monocrystalline Module, ZEP frame | UL 1703 | 275 | 249.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.31 | 38.3 | 8.8 | 31.3 | 46.4 | -0.431 | 0.042 | -0.359 | -0.023 | -0.406 | 1.757 | 31.1387 | 7.036 | 28.5273 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19895 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-275P | 275 W Polycrystalline Module | UL 1703 | 275 | 251.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5928 | 60 | 1 | N | 9.45 | 38 | 8.88 | 31 | 45.8 | -0.4002 | -0.0474 | -0.3071 | -0.4069 | 0.0084 | 1.7865 | 29.7609 | 7.111 | 28.27 | Rack | Flat Plate | 0.976 | 1.632 | 1 | 0.19334 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-275P | 275 W, 108 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 275 | 255.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.55 | 54 | 2 | N | 9.9 | 35.2 | 9.3 | 29.6 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.938 | 27.834 | 7.59 | 27.206 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-275P | 275 W Polycrystalline Module | UL 1703 | 275 | 244.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8518 | 72 | 1 | N | 8.31 | 44.1 | 7.76 | 35.5 | 44.8 | -0.53 | 0.06 | -0.39 | -0.02 | -0.51 | 1.4676 | 34.2087 | 6.4332 | 31.949 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.18256 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-280M | 280 W Monocrystalline Module | UL 1703 | 280 | 254.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.43 | 38.5 | 8.89 | 31.5 | 46.4 | -0.431 | 0.042 | -0.359 | -0.023 | -0.406 | 1.775 | 31.3376 | 7.108 | 28.7096 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19866 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-280MX | 280 W Monocrystalline Module, ZEP frame | UL 1703 | 280 | 254.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.43 | 38.5 | 8.89 | 31.5 | 46.4 | -0.431 | 0.042 | -0.359 | -0.023 | -0.406 | 1.775 | 31.3376 | 7.108 | 28.7096 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.19866 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-280M | 280 W, 108 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 280 | 259.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.55 | 54 | 2 | N | 9.96 | 36.5 | 9.34 | 30 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 1.934 | 28.6692 | 7.6138 | 27.7394 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-280P | 280 W, 108 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 280 | 260.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.55 | 54 | 2 | N | 9.97 | 35.4 | 9.4 | 29.8 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.9588 | 28.0221 | 7.6716 | 27.3898 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-280P | 280 W Polycrystalline Module | UL 1703 | 280 | 249.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8518 | 72 | 1 | N | 8.42 | 44.2 | 7.86 | 35.6 | 44.8 | -0.53 | 0.06 | -0.39 | -0.02 | -0.51 | 1.5028 | 34.9185 | 5.586 | 26.7802 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.18741 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-285M | 285 W Monocrystalline Module | UL 1703 | 285 | 258.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.51 | 38.6 | 8.98 | 31.7 | 46.4 | -0.431 | 0.042 | -0.359 | -0.023 | -0.406 | 1.793 | 31.5366 | 7.18 | 28.8919 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.1984 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6P-285MX | 285 W Monocrystalline Module, ZEP frame | UL 1703 | 285 | 258.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5488 | 60 | 1 | N | 9.51 | 38.6 | 8.98 | 31.7 | 46.4 | -0.431 | 0.042 | -0.359 | -0.023 | -0.406 | 1.793 | 31.5366 | 7.18 | 28.8919 | Rack | Flat Plate | 0.959 | 1.615 | 1 | 0.1984 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-285M | 285 W, 108 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 285 | 264.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.55 | 54 | 2 | N | 10.02 | 36.7 | 9.41 | 30.3 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 1.9485 | 28.9559 | 7.6708 | 28.0168 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-285P | 285 W Polycrystalline Module | UL 1703 | 285 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8518 | 72 | 1 | N | 8.53 | 44.3 | 7.96 | 35.8 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.5975 | 35.1557 | 6.4044 | 33.4685 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.19706 |  | 2021-07-12
CSI Solar Co., Ltd. | CS3K-290MS | 120 half cut cell Module | UL 1703 | 290 | 269.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.603 | 3 |  |  | 9.65 | 38.9 | 9.04 | 32.1 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.85 | 32 | 7.39 | 30.5 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-290M | 290 W, 108 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 290 | 269 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.55 | 54 | 2 | N | 10.08 | 36.9 | 9.48 | 30.6 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 1.963 | 29.2426 | 7.7279 | 28.2942 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-290P | 290 W Polycrystalline Module | UL 1703 | 290 | 266.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8518 | 72 | 1 | N | 8.64 | 44.4 | 8.08 | 35.9 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.6216 | 35.2539 | 6.501 | 33.562 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.19713 |  | 2021-07-12
CSI Solar Co., Ltd. | CS3K-295MS | 120 half cut cell Module | UL 61730 | 295 | 274.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.603 | 3 |  |  | 9.73 | 39.1 | 9.14 | 32.3 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.85 | 32 | 7.39 | 30.5 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-295M | 295 W, 108 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 295 | 273.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.55 | 54 | 2 | N | 10.14 | 37.1 | 9.55 | 30.9 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 1.9775 | 29.5293 | 7.7849 | 28.5716 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-295P | 295 W Polycrystalline Module | UL 1703 | 295 | 270.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8518 | 72 | 1 | N | 8.76 | 44.5 | 8.19 | 36 | 43.6 | -0.424 | 0.039 | -0.301 | -0.004 | -0.409 | 1.6437 | 35.3521 | 6.5895 | 33.6555 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.19698 |  | 2021-07-12
CSI Solar Co., Ltd. | CS3K-300MS | 120 half cut cell Module | UL 61730 | 300 | 279 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.603 | 3 |  |  | 9.82 | 39.3 | 9.24 | 32.5 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.85 | 32 | 7.39 | 30.5 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-300M | 300 W, 108 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 300 | 278.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.55 | 54 | 2 | N | 10.19 | 37.3 | 9.62 | 31.2 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 1.992 | 29.816 | 7.842 | 28.849 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-300P | 300 W Polycrystalline Module | UL 1703 | 300 | 274.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9012 | 72 | 1 | N | 8.87 | 44.6 | 8.3 | 36.1 | 45.8 | -0.4002 | -0.0474 | -0.3071 | -0.4069 | 0.0084 | 1.6426 | 34.2183 | 6.7249 | 32.7718 | Rack | Flat Plate | 0.976 | 1.948 | 1 | 0.18735 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-300P | 300 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 300 | 278.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 9.56 | 41.6 | 8.68 | 34.6 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.8104 | 32.9792 | 7.2161 | 31.7576 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS3K-305MS | 120 half cut cell Module | UL 61730 | 305 | 283.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.603 | 3 |  |  | 9.9 | 39.5 | 9.33 | 32.7 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.85 | 32 | 7.39 | 30.5 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-305M | 305 W, 108 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 305 | 283.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.55 | 54 | 2 | N | 10.25 | 37.5 | 9.69 | 31.5 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 2.0065 | 30.1027 | 7.8991 | 29.1264 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-305P | 305 W Polycrystalline Module | UL 1703 | 305 | 278.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9012 | 72 | 1 | N | 8.97 | 44.8 | 8.41 | 36.3 | 45.8 | -0.4002 | -0.0474 | -0.3071 | -0.4069 | 0.0084 | 1.6643 | 34.4079 | 6.814 | 32.9533 | Rack | Flat Plate | 0.976 | 1.948 | 1 | 0.18776 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-305P | 305 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 305 | 283 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 9.6 | 41.8 | 8.77 | 34.8 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.8291 | 33.1698 | 7.2909 | 31.9412 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS1H-310MS | 310 W, 396 sixth cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 310 | 288.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 66 | 6 | N | 9.37 | 43.1 | 8.82 | 35.2 | 45.1 | -0.3448 | 0.0626 | -0.2754 | 0.0174 | -0.3604 | 1.7543 | 33.6258 | 7.0909 | 32.7331 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3K-310MS | 120 half cut cell Module | UL 61730 | 310 | 288.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.603 | 3 |  |  | 9.98 | 39.7 | 9.43 | 32.9 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.85 | 32 | 7.39 | 30.5 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-310P-AG | 310 W, 144 half-cut cell double glass Polycrystalline module, white backsheet | UL 1703 | 310 | 285.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 8.88 | 44.7 | 8.34 | 37.2 | 44.6 | -0.3915 | 0.0367 | -0.3111 | 0.0045 | -0.3956 | 1.7079 | 34.9475 | 6.7043 | 34.4012 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6PH-310M | 310 W, 108 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 310 | 288 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.55 | 54 | 2 | N | 10.31 | 37.7 | 9.75 | 31.8 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 2.0189 | 30.3894 | 7.948 | 29.4038 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-310P | 310 W Polycrystalline Module | UL 1703 | 310 | 283.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9012 | 72 | 1 | N | 9.08 | 44.9 | 8.52 | 36.4 | 45.8 | -0.4002 | -0.0474 | -0.3071 | -0.4069 | 0.0084 | 1.6861 | 34.5027 | 6.9031 | 33.0441 | Rack | Flat Plate | 0.976 | 1.948 | 1 | 0.18766 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-310P | 310 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 310 | 287.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 9.64 | 42 | 8.86 | 35 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.8479 | 33.3605 | 7.3657 | 32.1247 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS1H-315MS | 315 W, 396 sixth cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 315 | 293.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 66 | 6 | N | 9.44 | 43.2 | 8.91 | 35.4 | 45.1 | -0.3448 | 0.0626 | -0.2754 | 0.0174 | -0.3604 | 1.7722 | 33.8169 | 7.1633 | 32.919 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3K-315MS | 120 half cut cell Module | UL 61730 | 315 | 293.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.603 | 3 |  |  | 10.06 | 39.9 | 9.52 | 33.1 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.85 | 32 | 7.39 | 30.5 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-315PB-AG | 315 W, 120 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 1703 | 315 | 293.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.82 | 60 | 2 | N | 10.58 | 38.6 | 9.97 | 31.6 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0008 | 30.5068 | 8.0033 | 29.5715 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-315P-AG | 315 W, 144 half-cut cell double glass Polycrystalline module, white backsheet | UL 1703 | 315 | 290.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 8.96 | 44.9 | 8.43 | 37.4 | 44.6 | -0.3915 | 0.0367 | -0.3111 | 0.0045 | -0.3956 | 1.7264 | 35.1354 | 6.7767 | 34.5862 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-315P | 315 W Polycrystalline Module | UL 1703 | 315 | 288.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9012 | 72 | 1 | N | 9.18 | 45.1 | 8.61 | 36.6 | 45.8 | -0.4002 | -0.0474 | -0.3071 | -0.4069 | 0.0084 | 1.7039 | 34.6923 | 6.976 | 33.2257 | Rack | Flat Plate | 0.976 | 1.948 | 1 | 0.18766 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-315P | 315 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 315 | 292.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 9.68 | 42.2 | 8.95 | 35.2 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.8667 | 33.5511 | 7.4405 | 32.3083 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS1H-320MS | 320 W, 396 sixth cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 320 | 298.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 66 | 6 | N | 9.51 | 43.3 | 9 | 35.6 | 45.1 | -0.3448 | 0.0626 | -0.2754 | 0.0174 | -0.3604 | 1.7901 | 34.0079 | 7.2356 | 33.105 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3K-320MS | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 320 | 298.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 | 2 | N | 10.14 | 40.1 | 9.61 | 33.3 | 45.5 | -0.3452 | 0.0476 | -0.2765 | 1.898 | 32.357 | 1.898 | 32.357 | 7.648 | 31.065 | [6 empty] | 2019-09-03 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-320P | 320 W, 120 half-cut cell polycrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 1703 | 320 | 297.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 10.66 | 38.8 | 10.07 | 31.8 | 44.7 | -0.3516 | 0.0467 | -0.2687 |  |  | 2.0347 | 29.7142 | 8.117 | 29.7093 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-320PB-AG | 320 W, 120 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 1703 | 320 | 298.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.82 | 60 | 2 | N | 10.66 | 38.8 | 10.07 | 31.8 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0209 | 30.6998 | 8.0835 | 29.7587 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-320P | 320 W Polycrystalline Module, 144 half-cut cells | UL 1703 | 320 | 295.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.04 | 45.1 | 8.52 | 37.6 | 44.6 | -0.3811 | 0.0501 | -0.2924 | 0.0045 | -0.3851 | 1.826 | 37.127 | 7.22 | 35.609 | [7 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3U-320P-AG | 320 W, 144 half-cut cell double glass Polycrystalline module, white backsheet | UL 1703 | 320 | 294.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.04 | 45.1 | 8.52 | 37.6 | 44.6 | -0.3915 | 0.0367 | -0.3111 | 0.0045 | -0.3956 | 1.7448 | 35.3233 | 6.849 | 34.7711 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-320P | 320 W Polycrystalline Module | UL 1703 | 320 | 292.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9012 | 72 | 1 | N | 9.26 | 45.3 | 8.69 | 36.8 | 45.8 | -0.4002 | 0.0474 | -0.3071 | -0.4069 | 0.0084 | 1.72 | 34.88 | 7.04 | 33.41 | Rack | Flat Plate | 0.976 | 1.948 | 1 | 0.18748 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-320P | 320 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 297.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 9.72 | 42.4 | 9.04 | 35.4 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.8855 | 33.7417 | 7.5154 | 32.4919 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS1H-325MS | 325 W, 396 sixth cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 325 | 303.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 66 | 6 | N | 9.58 | 43.4 | 9.09 | 35.8 | 45.1 | -0.3448 | 0.0626 | -0.2754 | 0.0174 | -0.3604 | 1.808 | 34.199 | 7.308 | 33.291 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3K-325MS | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 325 | 302.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 | 2 | N | 10.22 | 40.3 | 9.71 | 33.5 | 45.5 | -0.3452 | 0.0476 | -0.2765 | 1.9178 | 32.5513 | 1.9178 | 32.5513 | 7.7276 | 31.2516 | [6 empty] | 2019-09-03 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-325P | 325 W, 120 half-cut cell polycrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 1703 | 325 | 302.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 10.74 | 39 | 10.16 | 32 | 44.7 | -0.3516 | 0.0467 | -0.2687 |  |  | 2.0528 | 29.9011 | 8.1895 | 29.8961 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-325PB-AG | 325 W, 120 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 1703 | 325 | 303.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.82 | 60 | 2 | N | 10.74 | 39 | 10.16 | 32 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0389 | 30.8929 | 8.1558 | 29.9458 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-325P | 325 W Polycrystalline Module, 144 half-cut cells | UL 1703 | 325 | 300.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.12 | 45.3 | 8.6 | 37.8 | 44.6 | -0.3811 | 0.0501 | -0.2924 | 0.0045 | -0.3851 | 1.826 | 37.127 | 7.22 | 35.609 | [7 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3U-325P-AG | 325 W, 144 half-cut cell double glass Polycrystalline module, white backsheet | UL 1703 | 325 | 299.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.12 | 45.3 | 8.6 | 37.8 | 44.6 | -0.3915 | 0.0367 | -0.3111 | 0.0045 | -0.3956 | 1.7612 | 35.5112 | 6.9133 | 34.9561 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-325P | 325 W Polycrystalline Module | UL 1703 | 325 | 297.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9012 | 72 | 1 | N | 9.34 | 45.5 | 8.78 | 37 | 45.8 | -0.4002 | 0.0474 | -0.3071 | -0.4069 | 0.0084 | 1.74 | 35.07 | 7.11 | 33.59 | Rack | Flat Plate | 0.976 | 1.948 | 1 | 0.18776 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-325P | 325 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 325 | 302 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 9.76 | 42.6 | 9.13 | 35.6 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.9042 | 33.9324 | 7.5902 | 32.6754 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS1H-330MS | 330 W, 396 sixth cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 330 | 308 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 66 | 6 | N | 9.65 | 43.5 | 9.18 | 36 | 45.1 | -0.3448 | 0.0626 | -0.2754 | 0.0174 | -0.3604 | 1.8259 | 34.3901 | 7.3804 | 33.477 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3K-330MS | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 330 | 307.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 | 2 | N | 10.3 | 40.5 | 9.8 | 33.7 | 45.5 | -0.3452 | 0.0476 | -0.2765 | 1.9355 | 32.7457 | 1.9355 | 32.7457 | 7.7992 | 31.4382 | [6 empty] | 2019-09-03 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-330P | 330 W, 120 half-cut cell polycrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 1703 | 330 | 307.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 10.82 | 39.2 | 10.24 | 32.2 | 44.7 | -0.3516 | 0.0467 | -0.2687 |  |  | 2.069 | 30.088 | 8.254 | 30.083 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-330PB-AG | 330 W, 120 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 1703 | 330 | 308.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.82 | 60 | 2 | N | 10.82 | 39.2 | 10.24 | 32.2 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.055 | 31.086 | 8.22 | 30.133 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-330P | 330 W Polycrystalline Module, 144 half-cut cells | UL 1703 | 330 | 305 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.2 | 45.5 | 8.69 | 38 | 44.6 | -0.3811 | 0.0501 | -0.2924 | 0.0045 | -0.3851 | 1.826 | 37.127 | 7.22 | 35.609 | [7 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3U-330P-AG | 330 W, 144 half-cut cell double glass Polycrystalline module, white backsheet | UL 1703 | 330 | 304.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.2 | 45.5 | 8.69 | 38 | 44.6 | -0.3915 | 0.0367 | -0.3111 | 0.0045 | -0.3956 | 1.7796 | 35.6991 | 6.9857 | 35.141 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6X-330P | 330 W Polycrystalline Module | UL 1703 | 330 | 302.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9012 | 72 | 1 | N | 9.45 | 45.6 | 8.88 | 37.2 | 45.8 | -0.4002 | 0.0474 | -0.3071 | -0.4069 | 0.0084 | 1.76 | 35.26 | 7.19 | 33.77 | Rack | Flat Plate | 0.976 | 1.948 | 1 | 0.18805 |  | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-330P | 330 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 330 | 306.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 9.83 | 42.8 | 9.22 | 35.8 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.923 | 34.123 | 7.665 | 32.859 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS1H-335MS | 335 W, 396 sixth cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 335 | 312.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 66 | 6 | N | 9.73 | 43.6 | 9.27 | 36.2 | 45.1 | -0.3448 | 0.0626 | -0.2754 | 0.0174 | -0.3604 | 1.8438 | 34.5811 | 7.4527 | 33.663 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3K-335MS | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 335 | 312.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 | 2 | N | 10.39 | 41.2 | 9.89 | 33.9 | 45.5 | -0.3452 | 0.0476 | -0.2765 |  |  | 1.9533 | 32.94 | 7.8708 | 31.6247 | [6 empty] | 2019-12-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-335P | 335 W, 120 half-cut cell polycrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 1703 | 335 | 312.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 10.9 | 39.4 | 10.34 | 32.4 | 44.7 | -0.3516 | 0.0467 | -0.2687 |  |  | 2.0892 | 30.2749 | 8.3346 | 30.2699 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-335PB-AG | 335 W, 120 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 1703 | 335 | 312.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.82 | 60 | 2 | N | 10.9 | 39.4 | 10.34 | 32.4 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0751 | 31.2791 | 8.3003 | 30.3202 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-335P | 335 W Polycrystalline Module, 144 half-cut cells | UL 1703 | 335 | 309.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.28 | 45.7 | 8.77 | 38.2 | 44.6 | -0.3811 | 0.0501 | -0.2924 | 0.0045 | -0.3851 | 1.826 | 37.127 | 7.22 | 35.609 | [7 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3U-335P-AG | 335 W, 144 half-cut cell double glass Polycrystalline module, white backsheet | UL 1703 | 335 | 309 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.28 | 45.7 | 8.77 | 38.2 | 44.6 | -0.3915 | 0.0367 | -0.3111 | 0.0045 | -0.3956 | 1.796 | 35.887 | 7.05 | 35.326 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-335P | 335 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 335 | 311.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 9.9 | 43 | 9.31 | 36 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.9418 | 34.3136 | 7.7398 | 33.0426 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS1H-340MS | 340 W, 396 sixth cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 340 | 317.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 66 | 6 | N | 9.81 | 43.7 | 9.35 | 36.4 | 45.1 | -0.3448 | 0.0626 | -0.2754 | 0.0174 | -0.3604 | 1.8597 | 34.7722 | 7.517 | 33.8489 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-340P | 340 W, 120 half-cut cell polycrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 340 | 316.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 10.98 | 39.6 | 10.43 | 32.6 | 44.7 | -0.3516 | 0.0467 | -0.2687 |  |  | 2.1074 | 30.4618 | 8.4072 | 30.4567 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-340PB-AG | 340 W, 120 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 1703 | 340 | 317.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.82 | 60 | 2 | N | 10.98 | 39.6 | 10.43 | 32.6 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0931 | 31.4722 | 8.3725 | 30.5073 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-340P | 340 W Polycrystalline Module, 144 half-cut cells | UL 1703 | 340 | 314.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.36 | 45.9 | 8.86 | 38.4 | 44.6 | -0.3811 | 0.0501 | -0.2924 | 0.0045 | -0.3851 | 1.826 | 37.127 | 7.22 | 35.609 | [7 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3U-340P-AG | 340 W, 144 half-cut cell double glass Polycrystalline module, white backsheet | UL 1703 | 340 | 313.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.36 | 45.9 | 8.86 | 38.4 | 44.6 | -0.3915 | 0.0367 | -0.3111 | 0.0045 | -0.3956 | 1.8144 | 36.0749 | 7.1223 | 35.511 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-340P | 340 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 340 | 316.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 9.97 | 43.2 | 9.4 | 36.2 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.9605 | 34.5043 | 7.8146 | 33.2261 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-345MS | 345 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 345 | 320.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 2 | N | 11.23 | 39.8 | 10.43 | 34.1 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.0898 | 31.8575 | 8.4103 | 30.2074 | [6 empty] | 2021-03-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-345P | 345 W, 120 half-cut cell polycrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 345 | 321.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 11.06 | 39.8 | 10.52 | 32.8 | 44.7 | -0.3516 | 0.0467 | -0.2687 |  |  | 2.1256 | 30.6486 | 8.4797 | 30.6436 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-345PB-AG | 345 W, 120 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 1703 | 345 | 322.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.82 | 60 | 2 | N | 11.06 | 39.8 | 10.52 | 32.8 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.1112 | 31.6652 | 8.4448 | 30.6945 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-345P | 345 W Polycrystalline Module, 144 half-cut cells | UL 61730 | 345 | 319.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.44 | 46.1 | 8.94 | 38.6 | 44.6 | -0.3811 | 0.0501 | -0.2924 | 0.0045 | -0.3851 | 1.826 | 37.127 | 7.22 | 35.609 | [7 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3U-345P-AG | 345 W, 144 half-cut cell double glass Polycrystalline module, white backsheet | UL 1703 | 345 | 318.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.44 | 46.1 | 8.94 | 38.6 | 44.6 | -0.3915 | 0.0367 | -0.3111 | 0.0045 | -0.3956 | 1.8308 | 36.2628 | 7.1867 | 35.6959 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-345PB-AG | 345 W, 144 half cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 1703 | 345 | 318.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 2 | N | 9.43 | 46.4 | 8.86 | 39 | 44 | -0.4002 | 0.0318 | -0.295 | -0.0043 | -0.3967 | 1.7954 | 36.7073 | 7.3304 | 35.1788 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-345M | 345 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 345 | 320 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 66 | 2 | N | 9.94 | 44.4 | 9.46 | 36.5 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 1.9662 | 35.1504 | 7.7506 | 33.9769 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-345P | 345 W, 132 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 345 | 321.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.85 | 66 | 2 | N | 10.04 | 43.4 | 9.49 | 36.4 | 44.2 | -0.3654 | 0.056 | -0.2818 |  |  | 1.9793 | 34.6949 | 7.8895 | 33.4097 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-350MS | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 350 | 325.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 2 | N | 11.28 | 40 | 10.52 | 33.3 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.1079 | 32.05 | 8.4828 | 30.3899 | [6 empty] | 2021-02-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-350P | 350 W, 120 half-cut cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 350 | 326.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 11.24 | 40.2 | 10.61 | 33 | 44.7 | -0.3516 | 0.0467 | -0.2687 |  |  | 2.131 | 31.537 | 8.654 | 30.329 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-350MB-AG | 350 W, 144 half cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 350 | 323.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.53 | 46.6 | 9.03 | 38.8 | 44 | -0.4036 | 0.022 | -0.2869 | -0.0374 | -0.3711 | 1.8021 | 37.2116 | 7.4724 | 35.7433 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-350MS | 144 half cut cell Module | UL 61730 | 350 | 325.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.919 | 3 |  | N | 9.53 | 46.6 | 9.03 | 38.8 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.84 | 38.3 | 7.32 | 37 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-350MS-AG | 350 W, 144 half-cut cell double glass Monocrystalline module, white backsheet | UL 1703 | 350 | 322.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 9.53 | 46.6 | 9.03 | 38.8 | 45.7 | -0.3834 | 0.0353 | -0.2929 | 0.0022 | -0.3864 | 1.8473 | 37.2678 | 7.2397 | 36.0197 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-350P | 350 W Polycrystalline Module, 144 half-cut cells | UL 61730 | 350 | 324 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.51 | 46.6 | 8.94 | 39.2 | 44.6 | -0.3811 | 0.0501 | -0.2924 | 0.0045 | -0.3851 | 1.826 | 37.127 | 7.22 | 35.609 | [7 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3U-350P-AG | 350 W, 144 half-cut cell double glass Polycrystalline module, white backsheet | UL 1703 | 350 | 323.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.51 | 46.6 | 8.94 | 39.2 | 44.6 | -0.3915 | 0.0367 | -0.3111 | 0.0045 | -0.3956 | 1.8308 | 36.8265 | 7.1867 | 36.2508 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-350PB-AG | 350 W, 144 half cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 350 | 323.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 2 | N | 9.51 | 46.6 | 8.94 | 39.2 | 44 | -0.4002 | 0.0318 | -0.295 | -0.0043 | -0.3967 | 1.8116 | 36.8955 | 7.3966 | 35.3592 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-350M | 350 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 324.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 66 | 2 | N | 10 | 44.6 | 9.52 | 36.8 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 1.9787 | 35.4393 | 7.7997 | 34.2562 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-355MS | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 355 | 330.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 2 | N | 11.33 | 40.2 | 10.61 | 33.5 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.1259 | 32.2425 | 8.5554 | 30.5724 | [6 empty] | 2021-02-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-355P | 355 W, 120 half-cut cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 355 | 331.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 11.31 | 40.4 | 10.7 | 33.2 | 44.7 | -0.3516 | 0.0467 | -0.2687 |  |  | 2.1491 | 31.7281 | 8.7274 | 30.5128 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-355MB-AG | 355 W, 144 half cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 355 | 327.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.61 | 46.8 | 9.11 | 39 | 44 | -0.4036 | 0.022 | -0.2869 | -0.0374 | -0.3711 | 1.8181 | 37.4034 | 7.5386 | 35.9275 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-355MS | 144 half cut cell Module | UL 61730 | 355 | 330.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.919 | 3 |  | N | 9.61 | 46.8 | 9.11 | 39 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.84 | 38.3 | 7.32 | 37 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-355MS-AG | 355 W, 144 half-cut cell double glass Monocrystalline module, white backsheet | UL 1703 | 355 | 327.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 9.61 | 46.8 | 9.11 | 39 | 45.7 | -0.3834 | 0.0353 | -0.2929 | 0.0022 | -0.3864 | 1.8636 | 37.4599 | 7.3039 | 36.2053 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-355P | 355 W Polycrystalline Module, 144 half-cut cells | UL 61730 | 355 | 328.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.59 | 46.8 | 9.02 | 39.4 | 44.6 | -0.3811 | 0.0501 | -0.2924 | 0.0045 | -0.3851 | 1.826 | 37.127 | 7.22 | 35.609 | [6 empty] | 2018-02-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-355PB-AG | 355 W, 144 half cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 355 | 328.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 2 | N | 9.59 | 46.8 | 9.02 | 39.4 | 44 | -0.4002 | 0.0318 | -0.295 | -0.0043 | -0.3967 | 1.8278 | 37.0838 | 7.4628 | 35.5396 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-355M | 355 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 329.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 66 | 2 | N | 10.06 | 44.8 | 9.57 | 37.1 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 1.9891 | 35.7282 | 7.8407 | 34.5355 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-360MS | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 360 | 334.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 2 | N | 11.4 | 40.4 | 10.69 | 33.7 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.1419 | 32.435 | 8.6199 | 30.755 | [6 empty] | 2021-02-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-360P | 360 W, 120 half-cut cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 360 | 332.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 11.37 | 40.6 | 10.78 | 33.4 | 42.9 | -0.4406 | 0.0547 | -0.3272 |  |  | 2.181 | 31.89 | 8.831 | 30.05 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-360MB-AG | 360 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 360 | 337.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.69 | 47 | 9.19 | 39.2 | 43.06 | -0.35 | 0.044 | -0.275 | 1.8019 | 38.0427 | 1.8019 | 38.0427 | 7.3569 | 37.0479 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-360MS | 144 half cut cell Module | UL 61730 | 360 | 334.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.919 | 3 |  | N | 9.69 | 47 | 9.19 | 39.2 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.84 | 38.3 | 7.32 | 37 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-360MS-AG | 360 W, 144 half-cut cell double glass Monocrystalline module, white backsheet | UL 1703 | 360 | 331.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 9.69 | 47 | 9.19 | 39.2 | 45.7 | -0.3834 | 0.0353 | -0.2929 | 0.0022 | -0.3864 | 1.88 | 37.652 | 7.368 | 36.391 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-360P | 360 W Polycrystalline Module, 144 half-cut cells | UL 61730 | 360 | 333.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 2 | N | 9.67 | 47 | 9.1 | 39.6 | 44.6 | -0.3811 | 0.0501 | -0.2924 | 0.0045 | -0.3851 | 1.826 | 37.127 | 7.22 | 35.609 | [6 empty] | 2018-02-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-360PB-AG | 360 W, 144 half cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 360 | 332.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 2 | N | 9.67 | 47 | 9.1 | 39.6 | 44 | -0.4002 | 0.0318 | -0.295 | -0.0043 | -0.3967 | 1.844 | 37.272 | 7.529 | 35.72 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-360M | 360 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 334.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 66 | 2 | N | 10.12 | 45 | 9.63 | 37.4 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 2.0015 | 36.0171 | 7.8898 | 34.8147 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-365MS | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 365 | 339.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 2 | N | 11.47 | 40.6 | 10.78 | 33.9 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.16 | 32.6275 | 8.6925 | 30.9375 | [6 empty] | 2021-02-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-365P | 365 W, 120 half-cut cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 365 | 340.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 11.44 | 40.8 | 10.87 | 33.6 | 44.7 | -0.3516 | 0.0467 | -0.2687 |  |  | 2.1832 | 32.1104 | 8.8661 | 30.8804 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-365MB-AG | 365 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 365 | 342.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.77 | 47.2 | 9.27 | 39.4 | 43.06 | -0.35 | 0.044 | -0.275 | 1.8176 | 38.2368 | 1.8176 | 38.2368 | 7.4209 | 37.237 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-365MS | 144 half cut cell Module | UL 61730 | 365 | 339.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.919 | 3 |  | N | 9.77 | 47.2 | 9.27 | 39.4 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.84 | 38.3 | 7.32 | 37 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-365MS-AG | 365 W, 144 half-cut cell double glass Monocrystalline module, white backsheet | UL 1703 | 365 | 336.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 9.77 | 47.2 | 9.27 | 39.4 | 45.7 | -0.3834 | 0.0353 | -0.2929 | 0.0022 | -0.3864 | 1.8964 | 37.8441 | 7.4321 | 36.5767 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-365P | 365 W, 144 half cut cell polycrystalline module | UL 61730 | 365 | 339.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 1 | N | 9.75 | 47.2 | 9.18 | 39.8 | 43.5 | -0.3816 | 0.0436 | -0.2938 | 0.0073 | -0.3888 | 1.8662 | 37.1756 | 7.4015 | 36.4988 | [6 empty] | 2019-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-365PB-AG | 365 W, 144 half cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 365 | 337.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 2 | N | 9.75 | 47.2 | 9.18 | 39.8 | 44 | -0.4002 | 0.0318 | -0.295 | -0.0043 | -0.3967 | 1.8602 | 37.4602 | 7.5952 | 35.9004 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-365M | 365 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 339 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 66 | 2 | N | 10.18 | 45.2 | 9.69 | 37.7 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 2.014 | 36.306 | 7.939 | 35.094 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-370MS | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 370 | 344.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 2 | N | 11.54 | 40.8 | 10.86 | 34.1 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.176 | 32.82 | 8.757 | 31.12 | [6 empty] | 2021-02-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-370P | 370 W, 120 half-cut cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 370 | 342.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 11.51 | 41 | 10.95 | 33.8 | 42.9 | -0.4406 | 0.0547 | -0.3272 |  |  | 2.2154 | 32.2719 | 8.9703 | 30.4099 | [6 empty] | 2020-09-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-370MB-AG | 370 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 370 | 347.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.85 | 47.4 | 9.35 | 39.6 | 43.06 | -0.35 | 0.044 | -0.275 | 1.8333 | 38.4309 | 1.8333 | 38.4309 | 7.485 | 37.426 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-370MS | 144 half cut cell Module | UL 61730 | 370 | 344.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.919 | 3 |  | N | 9.85 | 47.4 | 9.35 | 39.6 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.84 | 38.3 | 7.32 | 37 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-370MS-AG | 370 W, 144 half-cut cell double glass Monocrystalline module, white backsheet | UL 1703 | 370 | 341.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 9.85 | 47.4 | 9.35 | 39.6 | 45.7 | -0.3834 | 0.0353 | -0.2929 | 0.0022 | -0.3864 | 1.9127 | 38.0362 | 7.4963 | 36.7623 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-370P | 370W, 144 half cut cell polycrystalline module | UL 61730 | 370 | 344.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 1 | N | 9.83 | 47.4 | 9.26 | 40 | 43.5 | -0.3816 | 0.0436 | -0.2938 | 0.0073 | -0.3888 | 1.8825 | 37.3624 | 7.466 | 36.6822 | [6 empty] | 2019-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-370PB-AG | 370 W, 144 half-cut cell bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 370 | 345.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.97 | 72 | 2 | N | 9.83 | 47.4 | 9.26 | 40 | 44.5 | -0.3402 | 0.0418 | -0.2643 | 1.85 | 38.353 | 1.85 | 38.353 | 7.399 | 36.83 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-370M | 370 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 343.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 66 | 2 | N | 10.24 | 45.4 | 9.74 | 38 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 2.0244 | 36.5949 | 7.98 | 35.3733 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-375MS | 375 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 375 | 349.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 2 | N | 11.61 | 41 | 10.94 | 34.3 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.192 | 33.0125 | 8.8215 | 31.3025 | [6 empty] | 2021-02-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-375P | 375 W, 120 half-cut cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 375 | 347 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.79 | 60 | 2 | N | 11.59 | 41.2 | 11.03 | 34 | 42.9 | -0.4406 | 0.0547 | -0.3272 |  |  | 2.2316 | 32.4629 | 9.0358 | 30.5898 | [6 empty] | 2020-09-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-375MS | 375 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 375 | 349.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.2 | 43.5 | 10.36 | 36.2 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.0967 | 35.0158 | 8.2918 | 34.1301 | [6 empty] | 2021-07-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-375MB-AG | 375 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 375 | 351.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.93 | 47.6 | 9.43 | 39.8 | 43.06 | -0.35 | 0.044 | -0.275 | 1.849 | 38.625 | 1.849 | 38.625 | 7.549 | 37.615 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-375MS | 144 half cut cell Module | UL 61730 | 375 | 349.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.919 | 3 |  | N | 9.93 | 47.6 | 9.43 | 39.8 | 43.3 | -0.3869 | 0.0359 | -0.2918 | -0.0097 | -0.3797 | 1.84 | 38.3 | 7.32 | 37 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-375MS-AG | 375 W, 144 half-cut cell double glass Monocrystalline module, white backsheet | UL 1703 | 375 | 346 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 9.93 | 47.6 | 9.43 | 39.8 | 45.7 | -0.3834 | 0.0353 | -0.2929 | 0.0022 | -0.3864 | 1.9291 | 38.2283 | 7.5604 | 36.948 | [6 empty] | 2018-06-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-375P | 375 W, 144 half cut cell polycrystalline module | UL 61730 | 375 | 349.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 1 | N | 9.91 | 47.6 | 9.34 | 40.2 | 43.5 | -0.3816 | 0.0436 | -0.2938 | 0.0073 | -0.3888 | 1.8987 | 37.5492 | 7.5305 | 36.8656 | [6 empty] | 2019-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-375PB-AG | 375 W, 144 half-cut cell bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 375 | 350.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.97 | 72 | 2 | N | 9.91 | 47.6 | 9.34 | 40.2 | 44.5 | -0.3402 | 0.0418 | -0.2643 | 1.866 | 38.5448 | 1.866 | 38.5448 | 7.4629 | 37.0142 | [6 empty] | 2019-09-03 | 2021-07-12
CSI Solar Co., Ltd. | CS6XH-375M | 375 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 348.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 66 | 2 | N | 10.3 | 45.6 | 9.8 | 38.3 | 44.7 | -0.3727 | 0.0335 | -0.2782 |  |  | 2.0369 | 36.8838 | 8.0291 | 35.6525 | [6 empty] | 2021-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS1Y-380MS | 380 W, 468 sixth-cut cell monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 380 | 357 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 78 | 6 | N | 9.74 | 51.5 | 8.89 | 42.7 | 42.9 | -0.3469 | 0.043 | -0.2726 |  |  | 1.75 | 41.3022 | 7.1487 | 40.0143 | [6 empty] | 2021-01-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-380MS | 380 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 380 | 358.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.68 | 41.2 | 11.02 | 34.5 | 43.4 | -0.3242 | 0.0524 | -0.2604 |  |  | 2.195 | 33.273 | 8.746 | 32.388 | [6 empty] | 2021-02-01 | 2021-09-13
CSI Solar Co., Ltd. | CS3N-380MS | 380 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 354.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.26 | 43.7 | 10.44 | 36.4 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.1129 | 35.2093 | 8.3558 | 34.3186 | [6 empty] | 2021-07-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-380MB-AG | 380 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 380 | 356.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 10.01 | 47.8 | 9.5 | 40 | 43.06 | -0.35 | 0.044 | -0.275 | 1.8627 | 38.8191 | 1.8627 | 38.8191 | 7.605 | 37.804 | [6 empty] | 2018-11-15 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-380MS | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 353.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 10.01 | 47.8 | 9.5 | 40 | 45.5 | -0.3452 | 0.0476 | -0.2765 | 1.826 | 38.729 | 1.826 | 38.729 | 7.497 | 37.396 | [6 empty] | 2017-09-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-380P | 380 W, 144 half cut cell polycrystalline module | UL 61730 | 380 | 354 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 1 | N | 9.99 | 47.8 | 9.42 | 40.4 | 43.5 | -0.3816 | 0.0436 | -0.2938 | 0.0073 | -0.3888 | 1.915 | 37.736 | 7.595 | 37.049 | [6 empty] | 2019-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-380PB-AG | 380 W, 144 half-cut cell bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 380 | 355.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.97 | 72 | 2 | N | 9.99 | 47.8 | 9.42 | 40.4 | 44.5 | -0.3402 | 0.0418 | -0.2643 | 1.882 | 38.7365 | 1.882 | 38.7365 | 7.5268 | 37.1983 | [6 empty] | 2019-09-03 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-380P | 380 W, 144 half cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 380 | 351 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 10.58 | 46.4 | 10.03 | 37.9 | 45.2 | -0.3768 | 0.0221 | -0.2787 | -0.0146 | -0.3643 | 1.9932 | 36.5641 | 8.023 | 35.2955 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-380PB-AG | 380 W, 144 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 1703 | 380 | 354.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 10.58 | 46.4 | 10.03 | 37.9 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 1.9963 | 36.7003 | 7.9784 | 35.3753 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS1Y-385MS | 385 W, 468 sixth-cut cell monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 385 | 361.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 78 | 6 | N | 9.78 | 51.7 | 8.97 | 42.9 | 42.9 | -0.3469 | 0.043 | -0.2726 |  |  | 1.7657 | 41.4956 | 7.2131 | 40.2017 | [6 empty] | 2021-01-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-385MS | 385 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 385 | 358.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 2 | N | 11.75 | 41.4 | 11.1 | 34.7 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.2241 | 33.3975 | 8.9505 | 31.6676 | [6 empty] | 2021-02-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-385MS | 385 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 359.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.32 | 43.9 | 10.52 | 36.6 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.1329 | 35.3978 | 8.4199 | 34.5052 | [6 empty] | 2021-04-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-385MB-AG | 385 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 385 | 361.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 10.09 | 48 | 9.58 | 40.2 | 43.06 | -0.35 | 0.044 | -0.275 | 1.8784 | 39.0132 | 1.8784 | 39.0132 | 7.6691 | 37.993 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-385MS | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 358.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 10.09 | 48 | 9.58 | 40.2 | 45.5 | -0.3452 | 0.0476 | -0.2765 | 1.8414 | 38.9226 | 1.8414 | 38.9226 | 7.5601 | 37.583 | [6 empty] | 2019-09-03 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-385P | 385 W, 144 half cut cell polycrystalline module | UL 61730 | 385 | 358.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 1 | N | 10.07 | 48 | 9.5 | 40.6 | 43.5 | -0.3816 | 0.0436 | -0.2938 | 0.0073 | -0.3888 | 1.9313 | 37.9228 | 7.6595 | 37.2324 | [6 empty] | 2019-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-385PB-AG | 385 W, 144 half-cut cell bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 385 | 360.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.97 | 72 | 2 | N | 10.07 | 48 | 9.5 | 40.6 | 44.5 | -0.3402 | 0.0418 | -0.2643 | 1.8979 | 38.9283 | 1.8979 | 38.9283 | 7.5908 | 37.3824 | [6 empty] | 2019-09-03 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-385P | 385 W, 144 half cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 355.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 10.66 | 46.6 | 10.11 | 38.1 | 45.2 | -0.3768 | 0.0221 | -0.2787 | -0.0146 | -0.3643 | 2.0091 | 36.757 | 8.087 | 35.4817 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-385PB-AG | 385 W, 144 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 1703 | 385 | 359.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 10.66 | 46.6 | 10.11 | 38.1 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0122 | 36.894 | 8.042 | 35.562 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS1Y-390MS | 390 W, 468 sixth-cut cell monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 390 | 366.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 78 | 6 | N | 9.82 | 51.9 | 9.05 | 43.1 | 42.9 | -0.3469 | 0.043 | -0.2726 |  |  | 1.7815 | 41.6891 | 7.2774 | 40.3892 | [6 empty] | 2021-01-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3L-390MS | 390 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 390 | 368.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.82 | 41.6 | 11.18 | 34.9 | 43.4 | -0.3242 | 0.0524 | -0.2604 |  |  | 2.2269 | 33.6588 | 8.873 | 32.7635 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS3N-390MS | 390 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 364.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.38 | 44.1 | 10.6 | 36.8 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.1491 | 35.5913 | 8.4839 | 34.6938 | [6 empty] | 2021-04-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-390MB-AG | 390 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 390 | 362.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 72 | 2 | N | 10.17 | 48.2 | 9.66 | 40.4 | 46.3 | -0.3469 | 0.0464 | -0.2694 | 1.8941 | 39.2073 | 1.921 | 39.099 | 7.756 | 37.327 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-390MS | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 363.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 10.17 | 48.2 | 9.66 | 40.4 | 45.5 | -0.3452 | 0.0476 | -0.2765 | 1.8568 | 39.1163 | 1.8568 | 39.1163 | 7.6233 | 37.77 | [6 empty] | 2019-09-03 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-390P | 390 W, 144 half cut cell polycrystalline module | UL 61730 | 390 | 363.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 1 | N | 10.15 | 48.2 | 9.56 | 40.8 | 43.5 | -0.3816 | 0.0436 | -0.2938 | 0.0073 | -0.3888 | 1.9435 | 38.1096 | 7.7079 | 37.4158 | [6 empty] | 2019-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-390P | 390 W, 144 half cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 360.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 10.74 | 46.8 | 10.19 | 38.3 | 45.2 | -0.3768 | 0.0221 | -0.2787 | -0.0146 | -0.3643 | 2.025 | 36.95 | 8.151 | 35.668 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-390PB-AG | 390 W, 144 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 390 | 364 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 10.74 | 46.8 | 10.19 | 38.3 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0281 | 37.0877 | 8.1057 | 35.7486 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS1Y-395MS | 395 W, 468 sixth-cut cell monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 395 | 371.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 78 | 6 | N | 9.86 | 52.1 | 9.13 | 43.3 | 42.9 | -0.3469 | 0.043 | -0.2726 |  |  | 1.7972 | 41.8825 | 7.3417 | 40.5766 | [6 empty] | 2021-01-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-395MS | 395 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 369.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.44 | 44.3 | 10.68 | 37 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.1653 | 35.7847 | 8.5479 | 34.8823 | [6 empty] | 2021-04-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-395MB-AG | 395 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 395 | 366.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 72 | 2 | N | 10.25 | 48.4 | 9.73 | 40.6 | 46.3 | -0.3469 | 0.0464 | -0.2694 |  |  | 1.9349 | 39.2926 | 7.8122 | 37.5118 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-395MS | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 367 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 10.25 | 48.4 | 9.73 | 40.6 | 46.2 | -0.3492 | 0.0371 | -0.2686 | 1.8702 | 39.3099 | 1.985 | 38.958 | 7.825 | 37.611 | [6 empty] | 2019-09-03 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-395P | 395 W, 144 half cut cell polycrystalline module | UL 61730 | 395 | 368.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 | 1 | N | 10.23 | 48.4 | 9.64 | 41 | 43.5 | -0.3816 | 0.0436 | -0.2938 | 0.0073 | -0.3888 | 1.9597 | 38.2964 | 7.7724 | 37.5992 | [6 empty] | 2019-03-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-395P | 395 W, 144 half cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 365.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 10.82 | 47 | 10.26 | 38.5 | 45.2 | -0.3768 | 0.0221 | -0.2787 | -0.0146 | -0.3643 | 2.0389 | 37.143 | 8.207 | 35.8543 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-395PB-AG | 395 W, 144 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 395 | 368.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 10.82 | 47 | 10.26 | 38.5 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0421 | 37.2813 | 8.1614 | 35.9353 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS1Y-400MS | 400 W, 468 sixth-cut cell monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 400 | 376.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 78 | 6 | N | 9.9 | 52.3 | 9.2 | 43.5 | 42.9 | -0.3469 | 0.043 | -0.2726 |  |  | 1.811 | 42.076 | 7.398 | 40.764 | [6 empty] | 2021-01-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-400MS | 400 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 373.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.5 | 44.5 | 10.76 | 37.2 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.1816 | 35.9781 | 8.6119 | 35.0709 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-400MB-AG | 400 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 400 | 371.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 72 | 2 | N | 10.33 | 48.6 | 9.81 | 40.8 | 46.3 | -0.3469 | 0.0464 | -0.2694 |  |  | 1.9508 | 39.4861 | 7.8764 | 37.6966 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-400MS | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 371.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 10.33 | 48.6 | 9.81 | 40.8 | 46.2 | -0.3492 | 0.0371 | -0.2686 |  |  | 2.0013 | 39.1499 | 7.8893 | 37.7963 | [6 empty] | 2019-12-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-400P | 400 W, 144 half cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 369.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 10.9 | 47.2 | 10.34 | 38.7 | 45.2 | -0.3768 | 0.0221 | -0.2787 | -0.0146 | -0.3643 | 2.0548 | 37.3359 | 8.271 | 36.0405 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-400PB-AG | 400 W, 144 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 400 | 373.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 10.9 | 47.2 | 10.34 | 38.7 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.058 | 37.475 | 8.225 | 36.122 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS1Y-405MS | 405 W, 468 sixth-cut cell monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 405 | 381.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 78 | 6 | N | 9.94 | 52.5 | 9.27 | 43.7 | 42.9 | -0.3469 | 0.043 | -0.2726 |  |  | 1.8248 | 42.2695 | 7.4543 | 40.9514 | [6 empty] | 2021-01-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-405MS | 405 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 378.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.56 | 44.7 | 10.83 | 37.4 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.1958 | 36.1716 | 8.668 | 35.2594 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-405MB-AG | 405 W, 144 half-cut cell double glass bifacial monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 405 | 376.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 72 | 2 | N | 10.44 | 49.3 | 9.88 | 41 | 46.3 | -0.3469 | 0.0464 | -0.2694 |  |  | 1.9647 | 39.6797 | 7.9326 | 37.8814 | [6 empty] | 2019-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-405MS | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 376.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 10.44 | 49.3 | 9.88 | 41 | 46.2 | -0.3492 | 0.0371 | -0.2686 |  |  | 2.0156 | 39.3418 | 7.9456 | 37.9816 | [6 empty] | 2019-12-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-405P | 405 W, 144 half cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 374.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 10.98 | 47.4 | 10.42 | 38.9 | 45.2 | -0.3768 | 0.0221 | -0.2787 | -0.0146 | -0.3643 | 2.0707 | 37.5289 | 8.335 | 36.2268 | [6 empty] | 2019-01-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-405PB-AG | 405 W, 144 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 405 | 378.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 10.98 | 47.4 | 10.42 | 38.9 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0739 | 37.6687 | 8.2886 | 36.3087 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS1Y-410MS | 410 W, 468 sixth-cut cell monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 410 | 385.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 78 | 6 | N | 9.98 | 52.7 | 9.37 | 43.8 | 42.9 | -0.3469 | 0.043 | -0.2726 |  |  | 1.8445 | 42.3662 | 7.5347 | 41.0451 | [6 empty] | 2021-01-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-410MS | 410 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 383.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.62 | 44.9 | 10.92 | 37.6 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.21 | 36.37 | 8.74 | 35.45 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS3U-410MS | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 381.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 2 | N | 10.52 | 49.5 | 9.96 | 41.2 | 46.2 | -0.3492 | 0.0371 | -0.2686 |  |  | 2.0319 | 39.5337 | 8.01 | 38.1668 | [6 empty] | 2019-12-02 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-410P | 410 W, 144 half-cut cell polycrystalline module, white backsheet,1000V or 1500V max system Vdc | UL 61730 | 410 | 382.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 11.06 | 47.6 | 10.49 | 39.1 | 44.7 | -0.3516 | 0.0467 | -0.2687 | 2.0603 | 38.0583 | 2.0603 | 38.0583 | 8.3274 | 36.6107 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-410PB-AG | 410 W, 144 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 410 | 383.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 11.06 | 47.6 | 10.49 | 39.1 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.0879 | 37.8623 | 8.3443 | 36.4954 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS1Y-415MS | 415 W, 468 sixth-cut cell monocrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 415 | 390.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 78 | 6 | N | 10.02 | 52.8 | 9.44 | 44 | 42.9 | -0.3469 | 0.043 | -0.2726 |  |  | 1.8582 | 42.5596 | 7.591 | 41.2326 | [6 empty] | 2021-01-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-415MS | 415 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 415 | 388.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.68 | 45.1 | 10.98 | 37.8 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.2262 | 36.5584 | 8.788 | 35.6366 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-415MB-AG | 415 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 384.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.22 | 47.7 | 10.46 | 39.7 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.0839 | 38.4807 | 8.2298 | 37.2029 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-415P | 415 W, 144 half-cut cell polycrystalline module, white backsheet,1000V or 1500V max system Vdc | UL 61730 | 415 | 386.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 11.14 | 47.8 | 10.56 | 39.3 | 44.7 | -0.3516 | 0.0467 | -0.2687 | 2.074 | 38.253 | 2.074 | 38.253 | 8.383 | 36.798 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-415PB-AG | 415 W, 144 half-cut cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 415 | 387.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 11.14 | 47.8 | 10.56 | 39.3 | 44 | -0.3605 | 0.0389 | -0.2703 | 1.85 |  | 2.086 | 38.47 | 8.37 | 37.338 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-420MS | 420 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 393.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.74 | 45.3 | 11.06 | 38 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.2424 | 36.7519 | 8.8521 | 35.8251 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-420MB-AG | 420 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 420 | 389.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.27 | 47.9 | 10.53 | 39.9 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.0978 | 38.6746 | 8.2848 | 37.3903 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-420P | 420 W, 144 half-cut cell polycrystalline module, white backsheet,1000V or 1500V max system Vdc | UL 61730 | 420 | 391.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 11.26 | 48 | 10.64 | 39.5 | 44.7 | -0.3516 | 0.0467 | -0.2687 | 2.0897 | 38.4477 | 2.0897 | 38.4477 | 8.4465 | 36.9853 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-420PB-AG | 420 W, 144 half-cut cell double glass bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 420 | 392.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 11.26 | 48 | 10.64 | 39.5 | 43.6 | -0.3581 | 0.0441 | -0.2706 |  |  | 2.1177 | 38.2497 | 8.4636 | 36.8687 | [6 empty] | 2019-06-17 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-425MS | 425 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 397.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.8 | 45.5 | 11.13 | 38.2 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.2566 | 36.9453 | 8.9081 | 36.0137 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-425MB-AG | 425 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 394.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.32 | 48.1 | 10.6 | 40.1 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.1117 | 38.8684 | 8.3399 | 37.5777 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-425P | 425 W, 144 half-cut cell polycrystalline module, white backsheet,1000V or 1500V max system Vdc | UL 61730 | 425 | 396.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 11.29 | 48.2 | 10.71 | 39.7 | 44.7 | -0.3516 | 0.0467 | -0.2687 | 2.1035 | 38.6423 | 2.1035 | 38.6423 | 8.5021 | 37.1725 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-425PB-AG | 425 W, 144 half-cut cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 425 | 392.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.16 | 72 | 2 | N | 11.29 | 48.2 | 10.71 | 39.7 | 43.1 | -0.4309 | 0.0582 | -0.3235 | 1.866 |  | 2.155 | 38.07 | 8.667 | 35.99 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3N-430MS | 430 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 430 | 402.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 66 | 2 | N | 11.86 | 45.7 | 11.2 | 38.4 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.2667 | 37.1438 | 8.9641 | 36.2043 | [6 empty] | 2021-07-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-430MB-AG | 430 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 399 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.37 | 48.3 | 10.68 | 40.3 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.1277 | 39.0623 | 8.4029 | 37.7652 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-430MS | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 430 | 400 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.37 | 48.3 | 10.68 | 40.3 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.134 | 38.3293 | 8.3763 | 37.3834 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-430P | 430 W, 144 half-cut cell polycrystalline module, white backsheet,1000V or 1500V max system Vdc | UL 61730 | 430 | 401.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 11.32 | 48.4 | 10.78 | 39.9 | 44.7 | -0.3516 | 0.0467 | -0.2687 | 2.1172 | 38.837 | 2.1172 | 38.837 | 8.5576 | 37.3598 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-430PB-AG | 430 W, 144 half-cut cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 430 | 401.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 11.32 | 48.4 | 10.78 | 39.9 | 44 | -0.3605 | 0.0389 | -0.2703 | 1.882 |  | 2.1295 | 39.0573 | 8.5444 | 37.908 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-435MB-AG | 435 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 403.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.42 | 48.5 | 10.75 | 40.5 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.1416 | 39.2561 | 8.4579 | 37.9526 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-435MS | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 435 | 404.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.42 | 48.5 | 10.75 | 40.5 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.148 | 38.5196 | 8.4312 | 37.5689 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-435P | 435 W, 144 half-cut cell polycrystalline module, white backsheet,1000V or 1500V max system Vdc" | UL 61730 | 435 | 402.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 11.35 | 48.6 | 10.85 | 40.1 | 42.9 | -0.4406 | 0.0547 | -0.3272 | 2.131 | 39.0317 | 2.183 | 38.42 | 8.829 | 36.51 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-435PB-AG | 435 W, 144 half-cut cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 435 | 406.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.17 | 72 | 2 | N | 11.35 | 48.6 | 10.85 | 40.1 | 44 | -0.3605 | 0.0389 | -0.2703 | 1.8979 |  | 2.1433 | 39.2531 | 8.5999 | 38.0981 | [6 empty] | 2019-11-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-435PB-AG | 435 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 435 | 407.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.35 | 48.6 | 10.85 | 40.1 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.0993 | 40.3953 | 8.3569 | 38.8468 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-440MB-AG | 440 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 408.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.48 | 48.7 | 10.82 | 40.7 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.157 | 39.45 | 8.513 | 38.14 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-440MS | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 440 | 409.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.48 | 48.7 | 10.82 | 40.7 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.162 | 38.7098 | 8.4861 | 37.7545 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-440P | 440 W, 144 half-cut cell polycrystalline module, white backsheet,1000V or 1500V max system Vdc | UL 61730 | 440 | 406.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 11.4 | 48.7 | 10.92 | 40.3 | 42.9 | -0.4406 | 0.0547 | -0.3272 |  |  | 2.1971 | 38.6116 | 8.886 | 36.6921 | [6 empty] | 2020-09-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-440PB-AG | 440 W, 144 half-cut cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 440 | 407.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.16 | 72 | 2 | N | 11.4 | 48.7 | 10.92 | 40.3 | 43.1 | -0.4309 | 0.0582 | -0.3235 |  |  | 2.1973 | 38.6454 | 8.8369 | 36.5339 | [6 empty] | 2020-12-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-440P | 440 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 409.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.18 | 51.2 | 10.48 | 42 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.0835 | 40.5543 | 8.3946 | 38.8733 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-440PB-AG | 440 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 440 | 412.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.18 | 51.2 | 10.48 | 42 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.1134 | 40.5886 | 8.4131 | 39.0327 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-445MB-AG | 445 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 413.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.54 | 48.9 | 10.89 | 40.9 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.1695 | 39.6439 | 8.5681 | 38.3274 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-445MS | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 445 | 414.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.54 | 48.9 | 10.89 | 40.9 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.176 | 38.9 | 8.541 | 37.94 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-445P | 445 W, 144 half-cut cell polycrystalline module, white backsheet,1000V or 1500V max system Vdc | UL 61730 | 445 | 411.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 11.45 | 48.8 | 10.99 | 40.5 | 42.9 | -0.4406 | 0.0547 | -0.3272 |  |  | 2.2112 | 38.8032 | 8.9429 | 36.8742 | [6 empty] | 2020-09-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-445PB-AG | 445 W, 144 half-cut cell double glass bifacial polycrystalline module, 1000V or 1500V max system Vdc | UL 61730 | 445 | 411.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.16 | 72 | 2 | N | 11.45 | 48.8 | 10.99 | 40.5 | 43.1 | -0.4309 | 0.0582 | -0.3235 |  |  | 2.2113 | 38.8372 | 8.8936 | 36.7152 | [6 empty] | 2020-11-12 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-445P | 445 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 413.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.23 | 51.4 | 10.55 | 42.2 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.0974 | 40.7474 | 8.4507 | 39.0584 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-445PB-AG | 445 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 445 | 416.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.23 | 51.4 | 10.55 | 42.2 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.1276 | 40.7819 | 8.4693 | 39.2185 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-450MB-AG | 450 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 418.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.6 | 49.1 | 10.96 | 41.1 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.1835 | 39.8377 | 8.6231 | 38.5148 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-450MS | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 450 | 419.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.6 | 49.1 | 10.96 | 41.1 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.19 | 39.0902 | 8.5959 | 38.1255 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-450P | 450 W, 144 half-cut cell polycrystalline module, white backsheet,1000V or 1500V max system Vdc | UL 61730 | 450 | 416.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.14 | 72 | 2 | N | 11.53 | 49 | 11.06 | 40.7 | 42.9 | -0.4406 | 0.0547 | -0.3272 |  |  | 2.2253 | 38.9949 | 8.9999 | 37.0563 | [6 empty] | 2020-09-11 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-450P | 450 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 418.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.28 | 51.6 | 10.62 | 42.4 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.1113 | 40.9405 | 8.5067 | 39.2436 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-450PB-AG | 450 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 450 | 421.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.28 | 51.6 | 10.62 | 42.4 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.1417 | 40.9752 | 8.5254 | 39.4044 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-455MB-AG | 455 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 422.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.66 | 49.3 | 11.02 | 41.3 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.1969 | 40.0316 | 8.6704 | 38.7023 | [6 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3W-455MS | 455 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 455 | 429.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.66 | 49.3 | 11.02 | 41.3 | 43.4 | -0.3242 | 0.0524 | -0.2604 | 2.175 | 39.913 | 2.175 | 39.913 | 8.683 | 38.89 | [6 empty] | 2020-11-23 | 2021-09-13
CSI Solar Co., Ltd. | CS3Y-455P | 455 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 423.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.33 | 51.8 | 10.69 | 42.6 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.1252 | 41.1337 | 8.5628 | 39.4287 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-455PB-AG | 455 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 455 | 426.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.33 | 51.8 | 10.69 | 42.6 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.1558 | 41.1684 | 8.5816 | 39.5903 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-460MB-AG | 460 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 427.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.72 | 49.5 | 11.09 | 41.5 | 43.4 | -0.4057 | 0.0574 | -0.3105 |  |  | 2.2108 | 40.2254 | 8.7254 | 38.8897 | [6 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3W-460MS | 460 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 460 | 428.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.72 | 49.5 | 11.09 | 41.5 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.216 | 39.4707 | 8.6979 | 38.4966 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-460P | 460 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 460 | 428.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.38 | 52 | 10.75 | 42.8 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.1372 | 41.3268 | 8.6109 | 39.6138 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-460PB-AG | 460 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 460 | 431.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.38 | 52 | 10.75 | 42.8 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.1679 | 41.3617 | 8.6298 | 39.7761 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-465MS | 465 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 465 | 433.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.78 | 49.7 | 11.16 | 41.7 | 43.3 | -0.3954 | 0.0502 | -0.2975 |  |  | 2.23 | 39.6609 | 8.7528 | 38.6821 | [6 empty] | 2020-11-23 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-465MB-AG | 465 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 465 | 434.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.3 | 78 | 2 | N | 11.42 | 52.3 | 10.67 | 43.6 | 46.3 | -0.323 | 0.06 | -0.254 |  |  | 2.1595 | 42.2387 | 8.5704 | 40.3685 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-465P | 465 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 465 | 433 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.43 | 52.2 | 10.82 | 43 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.1511 | 41.5199 | 8.6669 | 39.7989 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-465PB-AG | 465 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 465 | 436 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.43 | 52.2 | 10.82 | 43 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.182 | 41.555 | 8.686 | 39.962 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3W-470MS | 470 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 61730 | 470 | 443.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.174 | 72 | 2 | N | 11.84 | 49.9 | 11.22 | 41.9 | 43.4 | -0.3242 | 0.0524 | -0.2604 | 2.2145 | 40.4928 | 2.2145 | 40.4928 | 8.8406 | 39.455 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS3Y-470MB-AG | 470 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 470 | 439 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.3 | 78 | 2 | N | 11.47 | 52.5 | 10.74 | 43.8 | 46.3 | -0.323 | 0.06 | -0.254 |  |  | 2.1737 | 42.4325 | 8.6266 | 40.5536 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-470MS | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 470 | 439.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 78 | 2 | N | 11.47 | 52.5 | 10.74 | 43.8 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.1853 | 42.3341 | 8.6097 | 40.3256 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-470P | 470 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 470 | 437.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.48 | 52.4 | 10.88 | 43.2 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.163 | 41.713 | 8.715 | 39.984 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-470PB-AG | 470 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 470 | 440.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.48 | 52.4 | 10.88 | 43.2 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.1941 | 41.7483 | 8.7342 | 40.1479 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-475MB-AG | 475 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 475 | 443.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.3 | 78 | 2 | N | 11.52 | 52.7 | 10.81 | 44 | 46.3 | -0.323 | 0.06 | -0.254 |  |  | 2.1879 | 42.6262 | 8.6828 | 40.7388 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-475MS | 475 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 475 | 444.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 78 | 2 | N | 11.52 | 52.7 | 10.81 | 44 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.1995 | 42.5274 | 8.6658 | 40.5097 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-475P | 475 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 475 | 442.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.53 | 52.6 | 10.95 | 43.4 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.1769 | 41.9061 | 8.7711 | 40.1691 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-475PB-AG | 475 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 475 | 445.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.53 | 52.6 | 10.95 | 43.4 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.2082 | 41.9416 | 8.7904 | 40.3337 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-480MB-AG | 480 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 480 | 448.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.3 | 78 | 2 | N | 11.57 | 52.9 | 10.87 | 44.2 | 46.3 | -0.3228 | 0.0603 | -0.2536 |  |  | 2.2 | 42.821 | 8.731 | 40.924 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-480MS | 480 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 480 | 449 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 78 | 2 | N | 11.57 | 52.9 | 10.87 | 44.2 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.2118 | 42.7207 | 8.7139 | 40.6939 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-480P | 480 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 480 | 447.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.58 | 52.8 | 11.01 | 43.6 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.1888 | 42.0992 | 8.8191 | 40.3542 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-480PB-AG | 480 W, 156 half-cut cell bifacial polycrystalline module, 1500V max system Vdc | UL 61730 | 480 | 450.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.3 | 78 | 2 | N | 11.58 | 52.8 | 11.01 | 43.6 | 44.3 | -0.3356 | 0.0644 | -0.2677 |  |  | 2.2203 | 42.1348 | 8.8385 | 40.5196 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-485MB-AG | 485 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 485 | 453.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.3 | 78 | 2 | N | 11.62 | 53.1 | 10.94 | 44.4 | 46.3 | -0.323 | 0.06 | -0.254 |  |  | 2.2142 | 43.0138 | 8.7872 | 41.1092 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-485MS | 485 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 485 | 453.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 78 | 2 | N | 11.62 | 53.1 | 10.94 | 44.4 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.226 | 42.914 | 8.77 | 40.878 | [6 empty] | 2020-12-01 | 2021-07-01
CSI Solar Co., Ltd. | CS3Y-485P | 485 W, 156 half-cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 485 | 452.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.29 | 78 | 2 | N | 11.63 | 53 | 11.08 | 43.8 | 46.1 | -0.3398 | 0.0683 | -0.2744 |  |  | 2.2028 | 42.2923 | 8.8752 | 40.5393 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-490MB-AG | 490 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 490 | 458.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.3 | 78 | 2 | N | 11.67 | 53.3 | 11 | 44.6 | 46.3 | -0.323 | 0.06 | -0.254 |  |  | 2.2263 | 43.2075 | 8.8354 | 41.2944 | [6 empty] | 2021-01-21 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-490MS | 490 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 490 | 458.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 78 | 2 | N | 11.67 | 53.3 | 11 | 44.6 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.2382 | 43.1073 | 8.8181 | 41.0621 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-495MB-AG | 495 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 495 | 463 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.3 | 78 | 1.1111e+18 | N | 11.72 | 53.5 | 11.06 | 44.8 | 46.3 | -0.3228 | 0.0603 | -0.2536 |  |  | 2.2385 | 43.4023 | 8.8836 | 41.4795 | [6 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-495MS | 495 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 495 | 463.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 78 | 2 | N | 11.72 | 53.5 | 11.06 | 44.8 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.2504 | 43.3006 | 8.8662 | 41.2463 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-500MB-AG | 500 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 500 | 467.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.3 | 78 | 2 | N | 11.77 | 53.7 | 11.12 | 45 | 46.3 | -0.3228 | 0.0603 | -0.2536 |  |  | 2.2506 | 43.596 | 8.9318 | 41.6647 | [6 empty] | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-500MS | 500 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 500 | 468.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 78 | 2 | N | 11.77 | 53.7 | 11.12 | 45 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.2626 | 43.4939 | 8.9143 | 41.4304 | [6 empty] | 2020-12-01 | 2021-07-12
CSI Solar Co., Ltd. | CS3Y-505MS | 505 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 505 | 473 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 78 | 2 | N | 11.82 | 53.9 | 11.18 | 45.2 | 45.5 | -0.332 | 0.0478 | -0.2565 |  |  | 2.2748 | 43.6872 | 8.9624 | 41.6145 | [6 empty] | 2021-07-01 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-520MB-AG | 520 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc. | UL 61730 | 520 | 488.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 72 | 2 | N | 13.7 | 48.4 | 12.84 | 40.5 | 44.5 | -0.3241 | 0.0468 | -0.2573 |  |  | 2.5433 | 39.4397 | 10.1566 | 38.2582 | [6 empty] | 2021-03-11 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-525MB-AG | 525 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc. | UL 61730 | 525 | 493.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 72 | 2 | N | 13.75 | 48.6 | 12.9 | 40.7 | 44.5 | -0.3241 | 0.0468 | -0.2573 |  |  | 2.5552 | 39.6345 | 10.2041 | 38.4471 | [6 empty] | 2021-03-11 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-530MB-AG | 530 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc. | UL 61730 | 530 | 498.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 72 | 2 | N | 13.8 | 48.8 | 12.96 | 40.9 | 44.5 | -0.3241 | 0.0468 | -0.2573 |  |  | 2.5671 | 39.8292 | 10.2515 | 38.6361 | [6 empty] | 2021-03-11 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-530MS | 530 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 530 | 497.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.8 | 48.8 | 12.96 | 40.9 | 45.4 | -0.3201 | 0.0532 | -0.2573 |  |  | 2.5643 | 39.7166 | 10.3095 | 38.144 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-535MB-AG | 535 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc. | UL 61730 | 535 | 503.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 72 | 2 | N | 13.85 | 49 | 13.02 | 41.1 | 44.5 | -0.3241 | 0.0468 | -0.2573 |  |  | 2.579 | 40.024 | 10.299 | 38.825 | [6 empty] | 2021-03-11 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-535MS | 535 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 535 | 502.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.85 | 49 | 13.02 | 41.1 | 45.4 | -0.3201 | 0.0532 | -0.2573 |  |  | 2.5761 | 39.9108 | 10.3573 | 38.3305 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-540MB-AG | 540 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc. | UL 61730 | 540 | 508 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 72 | 2 | N | 13.9 | 49.2 | 13.08 | 41.3 | 44.5 | -0.3241 | 0.0468 | -0.2573 |  |  | 2.5909 | 40.2188 | 10.3465 | 39.0139 | [6 empty] | 2021-03-11 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-540MS | 540 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 540 | 507 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.9 | 49.2 | 13.08 | 41.3 | 45.4 | -0.3201 | 0.0532 | -0.2573 |  |  | 2.588 | 40.105 | 10.405 | 38.517 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-545MB-AG | 545 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc. | UL 61730 | 545 | 512.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 72 | 2 | N | 13.95 | 49.4 | 13.14 | 41.5 | 44.5 | -0.3241 | 0.0468 | -0.2573 |  |  | 2.6028 | 40.4135 | 10.3939 | 39.2029 | [6 empty] | 2021-03-11 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-545MS | 545 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 545 | 511.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.95 | 49.4 | 13.14 | 41.5 | 45.4 | -0.3201 | 0.0532 | -0.2573 |  |  | 2.5999 | 40.2992 | 10.4527 | 38.7035 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-550MB-AG | 550 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc. | UL 61730 | 550 | 517.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 72 | 2 | N | 14 | 49.6 | 13.2 | 41.7 | 44.5 | -0.3241 | 0.0468 | -0.2573 |  |  | 2.6147 | 40.6083 | 10.4414 | 39.3918 | [6 empty] | 2021-03-11 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-550MS | 550 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 550 | 516.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 14 | 49.6 | 13.2 | 41.7 | 45.4 | -0.3201 | 0.0532 | -0.2573 |  |  | 2.6117 | 40.4934 | 10.5005 | 38.89 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS6W-555MS | 555 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 555 | 521.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 14.05 | 49.8 | 13.25 | 41.9 | 45.4 | -0.3201 | 0.0532 | -0.2573 |  |  | 2.6216 | 40.6876 | 10.5402 | 39.0766 | [6 empty] | 2021-02-22 | 2021-07-12
CSI Solar Co., Ltd. | CS7L-570MB-AG | 570 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 570 | 534.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 60 | 2 | N | 18.17 | 40.1 | 16.93 | 33.7 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4148 | 32.7273 | 13.6551 | 30.8507 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7L-575MB-AG | 575 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 575 | 539.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 60 | 2 | N | 18.22 | 40.3 | 16.97 | 33.9 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4228 | 32.9215 | 13.6874 | 31.0338 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7L-580MB-AG | 580 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 580 | 544.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 60 | 2 | N | 18.27 | 40.5 | 17.02 | 34.1 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4329 | 33.1158 | 13.7277 | 31.2169 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7L-585MB-AG | 585 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 585 | 549.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 60 | 2 | N | 18.32 | 40.7 | 17.06 | 34.3 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.441 | 33.31 | 13.76 | 31.4 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7L-590MB-AG | 590 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 590 | 554.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 60 | 2 | N | 18.37 | 40.9 | 17.11 | 34.5 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4511 | 33.5042 | 13.8003 | 31.5831 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7L-595MB-AG | 595 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 595 | 559.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 60 | 2 | N | 18.42 | 41.1 | 17.15 | 34.7 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4592 | 33.6985 | 13.8326 | 31.7662 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7L-600MB-AG | 600 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 600 | 564 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 60 | 2 | N | 18.47 | 41.3 | 17.2 | 34.9 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4692 | 33.8927 | 13.8729 | 31.9493 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7L-605MB-AG | 605 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 605 | 568.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 60 | 2 | N | 18.52 | 41.5 | 17.25 | 35.1 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4793 | 34.0869 | 13.9132 | 32.1324 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7L-610MB-AG | 610 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 610 | 573.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 60 | 2 | N | 18.57 | 41.7 | 17.29 | 35.3 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4874 | 34.2811 | 13.9455 | 32.3155 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7N-630MB-AG | 630 W, 132 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 630 | 586.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.07 | 66 | 2 | N | 18.23 | 44.2 | 16.99 | 37.1 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4218 | 36.0372 | 13.7628 | 34.0395 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7N-635MB-AG | 635 W, 132 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 635 | 590.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.07 | 66 | 2 | N | 18.27 | 44.4 | 17.03 | 37.3 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4299 | 36.2315 | 13.7952 | 34.223 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7N-640MB-AG | 640 W, 132 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 640 | 595.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.07 | 66 | 2 | N | 18.31 | 44.6 | 17.07 | 37.5 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4379 | 36.4257 | 13.8276 | 34.4065 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7N-645MB-AG | 645 W, 132 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 645 | 600.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.07 | 66 | 2 | N | 18.35 | 44.8 | 17.11 | 37.7 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.446 | 36.62 | 13.86 | 34.59 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7N-650MB-AG | 650 W, 132 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 650 | 605.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.07 | 66 | 2 | N | 18.39 | 45 | 17.16 | 37.9 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4561 | 36.8143 | 13.9005 | 34.7735 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7N-655MB-AG | 655 W, 132 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 655 | 610 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.07 | 66 | 2 | N | 18.43 | 45.2 | 17.2 | 38.1 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4641 | 37.0085 | 13.9329 | 34.957 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7N-660MB-AG | 660 W, 132 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 660 | 614.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.07 | 66 | 2 | N | 18.47 | 45.4 | 17.24 | 38.3 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4722 | 37.2028 | 13.9653 | 35.1405 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7N-665MB-AG | 665 W, 132 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 665 | 619.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.07 | 66 | 2 | N | 18.51 | 45.6 | 17.28 | 38.5 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4802 | 37.3971 | 13.9977 | 35.324 | [6 empty] | 2021-09-13
CSI Solar Co., Ltd. | CS7N-670MB-AG | 670 W, 132 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 670 | 624.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 3.07 | 66 | 2 | N | 18.55 | 45.8 | 17.32 | 38.7 | 43.7 | -0.39 | 0.0531 | -0.2925 |  |  | 3.4883 | 37.5914 | 14.0301 | 35.5075 | [6 empty] | 2021-09-13
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860F 320W | 320 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 320 | 297.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.2 | 40.2 | 9.64 | 33.2 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.9153 | 32.3912 | 7.7305 | 31.6124 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860F 325W | 325 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 325 | 302 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.25 | 40.4 | 9.71 | 33.5 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.9292 | 32.6839 | 7.7867 | 31.898 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860W 325W | 325 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 325 | 300.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 2 | N | 10.3 | 40.4 | 9.68 | 33.6 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.8963 | 32.4722 | 7.6385 | 31.8158 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860F 330W | 330 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 330 | 306.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.3 | 40.6 | 9.77 | 33.8 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.9412 | 32.9766 | 7.8348 | 32.1837 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860W 330W | 330 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 330 | 305.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 2 | N | 10.39 | 40.6 | 9.77 | 33.8 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.9139 | 32.6655 | 7.7095 | 32.0052 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860F 335W | 335 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 335 | 311.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.35 | 40.8 | 9.83 | 34.1 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.9531 | 33.2693 | 7.8829 | 32.4693 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860W 335W | 335 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 335 | 310.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 2 | N | 10.48 | 40.7 | 9.86 | 34 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.9316 | 32.8588 | 7.7805 | 32.1946 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860F 340W | 340 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 340 | 316.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.4 | 41 | 9.89 | 34.4 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.965 | 33.562 | 7.931 | 32.755 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860W 340W | 340 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 340 | 314.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 2 | N | 10.55 | 41.1 | 9.95 | 34.2 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.9492 | 33.0521 | 7.8515 | 32.3839 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M860W 345W | 345 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 345 | 319.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 2 | N | 10.56 | 41.2 | 10 | 34.5 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.959 | 33.342 | 7.891 | 32.668 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760B 350W | 350W Monocrystalline module, black backsheet | UL 61730 | 350 | 326.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 40 | 3 | N | 11.15 | 40.1 | 10.42 | 33.6 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.1421 | 32.0519 | 7.3211 | 35.3073 | [6 empty] | 2021-06-21
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760F 350W | 350 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 350 | 323.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.78 | 60 | 2 | N | 11.15 | 40.1 | 10.45 | 33.5 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1056 | 31.7749 | 8.4273 | 30.9448 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760W 350W | 350 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 350 | 322.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.15 | 40.1 | 10.42 | 33.6 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1006 | 32.2472 | 8.4131 | 31.2264 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760B 355W | 355W Monocrystalline module, black backsheet | UL 61730 | 355 | 331.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 40 | 3 | N | 11.25 | 40.3 | 10.51 | 33.8 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.1606 | 32.2426 | 7.3843 | 35.5175 | [6 empty] | 2021-06-21
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760F 355W | 355 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 355 | 328.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.78 | 60 | 2 | N | 11.24 | 40.3 | 10.54 | 33.7 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1237 | 31.9646 | 8.4999 | 31.1295 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760W 355W | 355 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 355 | 327.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.25 | 40.3 | 10.51 | 33.8 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1187 | 32.4391 | 8.4857 | 31.4123 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760B 360W | 360W Monocrystalline module, black backsheet | UL 61730 | 360 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 40 | 3 | N | 11.35 | 40.5 | 10.59 | 34 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.1771 | 32.4334 | 7.4406 | 35.7277 | [6 empty] | 2021-06-21
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760F 360W | 360 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 360 | 333.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.78 | 60 | 2 | N | 11.33 | 40.5 | 10.62 | 33.9 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1399 | 32.1543 | 8.5644 | 31.3143 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760W 360W | 360 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 360 | 332.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.35 | 40.5 | 10.59 | 34 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1349 | 32.6311 | 8.5503 | 31.5981 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760B 365W | 365W Monocrystalline module, black backsheet | UL 61730 | 365 | 340.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 40 | 3 | N | 11.43 | 40.7 | 10.68 | 34.2 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.1956 | 32.6242 | 7.5038 | 35.9378 | [6 empty] | 2021-06-21
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760F 365W | 365 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 337.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.78 | 60 | 2 | N | 11.41 | 40.7 | 10.71 | 34.1 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.158 | 32.344 | 8.637 | 31.499 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760W 365W | 365 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 337 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.43 | 40.7 | 10.68 | 34.2 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.153 | 32.823 | 8.623 | 31.784 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760B 370W | 370W Monocrystalline module, black backsheet | UL 61730 | 370 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 40 | 3 | N | 11.52 | 40.9 | 10.76 | 34.4 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.212 | 32.815 | 7.56 | 36.148 | [6 empty] | 2021-06-21
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760F 370W | 370 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 342.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.78 | 60 | 2 | N | 11.5 | 40.9 | 10.79 | 34.3 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1741 | 32.5337 | 8.7015 | 31.6837 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760W 370W | 370 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 341.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.52 | 40.9 | 10.76 | 34.4 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1691 | 33.0149 | 8.6876 | 31.9699 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760B 375W | 375W Monocrystalline module, black backsheet | UL 61730 | 375 | 350.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 40 | 3 | N | 11.6 | 41.1 | 10.84 | 34.6 | 44.2 | -0.359 | 0.053 | -0.281 |  |  | 2.2284 | 33.0058 | 7.6162 | 36.3582 | [6 empty] | 2021-06-21
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760F 375W | 375 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 347.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.78 | 60 | 2 | N | 11.59 | 41.1 | 10.87 | 34.5 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1902 | 32.7234 | 8.766 | 31.8685 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M760W 375W | 375 W, 120 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 346.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.6 | 41.1 | 10.84 | 34.6 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1853 | 33.2069 | 8.7522 | 32.1557 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872F 390W | 390 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 362.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.25 | 48.5 | 9.71 | 40.2 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.9242 | 38.7841 | 7.7254 | 37.9447 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872F 395W | 395 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 367.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.29 | 48.7 | 9.76 | 40.5 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.9341 | 39.0736 | 7.7622 | 38.2278 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872W 395W | 395 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 365.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 2 | N | 10.37 | 48.7 | 9.86 | 40.1 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.9123 | 39.1758 | 7.6767 | 38.2861 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872F 400W | 400 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 371.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.33 | 48.9 | 9.81 | 40.8 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.944 | 39.363 | 7.805 | 38.511 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872W 400W | 400 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 370.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 2 | N | 10.45 | 49 | 9.93 | 40.3 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.9259 | 39.3712 | 7.7312 | 38.4771 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872F 405W | 405 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 376.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.37 | 49.1 | 9.86 | 41.1 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.9539 | 39.6524 | 7.8448 | 38.7942 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872W 405W | 405 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 375 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 2 | N | 10.52 | 49.2 | 10 | 40.5 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.9395 | 39.5666 | 7.7857 | 38.668 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872F 410W | 410 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 381.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.41 | 49.3 | 9.91 | 41.4 | 45.4 | -0.3609 | 0.0426 | -0.2609 |  |  | 1.9638 | 39.9419 | 7.8846 | 39.0773 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872W 410W | 410 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 379.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 2 | N | 10.59 | 49.4 | 10.08 | 40.7 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.955 | 39.762 | 7.848 | 38.859 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872W 415W | 415 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 384.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 2 | N | 10.66 | 49.6 | 10.15 | 40.9 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.9686 | 39.9574 | 7.9025 | 39.05 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M872W 420W | 420 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 420 | 389.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 2 | N | 10.76 | 49.7 | 10.25 | 41 | 46.5 | -0.3649 | 0.0417 | -0.2632 |  |  | 1.988 | 40.0551 | 7.9804 | 39.1454 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772F 425W | 425 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 393.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.22 | 48.7 | 10.52 | 40.4 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1216 | 38.92 | 8.4532 | 37.7572 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772W 425W | 425 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 392.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.23 | 48.3 | 10.5 | 40.5 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1156 | 38.9956 | 8.4411 | 37.7756 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772F 430W | 430 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 397.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.3 | 48.9 | 10.6 | 40.6 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1378 | 39.1127 | 8.5175 | 37.9442 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772W 430W | 430 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 397 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.19 | 49.2 | 10.6 | 40.6 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1358 | 39.0919 | 8.5215 | 37.8689 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772F 435W | 435 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 402.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.36 | 49.1 | 10.67 | 40.8 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1519 | 39.3053 | 8.5738 | 38.1311 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772W 435W | 435 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 401.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.26 | 49.4 | 10.67 | 40.8 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1499 | 39.2844 | 8.5777 | 38.0555 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772F 440W | 440 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 407.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.45 | 49.3 | 10.74 | 41 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.166 | 39.498 | 8.63 | 38.318 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772W 440W | 440 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 406.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.33 | 49.6 | 10.74 | 41 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.164 | 39.477 | 8.634 | 38.242 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772F 445W | 445 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 412.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.52 | 49.5 | 10.81 | 41.2 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1801 | 39.6907 | 8.6862 | 38.5049 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772W 445W | 445 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 411.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.4 | 49.8 | 10.81 | 41.2 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1781 | 39.6696 | 8.6903 | 38.4285 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772F 450W | 450 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 416.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.58 | 49.6 | 10.87 | 41.4 | 45.4 | -0.3807 | 0.0617 | -0.3125 |  |  | 2.1922 | 39.8833 | 8.7345 | 38.6918 | [6 empty] | 2021-05-03
Dehui Solar Power (Vietnam) Co.,Ltd | DH-M772W 450W | 450 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 416.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.47 | 50 | 10.88 | 41.4 | 46 | -0.3798 | 0.0554 | -0.2786 |  |  | 2.1922 | 39.8621 | 8.7465 | 38.6151 | [6 empty] | 2021-05-03
DEHUI SOLAR POWER INC. | DH-60M-270W | 270 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 270 | 246 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.1 | 38.57 | 8.62 | 31.4 | 46.34 | -0.4074 | 0.0466 | -0.3222 |  |  | 1.7297 | 30.0947 | 6.8856 | 28.1605 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-60M-275W | 275 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 275 | 250.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.28 | 38.58 | 8.71 | 31.63 | 46.34 | -0.4074 | 0.0466 | -0.3222 |  |  | 1.7478 | 30.3152 | 6.9574 | 28.3668 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-60M-280W | 280 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 280 | 255.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.46 | 38.7 | 8.84 | 31.7 | 46.34 | -0.4074 | 0.0466 | -0.3222 |  |  | 1.7738 | 30.3823 | 7.0613 | 28.4295 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-60M-285W | 285 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 285 | 260.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.52 | 38.7 | 8.86 | 32.2 | 46.34 | -0.4074 | 0.0466 | -0.3222 |  |  | 1.7779 | 30.8615 | 7.0773 | 28.878 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-60M-290W | 290 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 290 | 264.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.58 | 39.3 | 9.01 | 32.2 | 46.34 | -0.4074 | 0.0466 | -0.3222 |  |  | 1.808 | 30.8615 | 7.1971 | 28.878 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-60M-295W | 295 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 295 | 269.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.61 | 39.6 | 9.08 | 32.5 | 46.34 | -0.4074 | 0.0466 | -0.3222 |  |  | 1.822 | 31.149 | 7.253 | 29.147 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-60M-300W | 300 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 300 | 274.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.7 | 39.9 | 9.15 | 32.8 | 46.34 | -0.4074 | 0.0466 | -0.3222 |  |  | 1.836 | 31.4365 | 7.3089 | 29.416 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72P-300W | 300 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 300 | 271.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.79 | 45.3 | 8.22 | 36.5 | 46.8 | -0.42 | 0.0526 | -0.3527 |  |  | 1.6355 | 35.1974 | 6.6512 | 32.8037 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-60M-305W | 305 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 305 | 278.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.77 | 40.3 | 9.19 | 33.2 | 46.34 | -0.4074 | 0.0466 | -0.3222 |  |  | 1.8441 | 31.8199 | 7.3409 | 29.7748 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72P-305W | 305 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 305 | 276.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.96 | 45.07 | 8.43 | 36.19 | 46.8 | -0.42 | 0.0526 | -0.3527 |  |  | 1.6773 | 34.8985 | 6.8212 | 32.525 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-60M-310W | 310 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 310 | 283.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.83 | 40.7 | 9.26 | 33.5 | 46.34 | -0.4074 | 0.0466 | -0.3222 |  |  | 1.8581 | 32.1074 | 7.3968 | 30.0438 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72P-310W | 310 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 310 | 280.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.99 | 45.6 | 8.49 | 36.52 | 46.8 | -0.42 | 0.0526 | -0.3527 |  |  | 1.6893 | 35.2167 | 6.8697 | 32.8216 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72P-315W | 315 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 315 | 285.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.03 | 46.1 | 8.56 | 36.8 | 46.8 | -0.42 | 0.0526 | -0.3527 |  |  | 1.7032 | 35.4867 | 6.9264 | 33.0733 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72P-320W | 320 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 320 | 290 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.07 | 46.6 | 8.63 | 37.1 | 46.8 | -0.42 | 0.0526 | -0.3527 |  |  | 1.7171 | 35.776 | 6.983 | 33.3429 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72P-325W | 325 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 325 | 294.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.12 | 47.1 | 8.69 | 37.4 | 46.8 | -0.42 | 0.0526 | -0.3527 |  |  | 1.7291 | 36.0653 | 7.0315 | 33.6125 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72P-330W | 330 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 330 | 299.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.18 | 47.5 | 8.74 | 37.8 | 46.8 | -0.42 | 0.0526 | -0.3527 |  |  | 1.739 | 36.451 | 7.072 | 33.972 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72M-335W | 335 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 335 | 305.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.25 | 46.7 | 8.89 | 37.7 | 46.34 | -0.407 | 0.0466 | -0.32222 |  |  | 1.7847 | 36.6108 | 7.2624 | 33.3555 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72P-335W | 335 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 335 | 304 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.26 | 47.8 | 8.77 | 38.2 | 46.8 | -0.42 | 0.0526 | -0.3527 |  |  | 1.745 | 36.8367 | 7.0963 | 34.3315 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72M-340W | 340 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 340 | 310.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.29 | 47.3 | 8.91 | 38.2 | 46.34 | -0.407 | 0.0466 | -0.32222 |  |  | 1.7887 | 37.0963 | 7.2787 | 33.7979 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72P-340W | 340 W, 72 cell polycrystalline module, 1000V max system Vdc | UL 1703 | 340 | 308.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.31 | 48.1 | 8.84 | 38.5 | 46.8 | -0.42 | 0.0526 | -0.3527 |  |  | 1.7589 | 37.126 | 7.1529 | 34.6011 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72M-345W | 345 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 345 | 315 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.31 | 47.8 | 9.03 | 38.22 | 46.34 | -0.407 | 0.0466 | -0.32222 |  |  | 1.8128 | 37.1158 | 7.3768 | 33.8156 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72M-350W | 350 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 350 | 319.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.34 | 48.3 | 9.1 | 38.5 | 46.34 | -0.407 | 0.0466 | -0.32222 |  |  | 1.8268 | 37.3877 | 7.4339 | 34.0633 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72M-355W | 355 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 355 | 324.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.4 | 48.7 | 9.15 | 38.8 | 46.34 | -0.407 | 0.0466 | -0.32222 |  |  | 1.8369 | 37.679 | 7.4748 | 34.3287 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72M-360W | 360 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 360 | 329.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.45 | 49.1 | 9.21 | 39.1 | 46.34 | -0.407 | 0.0466 | -0.32222 |  |  | 1.8489 | 37.9703 | 7.5238 | 34.5941 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72M-365W | 365 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 365 | 333.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.52 | 49.4 | 9.27 | 39.4 | 46.34 | -0.407 | 0.0466 | -0.32222 |  |  | 1.8609 | 38.2617 | 7.5728 | 34.8596 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72M-370W | 370 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 370 | 338.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.6 | 49.7 | 9.34 | 39.7 | 46.34 | -0.407 | 0.0466 | -0.32222 |  |  | 1.875 | 38.553 | 7.63 | 35.125 | [6 empty] | 2020-01-21
DEHUI SOLAR POWER INC. | DH-72M-375W | 375 W, 72 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 375 | 343.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.65 | 50.1 | 9.38 | 40 | 46.34 | -0.407 | 0.0466 | -0.32222 |  |  | 1.883 | 38.8443 | 7.6627 | 35.3904 | [6 empty] | 2020-01-21
Du Pont Apollo | DA095-A2 | 95 W a-Si Thin Film Module | UL 1703 | 95 | 86.3 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.62 | 100 | 1.3 | 73 | 46.7 | -0.3514 | 0.0809 | -0.3283 | 0.0954 | -0.4311 | 0.26 | 69.7236 | 1.04 | 68.7281 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.19082
Du Pont Apollo | DA095-A6 | 95 W a-Si Thin Film Module | UL 1703 | 95 | 89.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.62 | 100 | 1.3 | 73 | 46.1 | -0.22912 | 0.077952 | -0.31615 | 0.13283 | -0.34989 | 0.24165 | 71.6858 | 1.0611 | 67.5353 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.18235
Du Pont Apollo | DA100-A2 | 100 W a-Si Thin Film Module | UL 1703 | 100 | 90.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.66 | 100 | 1.34 | 75 | 46.7 | -0.3514 | 0.0809 | -0.3283 | 0.0954 | -0.4311 | 0.268 | 71.6338 | 1.072 | 70.611 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.19198
Du Pont Apollo | DA100-A6 | 100 W a-Si Thin Film Module | UL 1703 | 100 | 94.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.66 | 100 | 1.34 | 75 | 46.1 | -0.22912 | 0.077952 | -0.31615 | 0.13283 | -0.34989 | 0.24908 | 73.6498 | 1.0937 | 69.3856 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.18345
Du Pont Apollo | DA102-A6 | 102W a-Si Thin Film Module | UL 1703 | 102 | 96.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.66 | 100 | 1.4 | 75 | 46.1 | -0.22912 | 0.077952 | -0.31615 | 0.13283 | -0.34989 | 0.26024 | 73.6498 | 1.1427 | 69.3856 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.18791
Du Pont Apollo | DA105-A2 | 105 W a-Si Thin Film Module | UL 1703 | 105 | 95.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.66 | 100 | 1.4 | 75 | 46.7 | -0.3514 | 0.0809 | -0.3283 | 0.0954 | -0.4311 | 0.28 | 71.6338 | 1.12 | 70.611 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.19102
Du Pont Apollo | DA105-A6 | 105 W a-Si Thin Film Module | UL 1703 | 105 | 98.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.66 | 100 | 1.4 | 75 | 46.1 | -0.22912 | 0.077952 | -0.31615 | 0.13283 | -0.34989 | 0.26024 | 73.6498 | 1.1427 | 69.3856 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.18254
Du Pont Apollo | DA130-C2 | 130 W Tandem Junction Thin Film Module | UL 1703 | 130 | 119.6 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.28 | 154.96 | 1.08 | 120.75 | 46.8 | -0.316 | -0.055 | -0.31 | 0.01 | -0.322 | 0.2025 | 113.4536 | 0.83893 | 110.8221 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.17673
Du Pont Apollo | DA133-C2 | 133W Tandem Junction Thin Film Module | UL 1703 | 133 | 122.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.29 | 156.73 | 1.09 | 122.13 | 46.8 | -0.316 | -0.055 | -0.31 | 0.01 | -0.322 | 0.20438 | 114.7502 | 0.8467 | 112.0886 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.17633
Du Pont Apollo | DA136-C2 | 136W Tandem Junction Thin Film Module | UL 1703 | 136 | 125.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.54 | 119 | 1 | N | 1.31 | 158.49 | 1.1 | 123.5 | 46.8 | -0.316 | -0.055 | -0.31 | 0.01 | -0.322 | 0.20625 | 116.0374 | 0.85446 | 113.346 | Rack | Flat Plate | 1.1 | 1.4 | 1 | 0.17598
DualSun SAS | DualSun 280M-60-00 | 280 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 280 | 254.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.34 | 39.3 | 8.75 | 32 | 48.2 | -0.391 | 0.036 | -0.284 |  |  | 1.76 | 31.14 | 7.01 | 29.18 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 285M-60-00 | 285 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 285 | 258.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.46 | 39.5 | 8.88 | 32.1 | 48.2 | -0.391 | 0.036 | -0.284 |  |  | 1.78 | 31.24 | 7.11 | 29.28 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 290M-60-00 | 290 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 290 | 263.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.58 | 39.7 | 8.98 | 32.3 | 48.2 | -0.391 | 0.036 | -0.284 |  |  | 1.8 | 31.43 | 7.19 | 29.46 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 295M-60-00 | 295 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 295 | 268.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.69 | 39.9 | 9.05 | 32.6 | 48.2 | -0.391 | 0.036 | -0.284 |  |  | 1.82 | 31.73 | 7.25 | 29.73 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 300M-60-00 | 300 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 300 | 272.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.81 | 40.1 | 9.15 | 32.8 | 48.2 | -0.391 | 0.036 | -0.284 |  |  | 1.84 | 31.92 | 7.33 | 29.91 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 305M-60-00 | 305 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 305 | 278.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.94 | 40.2 | 9.24 | 33 | 48.75 | -0.368 | 0.042 | -0.279 |  |  | 1.798 | 32.024 | 7.198 | 30.246 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 310M-60-00 | 310 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 310 | 283.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.98 | 40.3 | 9.35 | 33.2 | 48.75 | -0.368 | 0.042 | -0.279 |  |  | 1.8194 | 32.2181 | 7.2837 | 30.4293 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 315M-60-00 | 315 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 315 | 288 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 10.1 | 40.5 | 9.43 | 33.4 | 48.75 | -0.368 | 0.042 | -0.279 |  |  | 1.835 | 32.4122 | 7.346 | 30.6126 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 320M-60-00 | 320 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 320 | 292.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 10.19 | 40.8 | 9.52 | 33.6 | 48.75 | -0.368 | 0.042 | -0.279 |  |  | 1.8525 | 32.6063 | 7.4161 | 30.7959 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 335M-120-00 | 335 W, 120 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 335 | 312 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 10.76 | 39.9 | 10.25 | 32.7 | 45.55 | -0.337 | 0.044 | -0.269 |  |  | 1.9506 | 31.9792 | 7.9184 | 30.9481 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 340M-120-00 | 340 W, 120 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 340 | 316.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 10.84 | 40.1 | 10.34 | 32.9 | 45.55 | -0.337 | 0.044 | -0.269 |  |  | 1.9677 | 32.1748 | 7.9879 | 31.1374 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 345M-120-00 | 345 W, 120 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 345 | 321.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 10.93 | 40.3 | 10.43 | 33.1 | 45.55 | -0.337 | 0.044 | -0.269 |  |  | 1.9849 | 32.3704 | 8.0575 | 31.3267 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 350M-120-00 | 350 W, 120 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 350 | 326.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.02 | 40.5 | 10.52 | 33.3 | 45.55 | -0.337 | 0.044 | -0.269 |  |  | 2.002 | 32.566 | 8.127 | 31.516 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 350M-120-01 | 350 W, 120 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 326 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.02 | 40.5 | 10.52 | 33.3 | 45.71 | -0.339 | 0.044 | -0.268 |  |  | 2.0568 | 32.2486 | 8.3648 | 31.1656 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 355M-120-00 | 355 W, 120 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 355 | 331.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.1 | 40.7 | 10.6 | 33.5 | 45.55 | -0.337 | 0.044 | -0.269 |  |  | 2.0172 | 32.7616 | 8.1888 | 31.7053 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 355M-120-01 | 355 W, 120 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 330.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.1 | 40.7 | 10.6 | 33.5 | 45.71 | -0.339 | 0.044 | -0.268 |  |  | 2.0724 | 32.4423 | 8.4284 | 31.3528 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 360M-120-00 | 360 W, 120 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.2 | 40.9 | 10.69 | 33.7 | 45.55 | -0.337 | 0.044 | -0.269 |  |  | 2.0344 | 32.9572 | 8.2583 | 31.8946 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 360M-120-01 | 360 W, 120 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 335.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.2 | 40.9 | 10.69 | 33.7 | 45.71 | -0.339 | 0.044 | -0.268 |  |  | 2.09 | 32.636 | 8.5 | 31.54 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 365M-120-00 | 365 W, 120 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 340.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.28 | 41.1 | 10.77 | 33.9 | 45.55 | -0.337 | 0.044 | -0.269 |  |  | 2.0496 | 33.1528 | 8.3201 | 32.0839 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 365M-120-01 | 365 W, 120 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 340.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.28 | 41.1 | 10.77 | 33.9 | 45.71 | -0.339 | 0.044 | -0.268 |  |  | 2.1056 | 32.8297 | 8.5636 | 31.7272 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 370M-120-01 | 370 W, 120 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 345.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.37 | 41.3 | 10.86 | 34.1 | 45.71 | -0.339 | 0.044 | -0.268 |  |  | 2.1232 | 33.0234 | 8.6352 | 31.9144 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 420M-144-01 | 420 W, 144 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 394.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.04 | 48.8 | 10.45 | 40.2 | 43.92 | -0.334 | 0.049 | -0.268 |  |  | 2.0604 | 38.8801 | 8.3748 | 37.7682 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 425M-144-01 | 425 W, 144 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 398.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.11 | 49 | 10.52 | 40.4 | 43.92 | -0.334 | 0.049 | -0.268 |  |  | 2.0742 | 39.0736 | 8.4309 | 37.9561 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 430M-144-01 | 430 W, 144 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 403.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.19 | 49.2 | 10.6 | 40.6 | 43.92 | -0.334 | 0.049 | -0.268 |  |  | 2.09 | 39.267 | 8.495 | 38.144 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 435M-144-01 | 435 W, 144 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 408.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.26 | 49.4 | 10.67 | 40.8 | 43.92 | -0.334 | 0.049 | -0.268 |  |  | 2.1038 | 39.4604 | 8.5511 | 38.3319 | [6 empty] | 2020-05-01
DualSun SAS | DualSun 440M-144-01 | 440 W, 144 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 413.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | N | 11.33 | 49.6 | 10.74 | 41 | 43.92 | -0.334 | 0.049 | -0.268 |  |  | 2.1176 | 39.6539 | 8.6072 | 38.5198 | [6 empty] | 2020-05-01
DuCal Solar Technology LLC | DST265M-60 | 265 W, 60 cell Monocrystalline Module, white backsheet | UL 1703 | 265 | 238.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.05 | 38.26 | 8.52 | 31.11 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.5432 | 30.4901 | 6.6044 | 27.901 | [6 empty] | 2018-05-01
DuCal Solar Technology LLC | DST270M-60 | 270 W, 60 cell Monocrystalline Module, white backsheet | UL 1703 | 270 | 242.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.17 | 38.46 | 8.62 | 31.33 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.5613 | 30.7057 | 6.6819 | 28.0983 | [6 empty] | 2018-05-01
DuCal Solar Technology LLC | DST275M-60 | 275 W, 60 cell Monocrystalline Module, white backsheet | UL 1703 | 275 | 247.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.25 | 38.86 | 8.73 | 31.51 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.5812 | 30.8822 | 6.7672 | 28.2598 | [6 empty] | 2018-05-01
DuCal Solar Technology LLC | DST280M-60 | 280 W, 60 cell Monocrystalline Module, white backsheet | UL 1703 | 280 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.37 | 39.05 | 8.84 | 31.68 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.6012 | 31.0488 | 6.8525 | 28.4122 | [6 empty] | 2018-05-01
DuCal Solar Technology LLC | DST285M-60 | 285 W, 60 cell Monocrystalline Module, white backsheet | UL 1703 | 285 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.49 | 39.25 | 8.95 | 31.85 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.6211 | 31.2154 | 6.9377 | 28.5647 | [6 empty] | 2018-05-01
DuCal Solar Technology LLC | DST290M-60 | 290 W, 60 cell Monocrystalline Module, white backsheet | UL 1703 | 290 | 261.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.56 | 39.46 | 9.06 | 32.07 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.641 | 31.431 | 7.023 | 28.762 | [6 empty] | 2018-05-01
DuCal Solar Technology LLC | DST295M-60 | 295 W, 60 cell Monocrystalline Module, white backsheet | UL 1703 | 295 | 266 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.72 | 39.64 | 9.14 | 32.29 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.6555 | 31.6466 | 7.085 | 28.9593 | [6 empty] | 2018-05-01
DuCal Solar Technology LLC | DST300M-60 | 300 W, 60 cell Monocrystalline Module, white backsheet | UL 1703 | 300 | 270.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.84 | 39.82 | 9.23 | 32.51 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.6718 | 31.8622 | 7.1548 | 29.1566 | [6 empty] | 2018-05-01
DuCal Solar Technology LLC | DST305M-60 | 305 W, 60 cell Monocrystalline Module, white backsheet | UL 1703 | 305 | 275.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6268 | 60 |  | N | 9.96 | 40 | 9.32 | 32.73 | 46.6 | -0.4567 | 0.0634 | -0.3541 | 0.0288 | -0.4812 | 1.6881 | 32.0778 | 7.2245 | 29.3539 | [6 empty] | 2018-05-01
EMMVEE Photovoltaic Power Private Ltd. | E375M72 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 344.8 |  | 2020-06-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.993 | 72 | 1 | N | 9.88 | 48.5 | 9.37 | 40 | 46.95 | -0.3716 | 0.0525 | -0.2735 |  |  | 1.81 | 39.54 | 7.49 | 36.53 | [6 empty] | 2021-08-02
EMMVEE Photovoltaic Power Private Ltd. | E380M72 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 349.6 |  | 2020-06-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.993 | 72 | 1 | N | 9.96 | 48.7 | 9.45 | 40.2 | 46.95 | -0.3716 | 0.0525 | -0.2735 |  |  | 1.82 | 39.73 | 7.55 | 36.71 | [6 empty] | 2021-08-02
EMMVEE Photovoltaic Power Private Ltd. | E385M72 | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 354.3 |  | 2020-06-30 | 2020-05-28 | Monocrystalline | Mono-c-Si | 1.993 | 72 | 1 | N | 10.06 | 48.9 | 9.55 | 40.32 | 46.95 | -0.3716 | 0.0525 | -0.2735 |  |  | 1.84 | 39.85 | 7.63 | 36.82 | [6 empty] | 2021-08-02
EMMVEE Photovoltaic Power Private Ltd. | E390M72 | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 359 |  | 2020-06-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.993 | 72 | 1 | N | 10.12 | 49 | 9.66 | 40.37 | 46.95 | -0.3716 | 0.0525 | -0.2735 |  |  | 1.86 | 39.9 | 7.72 | 36.87 | [6 empty] | 2021-08-02
EMMVEE Photovoltaic Power Private Ltd. | E395M72 | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 363.8 |  | 2020-06-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.993 | 72 | 1 | N | 10.21 | 49.1 | 9.75 | 40.45 | 46.95 | -0.3716 | 0.0525 | -0.2735 |  |  | 1.88 | 39.98 | 7.79 | 36.94 | [6 empty] | 2021-08-02
Enp Sonne Solar Technikk | ENP-M165MO | 165 W Monocrystalline Module | UL 1703 | 165 | 147.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.279 | 72 | 1 | N | 5.08 | 43.6 | 4.66 | 35.4 | 44.4 | -0.50873 | 0.047152 | -0.37924 | -0.0040233 | -0.50164 | 0.93403 | 34.6291 | 3.797 | 31.7058 | Rack | Flat Plate | 0.809 | 1.581 | 1 | 0.19603
Enp Sonne Solar Technikk | ENP-M170MO | 170 W Monocrystalline Module | UL 1703 | 170 | 151.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.279 | 72 | 1 | N | 5.15 | 44.2 | 4.78 | 35 | 44.4 | -0.50873 | 0.047152 | -0.37924 | -0.0040233 | -0.50164 | 0.95808 | 34.2378 | 3.8948 | 31.3476 | Rack | Flat Plate | 0.809 | 1.581 | 1 | 0.19296
Enphase Energy Inc. | XACM-IQ7-LR6-60PB-300M | 240 W 60 Cell Monocrystalline ACPV Module, Black Backsheet. DC module: LR6-60PB-300M. Microinverter: IQ7-60-ACM-US | UL 1741 | 300 | 273.2 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 | 1 | N | 9.81 | 40.1 | 9.15 | 32.8 | 48.2 | -0.391 | 0.036 | -0.284 |  |  | 1.84 | 31.92 | 7.33 | 29.91 | [6 empty] | 2020-03-11 | 2021-06-21
Enphase Energy Inc. | XACM-IQ7-LR6-60PB-305M | 240 W 60 Cell Monocrystalline ACPV Module, Black Backsheet. DC module: LR6-60PB-305M. Microinverter: IQ7-60-ACM-US | UL 1741 | 305 | 278.9 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 | 1 | N | 9.94 | 40.2 | 9.24 | 33 | 48.75 | -0.368 | 0.042 | -0.279 |  |  | 1.798 | 32.024 | 7.198 | 30.246 | [6 empty] | 2020-03-11 | 2021-06-21
Eoplly New Energy Technology | EP125M/72-205W | 205 W Monocrystalline Module | UL 1741 | 205 | 182.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.92 | 46.21 | 5.52 | 37.47 | 46.8 | -0.49 | 0.06 | -0.36 | 0.01 | -0.5 | 1.0998 | 37.409 | 4.4516 | 33.6959 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.2007
Eoplly New Energy Technology | EP156P/60-225S AC | 225 W DC, Polycrystalline ACPV Module | UL 1741 | 225 | 200.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.48 | 36.13 | 7.65 | 29.62 | 46 | -0.48 | 0.06 | -0.35 | 0.001 | -0.48 | 1.5248 | 28.6505 | 6.0714 | 27.1707 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19416
Eoplly New Energy Technology | EP156M/60-230S AC | 230 W DC, Monocrystalline ACPV Module | UL 1741 | 230 | 205.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.48 | 36.55 | 7.87 | 29.24 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.594 | 28.1784 | 6.2219 | 26.9467 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19529
Eoplly New Energy Technology | EP156MB/60-230S AC | 230 W DC, Monocrystalline ACPV Module, Black Backsheet | UL 1741 | 230 | 205.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.48 | 36.55 | 7.87 | 29.24 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.594 | 28.1784 | 6.2219 | 26.9467 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19529
Eoplly New Energy Technology | EP156P/60-230S AC | 230 W DC, Polycrystalline ACPV Module | UL 1741 | 230 | 205.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.56 | 36.42 | 7.71 | 30.05 | 46 | -0.48 | 0.06 | -0.35 | 0.001 | -0.48 | 1.5354 | 29.0596 | 6.1134 | 27.5587 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19399
Eoplly New Energy Technology | EP156M/60-235S AC | 235 W DC, Monocrystalline ACPV Module | UL 1741 | 235 | 210.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.56 | 36.72 | 7.94 | 29.6 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.6078 | 28.5225 | 6.2758 | 27.2758 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19515
Eoplly New Energy Technology | EP156MB/60-235S AC | 235 W DC, Monocrystalline ACPV Module, Black Backsheet | UL 1741 | 235 | 210.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.56 | 36.72 | 7.94 | 29.6 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.6078 | 28.5225 | 6.2758 | 27.2758 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19515
Eoplly New Energy Technology | EP156P/60-235S AC | 235 W DC, Polycrystalline ACPV Module | UL 1741 | 235 | 209.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.64 | 36.72 | 7.79 | 30.29 | 46 | -0.48 | 0.06 | -0.35 | 0.001 | -0.48 | 1.5527 | 29.2975 | 6.1825 | 27.7843 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19358
Eoplly New Energy Technology | EP156M/60-240S AC | 240 W DC, Monocrystalline ACPV Module | UL 1741 | 240 | 215.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.68 | 36.9 | 8.01 | 30.01 | 46.2 | -0.46 | 0.05 | -0.34 | -0.01 | -0.46 | 1.641 | 28.5299 | 6.4609 | 26.99 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19508
Eoplly New Energy Technology | EP156MB/60-240 AC | 240 W DC, Monocrystalline ACPV Module | UL 1741 | 240 | 214.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.68 | 36.9 | 8.01 | 30.01 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.6218 | 28.9205 | 6.3305 | 27.6564 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19543
Eoplly New Energy Technology | EP156MB/60-240S AC | 240 W DC, Monocrystalline ACPV Module, Black Backsheet | UL 1741 | 240 | 214.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.68 | 36.9 | 8.01 | 30.01 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.6218 | 28.9205 | 6.3305 | 27.6564 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19543
Eoplly New Energy Technology | EP156P/60-240 AC | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 214.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.68 | 37.02 | 7.9 | 30.54 | 46 | -0.48 | 0.06 | -0.35 | 0.001 | -0.48 | 1.5742 | 29.5364 | 6.2682 | 28.0109 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19374
Eoplly New Energy Technology | EP156P/60-240S AC | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 214.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.68 | 37.02 | 7.9 | 30.54 | 46 | -0.48 | 0.06 | -0.35 | 0.001 | -0.48 | 1.5742 | 29.5364 | 6.2682 | 28.0109 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19374
Eoplly New Energy Technology | EP156P/60-240W | 240 W Polycrystalline Module | UL 1741 | 240 | 214.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.68 | 37.02 | 7.9 | 30.54 | 46 | -0.48 | 0.06 | -0.35 | 0.001 | -0.48 | 1.5742 | 29.5364 | 6.2682 | 28.0109 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19374
Eoplly New Energy Technology | EP156M/60-245S AC | 245 W DC, Monocrystalline ACPV Module | UL 1741 | 245 | 219.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.78 | 37.08 | 8.08 | 30.42 | 46.2 | -0.46 | 0.05 | -0.34 | -0.01 | -0.46 | 1.6552 | 28.9196 | 6.5165 | 27.3587 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19537
Eoplly New Energy Technology | EP156MB/60-245 AC | 245 W DC, Monocrystalline ACPV Module | UL 1741 | 245 | 219.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.78 | 37.08 | 8.08 | 30.42 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.6358 | 29.3156 | 6.385 | 28.0342 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19573
Eoplly New Energy Technology | EP156MB/60-245S AC | 245 W DC, Monocrystalline ACPV Module, Black Backsheet | UL 1741 | 245 | 219.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.78 | 37.08 | 8.08 | 30.42 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.6358 | 29.3156 | 6.385 | 28.0342 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19573
Eoplly New Energy Technology | EP156MB/60-245W | 245 W Monocrystalline Module | UL 1741 | 245 | 219.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.78 | 37.08 | 8.08 | 30.42 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.6358 | 29.3156 | 6.385 | 28.0342 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19573
Eoplly New Energy Technology | EP156P/60-245 AC | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 220 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.75 | 37.38 | 7.96 | 31.02 | 47.1 | -0.44 | 0.05 | -0.33 | 0.001 | -0.44 | 1.5823 | 30.4817 | 6.368 | 28.0947 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19686
Eoplly New Energy Technology | EP156P/60-245S AC | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 220 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.75 | 37.38 | 7.96 | 31.02 | 47.1 | -0.44 | 0.05 | -0.33 | 0.001 | -0.44 | 1.5823 | 30.4817 | 6.368 | 28.0947 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19686
Eoplly New Energy Technology | EP156P/60-245W | 245 W Polycrystalline Module | UL 1741 | 245 | 220 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.75 | 37.38 | 7.96 | 31.02 | 47.1 | -0.44 | 0.05 | -0.33 | 0.001 | -0.44 | 1.5823 | 30.4817 | 6.368 | 28.0947 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19686
Eoplly New Energy Technology | EP156M/60-250 AC | 250 W DC, Monocrystalline ACPV Module | UL 1741 | 250 | 224.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.91 | 37.26 | 8.15 | 30.84 | 46.2 | -0.46 | 0.05 | -0.34 | -0.01 | -0.46 | 1.6695 | 29.3189 | 6.573 | 27.7365 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19579
Eoplly New Energy Technology | EP156M/60-250S AC | 250 W DC, Monocrystalline ACPV Module | UL 1741 | 250 | 224.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.91 | 37.26 | 8.15 | 30.84 | 46.2 | -0.46 | 0.05 | -0.34 | -0.01 | -0.46 | 1.6695 | 29.3189 | 6.573 | 27.7365 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19579
Eoplly New Energy Technology | EP156MB/60-250S AC | 250 W DC, Monocrystalline ACPV Module, Black Backsheet | UL 1741 | 250 | 223.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.91 | 37.26 | 8.15 | 30.84 | 46.3 | -0.47 | 0.06 | -0.35 | -0.01 | -0.46 | 1.65 | 29.7203 | 6.4403 | 28.4213 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19615
Eoplly New Energy Technology | EP156P/60-250S AC | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 224.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.79 | 37.56 | 8 | 31.32 | 47.1 | -0.44 | 0.05 | -0.33 | 0.001 | -0.44 | 1.5902 | 30.7765 | 6.4 | 28.3664 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19577
Eoplly New Energy Technology | EP156M/60-255 AC | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.98 | 37.56 | 8.22 | 31.2 | 46.2 | -0.46 | 0.05 | -0.34 | -0.01 | -0.46 | 1.6838 | 29.6612 | 6.6294 | 28.0603 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19586
Eoplly New Energy Technology | EP156M/60-255S AC | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 8.98 | 37.56 | 8.22 | 31.2 | 46.2 | -0.46 | 0.05 | -0.34 | -0.01 | -0.46 | 1.6838 | 29.6612 | 6.6294 | 28.0603 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19586
Eoplly New Energy Technology | EP156P/60-255S AC | 255 W DC, Polycrystalline ACPV Module | UL 1741 | 255 | 229.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 8.9 | 37.68 | 8.1 | 31.56 | 47.1 | -0.44 | 0.05 | -0.33 | 0.001 | -0.44 | 1.6101 | 31.0123 | 6.48 | 28.5838 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19582
Eoplly New Energy Technology | EP156M/60-260 AC | 260 W DC, Monocrystalline ACPV Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 9.12 | 37.74 | 8.3 | 31.62 | 46.2 | -0.46 | 0.05 | -0.34 | -0.01 | -0.46 | 1.7002 | 30.0605 | 6.694 | 28.438 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19658
Eoplly New Energy Technology | EP156M/60-260S AC | 260 W DC, Monocrystalline ACPV Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6183 | 60 | 1 | N | 9.12 | 37.74 | 8.3 | 31.62 | 46.2 | -0.46 | 0.05 | -0.34 | -0.01 | -0.46 | 1.7002 | 30.0605 | 6.694 | 28.438 | Rack | Flat Plate | 0.988 | 1.638 | 1 | 0.19658
Eoplly New Energy Technology | EP156P/60-260S AC | 260 W DC, Polycrystalline ACPV Module | UL 1741 | 260 | 233.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6341 | 60 | 1 | N | 9.01 | 37.8 | 8.2 | 31.8 | 47.1 | -0.44 | 0.05 | -0.33 | 0.001 | -0.44 | 1.6302 | 31.2499 | 6.561 | 28.8028 | Rack | Flat Plate | 0.994 | 1.644 | 1 | 0.19594
ET Solar Industry | ET-M572165WW | 165 W Monocrystalline Module | UL 1703 | 165 | 146.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.19 | 44.12 | 4.6 | 35.8 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.91423 | 34.7887 | 3.5703 | 31.9571 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19276
ET Solar Industry | ET-M572165WWZ | 165 W Monocrystalline Module | UL 1703 | 165 | 146.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.19 | 44.12 | 4.6 | 35.8 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.91423 | 34.7887 | 3.5703 | 31.9571 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19276
ET Solar Industry | ET-M572170WW | 170 W Monocrystalline Module | UL 1703 | 170 | 151.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.3 | 44.16 | 4.71 | 36.13 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.93609 | 35.1094 | 3.6557 | 32.2516 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19333
ET Solar Industry | ET-M572170WWZ | 170 W Monocrystalline Module | UL 1703 | 170 | 151.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.3 | 44.16 | 4.71 | 36.13 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.93609 | 35.1094 | 3.6557 | 32.2516 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19333
ET Solar Industry | ET-M572175BB | 175 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 175 | 155.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.5 | 44.25 | 4.83 | 36.24 | 48.4 | -0.454 | 0.109 | -0.36 | 0.089 | -0.53 | 1.0018 | 35.6444 | 3.9244 | 32.4343 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20404
ET Solar Industry | ET-M572175BBZ | 175 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 175 | 155.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.5 | 44.25 | 4.83 | 36.24 | 48.4 | -0.454 | 0.109 | -0.36 | 0.089 | -0.53 | 1.0018 | 35.6444 | 3.9244 | 32.4343 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20404
ET Solar Industry | ET-M572175WW | 175 W Monocrystalline Module | UL 1703 | 175 | 155.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.5 | 44.25 | 4.83 | 36.24 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.95994 | 35.2163 | 3.7488 | 32.3498 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19317
ET Solar Industry | ET-M572175WWZ | 175 W Monocrystalline Module | UL 1703 | 175 | 155.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.5 | 44.25 | 4.83 | 36.24 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.95994 | 35.2163 | 3.7488 | 32.3498 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19317
ET Solar Industry | ET-M572180BB | 180 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 180 | 160.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.61 | 44.6 | 4.95 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0266 | 35.7034 | 4.0219 | 32.488 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20364
ET Solar Industry | ET-M572180BBZ | 180 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 180 | 160.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.61 | 44.6 | 4.95 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0266 | 35.7034 | 4.0219 | 32.488 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20364
ET Solar Industry | ET-M572180WW | 180 W Monocrystalline Module | UL 1703 | 180 | 160.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.61 | 44.6 | 4.95 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.98531 | 35.9867 | 3.9603 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19699
ET Solar Industry | ET-M572180WWZ | 180 W Monocrystalline Module | UL 1703 | 180 | 160.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.61 | 44.6 | 4.95 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.98531 | 35.9867 | 3.9603 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19699
ET Solar Industry | ET-M572185BB | 185 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 185 | 164.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.8 | 44.6 | 5.09 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0557 | 35.7034 | 4.1357 | 32.488 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20374
ET Solar Industry | ET-M572185BBZ | 185 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 185 | 164.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.8 | 44.6 | 5.09 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0557 | 35.7034 | 4.1357 | 32.488 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20374
ET Solar Industry | ET-M572185WW | 185 W Monocrystalline Module | UL 1703 | 185 | 165.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.8 | 44.6 | 5.09 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0132 | 35.9867 | 4.0723 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19709
ET Solar Industry | ET-M572185WWZ | 185 W Monocrystalline Module | UL 1703 | 185 | 165.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.8 | 44.6 | 5.09 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0132 | 35.9867 | 4.0723 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19709
ET Solar Industry | ET-M572190BBZ | 190 W Monocrystalline Module, Black Frame | UL 1703 | 190 | 169.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.64 | 44.85 | 5.15 | 36.89 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.94649 | 35.0327 | 4.0832 | 32.9 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.17452
ET Solar Industry | ET-M572190WB | 190 W Monocrystalline Module, Black Frame | UL 1703 | 190 | 169.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.64 | 44.85 | 5.15 | 36.89 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.94649 | 35.0327 | 4.0832 | 32.9 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.17452
ET Solar Industry | ET-M572190WW | 190 W Monocrystalline Module | UL 1703 | 190 | 169.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.64 | 44.85 | 5.15 | 36.89 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.94649 | 35.0327 | 4.0832 | 32.9 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.17452
ET Solar Industry | ET-M572190WWZ | 190 W Monocrystalline Module | UL 1703 | 190 | 169.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.64 | 44.85 | 5.15 | 36.89 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.94649 | 35.0327 | 4.0832 | 32.9 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.17452
ET Solar Industry | ET-P654190WB | 190 W Polycrystalline Module, Black Frame | UL 1703 | 190 | 167.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.72 | 32.5 | 7.1 | 26.78 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4031 | 26.6766 | 5.4992 | 23.9159 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19699
ET Solar Industry | ET-P654190WW | 190 W Polycrystalline Module | UL 1703 | 190 | 167.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.72 | 32.5 | 7.1 | 26.78 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4031 | 26.6766 | 5.4992 | 23.9159 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19699
ET Solar Industry | ET-P654195WB | 195 W Polycrystalline Module, Black Frame | UL 1703 | 195 | 172.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.98 | 32.75 | 7.22 | 27 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4268 | 26.8958 | 5.5921 | 24.1124 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19679
ET Solar Industry | ET-P654195WW | 195 W Polycrystalline Module | UL 1703 | 195 | 172.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.98 | 32.75 | 7.22 | 27 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4268 | 26.8958 | 5.5921 | 24.1124 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19679
ET Solar Industry | ET-P654200WB | 200 W Polycrystalline Module, Black Frame | UL 1703 | 200 | 176.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.86 | 32.72 | 7.36 | 27.21 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4544 | 27.1049 | 5.7006 | 24.2999 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19711
ET Solar Industry | ET-P654200WW | 200 W Polycrystalline Module | UL 1703 | 200 | 176.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.86 | 32.72 | 7.36 | 27.21 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4544 | 27.1049 | 5.7006 | 24.2999 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19711
ET Solar Industry | ET-P654205WB | 205 W Polycrystalline Module, Black Frame | UL 1703 | 205 | 181.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.1 | 32.8 | 7.5 | 27.3 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4821 | 27.1946 | 5.809 | 24.3803 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19661
ET Solar Industry | ET-P654205WW | 205 W Polycrystalline Module | UL 1703 | 205 | 181.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.1 | 32.8 | 7.5 | 27.3 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4821 | 27.1946 | 5.809 | 24.3803 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19661
ET Solar Industry | ET-P654210WB | 210 W Polycrystalline Module, Black Frame | UL 1703 | 210 | 186.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.3 | 32.83 | 7.63 | 27.54 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.5078 | 27.4337 | 5.9097 | 24.5946 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19697
ET Solar Industry | ET-P654210WW | 210 W Polycrystalline Module | UL 1703 | 210 | 186.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.3 | 32.83 | 7.63 | 27.54 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.5078 | 27.4337 | 5.9097 | 24.5946 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19697
ET Solar Industry | ET-P660235B | 235 W Polycrystalline Module, Black Frame | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar Industry | ET-P660235BB | 235 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 235 | 210.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.5 | 37.08 | 7.88 | 29.83 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.5841 | 28.9978 | 6.3056 | 26.1401 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19548
ET Solar Industry | ET-P660235BBZ | 235 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 235 | 210.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.5 | 37.08 | 7.88 | 29.83 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.5841 | 28.9978 | 6.3056 | 26.1401 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19548
ET Solar Industry | ET-P660235WB | 235 W Polycrystalline Module, Black Frame | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar Industry | ET-P660235WBZ | 235 W Polycrystalline Module, Black Frame | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar Industry | ET-P660235WW | 235 W Polycrystalline Module | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar Industry | ET-P660235WWZ | 235 W Polycrystalline Module | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar Industry | ET-P660240B | 240 W Polycrystalline Module, Black Frame | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar Industry | ET-P660240BB | 240 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 240 | 215.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.58 | 37.17 | 8.02 | 29.96 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6123 | 29.1241 | 6.4176 | 26.254 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19565
ET Solar Industry | ET-P660240BBZ | 240 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 240 | 215.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.58 | 37.17 | 8.02 | 29.96 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6123 | 29.1241 | 6.4176 | 26.254 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19565
ET Solar Industry | ET-P660240WB | 240 W Polycrystalline Module, Black Frame | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar Industry | ET-P660240WBZ | 240 W Polycrystalline Module, Black Frame | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar Industry | ET-P660240WW | 240 W Polycrystalline Module | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar Industry | ET-P660240WWZ | 240 W Polycrystalline Module | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar Industry | ET-P660245B | 245 W Polycrystalline Module, Black frame | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar Industry | ET-P660245BAC | 245 W DC, Polycrystalline ACPV Module, Black Frame | UL 1741 | 245 | 219 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar Industry | ET-P660245BB | 245 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 245 | 219.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.73 | 37.27 | 8.13 | 30.14 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6344 | 29.2991 | 6.5056 | 26.4118 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19546
ET Solar Industry | ET-P660245BBAC | 245 W DC, Polycrystalline ACPV Module, Black Frame, Black Backsheet | UL 1741 | 245 | 211.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.73 | 37.27 | 8.13 | 30.14 | 52.2 | -0.475 | 0.029 | -0.349 | -0.025 | -0.456 | 1.6344 | 29.2991 | 6.5056 | 26.4118 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19546
ET Solar Industry | ET-P660245BBZ | 245 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 245 | 219.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.73 | 37.27 | 8.13 | 30.14 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6344 | 29.2991 | 6.5056 | 26.4118 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19546
ET Solar Industry | ET-P660245BBZAC | 245 W DC, Polycrystalline ACPV Module, Zero Rack, Black Frame, Black Backsheet | UL 1741 | 245 | 211.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.73 | 37.27 | 8.13 | 30.14 | 52.2 | -0.475 | 0.029 | -0.349 | -0.025 | -0.456 | 1.6344 | 29.2991 | 6.5056 | 26.4118 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19546
ET Solar Industry | ET-P660245WB | 245 W Polycrystalline Module, Black frame | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar Industry | ET-P660245WBZ | 245 W Polycrystalline Module, Zero Rack, Black Frame | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar Industry | ET-P660245WBZAC | 245 W DC, Polycrystalline ACPV Module, Zero Rack, Black Frame | UL 1741 | 245 | 219 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar Industry | ET-P660245WW | 245 W Polycrystalline Module, Zero Rack | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar Industry | ET-P660245WWZ | 245 W Polycrystalline Module, Zero Rack | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar Industry | ET-P660250BAC | 250 W DC, Polycrystalline ACPV Module, Black Frame | UL 1741 | 250 | 223.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar Industry | ET-P660250BB | 250 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 250 | 224.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.47 | 8.24 | 30.34 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6565 | 29.4935 | 6.5936 | 26.587 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar Industry | ET-P660250BBAC | 250 W DC, Polycrystalline ACPV Module, Black Frame, Black Backsheet | UL 1741 | 250 | 216.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.47 | 8.24 | 30.34 | 52.2 | -0.475 | 0.029 | -0.349 | -0.025 | -0.456 | 1.6565 | 29.4935 | 6.5936 | 26.587 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar Industry | ET-P660250BBZ | 250 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 250 | 224.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.47 | 8.24 | 30.34 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6565 | 29.4935 | 6.5936 | 26.587 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar Industry | ET-P660250BBZAC | 250 W DC, Polycrystalline ACPV Module, Zero Rack, Black Frame, Black Backsheet | UL 1741 | 250 | 216.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.47 | 8.24 | 30.34 | 52.2 | -0.475 | 0.029 | -0.349 | -0.025 | -0.456 | 1.6565 | 29.4935 | 6.5936 | 26.587 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar Industry | ET-P660250WB | 250 W Polycrystalline Module, Black Frame | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar Industry | ET-P660250WBAC | 250 W DC, Polycrystalline ACPV Module, Black Frame | UL 1741 | 250 | 225.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7 | 27.19 | 6.62 | 27.89 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18489
ET Solar Industry | ET-P660250WBZ | 250 W Polycrystalline Module, Zero Rack, Black Frame | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar Industry | ET-P660250WBZAC | 250 W DC, Polycrystalline ACPV Module, Zero Rack, Black Frame | UL 1741 | 250 | 223.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar Industry | ET-P660250WW | 250 W Polycrystalline Module | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar Industry | ET-P660250WWZ | 250 W Polycrystalline Module, Zero Rack | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar Industry | ET-P660255BB | 255 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 255 | 229 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6585 | 30.0476 | 6.6016 | 27.0865 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar Industry | ET-P660255BBAC | 255 W DC, Polycrystalline ACPV Module, Black Backsheet, Black Frame | UL 1741 | 255 | 229 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.66 | 30.05 | 6.6 | 27.09 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19562
ET Solar Industry | ET-P660255BBZ | 255 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 255 | 229 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6585 | 30.0476 | 6.6016 | 27.0865 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar Industry | ET-P660255BBZAC | 255 W DC, Polycrystalline ACPV Module, Black Backsheet, Black Zero Rack Frame | UL 1741 | 255 | 229 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.66 | 30.05 | 6.6 | 27.09 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19562
ET Solar Industry | ET-P660255WB | 255 W Polycrystalline Module, Black Frame | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
ET Solar Industry | ET-P660255WBAC | 255 W DC, Polycrystalline ACPV Module ,White Backsheet, Black Frame | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.01 | 6.57 | 27.41 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19536
ET Solar Industry | ET-P660255WBZ | 255 W Polycrystalline Module, Zero Rack, Black Frame | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
ET Solar Industry | ET-P660255WBZAC | 255 W DC, Polycrystalline ACPV Module, White Backsheet, Black Zero Rack Frame | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.01 | 6.57 | 27.41 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19536
ET Solar Industry | ET-P660255WW | 255 W Polycrystalline Module | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
ET Solar Industry | ET-P660255WWAC | 255 W DC, Polycrystalline ACPV Module, White Backsheet, White Frame | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.01 | 6.57 | 27.41 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19536
ET Solar Industry | ET-P660255WWZ | 255 W Polycrystalline Module, Zero Rack | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
ET Solar Industry | ET-P660255WWZAC | 255 W DC, Polycrystalline ACPV Module, White Backsheet, White Zero Rack Frame | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.01 | 6.57 | 27.41 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19536
ET Solar Industry | ET-M660260BB | 260 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 260 | 236.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.22 | 8.49 | 30.63 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.6357 | 30.3035 | 6.8251 | 28.1047 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19064
ET Solar Industry | ET-M660260WW | 260 W Monocrystalline Module | UL 1703 | 260 | 234.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6308 | 60 | 1 | N | 8.89 | 37.8 | 8.49 | 30.65 | 46.1 | -0.45 | 0.04 | -0.32 | -0.02 | -0.43 | 1.696 | 29.1658 | 6.7539 | 27.7713 | Rack | Flat Plate | 0.992 | 1.644 | 1 | 0.19025
ET Solar Industry | ET-P660260WB | 260 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 260 | 237 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.07 | 38.16 | 8.5 | 30.59 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6624 | 30.2766 | 6.7782 | 28.0531 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19358
ET Solar Industry | ET-P660260WBAC | 260 W DC, Polycrystalline ACPV Module, White Backsheet, Black Frame | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.56 | 6.57 | 27.92 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19511
ET Solar Industry | ET-P660260WBZ | 260 W Polycrystalline Module, Zero Rack, Black Frame | UL 1703 | 260 | 235.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6579 | 30.5626 | 6.5743 | 27.917 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19489
ET Solar Industry | ET-P660260WBZAC | 260 W DC, Polycrystalline ACPV Module, White Backsheet, Black Zero Rack Frame | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.56 | 6.57 | 27.92 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19511
ET Solar Industry | ET-P660260WW | 260 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 260 | 237 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.07 | 38.16 | 8.5 | 30.59 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6624 | 30.2766 | 6.7782 | 28.0531 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19358
ET Solar Industry | ET-P660260WWAC | 260 W DC, Polycrystalline ACPV Module, White Backsheet, White Frame | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.56 | 6.57 | 27.92 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19511
ET Solar Industry | ET-P660260WWZ | 260 W Polycrystalline Module, Zero Rack | UL 1703 | 260 | 235.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6579 | 30.5626 | 6.5743 | 27.917 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19489
ET Solar Industry | ET-P660260WWZAC | 260 W DC, Polycrystalline ACPV Module, White Backsheet, White Zero Rack Frame | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.56 | 6.57 | 27.92 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19511
ET Solar Industry | ET-M660265BB | 265 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 265 | 241.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.1 | 38.29 | 8.65 | 30.64 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.6665 | 30.3134 | 6.9537 | 28.1139 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19063
ET Solar Industry | ET-M660265WB | 265 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 265 | 241.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.1 | 38.29 | 8.65 | 30.64 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6665 | 30.3134 | 6.9537 | 28.1139 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19063
ET Solar Industry | ET-M660265WW | 265 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 265 | 241.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.1 | 38.29 | 8.65 | 30.64 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6665 | 30.3134 | 6.9537 | 28.1139 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19063
ET Solar Industry | ET-P660265WB | 265 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 265 | 241.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.24 | 38.29 | 8.62 | 30.74 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6859 | 30.425 | 6.8739 | 28.1906 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
ET Solar Industry | ET-P660265WW | 265 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 265 | 241.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.24 | 38.29 | 8.62 | 30.74 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6859 | 30.425 | 6.8739 | 28.1906 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
ET Solar Industry | ET-M660270BB | 270 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 270 | 245.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.12 | 38.68 | 8.76 | 30.83 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.6877 | 30.5014 | 7.0422 | 28.2882 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19066
ET Solar Industry | ET-M660270WB | 270 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 270 | 246.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.12 | 38.68 | 8.76 | 30.83 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6877 | 30.5014 | 7.0422 | 28.2882 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19066
ET Solar Industry | ET-M660270WW | 270 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 270 | 246.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.12 | 38.68 | 8.76 | 30.83 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6877 | 30.5014 | 7.0422 | 28.2882 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19066
ET Solar Industry | ET-P660270WB | 270 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 270 | 246.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.31 | 38.72 | 8.72 | 30.97 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7054 | 30.6527 | 6.9537 | 28.4016 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
ET Solar Industry | ET-P660270WW | 270 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 270 | 246.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.31 | 38.72 | 8.72 | 30.97 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7054 | 30.6527 | 6.9537 | 28.4016 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
ET Solar Industry | ET-M660275BB | 275 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 275 | 250.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.14 | 39.08 | 8.88 | 30.97 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.7108 | 30.6399 | 7.1386 | 28.4167 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar Industry | ET-M660275WB | 275 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 275 | 251.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.14 | 39.08 | 8.88 | 30.97 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7108 | 30.6399 | 7.1386 | 28.4167 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar Industry | ET-M660275WW | 275 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 275 | 251.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.14 | 39.08 | 8.88 | 30.97 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7108 | 30.6399 | 7.1386 | 28.4167 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar Industry | ET-P660275WB | 275 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 275 | 251.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.35 | 38.92 | 8.78 | 31.32 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7172 | 30.9991 | 7.0015 | 28.7225 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
ET Solar Industry | ET-P660275WW | 275 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 275 | 251.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.35 | 38.92 | 8.78 | 31.32 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7172 | 30.9991 | 7.0015 | 28.7225 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
ET Solar Industry | ET-M660280BB | 280 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 280 | 255.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar Industry | ET-M660280WB | 280 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar Industry | ET-M660280WW | 280 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar Industry | ET-P660280WB | 280 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 280 | 255.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.47 | 39.16 | 8.84 | 31.68 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7289 | 31.3554 | 7.0494 | 29.0527 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
ET Solar Industry | ET-P660280WW | 280 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 280 | 255.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.47 | 39.16 | 8.84 | 31.68 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7289 | 31.3554 | 7.0494 | 29.0527 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
ET Solar Industry | ET-M660285BB | 285 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 285 | 259.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065
ET Solar Industry | ET-M660285WB | 285 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065
ET Solar Industry | ET-M660285WW | 285 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065
ET Solar Industry | ET-P672285WB | 285 W Polycrystalline Module, Black Frame | UL 1703 | 285 | 254.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.52 | 44.35 | 7.91 | 36.03 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5287 | 35.7661 | 6.3872 | 32.9263 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
ET Solar Industry | ET-P672285WBG | 285 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 285 | 256.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.55 | 44.72 | 7.95 | 35.86 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5515 | 35.3011 | 6.4275 | 32.0574 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19217
ET Solar Industry | ET-P672285WW | 285 W Polycrystalline Module | UL 1703 | 285 | 254.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.52 | 44.35 | 7.91 | 36.03 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5287 | 35.7661 | 6.3872 | 32.9263 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
ET Solar Industry | ET-P672285WWG | 285 W Polycrystalline Module, White Frame, White Backsheet | UL 1703 | 285 | 256.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.55 | 44.72 | 7.95 | 35.86 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5515 | 35.3011 | 6.4275 | 32.0574 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19217
ET Solar Industry | ET-M660290WB | 290 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 290 | 265.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.59 | 39.68 | 9.03 | 32.12 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 31.7777 | 7.2592 | 29.4719 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19064
ET Solar Industry | ET-M660290WW | 290 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 290 | 265.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.59 | 39.68 | 9.03 | 32.12 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 31.7777 | 7.2592 | 29.4719 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19064
ET Solar Industry | ET-P672290WB | 290 W Polycrystalline Module, Black Frame | UL 1703 | 290 | 259.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.61 | 44.5 | 8 | 36.25 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5461 | 35.9845 | 6.4599 | 33.1274 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
ET Solar Industry | ET-P672290WBG | 290 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 290 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.62 | 44.75 | 8.08 | 35.92 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5768 | 35.3602 | 6.5326 | 32.1111 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19226
ET Solar Industry | ET-P672290WW | 290 W Polycrystalline Module | UL 1703 | 290 | 259.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.61 | 44.5 | 8 | 36.25 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5461 | 35.9845 | 6.4599 | 33.1274 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
ET Solar Industry | ET-P672290WWG | 290 WPolycrystalline Module, White Frame, White Backsheet | UL 1703 | 290 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.62 | 44.75 | 8.08 | 35.92 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5768 | 35.3602 | 6.5326 | 32.1111 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19226
ET Solar Industry | ET-P672295WB | 295 W Polycrystalline Module, Black Frame | UL 1703 | 295 | 263.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6945 | 32.7533 | 6.7469 | 30.0578 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18814
ET Solar Industry | ET-P672295WBG | 295 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5924 | 35.6063 | 6.5972 | 32.3346 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19221
ET Solar Industry | ET-P672295WW | 295 W Polycrystalline Module | UL 1703 | 295 | 263.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6945 | 32.7533 | 6.7469 | 30.0578 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18814
ET Solar Industry | ET-P672295WWG | 295 W Polycrystalline Module, White Frame, White backsheet | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5924 | 35.6063 | 6.5972 | 32.3346 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19221
ET Solar Industry | ET-P672300WB | 300 W Polycrystalline Module, Black Frame | UL 1703 | 300 | 268.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6986 | 33.2151 | 6.7634 | 30.4816 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18807
ET Solar Industry | ET-P672300WBG | 300 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5963 | 36.1083 | 6.6134 | 32.7905 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19214
ET Solar Industry | ET-P672300WW | 300 W Polycrystalline Module | UL 1703 | 300 | 268.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6986 | 33.2151 | 6.7634 | 30.4816 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18807
ET Solar Industry | ET-P672300WWG | 300 W Polycrystalline Module, White Frame, White Backsheet | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5963 | 36.1083 | 6.6134 | 32.7905 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19214
ET Solar Industry | ET-P672305WB | 305 W Polycrystalline Module, Black Frame | UL 1703 | 305 | 272.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.78 | 45.12 | 8.21 | 37.18 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.7049 | 33.6679 | 6.7882 | 30.8972 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18819
ET Solar Industry | ET-P672305WBG | 305 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 305 | 275.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.78 | 45.12 | 8.21 | 37.18 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.6022 | 36.6005 | 6.6377 | 33.2375 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19227
ET Solar Industry | ET-P672305WW | 305 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 305 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.04 | 45.18 | 8.42 | 36.23 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6234 | 35.9571 | 6.7282 | 33.7152 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138
ET Solar Industry | ET-P672305WWG | 305 W Polycrystalline Module, White Frame, White Backsheet | UL 1703 | 305 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.78 | 45.12 | 8.21 | 37.18 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.6022 | 36.6005 | 6.6377 | 33.2375 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19227
ET Solar Industry | ET-P672310WB | 310 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 310 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 45.65 | 8.49 | 36.54 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6369 | 36.2647 | 6.7841 | 34.0037 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19149
ET Solar Industry | ET-P672310WW | 310 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 310 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 45.65 | 8.49 | 36.54 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6369 | 36.2647 | 6.7841 | 34.0037 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19149
ET Solar Industry | ET-P672315WB | 315 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 315 | 287.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.12 | 45.75 | 8.56 | 36.81 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6504 | 36.5327 | 6.84 | 34.255 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1914
ET Solar Industry | ET-P672315WW | 315 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 315 | 287.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.12 | 45.75 | 8.56 | 36.81 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6504 | 36.5327 | 6.84 | 34.255 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1914
ET Solar Industry | ET-M672320WB | 320 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 320 | 292.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 46.31 | 8.65 | 37 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6892 | 36.1108 | 6.9511 | 33.994 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
ET Solar Industry | ET-M672320WW | 320 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 320 | 292.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 46.31 | 8.65 | 37 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6892 | 36.1108 | 6.9511 | 33.994 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
ET Solar Industry | ET-P672320WB | 320 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 320 | 291.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.24 | 45.94 | 8.62 | 37.13 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6619 | 36.8503 | 6.888 | 34.5528 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138
ET Solar Industry | ET-P672320WW | 320 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 320 | 291.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.24 | 45.94 | 8.62 | 37.13 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6619 | 36.8503 | 6.888 | 34.5528 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138
ET Solar Industry | ET-M672325WB | 325 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 325 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.11 | 46.54 | 8.76 | 37.11 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7107 | 36.2181 | 7.0395 | 34.0951 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19064
ET Solar Industry | ET-M672325WW | 325 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 325 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.11 | 46.54 | 8.76 | 37.11 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7107 | 36.2181 | 7.0395 | 34.0951 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19064
ET Solar Industry | ET-P672325WB | 325 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 325 | 296.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.28 | 46.31 | 8.72 | 37.28 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6812 | 36.9992 | 6.9679 | 34.6924 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19139
ET Solar Industry | ET-P672325WW | 325 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 325 | 296.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.28 | 46.31 | 8.72 | 37.28 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6812 | 36.9992 | 6.9679 | 34.6924 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19139
ET Solar Industry | ET-M672330WB | 330 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 330 | 301.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.29 | 46.64 | 8.79 | 37.55 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7166 | 36.6475 | 7.0636 | 34.4993 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19063
ET Solar Industry | ET-M672330WW | 330 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 330 | 301.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.29 | 46.64 | 8.79 | 37.55 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7166 | 36.6475 | 7.0636 | 34.4993 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19063
ET Solar Industry | ET-P672330WB | 330 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 330 | 301.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.35 | 46.65 | 8.78 | 37.58 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6928 | 37.2969 | 7.0158 | 34.9715 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19132
ET Solar Industry | ET-P672330WW | 330 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 330 | 301.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.35 | 46.65 | 8.78 | 37.58 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6928 | 37.2969 | 7.0158 | 34.9715 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19132
ET Solar Industry | ET-M672335WB | 335 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.33 | 46.75 | 8.83 | 37.94 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7244 | 37.0282 | 7.0957 | 34.8576 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1906
ET Solar Industry | ET-M672335WW | 335 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.33 | 46.75 | 8.83 | 37.94 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7244 | 37.0282 | 7.0957 | 34.8576 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1906
ET Solar Industry | ET-P672335WB | 335 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 335 | 306 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.47 | 46.83 | 8.84 | 37.9 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7043 | 37.6145 | 7.0638 | 35.2693 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19137
ET Solar Industry | ET-P672335WW | 335 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 335 | 306 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.47 | 46.83 | 8.84 | 37.9 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7043 | 37.6145 | 7.0638 | 35.2693 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19137
ET Solar Industry | ET-M672340WB | 340 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 340 | 310.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.41 | 46.91 | 8.91 | 38.17 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.74 | 37.2526 | 7.16 | 35.0689 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19065
ET Solar Industry | ET-M672340WW | 340 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 340 | 310.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.41 | 46.91 | 8.91 | 38.17 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.74 | 37.2526 | 7.16 | 35.0689 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19065
ET Solar Industry | ET-M672345WB | 345 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.48 | 47.13 | 8.99 | 38.38 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7556 | 37.4576 | 7.2243 | 35.2619 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19061
ET Solar Industry | ET-M672345WW | 345 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.48 | 47.13 | 8.99 | 38.38 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7556 | 37.4576 | 7.2243 | 35.2619 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19061
ET Solar Industry | ET-M672350WB | 350 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.59 | 47.64 | 9.09 | 38.51 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7752 | 37.5845 | 7.3046 | 35.3813 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
ET Solar Industry | ET-M672350WW | 350 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.59 | 47.64 | 9.09 | 38.51 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7752 | 37.5845 | 7.3046 | 35.3813 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
ET Solar New Energy | ET-M572165WW | 165 W Monocrystalline Module | UL 1703 | 165 | 146.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.19 | 44.12 | 4.6 | 35.8 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.91423 | 34.7887 | 3.5703 | 31.9571 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19276
ET Solar New Energy | ET-M572165WWZ | 165 W Monocrystalline Module | UL 1703 | 165 | 146.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.19 | 44.12 | 4.6 | 35.8 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.91423 | 34.7887 | 3.5703 | 31.9571 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19276
ET Solar New Energy | ET-M572170WW | 170 W Monocrystalline Module | UL 1703 | 170 | 151.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.3 | 44.16 | 4.71 | 36.13 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.93609 | 35.1094 | 3.6557 | 32.2516 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19333
ET Solar New Energy | ET-M572170WWZ | 170 W Monocrystalline Module | UL 1703 | 170 | 151.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.3 | 44.16 | 4.71 | 36.13 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.93609 | 35.1094 | 3.6557 | 32.2516 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19333
ET Solar New Energy | ET-M572175BB | 175 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 175 | 155.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.5 | 44.25 | 4.83 | 36.24 | 48.4 | -0.454 | 0.109 | -0.36 | 0.089 | -0.53 | 1.0018 | 35.6444 | 3.9244 | 32.4343 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20404
ET Solar New Energy | ET-M572175BBZ | 175 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 175 | 155.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.5 | 44.25 | 4.83 | 36.24 | 48.4 | -0.454 | 0.109 | -0.36 | 0.089 | -0.53 | 1.0018 | 35.6444 | 3.9244 | 32.4343 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20404
ET Solar New Energy | ET-M572175WW | 175 W Monocrystalline Module | UL 1703 | 175 | 155.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.5 | 44.25 | 4.83 | 36.24 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.95994 | 35.2163 | 3.7488 | 32.3498 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19317
ET Solar New Energy | ET-M572175WWZ | 175 W Monocrystalline Module | UL 1703 | 175 | 155.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.5 | 44.25 | 4.83 | 36.24 | 44.4 | -0.54641 | 0.058491 | -0.40308 | -0.012739 | -0.52505 | 0.95994 | 35.2163 | 3.7488 | 32.3498 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19317
ET Solar New Energy | ET-M572180BB | 180 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 180 | 160.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.61 | 44.6 | 4.95 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0266 | 35.7034 | 4.0219 | 32.488 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20364
ET Solar New Energy | ET-M572180BBZ | 180 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 180 | 160.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.61 | 44.6 | 4.95 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0266 | 35.7034 | 4.0219 | 32.488 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20364
ET Solar New Energy | ET-M572180WW | 180 W Monocrystalline Module | UL 1703 | 180 | 160.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.61 | 44.6 | 4.95 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.98531 | 35.9867 | 3.9603 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19699
ET Solar New Energy | ET-M572180WWZ | 180 W Monocrystalline Module | UL 1703 | 180 | 160.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.61 | 44.6 | 4.95 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.98531 | 35.9867 | 3.9603 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19699
ET Solar New Energy | ET-M572185BB | 185 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 185 | 164.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.8 | 44.6 | 5.09 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0557 | 35.7034 | 4.1357 | 32.488 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20374
ET Solar New Energy | ET-M572185BBZ | 185 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 185 | 164.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.8 | 44.6 | 5.09 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0557 | 35.7034 | 4.1357 | 32.488 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20374
ET Solar New Energy | ET-M572185WW | 185 W Monocrystalline Module | UL 1703 | 185 | 165.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.8 | 44.6 | 5.09 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0132 | 35.9867 | 4.0723 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19709
ET Solar New Energy | ET-M572185WWZ | 185 W Monocrystalline Module | UL 1703 | 185 | 165.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.1144 | 72 | 1 | N | 5.8 | 44.6 | 5.09 | 36.3 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 1.0132 | 35.9867 | 4.0723 | 31.8231 | Rack | Flat Plate | 0.738 | 1.51 | 1 | 0.19709
ET Solar New Energy | ET-M572190BBZ | 190 W Monocrystalline Module, Black Frame | UL 1703 | 190 | 169.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.64 | 44.85 | 5.15 | 36.89 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.94649 | 35.0327 | 4.0832 | 32.9 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.17452
ET Solar New Energy | ET-M572190WB | 190 W Monocrystalline Module, Black Frame | UL 1703 | 190 | 169.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.64 | 44.85 | 5.15 | 36.89 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.94649 | 35.0327 | 4.0832 | 32.9 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.17452
ET Solar New Energy | ET-M572190WW | 190 W Monocrystalline Module | UL 1703 | 190 | 169.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.64 | 44.85 | 5.15 | 36.89 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.94649 | 35.0327 | 4.0832 | 32.9 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.17452
ET Solar New Energy | ET-M572190WWZ | 190 W Monocrystalline Module | UL 1703 | 190 | 169.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2623 | 72 | 1 | N | 5.64 | 44.85 | 5.15 | 36.89 | 48.3 | -0.446 | 0.019 | -0.314 | -0.046 | -0.408 | 0.94649 | 35.0327 | 4.0832 | 32.9 | Rack | Flat Plate | 0.802 | 1.574 | 1 | 0.17452
ET Solar New Energy | ET-P654190WB | 190 W Polycrystalline Module, Black Frame | UL 1703 | 190 | 167.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.72 | 32.5 | 7.1 | 26.78 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4031 | 26.6766 | 5.4992 | 23.9159 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19699
ET Solar New Energy | ET-P654190WW | 190 W Polycrystalline Module | UL 1703 | 190 | 167.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.72 | 32.5 | 7.1 | 26.78 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4031 | 26.6766 | 5.4992 | 23.9159 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19699
ET Solar New Energy | ET-P654195WB | 195 W Polycrystalline Module, Black Frame | UL 1703 | 195 | 172.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.98 | 32.75 | 7.22 | 27 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4268 | 26.8958 | 5.5921 | 24.1124 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19679
ET Solar New Energy | ET-P654195WW | 195 W Polycrystalline Module | UL 1703 | 195 | 172.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.98 | 32.75 | 7.22 | 27 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4268 | 26.8958 | 5.5921 | 24.1124 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19679
ET Solar New Energy | ET-P654200WB | 200 W Polycrystalline Module, Black Frame | UL 1703 | 200 | 176.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.86 | 32.72 | 7.36 | 27.21 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4544 | 27.1049 | 5.7006 | 24.2999 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19711
ET Solar New Energy | ET-P654200WW | 200 W Polycrystalline Module | UL 1703 | 200 | 176.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.86 | 32.72 | 7.36 | 27.21 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4544 | 27.1049 | 5.7006 | 24.2999 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19711
ET Solar New Energy | ET-P654205WB | 205 W Polycrystalline Module, Black Frame | UL 1703 | 205 | 181.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.1 | 32.8 | 7.5 | 27.3 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4821 | 27.1946 | 5.809 | 24.3803 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19661
ET Solar New Energy | ET-P654205WW | 205 W Polycrystalline Module | UL 1703 | 205 | 181.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.1 | 32.8 | 7.5 | 27.3 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.4821 | 27.1946 | 5.809 | 24.3803 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19661
ET Solar New Energy | ET-P654210WB | 210 W Polycrystalline Module, Black Frame | UL 1703 | 210 | 186.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.3 | 32.83 | 7.63 | 27.54 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.5078 | 27.4337 | 5.9097 | 24.5946 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19697
ET Solar New Energy | ET-P654210WW | 210 W Polycrystalline Module | UL 1703 | 210 | 186.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.3 | 32.83 | 7.63 | 27.54 | 45.3 | -0.5278 | 0.0501 | -0.3569 | -0.0074 | -0.5207 | 1.5078 | 27.4337 | 5.9097 | 24.5946 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.19697
ET Solar New Energy | ET-P660235B | 235 W Polycrystalline Module, Black Frame | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar New Energy | ET-P660235BB | 235 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 235 | 210.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.5 | 37.08 | 7.88 | 29.83 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.5841 | 28.9978 | 6.3056 | 26.1401 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19548
ET Solar New Energy | ET-P660235BBZ | 235 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 235 | 210.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.5 | 37.08 | 7.88 | 29.83 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.5841 | 28.9978 | 6.3056 | 26.1401 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19548
ET Solar New Energy | ET-P660235WB | 235 W Polycrystalline Module, Black Frame | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar New Energy | ET-P660235WBZ | 235 W Polycrystalline Module, Black Frame | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar New Energy | ET-P660235WW | 235 W Polycrystalline Module | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar New Energy | ET-P660235WWZ | 235 W Polycrystalline Module | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 36.5 | 7.99 | 29.4 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7475 | 28.8667 | 6.6911 | 25.9287 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21466
ET Solar New Energy | ET-P660240B | 240 W Polycrystalline Module, Black Frame | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar New Energy | ET-P660240BB | 240 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 240 | 215.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.58 | 37.17 | 8.02 | 29.96 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6123 | 29.1241 | 6.4176 | 26.254 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19565
ET Solar New Energy | ET-P660240BBZ | 240 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 240 | 215.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.58 | 37.17 | 8.02 | 29.96 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6123 | 29.1241 | 6.4176 | 26.254 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19565
ET Solar New Energy | ET-P660240WB | 240 W Polycrystalline Module, Black Frame | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar New Energy | ET-P660240WBZ | 240 W Polycrystalline Module, Black Frame | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar New Energy | ET-P660240WW | 240 W Polycrystalline Module | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar New Energy | ET-P660240WWZ | 240 W Polycrystalline Module | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.64 | 37 | 7.94 | 30.23 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.5365 | 29.9329 | 6.3073 | 27.1635 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19163
ET Solar New Energy | ET-P660245B | 245 W Polycrystalline Module, Black frame | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar New Energy | ET-P660245BAC | 245 W DC, Polycrystalline ACPV Module, Black Frame | UL 1741 | 245 | 219 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar New Energy | ET-P660245BB | 245 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 245 | 219.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.73 | 37.27 | 8.13 | 30.14 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6344 | 29.2991 | 6.5056 | 26.4118 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19546
ET Solar New Energy | ET-P660245BBAC | 245 W DC, Polycrystalline ACPV Module, Black Frame, Black Backsheet | UL 1741 | 245 | 211.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.73 | 37.27 | 8.13 | 30.14 | 52.2 | -0.475 | 0.029 | -0.349 | -0.025 | -0.456 | 1.6344 | 29.2991 | 6.5056 | 26.4118 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19546
ET Solar New Energy | ET-P660245BBZ | 245 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 245 | 219.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.73 | 37.27 | 8.13 | 30.14 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6344 | 29.2991 | 6.5056 | 26.4118 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19546
ET Solar New Energy | ET-P660245BBZAC | 245 W DC, Polycrystalline ACPV Module, Zero Rack, Black Frame, Black Backsheet | UL 1741 | 245 | 211.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.73 | 37.27 | 8.13 | 30.14 | 52.2 | -0.475 | 0.029 | -0.349 | -0.025 | -0.456 | 1.6344 | 29.2991 | 6.5056 | 26.4118 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19546
ET Solar New Energy | ET-P660245WB | 245 W Polycrystalline Module, Black frame | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar New Energy | ET-P660245WBZ | 245 W Polycrystalline Module, Zero Rack, Black Frame | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar New Energy | ET-P660245WBZAC | 245 W DC, Polycrystalline ACPV Module, Zero Rack, Black Frame | UL 1741 | 245 | 219 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar New Energy | ET-P660245WW | 245 W Polycrystalline Module, Zero Rack | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar New Energy | ET-P660245WWZ | 245 W Polycrystalline Module, Zero Rack | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.2 | 8.05 | 30.43 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6821 | 26.9423 | 6.5467 | 27.6336 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18498
ET Solar New Energy | ET-P660250BAC | 250 W DC, Polycrystalline ACPV Module, Black Frame | UL 1741 | 250 | 223.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar New Energy | ET-P660250BB | 250 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 250 | 224.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.47 | 8.24 | 30.34 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6565 | 29.4935 | 6.5936 | 26.587 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar New Energy | ET-P660250BBAC | 250 W DC, Polycrystalline ACPV Module, Black Frame, Black Backsheet | UL 1741 | 250 | 216.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.47 | 8.24 | 30.34 | 52.2 | -0.475 | 0.029 | -0.349 | -0.025 | -0.456 | 1.6565 | 29.4935 | 6.5936 | 26.587 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar New Energy | ET-P660250BBZ | 250 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 250 | 224.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.47 | 8.24 | 30.34 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6565 | 29.4935 | 6.5936 | 26.587 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar New Energy | ET-P660250BBZAC | 250 W DC, Polycrystalline ACPV Module, Zero Rack, Black Frame, Black Backsheet | UL 1741 | 250 | 216.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.76 | 37.47 | 8.24 | 30.34 | 52.2 | -0.475 | 0.029 | -0.349 | -0.025 | -0.456 | 1.6565 | 29.4935 | 6.5936 | 26.587 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar New Energy | ET-P660250WB | 250 W Polycrystalline Module, Black Frame | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar New Energy | ET-P660250WBAC | 250 W DC, Polycrystalline ACPV Module, Black Frame | UL 1741 | 250 | 225.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7 | 27.19 | 6.62 | 27.89 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18489
ET Solar New Energy | ET-P660250WBZ | 250 W Polycrystalline Module, Zero Rack, Black Frame | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar New Energy | ET-P660250WBZAC | 250 W DC, Polycrystalline ACPV Module, Zero Rack, Black Frame | UL 1741 | 250 | 223.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 46.8 | -0.465 | 0.056 | -0.465 | 0 | -0.333 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar New Energy | ET-P660250WW | 250 W Polycrystalline Module | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar New Energy | ET-P660250WWZ | 250 W Polycrystalline Module, Zero Rack | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.8 | 37.44 | 8.14 | 30.71 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.7009 | 27.1902 | 6.6198 | 27.8879 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.18499
ET Solar New Energy | ET-P660255BB | 255 W Polycrystalline Module, Black Backsheet, Black Frame | UL 1703 | 255 | 229 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6585 | 30.0476 | 6.6016 | 27.0865 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar New Energy | ET-P660255BBAC | 255 W DC, Polycrystalline ACPV Module, Black Backsheet, Black Frame | UL 1741 | 255 | 229 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.66 | 30.05 | 6.6 | 27.09 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19562
ET Solar New Energy | ET-P660255BBZ | 255 W Polycrystalline Module, Zero Rack, Black Backsheet, Black Frame | UL 1703 | 255 | 229 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.6585 | 30.0476 | 6.6016 | 27.0865 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19543
ET Solar New Energy | ET-P660255BBZAC | 255 W DC, Polycrystalline ACPV Module, Black Backsheet, Black Zero Rack Frame | UL 1741 | 255 | 229 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 46.5 | -0.458 | 0.04 | -0.35 | 0.02 | -0.44 | 1.66 | 30.05 | 6.6 | 27.09 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19562
ET Solar New Energy | ET-P660255WB | 255 W Polycrystalline Module, Black Frame | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
ET Solar New Energy | ET-P660255WBAC | 255 W DC, Polycrystalline ACPV Module ,White Backsheet, Black Frame | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.01 | 6.57 | 27.41 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19536
ET Solar New Energy | ET-P660255WBZ | 255 W Polycrystalline Module, Zero Rack, Black Frame | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
ET Solar New Energy | ET-P660255WBZAC | 255 W DC, Polycrystalline ACPV Module, White Backsheet, Black Zero Rack Frame | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.01 | 6.57 | 27.41 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19536
ET Solar New Energy | ET-P660255WW | 255 W Polycrystalline Module | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
ET Solar New Energy | ET-P660255WWAC | 255 W DC, Polycrystalline ACPV Module, White Backsheet, White Frame | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.01 | 6.57 | 27.41 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19536
ET Solar New Energy | ET-P660255WWZ | 255 W Polycrystalline Module, Zero Rack | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6559 | 30.0092 | 6.5663 | 27.4115 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19488
ET Solar New Energy | ET-P660255WWZAC | 255 W DC, Polycrystalline ACPV Module, White Backsheet, White Zero Rack Frame | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.82 | 37.54 | 8.25 | 30.91 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.01 | 6.57 | 27.41 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19536
ET Solar New Energy | ET-M660260BB | 260 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 260 | 236.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.01 | 38.22 | 8.49 | 30.63 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.6357 | 30.3035 | 6.8251 | 28.1047 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19064
ET Solar New Energy | ET-M660260WW | 260 W Monocrystalline Module | UL 1703 | 260 | 234.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6308 | 60 | 1 | N | 8.89 | 37.8 | 8.49 | 30.65 | 46.1 | -0.45 | 0.04 | -0.32 | -0.02 | -0.43 | 1.696 | 29.1658 | 6.7539 | 27.7713 | Rack | Flat Plate | 0.992 | 1.644 | 1 | 0.19025
ET Solar New Energy | ET-P660260WB | 260 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 260 | 237 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.07 | 38.16 | 8.5 | 30.59 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6624 | 30.2766 | 6.7782 | 28.0531 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19358
ET Solar New Energy | ET-P660260WBAC | 260 W DC, Polycrystalline ACPV Module, White Backsheet, Black Frame | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.56 | 6.57 | 27.92 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19511
ET Solar New Energy | ET-P660260WBZ | 260 W Polycrystalline Module, Zero Rack, Black Frame | UL 1703 | 260 | 235.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6579 | 30.5626 | 6.5743 | 27.917 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19489
ET Solar New Energy | ET-P660260WBZAC | 260 W DC, Polycrystalline ACPV Module, White Backsheet, Black Zero Rack Frame | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.56 | 6.57 | 27.92 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19511
ET Solar New Energy | ET-P660260WW | 260 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 260 | 237 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.07 | 38.16 | 8.5 | 30.59 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6624 | 30.2766 | 6.7782 | 28.0531 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19358
ET Solar New Energy | ET-P660260WWAC | 260 W DC, Polycrystalline ACPV Module, White Backsheet, White Frame | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.56 | 6.57 | 27.92 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19511
ET Solar New Energy | ET-P660260WWZ | 260 W Polycrystalline Module, Zero Rack | UL 1703 | 260 | 235.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.6579 | 30.5626 | 6.5743 | 27.917 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19489
ET Solar New Energy | ET-P660260WWZAC | 260 W DC, Polycrystalline ACPV Module, White Backsheet, White Zero Rack Frame | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.84 | 38.09 | 8.26 | 31.48 | 45.5 | -0.45 | 0.04 | -0.33 | 0.01 | -0.41 | 1.66 | 30.56 | 6.57 | 27.92 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19511
ET Solar New Energy | ET-M660265BB | 265 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 265 | 241.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.1 | 38.29 | 8.65 | 30.64 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.6665 | 30.3134 | 6.9537 | 28.1139 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19063
ET Solar New Energy | ET-M660265WB | 265 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 265 | 241.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.1 | 38.29 | 8.65 | 30.64 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6665 | 30.3134 | 6.9537 | 28.1139 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19063
ET Solar New Energy | ET-M660265WW | 265 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 265 | 241.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.1 | 38.29 | 8.65 | 30.64 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6665 | 30.3134 | 6.9537 | 28.1139 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19063
ET Solar New Energy | ET-P660265WB | 265 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 265 | 241.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.24 | 38.29 | 8.62 | 30.74 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6859 | 30.425 | 6.8739 | 28.1906 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
ET Solar New Energy | ET-P660265WW | 265 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 265 | 241.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.24 | 38.29 | 8.62 | 30.74 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6859 | 30.425 | 6.8739 | 28.1906 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356 |  | 2018-04-02
ET Solar New Energy | ET-M660270BB | 270 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 270 | 245.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.12 | 38.68 | 8.76 | 30.83 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.6877 | 30.5014 | 7.0422 | 28.2882 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19066
ET Solar New Energy | ET-M660270WB | 270 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 270 | 246.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.12 | 38.68 | 8.76 | 30.83 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6877 | 30.5014 | 7.0422 | 28.2882 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19066
ET Solar New Energy | ET-M660270WW | 270 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 270 | 246.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.12 | 38.68 | 8.76 | 30.83 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6877 | 30.5014 | 7.0422 | 28.2882 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19066
ET Solar New Energy | ET-P660270WB | 270 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 270 | 246.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.31 | 38.72 | 8.72 | 30.97 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7054 | 30.6527 | 6.9537 | 28.4016 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
ET Solar New Energy | ET-P660270WW | 270 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 270 | 246.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.31 | 38.72 | 8.72 | 30.97 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7054 | 30.6527 | 6.9537 | 28.4016 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361 |  | 2018-04-02
ET Solar New Energy | ET-M660275BB | 275 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 275 | 250.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.14 | 39.08 | 8.88 | 30.97 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.7108 | 30.6399 | 7.1386 | 28.4167 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar New Energy | ET-M660275WB | 275 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 275 | 251.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.14 | 39.08 | 8.88 | 30.97 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7108 | 30.6399 | 7.1386 | 28.4167 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar New Energy | ET-M660275WW | 275 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 275 | 251.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.14 | 39.08 | 8.88 | 30.97 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7108 | 30.6399 | 7.1386 | 28.4167 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar New Energy | ET-P660275WB | 275 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 275 | 251.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.35 | 38.92 | 8.78 | 31.32 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7172 | 30.9991 | 7.0015 | 28.7225 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356
ET Solar New Energy | ET-P660275WW | 275 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 275 | 251.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.35 | 38.92 | 8.78 | 31.32 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7172 | 30.9991 | 7.0015 | 28.7225 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19356 |  | 2018-04-02
ET Solar New Energy | ET-M660280BB | 280 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 280 | 255.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar New Energy | ET-M660280WB | 280 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062
ET Solar New Energy | ET-M660280WW | 280 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.23 | 39.26 | 9.03 | 31.01 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 30.6795 | 7.2592 | 28.4534 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19062 |  | 2018-04-02
ET Solar New Energy | ET-M6605280WW | 280 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 280 | 257.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 9.29 | 39.12 | 8.91 | 31.43 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.6379 | 31.4977 | 7.1631 | 29.5221 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-P660280WB | 280 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 280 | 255.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.47 | 39.16 | 8.84 | 31.68 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7289 | 31.3554 | 7.0494 | 29.0527 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361
ET Solar New Energy | ET-P660280WW | 280 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 280 | 255.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.47 | 39.16 | 8.84 | 31.68 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7289 | 31.3554 | 7.0494 | 29.0527 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19361 |  | 2018-04-02
ET Solar New Energy | ET-M660285BB | 285 W Monocrystalline Module, Black Backsheet, Black Frame | UL 1703 | 285 | 259.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.4 | -0.43 | 0.0618 | -0.303 | -0.0242 | -0.451 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065
ET Solar New Energy | ET-M660285WB | 285 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065
ET Solar New Energy | ET-M660285WW | 285 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7243 | 31.5105 | 7.1949 | 29.2241 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19065 |  | 2018-04-02
ET Solar New Energy | ET-M6605285WW | 285 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 285 | 262.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 9.46 | 39.18 | 8.95 | 31.85 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.6453 | 31.9186 | 7.1952 | 29.9166 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-P672285WB | 285 W Polycrystalline Module, Black Frame | UL 1703 | 285 | 254.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.52 | 44.35 | 7.91 | 36.03 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5287 | 35.7661 | 6.3872 | 32.9263 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
ET Solar New Energy | ET-P672285WBG | 285 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 285 | 256.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.55 | 44.72 | 7.95 | 35.86 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5515 | 35.3011 | 6.4275 | 32.0574 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19217
ET Solar New Energy | ET-P672285WW | 285 W Polycrystalline Module | UL 1703 | 285 | 254.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.52 | 44.35 | 7.91 | 36.03 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5287 | 35.7661 | 6.3872 | 32.9263 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
ET Solar New Energy | ET-P672285WWG | 285 W Polycrystalline Module, White Frame, White Backsheet | UL 1703 | 285 | 256.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.55 | 44.72 | 7.95 | 35.86 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5515 | 35.3011 | 6.4275 | 32.0574 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19217
ET Solar New Energy | ET-M660290WB | 290 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 290 | 265.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.59 | 39.68 | 9.03 | 32.12 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 31.7777 | 7.2592 | 29.4719 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19064
ET Solar New Energy | ET-M660290WW | 290 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 290 | 265.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.59 | 39.68 | 9.03 | 32.12 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7397 | 31.7777 | 7.2592 | 29.4719 | Rack | Flat Plate | 0.986 | 1.634 | 1 | 0.19064
ET Solar New Energy | ET-M6605290WW | 290 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 9.59 | 39.68 | 9.03 | 32.12 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.66 | 32.1891 | 7.2595 | 30.1702 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-P672290WB | 290 W Polycrystalline Module, Black Frame | UL 1703 | 290 | 259.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.61 | 44.5 | 8 | 36.25 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5461 | 35.9845 | 6.4599 | 33.1274 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
ET Solar New Energy | ET-P672290WBG | 290 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 290 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.62 | 44.75 | 8.08 | 35.92 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5768 | 35.3602 | 6.5326 | 32.1111 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19226
ET Solar New Energy | ET-P672290WW | 290 W Polycrystalline Module | UL 1703 | 290 | 259.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.61 | 44.5 | 8 | 36.25 | 46.8 | -0.463 | 0.104 | -0.355 | 0.065 | -0.517 | 1.5461 | 35.9845 | 6.4599 | 33.1274 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19185
ET Solar New Energy | ET-P672290WWG | 290 WPolycrystalline Module, White Frame, White Backsheet | UL 1703 | 290 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.62 | 44.75 | 8.08 | 35.92 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5768 | 35.3602 | 6.5326 | 32.1111 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19226
ET Solar New Energy | ET-M6605295WW | 295 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 9.65 | 39.78 | 9.12 | 32.35 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.6765 | 32.4196 | 7.3319 | 30.3862 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-P672295WB | 295 W Polycrystalline Module, Black Frame | UL 1703 | 295 | 263.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6945 | 32.7533 | 6.7469 | 30.0578 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18814
ET Solar New Energy | ET-P672295WBG | 295 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5924 | 35.6063 | 6.5972 | 32.3346 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19221
ET Solar New Energy | ET-P672295WW | 295 W Polycrystalline Module | UL 1703 | 295 | 263.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6945 | 32.7533 | 6.7469 | 30.0578 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18814
ET Solar New Energy | ET-P672295WWG | 295 W Polycrystalline Module, White Frame, White backsheet | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.68 | 44.78 | 8.16 | 36.17 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5924 | 35.6063 | 6.5972 | 32.3346 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19221
ET Solar New Energy | ET-M6605300WW | 300 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 9.69 | 39.97 | 9.22 | 32.54 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.6949 | 32.6101 | 7.4123 | 30.5647 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-P672300WB | 300 W Polycrystalline Module, Black Frame | UL 1703 | 300 | 268.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6986 | 33.2151 | 6.7634 | 30.4816 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18807
ET Solar New Energy | ET-P672300WBG | 300 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5963 | 36.1083 | 6.6134 | 32.7905 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19214
ET Solar New Energy | ET-P672300WW | 300 W Polycrystalline Module | UL 1703 | 300 | 268.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.6986 | 33.2151 | 6.7634 | 30.4816 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18807
ET Solar New Energy | ET-P672300WWG | 300 W Polycrystalline Module, White Frame, White Backsheet | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 44.89 | 8.18 | 36.68 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.5963 | 36.1083 | 6.6134 | 32.7905 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19214
ET Solar New Energy | ET-M6605305WW | 305 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 305 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 9.78 | 40.26 | 9.31 | 32.76 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.7115 | 32.8305 | 7.4846 | 30.7714 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-P672305WB | 305 W Polycrystalline Module, Black Frame | UL 1703 | 305 | 272.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.78 | 45.12 | 8.21 | 37.18 | 47.7 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.7049 | 33.6679 | 6.7882 | 30.8972 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18819
ET Solar New Energy | ET-P672305WBG | 305 W Polycrystalline Module, Black Frame, White Backsheet | UL 1703 | 305 | 275.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.78 | 45.12 | 8.21 | 37.18 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.6022 | 36.6005 | 6.6377 | 33.2375 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19227
ET Solar New Energy | ET-P672305WW | 305 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 305 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.04 | 45.18 | 8.42 | 36.23 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6234 | 35.9571 | 6.7282 | 33.7152 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138
ET Solar New Energy | ET-P672305WWG | 305 W Polycrystalline Module, White Frame, White Backsheet | UL 1703 | 305 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 8.78 | 45.12 | 8.21 | 37.18 | 45.7 | -0.452 | 0.04 | -0.34 | 0.02 | -0.43 | 1.6022 | 36.6005 | 6.6377 | 33.2375 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19227
ET Solar New Energy | ET-M6605310WW | 310 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 9.86 | 40.75 | 9.4 | 32.98 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.728 | 33.051 | 7.557 | 30.978 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-P672310WB | 310 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 310 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 45.65 | 8.49 | 36.54 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6369 | 36.2647 | 6.7841 | 34.0037 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19149
ET Solar New Energy | ET-P672310WW | 310 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 310 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 45.65 | 8.49 | 36.54 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6369 | 36.2647 | 6.7841 | 34.0037 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19149
ET Solar New Energy | ET-M6605315WW | 315 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 9.93 | 41.05 | 9.49 | 33.2 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.7445 | 33.2715 | 7.6294 | 31.1846 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-P672315WB | 315 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 315 | 287.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.12 | 45.75 | 8.56 | 36.81 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6504 | 36.5327 | 6.84 | 34.255 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1914
ET Solar New Energy | ET-P672315WW | 315 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 315 | 287.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.12 | 45.75 | 8.56 | 36.81 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6504 | 36.5327 | 6.84 | 34.255 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1914
ET Solar New Energy | ET-M6605320WW | 320 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 320 | 295.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 9.99 | 41.34 | 9.58 | 33.4 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.7611 | 33.4719 | 7.7017 | 31.3725 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M672320WB | 320 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 320 | 292.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 46.31 | 8.65 | 37 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6892 | 36.1108 | 6.9511 | 33.994 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
ET Solar New Energy | ET-M672320WW | 320 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 320 | 292.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.08 | 46.31 | 8.65 | 37 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.6892 | 36.1108 | 6.9511 | 33.994 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
ET Solar New Energy | ET-P672320WB | 320 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 320 | 291.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.24 | 45.94 | 8.62 | 37.13 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6619 | 36.8503 | 6.888 | 34.5528 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138
ET Solar New Energy | ET-P672320WW | 320 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 320 | 291.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.24 | 45.94 | 8.62 | 37.13 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6619 | 36.8503 | 6.888 | 34.5528 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19138 |  | 2018-04-02
ET Solar New Energy | ET-M6605325WW | 325 W, 60 cell monocrystalline module, white backsheet and frame | UL 1703 | 325 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.637 | 60 | 1 | N | 10.08 | 41.87 | 9.66 | 33.63 | 45.1 | -0.3947 | 0.0394 | -0.3011 |  |  | 1.7758 | 33.7024 | 7.766 | 31.5885 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M672325WB | 325 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 325 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.11 | 46.54 | 8.76 | 37.11 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7107 | 36.2181 | 7.0395 | 34.0951 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19064
ET Solar New Energy | ET-M672325WW | 325 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 325 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.11 | 46.54 | 8.76 | 37.11 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7107 | 36.2181 | 7.0395 | 34.0951 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19064
ET Solar New Energy | ET-P672325WB | 325 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 325 | 296.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.28 | 46.31 | 8.72 | 37.28 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6812 | 36.9992 | 6.9679 | 34.6924 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19139
ET Solar New Energy | ET-P672325WW | 325 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 325 | 296.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.28 | 46.31 | 8.72 | 37.28 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6812 | 36.9992 | 6.9679 | 34.6924 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19139 |  | 2018-04-02
ET Solar New Energy | ET-M672330WB | 330 W Monocrystalline Module, White Backsheet, Black Frame | UL 1741 | 330 | 301.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.29 | 46.64 | 8.79 | 37.55 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7166 | 36.6475 | 7.0636 | 34.4993 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19063
ET Solar New Energy | ET-M672330WW | 330 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 330 | 301.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.29 | 46.64 | 8.79 | 37.55 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7166 | 36.6475 | 7.0636 | 34.4993 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19063
ET Solar New Energy | ET-P672330WB | 330 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 330 | 301.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.35 | 46.65 | 8.78 | 37.58 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6928 | 37.2969 | 7.0158 | 34.9715 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19132
ET Solar New Energy | ET-P672330WW | 330 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 330 | 301.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.35 | 46.65 | 8.78 | 37.58 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.6928 | 37.2969 | 7.0158 | 34.9715 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19132 |  | 2018-04-02
ET Solar New Energy | ET-M672335WB | 335 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.33 | 46.75 | 8.83 | 37.94 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7244 | 37.0282 | 7.0957 | 34.8576 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1906
ET Solar New Energy | ET-M672335WW | 335 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.33 | 46.75 | 8.83 | 37.94 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7244 | 37.0282 | 7.0957 | 34.8576 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.1906 |  | 2018-04-02
ET Solar New Energy | ET-P672335WB | 335 W Polycrystalline Module, White Backsheet, Black Frame | UL 1703 | 335 | 306 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.47 | 46.83 | 8.84 | 37.9 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7043 | 37.6145 | 7.0638 | 35.2693 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19137
ET Solar New Energy | ET-P672335WW | 335 W Polycrystalline Module, White Backsheet, White Frame | UL 1703 | 335 | 306 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9227 | 72 | 1 | N | 9.47 | 46.83 | 8.84 | 37.9 | 45.3 | -0.422 | 0.0551 | -0.313 | 0.0599 | -0.435 | 1.7043 | 37.6145 | 7.0638 | 35.2693 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19137 |  | 2018-04-02
ET Solar New Energy | ET-M672340WB | 340 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 340 | 310.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.41 | 46.91 | 8.91 | 38.17 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.74 | 37.2526 | 7.16 | 35.0689 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19065
ET Solar New Energy | ET-M672340WW | 340 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 340 | 310.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.41 | 46.91 | 8.91 | 38.17 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.74 | 37.2526 | 7.16 | 35.0689 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19065 |  | 2018-04-02
ET Solar New Energy | ET-M672345WB | 345 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.48 | 47.13 | 8.99 | 38.38 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7556 | 37.4576 | 7.2243 | 35.2619 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19061
ET Solar New Energy | ET-M672345WW | 345 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.48 | 47.13 | 8.99 | 38.38 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7556 | 37.4576 | 7.2243 | 35.2619 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19061 |  | 2018-04-02
ET Solar New Energy | ET-M6725345WW | 345 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 345 | 318.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 9.48 | 47.13 | 8.99 | 38.38 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.6167 | 38.9784 | 7.2448 | 35.8261 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M672350WB | 350 W Monocrystalline Module, White Backsheet, Black Frame | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.59 | 47.64 | 9.09 | 38.51 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7752 | 37.5845 | 7.3046 | 35.3813 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062
ET Solar New Energy | ET-M672350WW | 350 W Monocrystalline Module, White Backsheet, White Frame | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 9.59 | 47.64 | 9.09 | 38.51 | 45.2 | -0.421 | 0.0491 | -0.297 | -0.0035 | -0.418 | 1.7752 | 37.5845 | 7.3046 | 35.3813 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19062 |  | 2018-04-02
ET Solar New Energy | ET-M6725350WW | 350 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 350 | 323.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 9.59 | 47.64 | 9.09 | 38.51 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.6346 | 39.1105 | 7.3254 | 35.9475 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M6725355WW | 355 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 355 | 328.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 9.65 | 47.74 | 9.12 | 38.93 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.64 | 39.537 | 7.3495 | 36.3395 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M6725360WW | 360 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 360 | 333.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 9.69 | 47.96 | 9.22 | 39.05 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.658 | 39.6589 | 7.4301 | 36.4515 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M6725365WW | 365 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 365 | 337.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 9.77 | 48.22 | 9.27 | 39.38 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.667 | 39.994 | 7.4704 | 36.7596 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M6725370WW | 370 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 370 | 342.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 9.88 | 48.45 | 9.32 | 39.7 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.676 | 40.319 | 7.5107 | 37.0583 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M6725375WW | 375 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 375 | 347.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 9.93 | 49.04 | 9.37 | 40.02 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.685 | 40.644 | 7.551 | 37.357 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M6725380WW | 380 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 380 | 352.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 9.98 | 49.45 | 9.42 | 40.34 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.694 | 40.969 | 7.5913 | 37.6557 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M6725385WW | 385 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 385 | 356.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 10.03 | 49.84 | 9.47 | 40.65 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.703 | 41.2838 | 7.6316 | 37.9451 | [6 empty] | 2019-12-11
ET Solar New Energy | ET-M6725390WW | 390 W, 72 cell monocrystalline module, white backsheet and frame | UL 1703 | 390 | 361.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 1 | N | 10.08 | 50.24 | 9.52 | 40.96 | 45.2 | -0.3728 | 0.0639 | -0.2858 |  |  | 1.712 | 41.5987 | 7.6719 | 38.2345 | [6 empty] | 2019-12-11
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH390GL | 390 W, 144 half-cut cell, double glass bificial monocrystalline module,1500V max system Vdc | UL 61730 | 390 | 363.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.2 | 49.5 | 9.45 | 41.3 | 43.6 | -0.3755 | 0.0594 | -0.2998 |  |  | 1.9205 | 39.1261 | 7.8602 | 36.7045 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH390WW | 390 W 144 half-cut cell monocrystalline module, white backsheet and frame, 1500V max system Vdc | UL 61730 | 390 | 364 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 2 | N | 10.12 | 49.3 | 9.49 | 41.1 | 43.4 | -0.3734 | 0.0587 | -0.3003 |  |  | 1.9705 | 38.3338 | 7.9358 | 36.3876 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH395GL | 395 W, 144 half-cut cell, double glass bificial monocrystalline module,1500V max system Vdc | UL 61730 | 395 | 368.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.24 | 49.6 | 9.52 | 41.5 | 43.6 | -0.3755 | 0.0594 | -0.2998 |  |  | 1.9347 | 39.3155 | 7.9185 | 36.8823 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH395WW | 395 W 144 half-cut cell monocrystalline module, white backsheet and frame, 1500V max system Vdc | UL 61730 | 395 | 368.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 2 | N | 10.23 | 49.5 | 9.55 | 41.4 | 43.4 | -0.3734 | 0.0587 | -0.3003 |  |  | 1.9829 | 38.6136 | 7.9859 | 36.6532 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH400GL | 400 W, 144 half-cut cell, double glass bificial monocrystalline module,1500V max system Vdc | UL 61730 | 400 | 372.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.34 | 49.7 | 9.6 | 41.7 | 43.6 | -0.3755 | 0.0594 | -0.2998 |  |  | 1.951 | 39.505 | 7.985 | 37.06 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH400WW | 400 W 144 half-cut cell monocrystalline module, white backsheet and frame, 1500V max system Vdc | UL 61730 | 400 | 373.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 2 | N | 10.36 | 49.8 | 9.6 | 41.7 | 43.4 | -0.3734 | 0.0587 | -0.3003 |  |  | 1.9933 | 38.8934 | 8.0277 | 36.9188 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH405GL | 405 W, 144 half-cut cell, double glass bificial monocrystalline module,1500V max system Vdc | UL 61730 | 405 | 377.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.44 | 49.8 | 9.62 | 42.1 | 43.6 | -0.3755 | 0.0594 | -0.2998 |  |  | 1.9551 | 39.8839 | 8.0016 | 37.4155 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH405WW | 405 W 144 half-cut cell monocrystalline module, white backsheet and frame, 1500V max system Vdc | UL 61730 | 405 | 378.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 2 | N | 10.48 | 50.1 | 9.65 | 42 | 43.4 | -0.3734 | 0.0587 | -0.3003 |  |  | 2.0037 | 39.1732 | 8.0696 | 37.1844 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH410GL | 410 W, 144 half-cut cell, double glass bificial monocrystalline module,1500V max system Vdc | UL 61730 | 410 | 382.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.54 | 49.9 | 9.65 | 42.5 | 43.6 | -0.3755 | 0.0594 | -0.2998 |  |  | 1.9612 | 40.2629 | 8.0266 | 37.771 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH410WW | 410 W 144 half-cut cell monocrystalline module, white backsheet and frame, 1500V max system Vdc | UL 61730 | 410 | 383.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 72 | 2 | N | 10.6 | 50.4 | 9.69 | 42.3 | 43.4 | -0.3734 | 0.0587 | -0.3003 |  |  | 2.012 | 39.453 | 8.103 | 37.45 | [6 empty] | 2020-10-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH435TW | 435 W, 144 half-cut cell bificial monocrystalline module, transparent backhseet, silver frame, 1500V max system Vdc | UL 61730 | 435 | 406.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.36 | 49.1 | 10.66 | 40.8 | 43 | -0.383 | 0.0456 | -0.2767 |  |  | 2.1876 | 40.184 | 8.8092 | 37.8753 | [6 empty] | 2021-04-01
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH435WW | 435 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 435 | 406.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.39 | 48.7 | 10.64 | 40.9 | 43.3 | -0.3708 | 0.049 | -0.283 |  |  | 2.1398 | 40.2781 | 8.6101 | 38.1976 | [6 empty] | 2021-04-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH440TW | 440 W, 144 half-cut cell bificial monocrystalline module, transparent backhseet, silver frame, 1500V max system Vdc | UL 61730 | 440 | 411 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.48 | 49.2 | 10.73 | 41 | 43 | -0.383 | 0.0456 | -0.2767 |  |  | 2.202 | 40.381 | 8.867 | 38.061 | [6 empty] | 2021-04-01
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH440WW | 440 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 440 | 411.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.46 | 48.9 | 10.71 | 41.1 | 43.3 | -0.3708 | 0.049 | -0.283 |  |  | 2.1538 | 40.4751 | 8.6667 | 38.3844 | [6 empty] | 2021-04-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH445TW | 445 W, 144 half-cut cell bificial monocrystalline module, transparent backhseet, silver frame, 1500V max system Vdc | UL 61730 | 445 | 415.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.52 | 49.4 | 10.8 | 41.2 | 43 | -0.383 | 0.0456 | -0.2767 |  |  | 2.2164 | 40.578 | 8.9248 | 38.2467 | [6 empty] | 2021-04-01
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH445WW | 445 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 445 | 416.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.53 | 49.1 | 10.78 | 41.3 | 43.3 | -0.3708 | 0.049 | -0.283 |  |  | 2.1679 | 40.672 | 8.7234 | 38.5712 | [6 empty] | 2021-04-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH450TW | 450 W, 144 half-cut cell bificial monocrystalline module, transparent backhseet, silver frame, 1500V max system Vdc | UL 61730 | 450 | 420.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.58 | 49.6 | 10.87 | 41.4 | 43 | -0.383 | 0.0456 | -0.2767 |  |  | 2.2307 | 40.775 | 8.9827 | 38.4323 | [6 empty] | 2021-04-01
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH450WW | 450 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 450 | 421 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.6 | 49.3 | 10.85 | 41.5 | 43.3 | -0.3708 | 0.049 | -0.283 |  |  | 2.182 | 40.869 | 8.78 | 38.758 | [6 empty] | 2021-04-21
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH455TW | 455 W, 144 half-cut cell bificial monocrystalline module, transparent backhseet, silver frame, 1500V max system Vdc | UL 61730 | 455 | 425.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.65 | 49.8 | 10.93 | 41.6 | 43 | -0.383 | 0.0456 | -0.2767 |  |  | 2.243 | 40.9719 | 9.0323 | 38.618 | [6 empty] | 2021-04-01
ET SOLAR POWER HONGKONG LIMITED | ET-M672BH455WW | 455 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 455 | 425.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.66 | 49.5 | 10.92 | 41.7 | 43.3 | -0.3708 | 0.049 | -0.283 |  |  | 2.1961 | 41.066 | 8.8366 | 38.9448 | [6 empty] | 2021-04-21
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH530TB | 530 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, black frame, 1500V max system Vdc | UL 61730 | 530 | 495.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.72 | 49.3 | 12.83 | 41.31 | 43.4 | -0.3722 | 0.0376 |  |  |  | 2.588 | 39.405 | 10.374 | 39.11 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH530TW | 530 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 61730 | 530 | 495.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.72 | 49.3 | 12.83 | 41.31 | 43.4 | -0.3722 | 0.0376 | -0.2872 |  |  | 2.588 | 39.405 | 10.374 | 39.11 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH530WB | 530 W, 144 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 530 | 495.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.72 | 49.3 | 12.83 | 41.31 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.604 | 39.359 | 10.455 | 38.411 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH530WW | 530 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 530 | 495.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.72 | 49.3 | 12.83 | 41.31 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.604 | 39.359 | 10.455 | 38.411 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH535TB | 535 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, black frame, 1500V max system Vdc | UL 61730 | 535 | 500.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.79 | 49.45 | 12.9 | 41.47 | 43.4 | -0.3722 | 0.0376 |  |  |  | 2.6021 | 39.5576 | 10.4306 | 39.2615 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH535TW | 535 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 61730 | 535 | 500.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.79 | 49.45 | 12.9 | 41.47 | 43.4 | -0.3722 | 0.0376 | -0.2872 |  |  | 2.6021 | 39.5576 | 10.4306 | 39.2615 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH535WB | 535 W, 144 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 535 | 500.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.79 | 49.45 | 12.9 | 41.47 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.6182 | 39.5114 | 10.512 | 38.5598 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH535WW | 535 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 535 | 500.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.79 | 49.45 | 12.9 | 41.47 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.6182 | 39.5114 | 10.512 | 38.5598 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH540TB | 540 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, black frame, 1500V max system Vdc | UL 61730 | 540 | 505 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.86 | 49.6 | 12.97 | 41.64 | 43.4 | -0.3722 | 0.0376 |  |  |  | 2.6162 | 39.7198 | 10.4872 | 39.4224 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH540TW | 540 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 61730 | 540 | 505 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.86 | 49.6 | 12.97 | 41.64 | 43.4 | -0.3722 | 0.0376 | -0.2872 |  |  | 2.6162 | 39.7198 | 10.4872 | 39.4224 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH540WB | 540 W, 144 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 540 | 505.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.86 | 49.6 | 12.97 | 41.64 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.6324 | 39.6734 | 10.5691 | 38.7178 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH540WW | 540 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 540 | 505.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.86 | 49.6 | 12.97 | 41.64 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.6324 | 39.6734 | 10.5691 | 38.7178 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH545TB | 545 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, black frame, 1500V max system Vdc | UL 61730 | 545 | 509.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.93 | 49.75 | 13.04 | 41.8 | 43.4 | -0.3722 | 0.0376 |  |  |  | 2.6304 | 39.8724 | 10.5438 | 39.5739 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH545TW | 545 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 61730 | 545 | 509.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.93 | 49.75 | 13.04 | 41.8 | 43.4 | -0.3722 | 0.0376 | -0.2872 |  |  | 2.6304 | 39.8724 | 10.5438 | 39.5739 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH545WB | 545 W, 144 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 545 | 510.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.93 | 49.75 | 13.04 | 41.8 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.6466 | 39.8259 | 10.6261 | 38.8666 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH545WW | 545 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 545 | 510.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 13.93 | 49.75 | 13.04 | 41.8 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.6466 | 39.8259 | 10.6261 | 38.8666 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH550TB | 550 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, black frame, 1500V max system Vdc | UL 61730 | 550 | 514.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 14 | 49.9 | 13.11 | 41.96 | 43.4 | -0.3722 | 0.0376 |  |  |  | 2.6445 | 40.025 | 10.6004 | 39.7254 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH550TW | 550 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 61730 | 550 | 514.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 14 | 49.9 | 13.11 | 41.96 | 43.4 | -0.3722 | 0.0376 | -0.2872 |  |  | 2.6445 | 40.025 | 10.6004 | 39.7254 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH550WB | 550 W, 144 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 550 | 514.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 14 | 49.9 | 13.11 | 41.96 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.6608 | 39.9783 | 10.6832 | 39.0154 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH550WW | 550 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 550 | 514.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 14 | 49.9 | 13.11 | 41.96 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.6608 | 39.9783 | 10.6832 | 39.0154 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH555TB | 555 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, black frame, 1500V max system Vdc | UL 61730 | 555 | 519.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 14.07 | 50.05 | 13.18 | 42.11 | 43.4 | -0.3722 | 0.0376 |  |  |  | 2.6586 | 40.1681 | 10.657 | 39.8674 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH555TW | 555 W, 144 half-cut cell bifacial monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 61730 | 555 | 519.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 14.07 | 50.05 | 13.18 | 42.11 | 43.4 | -0.3722 | 0.0376 | -0.2872 |  |  | 2.6586 | 40.1681 | 10.657 | 39.8674 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH555WB | 555 W, 144 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 555 | 519.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 14.07 | 50.05 | 13.18 | 42.11 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.675 | 40.1212 | 10.7402 | 39.1549 | [6 empty] | 2021-09-01 | 2021-09-13
ET SOLAR POWER HONGKONG LIMITED | ET-M772BH555WW | 555 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 555 | 519.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.56 | 72 | 2 | N | 14.07 | 50.05 | 13.18 | 42.11 | 43.6 | -0.3657 | 0.0368 | -0.2752 |  |  | 2.675 | 40.1212 | 10.7402 | 39.1549 | [6 empty] | 2021-09-01 | 2021-09-13
Exeltech | AM24-1-B-6-0-00 | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 211.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6997 | 96 | 1 | N | 5.28 | 59.5 | 4.95 | 48.6 | 47.3 | -0.4929 | 0.0406 | -0.3588 | -0.015 | -0.4787 | 0.99205 | 46.3491 | 3.825 | 43.4842 | Rack | Flat Plate | 1.065 | 1.596 | 1 | 0.19158
First Solar, Inc. | FS-267 | 67.5 W Thin Film CdTe Module | UL 1703 | 67.5 | 64.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 116 | 1 | N | 1.18 | 87 | 1.05 | 64.2 | 45.9 | -0.16723 | 0.0487 | -0.2518 | 0.082733 | -0.24377 | 0.21832 | 64.394 | 0.84208 | 61.1937 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.20827 |  | 2018-12-17
First Solar, Inc. | FS-367 | 67.5 W Thin Film CdTe Module | UL 1703 | 67.5 | 64 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 1.74 | 60.5 | 1.41 | 47.8 | 44.9 | -0.2246 | 0.0011 | -0.1714 | 0 | -0.131 | 0.27115 | 45.4346 | 1.1479 | 46.3216 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.18252 |  | 2018-12-17
First Solar, Inc. | FS-270 | 70 W Thin Film CdTe Module | UL 1703 | 70 | 67.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 116 | 1 | N | 1.19 | 89 | 1.07 | 67.9 | 45.9 | -0.16723 | 0.0487 | -0.2518 | 0.082733 | -0.24377 | 0.22248 | 68.1051 | 0.85812 | 64.7204 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.21645 |  | 2018-12-17
First Solar, Inc. | FS-370 | 70 W Thin Film CdTe Module | UL 1703 | 70 | 66.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 1.74 | 60.6 | 1.46 | 48.1 | 44.9 | -0.2246 | 0.0011 | -0.1714 | 0 | -0.131 | 0.28077 | 45.7198 | 1.1886 | 46.6124 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.18338 |  | 2018-12-17
First Solar, Inc. | FS-272 | 72.5 W Thin Film CdTe Module | UL 1703 | 72.5 | 69.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 116 | 1 | N | 1.19 | 90 | 1.07 | 67.9 | 44.9 | -0.1655 | 0.0476 | -0.2376 | 0.0014 | -0.1666 | 0.21 | 66.7508 | 0.86 | 64.7396 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19335 |  | 2018-12-17
First Solar, Inc. | FS-372 | 72.5 W Thin Film CdTe Module | UL 1703 | 72.5 | 68.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 1.75 | 61.4 | 1.46 | 49.5 | 44.9 | -0.2246 | 0.0011 | -0.1714 | 0 | -0.131 | 0.29019 | 47.5473 | 1.1517 | 46.9615 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19031 |  | 2018-12-17
First Solar, Inc. | FS-275 | 75 W Thin Film CdTe Module | UL 1703 | 75 | 72.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 116 | 1 | N | 1.2 | 92 | 1.08 | 69.4 | 44.9 | -0.1655 | 0.0476 | -0.2376 | 0.0014 | -0.1666 | 0.21196 | 68.2254 | 0.86804 | 66.1698 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19282 |  | 2018-12-17
First Solar, Inc. | FS-375 | 75 W Thin Film CdTe Module | UL 1703 | 75 | 71.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 1.76 | 61.6 | 1.51 | 49.8 | 44.9 | -0.2246 | 0.0011 | -0.1714 | 0 | -0.131 | 0.30012 | 47.8355 | 1.1911 | 47.2462 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19142 |  | 2018-12-17
First Solar, Inc. | FS-377 | 77W Thin Film CdTe Module | UL 1703 | 77 | 73.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 1.75 | 61.7 | 1.54 | 50.4 | 44.9 | -0.2246 | 0.0011 | -0.1714 | 0 | -0.131 | 0.30614 | 48.9147 | 1.2153 | 46.3403 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19448 |  | 2018-12-17
First Solar, Inc. | FS-277 | 77.5 W Thin Film CdTe Module | UL 1703 | 77.5 | 74.6 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 116 | 1 | N | 1.21 | 93 | 1.09 | 70.9 | 44.9 | -0.1655 | 0.0476 | -0.2376 | 0.0014 | -0.1666 | 0.21393 | 69.7 | 0.87607 | 67.6 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19239 |  | 2018-12-17
First Solar, Inc. | FS-280 | 80 W CdTe Thin Film Module | UL 1703 | 80 | 76.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 116 | 1 | N | 1.22 | 91.5 | 1.12 | 71.2 | 45.9 | -0.16723 | 0.0487 | -0.2518 | 0.082733 | -0.24377 | 0.21981 | 69.9949 | 0.90019 | 67.886 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19232 |  | 2018-12-17
First Solar, Inc. | FS-380 | 80 W Thin Film CdTe Module | UL 1703 | 80 | 76 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 1.76 | 61.7 | 1.58 | 50.7 | 44.9 | -0.2246 | 0.0011 | -0.1714 | 0 | -0.131 | 0.3141 | 49.2059 | 1.2469 | 46.6161 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19319 |  | 2018-12-17
First Solar, Inc. | FS-382 | 82.5 W Thin Film CdTe Module | UL 1703 | 82.5 | 78.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 1.78 | 62 | 1.62 | 51 | 44.9 | -0.2246 | 0.0011 | -0.1714 | 0 | -0.131 | 0.32205 | 49.4971 | 1.2784 | 46.8919 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19322 |  | 2018-12-17
First Solar, Inc. | FS-385 | 85 W Thin Film CdTe Module | UL 1703 | 85 | 80.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 1.98 | 61 | 1.76 | 48.5 | 44.9 | -0.2246 | 0.0011 | -0.1714 | 0 | -0.131 | 0.34165 | 49.0922 | 1.3976 | 46.0358 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19732 |  | 2018-12-17
First Solar, Inc. | FS-387 | 87.5 W Thin Film CdTe Module | UL 1703 | 87.5 | 83.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 1.98 | 61 | 1.78 | 49.2 | 48.4 | -0.183 | 0.043 | -0.236 | 0.033 | -0.213 | 0.36244 | 46.9414 | 1.4135 | 46.7315 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19444 |  | 2018-12-17
First Solar, Inc. | FS-387-Plus | 87.5 W Thin Film CdTe Module | UL 1703 | 87.5 | 82.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 146 | 1 | N | 2.26 | 56 | 2.01 | 43.6 | 44.6 | -0.2492 | 0.0391 | -0.2499 | 0.0013 | -0.2817 | 0.4 | 43.24 | 1.63 | 40.75 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19767 |  | 2018-12-17
First Solar, Inc. | FS-390 | 90 W Thin Film CdTe Module | UL 1703 | 90 | 85.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 2.04 | 61 | 1.83 | 49.2 | 48.4 | -0.183 | 0.043 | -0.236 | 0.033 | -0.213 | 0.37262 | 46.9414 | 1.4532 | 46.7315 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19435 |  | 2018-12-17
First Solar, Inc. | FS-390-Plus | 90 W Thin Film CdTe Module | UL 1703 | 90 | 85.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 146 | 1 | N | 2.27 | 56.9 | 2.03 | 44.4 | 44.6 | -0.2492 | 0.0391 | -0.2499 | 0.0013 | -0.2817 | 0.4 | 44.03 | 1.65 | 41.5 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19569 |  | 2018-12-17
First Solar, Inc. | FS-490 | 90 W Thin Film CdTe Module | UL 1703 | 90 | 84.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.53 | 85.5 | 1.36 | 66.5 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.088058 | 67.3537 | 1.0763 | 63.5994 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.0659 |  | 2018-12-17
First Solar, Inc. | FS-490A | 90 W Thin Film CdTe Module | UL 1703 | 90 | 84.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.53 | 85.5 | 1.36 | 66.5 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.088058 | 67.3537 | 1.0763 | 63.5994 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.0659 |  | 2018-12-17
First Solar, Inc. | FS-392 | 92.5 W Thin Film CdTe Module | UL 1703 | 92.5 | 88.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 1 | N | 2.06 | 61 | 1.87 | 49.5 | 46 | -0.19 | 0.032 | -0.217 | 0.033 | -0.22 | 0.3744 | 49.8064 | 1.5484 | 46.9527 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.20159 |  | 2018-12-17
First Solar, Inc. | FS-392-Plus | 92.5 W Thin Film CdTe Module | UL 1703 | 92.5 | 87.6 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 146 | 1 | N | 2.28 | 57.7 | 2.05 | 45.2 | 44.6 | -0.2492 | 0.0391 | -0.2499 | 0.0013 | -0.2817 | 0.4 | 45.54 | 1.61 | 43.69 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19693 |  | 2018-12-17
First Solar, Inc. | FS-492 | 92.5 W Thin Film CdTe Module | UL 1703 | 92.5 | 87.3 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.54 | 86 | 1.38 | 67 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.089353 | 67.8601 | 1.0921 | 64.0776 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065551 |  | 2018-12-17
First Solar, Inc. | Fs-492A | 92.5 W Thin Film CdTe Module | UL 1703 | 92.5 | 87.3 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.54 | 86 | 1.38 | 67 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.089353 | 67.8601 | 1.0921 | 64.0776 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065551 |  | 2018-12-17
First Solar, Inc. | FS-395 | 95.0 W Thin Film CdTe Module | UL 1703 | 95 | 90.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 77 | 2 | N | 2.17 | 60.5 | 2 | 47.5 | 46 | -0.19 | 0.032 | -0.217 | 0.033 | -0.22 | 0.40043 | 47.794 | 1.656 | 45.0556 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.20145 |  | 2018-12-17
First Solar, Inc. | FS-395-Plus | 95 W Thin Film CdTe Module | UL 1703 | 95 | 90 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 146 | 1 | N | 2.29 | 58 | 2.08 | 45.8 | 44.6 | -0.2492 | 0.0391 | -0.2499 | 0.0013 | -0.2817 | 0.4 | 46.14 | 1.64 | 44.27 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19427 |  | 2018-12-17
First Solar, Inc. | FS-495 | 95 W Thin Film CdTe Module | UL 1703 | 95 | 89.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.55 | 86.5 | 1.4 | 67.9 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.090647 | 68.7717 | 1.1079 | 64.9384 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065621 |  | 2018-12-17
First Solar, Inc. | FS-495A | 95 W Thin Film CdTe Module | UL 1703 | 95 | 89.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.55 | 86.5 | 1.4 | 67.9 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.090647 | 68.7717 | 1.1079 | 64.9384 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065621 |  | 2018-12-17
First Solar, Inc. | FS-397-Plus | 97.5 W Thin Film CdTe Module | UL 1703 | 97.5 | 92.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 146 | 1 | N | 2.29 | 58.6 | 2.11 | 46.3 | 44.6 | -0.2492 | 0.0391 | -0.2499 | 0.0013 | -0.2817 | 0.41 | 46.65 | 1.66 | 44.75 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19617 |  | 2018-12-17
First Solar, Inc. | FS-497 | 97.5 W Thin Film CdTe Module | UL 1703 | 97.5 | 92.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.55 | 87 | 1.42 | 68.7 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.091942 | 69.5819 | 1.1237 | 65.7035 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065616 |  | 2018-12-17
First Solar, Inc. | FS-497A | 97.5 W Thin Film CdTe Module | UL 1703 | 97.5 | 92.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.55 | 87 | 1.42 | 68.7 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.091942 | 69.5819 | 1.1237 | 65.7035 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065616 |  | 2018-12-17
First Solar, Inc. | FS-3100-Plus | 100 W Thin Film CdTe Module | UL 1703 | 100 | 94.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 146 | 1 | N | 2.33 | 58.8 | 2.14 | 46.8 | 44.6 | -0.2492 | 0.0391 | -0.2499 | 0.0013 | -0.2817 | 0.41 | 47.15 | 1.69 | 45.23 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19331 |  | 2018-12-17
First Solar, Inc. | FS-4100 | 100 W Thin Film CdTe Module | UL 1703 | 100 | 94.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.57 | 87.6 | 1.44 | 69.4 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.093237 | 70.2909 | 1.1396 | 66.3729 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065537 |  | 2018-12-17
First Solar, Inc. | FS-4100-2 | 100 W Thin Film CdTe Module | UL 1703 | 100 | 92.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.73 | 84.7 | 1.51 | 66.2 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.3 | 66.67 | 1.11 | 57.74 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.20001 |  | 2018-12-17
First Solar, Inc. | FS-4100A | 100 W Thin Film CdTe Module | UL 1703 | 100 | 94.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.57 | 87.6 | 1.44 | 69.4 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.093237 | 70.2909 | 1.1396 | 66.3729 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065537 |  | 2018-12-17
First Solar, Inc. | FS-4100A-2 | 100 W Thin Film CdTe Module | UL 1703 | 100 | 92.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.73 | 84.7 | 1.51 | 66.2 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.3 | 66.67 | 1.11 | 57.74 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.20001 |  | 2018-12-17
First Solar, Inc. | FS-4102 | 102W Thin Film CdTe Module | UL 1703 | 102.5 | 96.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.57 | 88 | 1.47 | 70 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.09518 | 70.8986 | 1.1633 | 66.9468 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065835 |  | 2018-12-17
First Solar, Inc. | FS-4102-2 | 102.5 W Thin Film CdTe Module | UL 1703 | 102.5 | 95 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.74 | 85.3 | 1.53 | 67 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.3 | 67.48 | 1.12 | 58.43 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.1975 |  | 2018-12-17
First Solar, Inc. | FS-4102A | 102W Thin Film CdTe Module | UL 1703 | 102.5 | 96.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.57 | 88 | 1.47 | 70 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.09518 | 70.8986 | 1.1633 | 66.9468 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065835 |  | 2018-12-17
First Solar, Inc. | FS-4102A-2 | 102.5 W Thin Film CdTe Module | UL 1703 | 102.5 | 95 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.74 | 85.3 | 1.53 | 67 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.3 | 67.48 | 1.12 | 58.43 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.1975 |  | 2018-12-17
First Solar, Inc. | FS-4105 | 105 W Thin Film CdTe Module | UL 1703 | 105 | 99.3 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.58 | 88.2 | 1.49 | 70.4 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.096475 | 71.3037 | 1.1791 | 67.3293 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065514 |  | 2018-12-17
First Solar, Inc. | FS-4105-2 | 105 W Thin Film CdTe Module | UL 1703 | 105 | 97.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.74 | 86 | 1.55 | 67.8 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.3 | 68.28 | 1.13 | 59.13 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19509 |  | 2018-12-17
First Solar, Inc. | FS-4105-3 | 105 W CdTe Module | UL 1703 | 105 | 97.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.81 | 85.2 | 1.59 | 66.2 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31 | 65.9187 | 1.26 | 65.675 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19462 |  | 2018-12-17
First Solar, Inc. | FS-4105A | 105 W Thin Film CdTe Module | UL 1703 | 105 | 99.3 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.58 | 88.2 | 1.49 | 70.4 | 44.6 | -0.2635 | 0.0596 | -0.2629 | 0.0408 | -0.3024 | 0.096475 | 71.3037 | 1.1791 | 67.3293 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.065514 |  | 2018-12-17
First Solar, Inc. | FS-4105A-2 | 105 W Thin Film CdTe Module | UL 1703 | 105 | 97.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.74 | 86 | 1.55 | 67.8 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.3 | 68.28 | 1.13 | 59.13 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19509 |  | 2018-12-17
First Solar, Inc. | FS-4105A-3 | 105 W CdTe Module | UL 1703 | 105 | 97.8 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.81 | 85.2 | 1.59 | 66.2 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31 | 65.9187 | 1.26 | 65.675 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19462 |  | 2018-12-17
First Solar, Inc. | FS-4107-2 | 107.5 W Thin Film CdTe Module | UL 1703 | 107.5 | 99.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 86.6 | 1.57 | 68.6 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 69.09 | 1.15 | 59.83 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19924 |  | 2018-12-17
First Solar, Inc. | FS-4107-3 | 107W CdTe Module | UL 1703 | 107.5 | 100.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.82 | 85.8 | 1.61 | 67 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.3139 | 66.7153 | 1.2758 | 66.4686 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19481 |  | 2018-12-17
First Solar, Inc. | FS-4107A-2 | 107.5 W Thin Film CdTe Module | UL 1703 | 107.5 | 99.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 86.6 | 1.57 | 68.6 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 69.09 | 1.15 | 59.83 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19924 |  | 2018-12-17
First Solar, Inc. | FS-4107A-3 | 107.5 W CdTe Module | UL 1703 | 107.5 | 100.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.82 | 85.8 | 1.61 | 67 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.3139 | 66.7153 | 1.2758 | 66.4686 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19481 |  | 2018-12-17
First Solar, Inc. | FS-4110-2 | 110 W Thin Film CdTe Module | UL 1703 | 110 | 102.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 87.2 | 1.59 | 69.4 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 69.89 | 1.16 | 60.53 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19696 |  | 2018-12-17
First Solar, Inc. | FS-4110-3 | 110 W CdTe Module | UL 1703 | 110 | 102.6 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.82 | 86.4 | 1.62 | 67.8 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31585 | 67.5119 | 1.2838 | 67.2623 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19385 |  | 2018-12-17
First Solar, Inc. | FS-4110A-2 | 110 W Thin Film CdTe Module | UL 1703 | 110 | 102.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 87.2 | 1.59 | 69.4 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 69.89 | 1.16 | 60.53 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19696 |  | 2018-12-17
First Solar, Inc. | FS-4110A-3 | 110 W CdTe Module | UL 1703 | 110 | 102.6 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.82 | 86.4 | 1.62 | 67.8 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31585 | 67.5119 | 1.2838 | 67.2623 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19385 |  | 2018-12-17
First Solar, Inc. | FS-4112-2 | 112.5 W Thin Film CdTe Module | UL 1703 | 112.5 | 104.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 87.7 | 1.6 | 70.2 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 70.7 | 1.17 | 61.23 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19482 |  | 2018-12-17
First Solar, Inc. | FS-4112-3 | 112.5 W CdTe Module | UL 1703 | 112.5 | 104.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.83 | 87 | 1.64 | 68.5 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31975 | 68.209 | 1.2996 | 67.9567 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19386 |  | 2018-12-17
First Solar, Inc. | FS-4112A-2 | 112.5 W Thin Film CdTe Module | UL 1703 | 112.5 | 104.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.75 | 87.7 | 1.6 | 70.2 | 47 | -0.312 | 0.043 | -0.268 | 0.011 | -0.342 | 0.31 | 70.7 | 1.17 | 61.23 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19482 |  | 2018-12-17
First Solar, Inc. | FS-4112A-3 | 112.5 W CdTe Module | UL 1703 | 112.5 | 104.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.83 | 87 | 1.64 | 68.5 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31975 | 68.209 | 1.2996 | 67.9567 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.19386 |  | 2018-12-17
First Solar, Inc. | FS-4115-2 | 115 W Thin Film CdTe Module | UL 1703 | 115 | 105.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.78 | 87.8 | 1.63 | 70.5 | 46.3 | -0.3878 | 0.0454 | -0.3548 | 0.0168 | -0.4244 | 0.10479 | 71.0388 | 1.2595 | 65.798 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.064729 |  | 2018-12-17
First Solar, Inc. | FS-4115-3 | 115 W CdTe Module | UL 1703 | 115 | 107.3 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.83 | 87.6 | 1.66 | 69.3 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31571 | 66.2292 | 1.273 | 61.4064 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.18182 |  | 2018-12-17
First Solar, Inc. | FS-4115A-2 | 115 W Thin Film CdTe Module | UL 1703 | 115 | 105.2 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.78 | 87.8 | 1.63 | 70.5 | 46.3 | -0.3878 | 0.0454 | -0.3548 | 0.0168 | -0.4244 | 0.10479 | 71.0388 | 1.2595 | 65.798 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.064729 |  | 2018-12-17
First Solar, Inc. | FS-4115A-3 | 115 W CdTe Module | UL 1703 | 115 | 107.3 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.83 | 87.6 | 1.66 | 69.3 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31571 | 66.2292 | 1.273 | 61.4064 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.18182 |  | 2018-12-17
First Solar, Inc. | FS-4117-2 | 117.5 W Thin Film CdTe Module | UL 1703 | 117.5 | 107.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.79 | 88.2 | 1.65 | 71.2 | 46.3 | -0.3878 | 0.0454 | -0.3548 | 0.0168 | -0.4244 | 0.10607 | 71.7441 | 1.275 | 66.4514 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.064766 |  | 2018-12-17
First Solar, Inc. | FS-4117-3 | 117.5 W CdTe Module | UL 1703 | 117.5 | 109.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.83 | 88.1 | 1.68 | 70.1 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31951 | 66.9937 | 1.2883 | 62.1153 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.18217 |  | 2018-12-17
First Solar, Inc. | FS-4117A-2 | 117.5 W Thin Film CdTe Module | UL 1703 | 117.5 | 107.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.79 | 88.2 | 1.65 | 71.2 | 46.3 | -0.3878 | 0.0454 | -0.3548 | 0.0168 | -0.4244 | 0.10607 | 71.7441 | 1.275 | 66.4514 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.064766 |  | 2018-12-17
First Solar, Inc. | FS-4117A-3 | 117.5 W CdTe Module | UL 1703 | 117.5 | 109.7 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.83 | 88.1 | 1.68 | 70.1 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.31951 | 66.9937 | 1.2883 | 62.1153 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.18217 |  | 2018-12-17
First Solar, Inc. | FS-4120-3 | 120 W CdTe Module | UL 1703 | 120 | 112.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.84 | 88.7 | 1.7 | 70.8 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.32331 | 67.6627 | 1.3037 | 62.7356 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.1823 |  | 2018-12-17
First Solar, Inc. | FS-4120A-3 | 120 W CdTe Module | UL 1703 | 120 | 112.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.84 | 88.7 | 1.7 | 70.8 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.32331 | 67.6627 | 1.3037 | 62.7356 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.1823 |  | 2018-12-17
First Solar, Inc. | FS-4122-3 | 122.5 W CdTe Module | UL 1703 | 122.5 | 114.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.85 | 88.7 | 1.71 | 71.5 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.32521 | 68.3317 | 1.3113 | 63.3558 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.18141 |  | 2018-12-17
First Solar, Inc. | FS-4122A-3 | 122.5 W CdTe Module | UL 1703 | 122.5 | 114.5 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 0.72 | 216 | 1 | N | 1.85 | 88.7 | 1.71 | 71.5 | 45.77 | -0.3108 | 0.0726 | -0.3587 | 0.066 | -0.3915 | 0.32521 | 68.3317 | 1.3113 | 63.3558 | Rack | Flat Plate | 0.6 | 1.2 | 1 | 0.18141 |  | 2018-12-17
First Solar, Inc. | FS-6385 | 385 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 385 | 358.5 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.49 | 214.3 | 2.23 | 172.8 | 50.37 | -0.2605 | 0.05505 | -0.2795 | 0.05395 | -0.30955 | 0.4683 | 173.6625 | 1.8267 | 164.504 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6390 | 390 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 390 | 363.2 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.49 | 214.8 | 2.24 | 173.9 | 50.37 | -0.2605 | 0.05505 | -0.2795 | 0.05395 | -0.30955 | 0.4704 | 174.768 | 1.8349 | 165.5512 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6390A | 390 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 390 | 365.6 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.49 | 214.8 | 2.24 | 173.9 | 49.64 | -0.24445 | 0.0568 | -0.27685 | 0.0593 | -0.29865 | 0.48 | 174.3849 | 1.8764 | 164.4921 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6395 | 395 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 395 | 368 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.5 | 215.4 | 2.26 | 175 | 50.37 | -0.2605 | 0.05505 | -0.2795 | 0.05395 | -0.30955 | 0.4746 | 175.8735 | 1.8512 | 166.5984 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6395A | 395 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 395 | 370.4 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.5 | 215.4 | 2.26 | 175 | 49.64 | -0.24445 | 0.0568 | -0.27685 | 0.0593 | -0.29865 | 0.48429 | 175.488 | 1.8931 | 165.5326 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6400 | 400 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 400 | 372.7 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.51 | 216.1 | 2.27 | 176.1 | 50.37 | -0.2605 | 0.05505 | -0.2795 | 0.05395 | -0.30955 | 0.4767 | 176.979 | 1.8594 | 167.6456 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6400A | 400 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 400 | 375.2 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.51 | 216.1 | 2.27 | 176.1 | 49.64 | -0.24445 | 0.0568 | -0.27685 | 0.0593 | -0.29865 | 0.48643 | 176.5911 | 1.9015 | 166.5731 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6400A-P-x | 400 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 400 | 367.3 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.51 | 216.1 | 2.27 | 176.1 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.47403 | 174.0501 | 1.8847 | 162.7042 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6405 | 405 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 405 | 377.5 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.52 | 216.8 | 2.29 | 177.2 | 50.37 | -0.2605 | 0.05505 | -0.2795 | 0.05395 | -0.30955 | 0.4809 | 178.0845 | 1.8758 | 168.6928 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6405A | 405 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 405 | 379.9 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.52 | 216.8 | 2.29 | 177.2 | 49.64 | -0.24445 | 0.0568 | -0.27685 | 0.0593 | -0.29865 | 0.49071 | 177.6941 | 1.9182 | 167.6136 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6405A-P-x | 405 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 405 | 372 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.52 | 216.8 | 2.29 | 177.2 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.47821 | 175.1373 | 1.9013 | 163.7205 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6410 | 410 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 410 | 382.2 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.52 | 217.4 | 2.3 | 178.3 | 50.37 | -0.2605 | 0.05505 | -0.2795 | 0.05395 | -0.30955 | 0.483 | 179.19 | 1.884 | 169.74 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6410A | 410 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 410 | 384.7 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.52 | 217.4 | 2.3 | 178.3 | 49.64 | -0.24445 | 0.0568 | -0.27685 | 0.0593 | -0.29865 | 0.49286 | 178.7972 | 1.9266 | 168.6541 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6410A-P-x | 410 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 410 | 376.7 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.52 | 217.4 | 2.3 | 178.3 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.48029 | 176.2245 | 1.9096 | 164.7368 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6415 | 415 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 415 | 387 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.53 | 218.1 | 2.31 | 179.3 | 50.37 | -0.2605 | 0.05505 | -0.2795 | 0.05395 | -0.30955 | 0.4851 | 180.195 | 1.8922 | 170.692 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6415A | 415 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 415 | 389.5 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.53 | 218.1 | 2.31 | 179.3 | 49.64 | -0.24445 | 0.0568 | -0.27685 | 0.0593 | -0.29865 | 0.495 | 179.8 | 1.935 | 169.6 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6415A-P-x | 415 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 415 | 381.4 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.53 | 218.1 | 2.31 | 179.3 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.48238 | 177.2129 | 1.9179 | 165.6608 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6420 | 420 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 420 | 395.1 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.475 | 264 | 1 | N | 2.54 | 218.5 | 2.33 | 180.4 | 48.8 | -0.2453 | 0.0493 | -0.2735 | 0.466 | 179.61 | 0.466 | 179.61 | 1.88 | 171.03 | [6 empty] | 2018-12-17 | 2020-01-21
First Solar, Inc. | FS-6420A | 420 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 420 | 394.2 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.54 | 218.5 | 2.33 | 180.4 | 49.64 | -0.24445 | 0.0568 | -0.27685 | 0.0593 | -0.29865 | 0.49929 | 180.9031 | 1.9518 | 170.6405 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6420A-P-x | 420 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 420 | 386.1 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.53 | 218.1 | 2.31 | 179.3 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.48238 | 177.2129 | 1.9179 | 165.6608 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6425 | 425 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 425 | 396.5 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.54 | 218.9 | 2.34 | 181.5 | 50.37 | -0.2605 | 0.05505 | -0.2795 | 0.05395 | -0.30955 | 0.4914 | 182.406 | 1.9168 | 172.7864 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6425A | 425 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 425 | 399 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.54 | 218.9 | 2.34 | 181.5 | 49.64 | -0.24445 | 0.0568 | -0.27685 | 0.0593 | -0.29865 | 0.50143 | 182.0061 | 1.9601 | 171.681 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6425A-P-x | 425 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 425 | 390.8 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.54 | 218.9 | 2.34 | 181.5 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.48865 | 179.3872 | 1.9428 | 167.6934 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6430 | 430 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 430 | 401.3 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.475 | 264 |  | N | 2.54 | 219.2 | 2.36 | 182.6 | 50.37 | -0.2605 | 0.05505 | -0.2795 | 0.05395 | -0.30955 | 0.4956 | 183.5115 | 1.9331 | 173.8336 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6430A | 430 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 430 | 403.8 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.48 | 264 |  | N | 2.54 | 219.2 | 2.36 | 182.6 | 49.64 | -0.24445 | 0.0568 | -0.27685 | 0.0593 | -0.29865 | 0.50571 | 183.1092 | 1.9769 | 172.7215 | [6 empty] | 2018-12-17
First Solar, Inc. | FS-6430A-P-x | 430 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 430 | 395.5 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.54 | 219.2 | 2.36 | 182.6 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.49282 | 180.4744 | 1.9594 | 168.7097 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6435 | 435 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 435 | 409.4 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.475 | 264 | 1 | N | 2.55 | 219.6 | 2.37 | 183.6 | 48.8 | -0.2453 | 0.0493 | -0.2735 | 0.474 | 182.796 | 0.474 | 182.796 | 1.9123 | 174.0638 | [6 empty] | 2020-01-21
First Solar, Inc. | FS-6435A | 435 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 435 | 409.9 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.475 | 264 | 1 | N | 2.55 | 219.6 | 2.37 | 183.6 | 51 | -0.2201 | 0.0527 | -0.2707 | 0.483 | 178.76 | 0.483 | 178.76 | 1.938 | 168.3 | [6 empty] | 2018-12-17 | 2020-01-21
First Solar, Inc. | FS-6435A-P-x | 435 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 435 | 400.2 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.55 | 219.6 | 2.37 | 183.6 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.49491 | 181.4628 | 1.9677 | 169.6337 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6440 | 440 W, 264 cell CdTe thin film, 1500V max system Vdc | UL 1703 | 440 | 414.2 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.475 | 264 | 1 | N | 2.55 | 220 | 2.38 | 184.7 | 48.8 | -0.2453 | 0.0493 | -0.2735 | 0.476 | 183.8912 | 0.476 | 183.8912 | 1.9203 | 175.1067 | [6 empty] | 2020-01-21
First Solar, Inc. | FS-6440A | 440 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 440 | 414.7 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.475 | 264 | 1 | N | 2.55 | 220 | 2.38 | 184.7 | 51 | -0.2201 | 0.0527 | -0.2707 | 0.48504 | 179.831 | 0.48504 | 179.831 | 1.9462 | 169.3083 | [6 empty] | 2020-01-21
First Solar, Inc. | FS-6440A-P-x | 440 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 440 | 405 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.56 | 220 | 2.38 | 184.7 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.497 | 182.55 | 1.976 | 170.65 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6445A | 445 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 445 | 419.5 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.475 | 264 | 1 | N | 2.56 | 220.4 | 2.4 | 185.7 | 51 | -0.2201 | 0.0527 | -0.2707 | 0.48911 | 180.8046 | 0.48911 | 180.8046 | 1.9625 | 170.225 | [6 empty] | 2020-01-21
First Solar, Inc. | FS-6445A-P-x | 445 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 445 | 409.7 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.56 | 220.4 | 2.4 | 185.7 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.50118 | 183.5384 | 1.9926 | 171.5739 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6450A | 450 W, 264 cell CdTe thin film with anti-reflective coating, 1500V max system Vdc | UL 1703 | 450 | 424.3 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.475 | 264 | 1 | N | 2.57 | 221.1 | 2.41 | 186.8 | 51 | -0.2201 | 0.0527 | -0.2707 | 0.49115 | 181.8756 | 0.49115 | 181.8756 | 1.9707 | 171.2333 | [6 empty] | 2020-01-21
First Solar, Inc. | FS-6450A-P-x | 450 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 450 | 414.4 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.57 | 221.1 | 2.41 | 186.8 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.50326 | 184.6256 | 2.0009 | 172.5903 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6455A-P-x | 455 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 455 | 419.1 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.58 | 222 | 2.42 | 187.8 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.50535 | 185.6139 | 2.0092 | 173.5142 | [6 empty] | 2021-10-21
First Solar, Inc. | FS-6460A-P-x | 460 W, 264 cell CdTe thin film module with anti-reflective coating, 1500V max system Vdc, where x can be blank or I | UL 61730 | 460 | 423.8 |  | No Information Submitted | No Information Submitted | Thin Film | CdTe | 2.52 | 264 | 1 | N | 2.59 | 222.9 | 2.44 | 188.8 | 50.71 | -0.307 | 0.05635 | -0.2818 |  |  | 0.50953 | 186.6023 | 2.0258 | 174.4381 | [6 empty] | 2021-10-21
Flextronics | FXS-260BB-MAA1B | 260 W Polycrystalline Module 1000 V system voltage, black back sheet | UL 1703 | 252.8 | 229.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.554 | 37.98 | 8.165 | 30.97 | 43.3 | -0.4802 | 0.0575 | -0.3583 | -0.021 | -0.4628 | 1.617 | 29.81 | 6.613 | 28.2 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19068
Flextronics | FXS-260BB-MAA1W | 260 W Polycrystalline Module 1000 V system voltage, white back sheet | UL 1703 | 252.8 | 229.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.554 | 37.98 | 8.165 | 30.97 | 43.3 | -0.4802 | 0.0575 | -0.3583 | -0.021 | -0.4628 | 1.617 | 29.81 | 6.613 | 28.2 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19068
Flextronics | FXS-270BB-SAC1B | 270 W Monocrystalline Module | UL 1703 | 270 | 246.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6414 | 60 | 1 | N | 9.1 | 38.5 | 8.58 | 31.5 | 44.2 | -0.44 | 0.05 | -0.32 | -0.02 | -0.43 | 1.7 | 30.04 | 6.85 | 28.82 | Rack | Flat Plate | 0.99 | 1.658 | 1 | 0.18914
Flextronics | FXS-275BB-SAC1B | 275 W Monocrystalline Module | UL 1703 | 275 | 251.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6414 | 60 | 1 | N | 9.2 | 38.6 | 8.72 | 31.6 | 44.2 | -0.44 | 0.05 | -0.32 | -0.02 | -0.43 | 1.73 | 30.13 | 6.96 | 28.91 | Rack | Flat Plate | 0.99 | 1.658 | 1 | 0.18955
Flextronics | FXS-285BB-SBC1B | 285 W Mono PERC Module,1000 V system voltage, black back sheet | UL 1703 | 278.8 | 254.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.305 | 39.27 | 8.83 | 31.57 | 43 | -0.4707 | 0.0505 | -0.335 | -0.0332 | -0.4439 | 1.765 | 30.79 | 7.116 | 28.98 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19492
Flextronics | FXS-285BB-SBC1W | 285 W Mono PERC Module,1000 V system voltage, white back sheet | UL 1703 | 278.8 | 254.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.305 | 39.27 | 8.83 | 31.57 | 43 | -0.4707 | 0.0505 | -0.335 | -0.0332 | -0.4439 | 1.765 | 30.79 | 7.116 | 28.98 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19492
Flextronics | FXS-325BB-MAB1W | 325 W Polycrystalline 72 Cell, Multi-Si, 1000v, White Backsheet | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8523 | 72 | 1 | N | 9.29 | 45.8 | 8.69 | 37.4 | 44.1 | -0.4373 | 0.055 | -0.3323 | -0.0105 | -0.4295 | 1.6754 | 35.9588 | 6.9276 | 34.4872 | Rack | Flat Plate | 0.947 | 1.956 | 1 | 0.18537
Flextronics | FXS-325BC-MAB1W | 325 W Polycrystalline 72 Cell, Multi-Si, 1500v, White Backsheet | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8523 | 72 | 1 | N | 9.29 | 45.8 | 8.69 | 37.4 | 44.1 | -0.4373 | 0.055 | -0.3323 | -0.0105 | -0.4295 | 1.6754 | 35.9588 | 6.9276 | 34.4872 | Rack | Flat Plate | 0.947 | 1.956 | 1 | 0.18537
Flextronics | FXS-330BB-SAD1W | 330 W Monocrystalline Module | UL 1703 | 330 | 300.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.18 | 46.15 | 8.78 | 37.6 | 45.2 | -0.43 | 0.05 | -0.31 | -0.02 | -0.42 | 1.7321 | 36.194 | 6.9782 | 33.7439 | Rack | Flat Plate | 0.99 | 1.976 | 1 | 0.18998
Flextronics | FXS-335BB-SAD1W | 335 W Monocrystalline Module | UL 1703 | 335 | 305.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.2 | 46.2 | 8.86 | 37.8 | 45.2 | -0.43 | 0.05 | -0.31 | -0.02 | -0.42 | 1.7479 | 36.3865 | 7.0418 | 33.9233 | Rack | Flat Plate | 0.99 | 1.976 | 1 | 0.18985
Flextronics | FXS-350BB-SBD1W | 350 W Mono PERC Module,1000 V system voltage, white back sheet | UL 1703 | 340.2 | 311.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9602 | 72 | 1 | N | 9.289 | 47.79 | 8.827 | 38.54 | 43.5 | -0.4519 | 0.0538 | -0.3228 | -0.0228 | -0.4335 | 1.773 | 37.62 | 7.059 | 22.29 | Rack | Flat Plate | 0.992 | 1.976 | 1 | 0.19606
Flextronics | FXS-350BC-SBD1W | 350 W Mono PERC Module,1500V system voltage, white back sheet | UL 1703 | 340.2 | 311.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9602 | 72 | 1 | N | 9.289 | 47.79 | 8.827 | 38.54 | 43.5 | -0.4519 | 0.0538 | -0.3228 | -0.0228 | -0.4335 | 1.773 | 37.62 | 7.059 | 22.29 | Rack | Flat Plate | 0.992 | 1.976 | 1 | 0.19606
FreeVolt | PV-GRAF-60M6-300/M | 300 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 300 | 273.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.7 | 39.6 | 9.24 | 32 | 46.5 | -0.4151 | 0.0444 | -0.3017 |  |  | 2.38 | 33.25 | 7.43 | 30.53 | [6 empty] | 2020-04-01
GAF | RIAC 1000 | 150 W DC, Thin Film CIGS ACPV Module | UL 1741 | 150 | 139.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0863 | 100 | 1 | N | 3.45 | 62.5 | 3.12 | 48.1 | 47 | -0.306 | 0.00651 | -0.286 | 0.00228 | -0.264 | 0.58264 | 46.3836 | 2.4559 | 43.5413 | Rack | Flat Plate | 0.656 | 1.656 | 1 | 0.18017
GCL System Integration Technology Co., Ltd. | GCL-P6/60255 | 255 W Polycrystalline Module | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.98 | 37.7 | 8.26 | 30.4 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.6522 | 29.294 | 8.3724 | 27.6693 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1898 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60260 | 260 W Polycrystalline Module | UL 1703 | 260 | 235.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.09 | 37.9 | 8.38 | 30.6 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.6762 | 29.4867 | 8.494 | 27.8513 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1901 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60B260 | 260 W Polycrystalline Module | UL 1703 | 260 | 234.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 1 |  | N | 9.09 | 37.9 | 8.44 | 30.8 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60265 | 265 W Polycrystalline Module | UL 1703 | 265 | 239.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.2 | 38.1 | 8.5 | 30.8 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.7002 | 29.6795 | 8.6157 | 28.0334 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19042 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60B265 | 265 W Polycrystalline Module | UL 1703 | 265 | 238.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 1 |  | N | 9.2 | 38.1 | 8.55 | 31 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60270 | 270 W Polycrystalline Module | UL 1703 | 270 | 244.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.29 | 38.3 | 8.61 | 31 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.7222 | 29.8722 | 8.7271 | 28.2154 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19054 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60B270 | 270 W Polycrystalline Module | UL 1703 | 270 | 243.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 1 |  | N | 9.29 | 38.3 | 8.65 | 31.2 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-M6/60275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.38 | 38.5 | 8.76 | 31.4 | 47.5 | -0.4348 | 0.0498 | -0.3276 | -0.0099 | -0.4266 | 1.89 | 30.9 | 7.23 | 28.95 | [6 empty] | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60275 | 275 W Polycrystalline Module | UL 1703 | 275 | 249.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.38 | 38.5 | 8.7 | 31.2 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.7402 | 30.0649 | 8.8184 | 28.3974 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19025 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-M6/60280 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.46 | 38.7 | 8.86 | 31.6 | 47.5 | -0.4348 | 0.0498 | -0.3276 | -0.0099 | -0.4266 | 1.89 | 30.9 | 7.23 | 28.95 | [6 empty] | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60280 | 280 W Polycrystalline Module | UL 1703 | 280 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.46 | 38.7 | 8.86 | 31.6 | 46.3 | -0.4341 | 0.0555 | -0.3705 | -0.0054 | -0.5001 | 1.93 | 30.2 | 7.3 | 28.53 | [6 empty] | 2017-12-15 | 2018-02-01
GCL System Integration Technology Co., Ltd. | GCL-M6/60285 | 285W Monocrystalline Module | UL 1703 | 285 | 256.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.54 | 38.9 | 8.96 | 31.8 | 47.5 | -0.4348 | 0.0498 | -0.3276 | -0.0099 | -0.4266 | 1.89 | 30.9 | 7.23 | 28.95 | [6 empty] | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60285 | 285 W Polycrystalline Module | UL 1703 | 285 | 258.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.54 | 38.9 | 8.96 | 31.8 | 46.3 | -0.4341 | 0.0555 | -0.3705 | -0.0054 | -0.5001 | 1.93 | 30.2 | 7.3 | 28.53 | [6 empty] | 2017-12-15 | 2018-02-01
GCL System Integration Technology Co., Ltd. | GCL-M6/60290 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.63 | 39.1 | 9.06 | 32 | 47.5 | -0.4348 | 0.0498 | -0.3276 | -0.0099 | -0.4266 | 1.89 | 30.9 | 7.23 | 28.95 | [6 empty] | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/60290 | 290W Polycrystalline Module | UL 1703 | 290 | 263.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.63 | 39.1 | 9.06 | 32 | 46.3 | -0.4341 | 0.0555 | -0.3705 | -0.0054 | -0.5001 | 1.93 | 30.2 | 7.3 | 28.53 | [6 empty] | 2017-12-15 | 2018-02-01
GCL System Integration Technology Co., Ltd. | GCL-M6/60295 | 295 W Monocrystalline Module | UL 1703 | 295 | 266.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.69 | 39.3 | 9.16 | 32.2 | 47.5 | -0.4348 | 0.0498 | -0.3276 | -0.0099 | -0.4266 | 1.89 | 30.9 | 7.23 | 28.95 | [6 empty] | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-M6/60300 | 300 W, 60 cell Monocrystalline module, white backsheet | UL 1703 | 300 | 273.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.78 | 39.5 | 9.26 | 32.4 | 46.6 | -0.4115 | 0.0369 | -0.2938 | -0.043 | -0.3753 | 1.8787 | 31.4787 | 7.2942 | 30.299 | [6 empty] | 2018-06-01
GCL System Integration Technology Co., Ltd. | GCL-P6/72300 | 300 W Polycrystalline Module | UL 1703 | 300 | 271.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.82 | 45 | 8.14 | 36.4 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.657 | 35.682 | 6.5049 | 31.807 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19709 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-M6/60305 | 305 W, 60 cell Monocrystalline module, white backsheet | UL 1703 | 305 | 278.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.87 | 39.7 | 9.36 | 32.6 | 46.6 | -0.4115 | 0.0369 | -0.2938 | -0.043 | -0.3753 | 1.899 | 31.673 | 7.373 | 30.486 | [6 empty] | 2018-06-01
GCL System Integration Technology Co., Ltd. | GCL-P6/72305 | 305 W Polycrystalline Module | UL 1703 | 305 | 275.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.91 | 45.2 | 8.22 | 36.6 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.6733 | 35.8781 | 6.5689 | 31.9817 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19684 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-M6/60310 | 310 W, 60 cell Monocrystalline module, white backsheet | UL 1703 | 310 | 282.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.96 | 39.9 | 9.46 | 32.8 | 46.6 | -0.4115 | 0.0369 | -0.2938 | -0.043 | -0.3753 | 1.9193 | 31.8673 | 7.4518 | 30.673 | [6 empty] | 2018-06-01
GCL System Integration Technology Co., Ltd. | GCL-P6/72310 | 310 W Polycrystalline Module | UL 1703 | 310 | 280.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.99 | 45.4 | 8.31 | 36.8 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.6916 | 36.0741 | 6.6408 | 32.1565 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19685 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-M6/60315 | 315 W, 60 cell Monocrystalline module, white backsheet | UL 1703 | 315 | 287.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 10.04 | 40.1 | 9.55 | 33 | 46.6 | -0.4115 | 0.0369 | -0.2938 | -0.043 | -0.3753 | 1.9375 | 32.0616 | 7.5227 | 30.8601 | [6 empty] | 2018-06-01
GCL System Integration Technology Co., Ltd. | GCL-P6/72315 | 315 W Polycrystalline Module | UL 1703 | 315 | 285.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.08 | 45.6 | 8.39 | 37 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.7079 | 36.2702 | 6.7047 | 32.3313 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19665 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72B315 | 315 W Polycrystalline Module | UL 1703 | 315 | 283.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 1 |  | N | 9.08 | 45.6 | 8.47 | 37.2 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-M6/60320 | 320 W, 60 cell Monocrystalline module, white backsheet | UL 1703 | 320 | 292.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 10.12 | 40.3 | 9.64 | 33.2 | 46.6 | -0.4115 | 0.0369 | -0.2938 | -0.043 | -0.3753 | 1.9558 | 32.2559 | 7.5936 | 31.0471 | [6 empty] | 2018-06-01
GCL System Integration Technology Co., Ltd. | GCL-P6/72320 | 320 W Polycrystalline Module | UL 1703 | 320 | 289.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.17 | 45.8 | 8.48 | 37.2 | 46.4 | -0.42929 | 0.04608 | -0.31757 | 0.00839 | -0.42929 | 1.7262 | 36.4663 | 6.7766 | 32.506 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19672 |  | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72B320 | 320 W Polycrystalline Module | UL 1703 | 320 | 288.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 1 |  | N | 9.17 | 45.8 | 8.56 | 37.4 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72325 | 325 W Monocrystalline Module | UL 1703 | 325 | 293.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.24 | 46 | 8.64 | 37.6 | 46.83 | -0.4321 | 0.0491 | -0.3283 | -0.0044 | -0.4279 | 1.88 | 36.72 | 7.37 | 33.73
GCL System Integration Technology Co., Ltd. | GCL-P6/72325 | 325W Polycrystalline Module | UL 1703 | 325 | 294.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.24 | 46 | 8.64 | 37.6 | 46.5 | -0.424 | 0.0564 | -0.3034 | -0.0057 | -0.4095 | 1.84 | 36.47 | 7.07 | 33.53 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20648 |  | 2018-02-01
GCL System Integration Technology Co., Ltd. | GCL-P6/72B325 | 325 W Polycrystalline Module | UL 1703 | 325 | 293.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 1 |  | N | 9.24 | 46 | 8.64 | 37.6 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72330 | 330 W Monocrystalline Module | UL 1703 | 330 | 298.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.33 | 46.2 | 8.73 | 37.8 | 46.83 | -0.4321 | 0.0491 | -0.3283 | -0.0044 | -0.4279 | 1.88 | 36.72 | 7.37 | 33.73
GCL System Integration Technology Co., Ltd. | GCL-M6/72H330 | 330 W, 72 cell Monocrystalline Module, white frame and backsheet, 1500 max system Vdc | UL 1703 | 330 | 301.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.33 | 46.2 | 8.73 | 37.8 | 45.5 | -0.4155 | 0.0365 | -0.2993 | -0.0634 | -0.361 | 1.7984 | 35.8864 | 7.0151 | 35.0782 | [6 empty] | 2018-04-16
GCL System Integration Technology Co., Ltd. | GCL-P6/72330 | 330W Polycrystalline Module | UL 1703 | 330 | 299.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.33 | 46.2 | 8.73 | 37.8 | 46.5 | -0.424 | 0.0564 | -0.3034 | -0.0057 | -0.4095 | 1.84 | 36.47 | 7.07 | 33.53 | [6 empty] | 2017-12-15 | 2018-02-01
GCL System Integration Technology Co., Ltd. | GCL-P6/72B330 | 330 W Polycrystalline Module | UL 1703 | 330 | 297.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 1 |  | N | 9.33 | 46.2 | 8.73 | 37.8 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72H330 | 330 W Polycrystalline Module, white backsheet and frame, 1500 V system voltage | UL 1703 | 330 | 302.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.33 | 46.2 | 8.73 | 37.8 | 45.9 | -0.3941 | 0.0367 | -0.2885 | -0.0371 | -0.3606 | 1.8031 | 36.0013 | 7.1159 | 34.296 | [6 empty] | 2018-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72335 | 335W Monocrystalline Module | UL 1703 | 335 | 303 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.41 | 46.4 | 8.82 | 38 | 46.83 | -0.4321 | 0.0491 | -0.3283 | -0.0044 | -0.4279 | 1.88 | 36.72 | 7.37 | 33.73
GCL System Integration Technology Co., Ltd. | GCL-M6/72H335 | 335 W, 72 cell Monocrystalline Module, white frame and backsheet, 1500 max system Vdc | UL 1703 | 335 | 306.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.41 | 46.4 | 8.82 | 38 | 45.5 | -0.4155 | 0.0365 | -0.2993 | -0.0634 | -0.361 | 1.817 | 36.0763 | 7.0874 | 35.2638 | [6 empty] | 2018-04-16
GCL System Integration Technology Co., Ltd. | GCL-P6/72335 | 335 W Polycrystalline Module | UL 1703 | 335 | 304.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.41 | 46.4 | 8.82 | 38 | 46.5 | -0.424 | 0.0564 | -0.3034 | -0.0057 | -0.4095 | 1.84 | 36.47 | 7.07 | 33.53 | [6 empty] | 2017-12-15 | 2018-02-01
GCL System Integration Technology Co., Ltd. | GCL-P6/72B335 | 335 W Polycrystalline Module | UL 1703 | 335 | 302.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 1 |  | N | 9.41 | 46.4 | 8.82 | 38 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72H335 | 335 W Polycrystalline Module, white backsheet and frame, 1500 V system voltage | UL 1703 | 335 | 307.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.41 | 46.4 | 8.82 | 38 | 45.9 | -0.3941 | 0.0367 | -0.2885 | -0.0371 | -0.3606 | 1.8217 | 36.1918 | 7.1892 | 34.4774 | [6 empty] | 2018-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72340 | 340 W Monocrystalline Module | UL 1703 | 340 | 307.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.49 | 46.6 | 8.9 | 38.2 | 46.83 | -0.4321 | 0.0491 | -0.3283 | -0.0044 | -0.4279 | 1.88 | 36.72 | 7.37 | 33.73
GCL System Integration Technology Co., Ltd. | GCL-M6/72H340 | 340 W, 72 cell Monocrystalline Module, white frame and backsheet, 1500 max system Vdc | UL 1703 | 340 | 310.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.49 | 46.6 | 8.9 | 38.2 | 45.5 | -0.4155 | 0.0365 | -0.2993 | -0.0634 | -0.361 | 1.8335 | 36.2661 | 7.1517 | 35.4494 | [6 empty] | 2018-04-16
GCL System Integration Technology Co., Ltd. | GCL-P3/72H340 | 340 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 340 | 316.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.01 | 72 | 2 | N | 9.4 | 46.65 | 8.81 | 38.61 | 44.2 | -0.3559 | 0.0462 | -0.2829 | 1.7415 | 36.6707 | 1.7415 | 36.6707 | 7.1262 | 35.7877 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72340 | 340W Polycrystalline Module | UL 1703 | 340 | 311.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.49 | 46.6 | 8.9 | 38.2 | 45.4 | -0.4125 | 0.0412 | -0.296 | -0.0287 | -0.3878 | 1.818 | 36.682 | 7.169 | 34.899 | [6 empty] | 2017-12-15 | 2018-04-02
GCL System Integration Technology Co., Ltd. | GCL-P6/72B340 | 340 W Polycrystalline Module | UL 1703 | 340 | 307.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 1 |  | N | 9.49 | 46.6 | 8.9 | 38.2 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72H340 | 340 W Polycrystalline Module, white backsheet and frame, 1500 V system voltage | UL 1703 | 340 | 311.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.49 | 46.6 | 8.9 | 38.2 | 45.9 | -0.3941 | 0.0367 | -0.2885 | -0.0371 | -0.3606 | 1.8382 | 36.3823 | 7.2545 | 34.6589 | [6 empty] | 2018-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72345 | 345 W Monocrystalline Module | UL 1703 | 345 | 312.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.57 | 46.8 | 8.99 | 38.4 | 46.83 | -0.4321 | 0.0491 | -0.3283 | -0.0044 | -0.4279 | 1.88 | 36.72 | 7.37 | 33.73
GCL System Integration Technology Co., Ltd. | GCL-M6/72H345 | 345 W, 72 cell Monocrystalline Module, white frame and backsheet, 1500 max system Vdc | UL 1703 | 345 | 315.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.57 | 46.8 | 8.99 | 38.4 | 45.5 | -0.4155 | 0.0365 | -0.2993 | -0.0634 | -0.361 | 1.852 | 36.456 | 7.224 | 35.635 | [6 empty] | 2018-04-16
GCL System Integration Technology Co., Ltd. | GCL-P3/72H345 | 345 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 345 | 321.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.01 | 72 | 2 | N | 9.49 | 46.88 | 8.88 | 38.84 | 44.2 | -0.3559 | 0.0462 | -0.2829 | 1.7553 | 36.8891 | 1.7553 | 36.8891 | 7.1828 | 36.0009 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72345 | 345W Polycrystalline Module | UL 1703 | 345 | 315.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.61 | 47.3 | 8.87 | 38.9 | 45.4 | -0.4125 | 0.0412 | -0.296 | -0.0287 | -0.3878 | 1.8119 | 37.3542 | 7.1448 | 35.5385 | [6 empty] | 2018-04-02
GCL System Integration Technology Co., Ltd. | GCL-P6/72B345 | 345 W Polycrystalline Module | UL 1703 | 345 | 311.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 1 |  | N | 9.57 | 46.8 | 8.99 | 38.4 | 46.62 | -0.443 | 0.067 | -0.34 | 0.003 | -0.443 | 1.79 | 29.64 | 6.97 | 27.51 | [6 empty] | 2017-09-01 | 2017-12-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72H345 | 345 W Polycrystalline Module, white backsheet and frame, 1500 V system voltage | UL 1703 | 345 | 316.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.61 | 47.3 | 8.87 | 38.9 | 45.9 | -0.3941 | 0.0367 | -0.2885 | -0.0371 | -0.3606 | 1.832 | 37.049 | 7.23 | 35.294 | [6 empty] | 2018-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72350 | 350 W Monocrystalline Module | UL 1703 | 350 | 317 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.65 | 47 | 9.07 | 38.6 | 46.83 | -0.4321 | 0.0491 | -0.3283 | -0.0044 | -0.4279 | 1.88 | 36.72 | 7.37 | 33.73
GCL System Integration Technology Co., Ltd. | GCL-M6/72H350 | 350 W, 72 cell Monocrystalline Module, white frame and backsheet, 1500 max system Vdc | UL 1703 | 350 | 320.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.65 | 47 | 9.07 | 38.6 | 45.5 | -0.4155 | 0.0365 | -0.2993 | -0.0634 | -0.361 | 1.8685 | 36.6459 | 7.2883 | 35.8206 | [6 empty] | 2018-04-16
GCL System Integration Technology Co., Ltd. | GCL-P3/72H350 | 350 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 350 | 325.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.01 | 72 | 2 | N | 9.58 | 47.1 | 8.95 | 39.11 | 44.2 | -0.3559 | 0.0462 | -0.2829 | 1.7691 | 37.1456 | 1.7691 | 37.1456 | 7.2395 | 36.2512 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72350 | 350 W Polycrystalline Module | UL 1703 | 350 | 320.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.68 | 47.6 | 8.93 | 39.2 | 45.4 | -0.4125 | 0.0412 | -0.296 | -0.0287 | 0.6122 | 1.8241 | 37.6423 | 7.1932 | 35.8126 | [6 empty] | 2018-04-02
GCL System Integration Technology Co., Ltd. | GCL-P6/72H350 | 350 W Polycrystalline Module, white backsheet and frame, 1500 V system voltage | UL 1703 | 350 | 321.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.68 | 47.6 | 8.93 | 39.2 | 45.9 | -0.3941 | 0.0367 | -0.2885 | -0.0371 | -0.3606 | 1.8444 | 37.3347 | 7.2789 | 35.5662 | [6 empty] | 2018-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72355 | 355 W Monocrystalline Module | UL 1703 | 355 | 321.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.73 | 47.2 | 9.16 | 38.8 | 46.83 | -0.4321 | 0.0491 | -0.3283 | -0.0044 | -0.4279 | 1.88 | 36.72 | 7.37 | 33.73
GCL System Integration Technology Co., Ltd. | GCL-M6/72H355 | 355 W, 72 cell Monocrystalline Module, white frame and backsheet, 1500 max system Vdc | UL 1703 | 355 | 324.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.73 | 47.2 | 9.16 | 38.8 | 45.5 | -0.4155 | 0.0365 | -0.2993 | -0.0634 | -0.361 | 1.887 | 36.8358 | 7.3606 | 36.0062 | [6 empty] | 2018-04-16
GCL System Integration Technology Co., Ltd. | GCL-P3/72H355 | 355 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 330.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.01 | 72 | 2 | N | 9.67 | 47.3 | 9.01 | 39.4 | 44.2 | -0.3559 | 0.0462 | -0.2829 | 1.781 | 37.421 | 1.781 | 37.421 | 7.288 | 36.52 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72355 | 355 W Polycrystalline Module | UL 1703 | 355 | 325.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.74 | 47.9 | 8.99 | 39.49 | 45.4 | -0.4125 | 0.0412 | -0.296 | -0.0287 | 1.6122 | 1.8364 | 37.9207 | 7.2415 | 36.0775 | [6 empty] | 2018-04-02
GCL System Integration Technology Co., Ltd. | GCL-P6/72H355 | 355 W Polycrystalline Module, white backsheet and frame, 1500 V system voltage | UL 1703 | 355 | 325.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.74 | 47.9 | 8.99 | 39.49 | 45.9 | -0.3941 | 0.0367 | -0.2885 | -0.0371 | -0.3606 | 1.8568 | 37.6109 | 7.3278 | 35.8293 | [6 empty] | 2018-03-15
GCL System Integration Technology Co., Ltd. | GCL-M3/72H360 | 360 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 335.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.63 | 47.52 | 9.07 | 39.7 | 43.8 | -0.3586 | 0.0352 | -0.2819 | 1.7747 | 37.3248 | 1.7747 | 37.3248 | 7.3502 | 36.2962 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72GDF360 | 360 W, 72 cell Monocrystalline Module, white backsheet, 1500 max system Vdc | UL 1703 | 360 | 336.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 9.72 | 47.73 | 9.25 | 38.92 | 42.4 | -0.3679 | 0.0462 | -0.2741 |  |  | 1.7979 | 37.5224 | 7.4256 | 35.9584 | [6 empty] | 2019-08-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72H360 | 360 W, 72 cell Monocrystalline Module, white frame and backsheet, 1500 max system Vdc | UL 1703 | 360 | 329.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.81 | 47.4 | 9.25 | 39 | 45.5 | -0.4155 | 0.0365 | -0.2993 | -0.0634 | -0.361 | 1.9056 | 37.0256 | 7.4329 | 36.1918 | [6 empty] | 2018-04-16
GCL System Integration Technology Co., Ltd. | GCL-P3/72H360 | 360 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 335.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.01 | 72 | 2 | N | 9.76 | 47.5 | 9.07 | 39.7 | 44.2 | -0.3559 | 0.0462 | -0.2829 | 1.7929 | 37.7059 | 1.7929 | 37.7059 | 7.3365 | 36.7981 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-P6/72H360 | 360 W Polycrystalline Module, white backsheet and frame, 1500 V system voltage | UL 1703 | 360 | 330.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.8 | 48.2 | 9.05 | 39.78 | 45.9 | -0.3941 | 0.0367 | -0.2885 | -0.0371 | -0.3606 | 1.8692 | 37.8871 | 7.3767 | 36.0924 | [6 empty] | 2018-03-15
GCL System Integration Technology Co., Ltd. | GCL-M3/72DH365 | 365 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 339 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.67 | 47.73 | 9.13 | 40 | 43.4 | -0.3884 | 0.0327 | -0.2971 |  |  | 1.8971 | 37.9113 | 7.4601 | 35.8424 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M3/72GDF365 | 365 W, 144 cell double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 338.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 9.72 | 47.89 | 9.22 | 39.59 | 43.72 | -0.3861 | 0.06 | -0.2985 |  |  | 1.9344 | 37.6442 | 7.4605 | 36.4648 | [6 empty] | 2019-11-01
GCL System Integration Technology Co., Ltd. | GCL-M3/72H365 | 365 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 340.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.67 | 47.73 | 9.13 | 40 | 43.8 | -0.3586 | 0.0352 | -0.2819 | 1.7865 | 37.6069 | 1.7865 | 37.6069 | 7.3989 | 36.5704 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72DH365 | 365 W, 72 cell monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 337.8 |  | 2019-10-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 1 | N | 9.8 | 47.93 | 9.33 | 39.13 | 43.9 | -0.398 | 0.0326 | -0.309 |  |  | 1.9037 | 37.6572 | 7.6643 | 35.0797 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M6/72GDF365 | 365 W, 72 cell Monocrystalline Module, white backsheet, 1500 max system Vdc | UL 1703 | 365 | 341.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 9.8 | 47.93 | 9.33 | 39.13 | 42.4 | -0.3679 | 0.0462 | -0.2741 |  |  | 1.8135 | 37.7248 | 7.4898 | 36.1525 | [6 empty] | 2019-08-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72H365 | 365 W, 72 cell monocrystalline module, white backsheet | UL 1703 | 365 | 340.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 1 | N | 9.89 | 47.6 | 9.31 | 39.2 | 44.3 | -0.3533 | 0.0315 | -0.2594 | 1.805 | 38.2372 | 1.805 | 38.2372 | 7.4577 | 36.4233 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-P3/72H365 | 365 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 340.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.01 | 72 | 2 | N | 9.85 | 47.7 | 9.13 | 40 | 44.2 | -0.3559 | 0.0462 | -0.2829 | 1.8047 | 37.9909 | 1.8047 | 37.9909 | 7.3851 | 37.0761 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M3/72DH370 | 370 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 343.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.71 | 47.93 | 9.18 | 40.3 | 43.4 | -0.3884 | 0.0327 | -0.2971 |  |  | 1.9075 | 38.1957 | 7.501 | 36.1112 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M3/72GDF370 | 370 W, 144 cell double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 343.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 9.8 | 48.09 | 9.3 | 39.79 | 43.72 | -0.3861 | 0.06 | -0.2985 |  |  | 1.9512 | 37.8343 | 7.5253 | 36.649 | [6 empty] | 2019-11-01
GCL System Integration Technology Co., Ltd. | GCL-M3/72H370 | 370 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 345.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.71 | 47.93 | 9.18 | 40.3 | 43.8 | -0.3586 | 0.0352 | -0.2819 | 1.7963 | 37.8889 | 1.7963 | 37.8889 | 7.4394 | 36.8447 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72DH370 | 370 W, 72 cell monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 342.5 |  | 2019-10-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 1 | N | 9.88 | 48.13 | 9.41 | 39.32 | 43.9 | -0.398 | 0.0326 | -0.309 |  |  | 1.92 | 37.84 | 7.73 | 35.25 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M6/72GDF370 | 370 W, 72 cell Monocrystalline Module, white backsheet, 1500 max system Vdc | UL 1703 | 370 | 346.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 9.88 | 48.13 | 9.41 | 39.32 | 42.4 | -0.3679 | 0.0462 | -0.2741 |  |  | 1.829 | 37.908 | 7.554 | 36.328 | [6 empty] | 2019-08-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72H370 | 370 W, 72 cell monocrystalline module, white backsheet | UL 1703 | 370 | 345.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 1 | N | 9.97 | 47.8 | 9.39 | 39.41 | 44.3 | -0.3533 | 0.0315 | -0.2594 | 1.8205 | 38.442 | 1.8205 | 38.442 | 7.5218 | 36.6184 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-P3/72H370 | 370 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 344.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.01 | 72 | 2 | N | 9.94 | 47.9 | 9.18 | 40.3 | 44.2 | -0.3559 | 0.0462 | -0.2829 | 1.8146 | 38.2758 | 1.8146 | 38.2758 | 7.4255 | 37.3542 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M3/72DH375 | 375 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 348.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.75 | 48.13 | 9.24 | 40.6 | 43.4 | -0.3884 | 0.0327 | -0.2971 |  |  | 1.92 | 38.48 | 7.55 | 36.38 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M3/72GDF375 | 375 W, 144 cell double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 348.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 9.88 | 48.28 | 9.38 | 39.98 | 43.72 | -0.3861 | 0.06 | -0.2985 |  |  | 1.968 | 38.015 | 7.59 | 36.824 | [6 empty] | 2019-11-01
GCL System Integration Technology Co., Ltd. | GCL-M3/72H375 | 375 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 350 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.75 | 48.13 | 9.24 | 40.6 | 43.8 | -0.3586 | 0.0352 | -0.2819 | 1.808 | 38.171 | 1.808 | 38.171 | 7.488 | 37.119 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72DH375 | 375 W, 72 cell monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 347.3 |  | 2019-10-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 1 | N | 9.96 | 48.33 | 9.49 | 39.52 | 43.9 | -0.398 | 0.0326 | -0.309 |  |  | 1.9363 | 38.0325 | 7.7957 | 35.4293 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M6/72GDF375 | 375 W, 72 cell Monocrystalline Module, white backsheet, 1500 max system Vdc | UL 1703 | 375 | 351.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 9.96 | 48.33 | 9.49 | 39.52 | 42.4 | -0.3679 | 0.0462 | -0.2741 |  |  | 1.8445 | 38.1008 | 7.6182 | 36.5128 | [6 empty] | 2019-08-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72H375 | 375 W, 72 cell monocrystalline module, white backsheet | UL 1703 | 375 | 349.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 1 | N | 10.05 | 48 | 9.47 | 39.6 | 44.3 | -0.3533 | 0.0315 | -0.2594 | 1.836 | 38.6273 | 1.836 | 38.6273 | 7.5858 | 36.7949 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M3/72DH380 | 380 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 353.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.79 | 48.34 | 9.29 | 40.9 | 43.4 | -0.3884 | 0.0327 | -0.2971 |  |  | 1.9304 | 38.7643 | 7.5909 | 36.6488 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M3/72GDF380 | 380 W, 144 cell double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 352.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 9.96 | 48.47 | 9.46 | 40.17 | 43.72 | -0.3861 | 0.06 | -0.2985 |  |  | 1.9848 | 38.1957 | 7.6547 | 36.999 | [6 empty] | 2019-11-01
GCL System Integration Technology Co., Ltd. | GCL-M3/72H380 | 380 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 354.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.79 | 48.34 | 9.29 | 40.9 | 43.8 | -0.3586 | 0.0352 | -0.2819 | 1.8178 | 38.4531 | 1.8178 | 38.4531 | 7.5285 | 37.3933 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72DH380 | 380 W, 72 cell monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 352 |  | 2019-10-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 1 | N | 10.04 | 48.53 | 9.57 | 39.72 | 43.9 | -0.398 | 0.0326 | -0.309 |  |  | 1.9526 | 38.2249 | 7.8614 | 35.6086 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M6/72GDF380 | 380 W, 72 cell Monocrystalline Module, white backsheet, 1500 max system Vdc | UL 1703 | 380 | 356.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.04 | 48.53 | 9.57 | 39.72 | 42.4 | -0.3679 | 0.0462 | -0.2741 |  |  | 1.8601 | 38.2936 | 7.6824 | 36.6976 | [6 empty] | 2019-08-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72H380 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 353.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.13 | 48.2 | 9.55 | 39.8 | 45 | -0.3599 | 0.0481 | -0.2716 | 1.8515 | 38.8224 | 1.846 | 38.459 | 7.52 | 36.614 | [6 empty] | 2019-03-15 | 2019-08-15
GCL System Integration Technology Co., Ltd. | GCL-M3/72DH385 | 385 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 358 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.83 | 48.54 | 9.35 | 41.2 | 43.4 | -0.3884 | 0.0327 | -0.2971 |  |  | 1.9429 | 39.0487 | 7.6399 | 36.9176 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M3/72GDF385 | 385 W, 144 cell double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 357.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.04 | 48.66 | 9.54 | 40.36 | 43.72 | -0.3861 | 0.06 | -0.2985 |  |  | 2.0016 | 38.3763 | 7.7195 | 37.174 | [6 empty] | 2019-11-01
GCL System Integration Technology Co., Ltd. | GCL-M3/72H385 | 385 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 359.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.83 | 48.54 | 9.35 | 41.2 | 43.8 | -0.3586 | 0.0352 | -0.2819 | 1.8295 | 38.7351 | 1.8295 | 38.7351 | 7.5771 | 37.6676 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72DH385 | 385 W, 72 cell monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 356.8 |  | 2019-10-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 1 | N | 10.12 | 48.73 | 9.65 | 39.92 | 43.9 | -0.398 | 0.0326 | -0.309 |  |  | 1.969 | 38.4174 | 7.9272 | 35.7879 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M6/72GDF385 | 385 W, 72 cell Monocrystalline Module, white backsheet, 1500 max system Vdc | UL 1703 | 385 | 360.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 1 | N | 10.12 | 48.73 | 9.65 | 39.92 | 42.4 | -0.3679 | 0.0462 | -0.2741 |  |  | 1.8756 | 38.4865 | 7.7467 | 36.8823 | [6 empty] | 2019-08-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72H385 | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 358.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.21 | 48.4 | 9.63 | 39.98 | 45 | -0.3599 | 0.0481 | -0.2716 | 1.867 | 38.998 | 1.8615 | 38.6329 | 7.583 | 36.7796 | [6 empty] | 2019-03-15 | 2019-08-15
GCL System Integration Technology Co., Ltd. | GCL-M3/72DH390 | 390 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 362.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.87 | 48.74 | 9.4 | 41.5 | 43.4 | -0.3884 | 0.0327 | -0.2971 |  |  | 1.9532 | 39.333 | 7.6807 | 37.1865 | [6 empty] | 2020-02-11
GCL System Integration Technology Co., Ltd. | GCL-M3/72GDF390 | 390 W, 144 cell double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 362.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.12 | 48.85 | 9.62 | 40.55 | 43.72 | -0.3861 | 0.06 | -0.2985 |  |  | 2.0184 | 38.557 | 7.7842 | 37.349 | [6 empty] | 2019-11-01
GCL System Integration Technology Co., Ltd. | GCL-M3/72H390 | 390 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 364.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.87 | 48.74 | 9.4 | 41.5 | 43.8 | -0.3586 | 0.0352 | -0.2819 | 1.8393 | 39.0172 | 1.8393 | 39.0172 | 7.6177 | 37.9418 | [6 empty] | 2019-03-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72H390 | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 363 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.29 | 48.6 | 9.71 | 40.17 | 45 | -0.3599 | 0.0481 | -0.2716 | 1.8825 | 39.1833 | 1.8769 | 38.8165 | 7.646 | 36.9544 | [6 empty] | 2019-03-15 | 2019-08-15
GCL System Integration Technology Co., Ltd. | GCL-M6/72H395 | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 367.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.37 | 48.8 | 9.79 | 40.35 | 45 | -0.3599 | 0.0481 | -0.2716 |  |  | 1.8924 | 38.9905 | 7.709 | 37.12 | [6 empty] | 2019-08-15
GE Energy | GEPVp-200-M | 200 W Polycrystalline Module | UL 1703 | 200 | 173.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4568 | 54 | 1 | N | 8.25 | 32.6 | 7.7 | 25.9 | 50.5 | -0.49162 | 0.074257 | -0.37148 | 0.032086 | -0.52083 | 1.5235 | 24.841 | 6.0015 | 22.2679 | Rack | Flat Plate | 0.981 | 1.485 | 1 | 0.18923
GE Energy | GEPVp-205-M | 205 W Polycrystalline Module | UL 1703 | 205 | 177.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4568 | 54 | 1 | N | 8.2 | 33 | 7.6 | 27.2 | 50.5 | -0.49162 | 0.074257 | -0.37148 | 0.032086 | -0.52083 | 1.5037 | 26.0879 | 5.9235 | 23.3856 | Rack | Flat Plate | 0.981 | 1.485 | 1 | 0.19136
GermanSolar USA | GSP6-60-245W | 245 W Polycrystalline Module | UL 1703 | 245 | 219.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.645 | 60 | 1 | N | 8.76 | 37.5 | 8.14 | 30.1 | 45.7 | -0.473 | 0.0513 | -0.3596 | 0.0035 | -0.473 | 1.6222 | 29.0324 | 6.4595 | 27.2234 | Rack | Flat Plate | 0.997 | 1.65 | 1 | 0.19223
GermanSolar USA | GSP6-60-250W | 250 W Polycrystalline Module | UL 1703 | 250 | 225.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.85 | 37.5 | 8.31 | 30.1 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.69 | 29.31 | 6.59 | 27.05 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19814
GermanSolar USA | GSP6-60-255W | 255 W Polycrystalline Module | UL 1703 | 255 | 230.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.95 | 37.8 | 8.39 | 30.5 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.7 | 29.7 | 6.66 | 27.41 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.198
GermanSolar USA | GSM6-60-260W | 260 W Monocrystalline Module | UL 1703 | 260 | 235.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.14 | 38.1 | 8.47 | 30.7 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.6 | 30.3 | 6.71 | 27.89 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18646
GermanSolar USA | GSP6-60-260W | 260 W Polycrystalline Module | UL 1703 | 260 | 234.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.01 | 38 | 8.42 | 30.7 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.71 | 29.9 | 6.68 | 27.59 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19665
GermanSolar USA | GSM6-60-265W | 265 W Monocrystalline Module | UL 1703 | 265 | 239.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.16 | 38.3 | 8.56 | 30.95 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.61 | 30.55 | 6.78 | 28.12 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18561
GermanSolar USA | GSP6-60-265W | 265 W Polycrystalline Module | UL 1703 | 265 | 239.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.2 | 38.3 | 8.47 | 30.89 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.72 | 30.08 | 6.72 | 27.76 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19524
GermanSolar USA | GSM6-60-270W | 270 W Monocrystalline Module | UL 1703 | 270 | 242.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.34 | 38.63 | 8.81 | 30.72 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.2417 | 29.8406 | 8.81 | 26.3425 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24775
GermanSolar USA | GSP6-60-270W | 270 W Polycrystalline Module | UL 1703 | 270 | 244.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.31 | 38.5 | 8.57 | 31.11 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.74 | 30.3 | 6.8 | 27.96 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19527
GermanSolar USA | GSM6-60-275W | 275 W Monocrystalline Module | UL 1703 | 275 | 246.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.42 | 38.97 | 8.88 | 30.99 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.2595 | 30.1029 | 8.88 | 26.574 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24733
GermanSolar USA | GSM6-60-280W | 280 W Monocrystalline Module | UL 1703 | 280 | 251.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.51 | 39.31 | 8.96 | 31.26 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.2798 | 30.3652 | 8.96 | 26.8055 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24724
GermanSolar USA | GSM6-60-285W | 285 W Monocrystalline Module | UL 1703 | 285 | 256 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.59 | 39.65 | 9.04 | 31.53 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.3002 | 30.6274 | 9.04 | 27.037 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24719
GermanSolar USA | GSM6-60-290W | 290 W Monocrystalline Module | UL 1703 | 290 | 260.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.67 | 39.99 | 9.12 | 31.8 | 47.4 | -0.4509 | 0.0521 | -0.3137 | 0.0113 | -0.4632 | 2.3205 | 30.8897 | 9.12 | 27.2686 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24718
GermanSolar USA | GSM6-60-295W | 295 W Monocrystalline Module | UL 1703 | 295 | 266.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.645 | 60 | 1 | N | 9.67 | 39.64 | 9.2 | 32.14 | 45.92 | -0.4566 | 0.0261 | -0.341 | -0.026 | -0.4525 | 1.8379 | 32.6941 | 7.2485 | 29.3077 | Rack | Flat Plate | 0.997 | 1.65 | 1 | 0.20369
GermanSolar USA | GSM6-60-300W | 300 W Monocrystalline Module | UL 1703 | 300 | 271.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.645 | 60 | 1 | N | 9.78 | 39.82 | 9.33 | 32.25 | 45.92 | -0.4566 | 0.0261 | -0.341 | -0.026 | -0.4525 | 1.8639 | 32.806 | 7.3509 | 29.408 | Rack | Flat Plate | 0.997 | 1.65 | 1 | 0.20382
GermanSolar USA | GSP6-72-300W | 300 W Polycrystalline Module | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.79 | 45.3 | 8.12 | 36.5 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.53 | 35.71 | 6.48 | 32.96 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18212
GermanSolar USA | GSP6-72-305W | 305 W Polycrystalline Module | UL 1703 | 305 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 45.6 | 8.16 | 37.4 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.54 | 36.59 | 6.52 | 33.77 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18475
GermanSolar USA | GSM6-72-310W | 310 W Monocrystalline Module | UL 1703 | 310 | 280.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9 | 46.1 | 8.33 | 37.2 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.56 | 36.59 | 6.55 | 34.06 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18413
GermanSolar USA | GSP6-72-310W | 310 W Polycrystalline Module | UL 1703 | 310 | 280 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.08 | 45.8 | 8.22 | 37.7 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.55 | 36.89 | 6.56 | 34.04 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18445
GermanSolar USA | GSM6-72-315W | 315 W Monocrystalline Module | UL 1703 | 315 | 285.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 46.1 | 8.38 | 37.6 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.57 | 36.99 | 6.59 | 34.42 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18436
GermanSolar USA | GSP6-72-315W | 315 W Polycrystalline Module | UL 1703 | 315 | 284.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.17 | 45.9 | 8.31 | 37.9 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.56 | 37.08 | 6.64 | 34.22 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18363
GermanSolar USA | GSM6-72-320W | 320 W Monocrystalline Module | UL 1703 | 320 | 289.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.08 | 46.3 | 8.46 | 37.8 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.59 | 37.18 | 6.65 | 34.61 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18474
GermanSolar USA | GSP6-72-320W | 320 W Polycrystalline Module | UL 1703 | 320 | 289.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.2 | 46.2 | 8.33 | 38.4 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.57 | 37.57 | 6.65 | 34.67 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18433
GermanSolar USA | GSM6-72-325W | 325 W Monocrystalline Module | UL 1703 | 325 | 294.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.11 | 46.55 | 8.55 | 37.98 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.6 | 37.36 | 6.73 | 34.77 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18393
GermanSolar USA | GSP6-72-325W | 325 W Polycrystalline Module | UL 1703 | 325 | 294 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.25 | 46.4 | 8.37 | 38.8 | 45.4 | -0.4577 | 0.0622 | -0.3529 | 0.0111 | -0.4691 | 1.58 | 37.96 | 6.68 | 35.04 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18454
GermanSolar USA | GSM6-72-330W | 330 W Monocrystalline Module | UL 1703 | 330 | 299.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.15 | 46.84 | 8.61 | 38.31 | 45.7 | -0.4436 | 0.0414 | -0.3583 | 0.018 | -0.4326 | 1.61 | 37.68 | 6.77 | 35.07 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18383
GermanSolar USA | GSM6-72-335W | 335 W Monocrystalline Module | UL 1703 | 335 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.18 | 46.99 | 8.7 | 38.49 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.69 | 37.56 | 6.93 | 34.79 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18948
Gintech Energy | GTE 200M | 200 W Polycrystalline Module | UL 1703 | 200 | 178.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6817 | 60 | 1 | N | 8.01 | 35.9 | 7.38 | 29.3 | 43.1 | -0.5417 | 0.0422 | -0.3701 | -0.0519 | -0.4928 | 1.424 | 29.9875 | 5.7924 | 26.5502 | Rack | Flat Plate | 1.01 | 1.665 | 1 | 0.21352
Gintech Energy | GTE 205M | 205 W Polycrystalline Module | UL 1703 | 205 | 182.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6817 | 60 | 1 | N | 8.02 | 35.9 | 7.39 | 29.3 | 43.1 | -0.5417 | 0.0422 | -0.3701 | -0.0519 | -0.4928 | 1.426 | 29.9875 | 5.8002 | 26.5502 | Rack | Flat Plate | 1.01 | 1.665 | 1 | 0.20859
Gintech Energy | GTE 210M | 210 W Polycrystalline Module | UL 1703 | 210 | 187.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6817 | 60 | 1 | N | 8.04 | 35.92 | 7.4 | 29.32 | 43.1 | -0.5417 | 0.0422 | -0.3701 | -0.0519 | -0.4928 | 1.4279 | 30.0079 | 5.8081 | 26.5683 | Rack | Flat Plate | 1.01 | 1.665 | 1 | 0.20404
Gintech Energy | GTE 215M | 215 W Polycrystalline Module | UL 1703 | 215 | 192 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6817 | 60 | 1 | N | 8.05 | 35.94 | 7.58 | 29.34 | 43.1 | -0.5417 | 0.0422 | -0.3701 | -0.0519 | -0.4928 | 1.4626 | 30.0284 | 5.9494 | 26.5864 | Rack | Flat Plate | 1.01 | 1.665 | 1 | 0.20428
Gintech Energy | GTE 220M | 220 W Polycrystalline Module | UL 1703 | 220 | 196.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6817 | 60 | 1 | N | 8.08 | 36.06 | 7.58 | 29.58 | 43.1 | -0.5417 | 0.0422 | -0.3701 | -0.0519 | -0.4928 | 1.5423 | 30.1905 | 5.9436 | 27.0972 | Rack | Flat Plate | 1.01 | 1.665 | 1 | 0.21165
Gintech Energy | GTE 225M | 225 W Polycrystalline Module | UL 1703 | 225 | 201.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6817 | 60 | 1 | N | 8.25 | 36.66 | 7.66 | 30 | 43.1 | -0.5417 | 0.0422 | -0.3701 | -0.0519 | -0.4928 | 1.5586 | 30.6192 | 6.0064 | 27.4819 | Rack | Flat Plate | 1.01 | 1.665 | 1 | 0.2121
Gintech Energy | GTE 230M | 230 W Polycrystalline Module | UL 1703 | 230 | 205.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6817 | 60 | 1 | N | 8.31 | 36.9 | 7.77 | 30.3 | 43.1 | -0.5417 | 0.0422 | -0.3701 | -0.0519 | -0.4928 | 1.581 | 30.9254 | 6.0926 | 27.7568 | Rack | Flat Plate | 1.01 | 1.665 | 1 | 0.21258
Gintech Energy | GTE 235M | 235 W Polycrystalline Module | UL 1703 | 235 | 210.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6817 | 60 | 1 | N | 8.41 | 37.32 | 7.92 | 30.54 | 43.1 | -0.5417 | 0.0422 | -0.3701 | -0.0519 | -0.4928 | 1.6115 | 31.1703 | 6.2102 | 27.9766 | Rack | Flat Plate | 1.01 | 1.665 | 1 | 0.21375
Gintech Energy | GTE 240M | 240 W Polycrystalline Module | UL 1703 | 240 | 214.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6817 | 60 | 1 | N | 8.46 | 37.5 | 7.97 | 30.72 | 43.1 | -0.5417 | 0.0422 | -0.3701 | -0.0519 | -0.4928 | 1.6217 | 31.3541 | 6.2494 | 28.1415 | Rack | Flat Plate | 1.01 | 1.665 | 1 | 0.21186
Gintung Energy | ASEC-120G6M | 120 W Polycrystalline Module | UL 1703 | 120 | 106.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 0.98287 | 36 | 1 | N | 7.49 | 21.6 | 6.93 | 17.33 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.3713 | 17.04 | 5.5495 | 15.79 | Rack | Flat Plate | 0.657 | 1.496 | 1 | 0.19472
Gintung Energy | ASEC-125G6M | 125 W Polycrystalline Module | UL 1703 | 125 | 111.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 0.98287 | 36 | 1 | N | 7.89 | 21.58 | 7.28 | 17.19 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.4405 | 16.9023 | 5.8298 | 15.6624 | Rack | Flat Plate | 0.657 | 1.496 | 1 | 0.19479
Gintung Energy | ASEC-125G6S | 125 W Monocrystalline Module | UL 1703 | 125 | 111.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.98287 | 36 | 1 | N | 8.01 | 21.55 | 7.23 | 17.29 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.4536 | 17.2801 | 5.7953 | 15.7947 | Rack | Flat Plate | 0.657 | 1.496 | 1 | 0.20094
Gintung Energy | ASEC-130G6M | 130 W Polycrystalline Module | UL 1703 | 130 | 116 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 0.98287 | 36 | 1 | N | 7.93 | 21.66 | 7.45 | 17.54 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.4919 | 17.3214 | 5.9581 | 15.9798 | Rack | Flat Plate | 0.657 | 1.496 | 1 | 0.19879
Gintung Energy | ASEC-130G6S | 130 W Monocrystalline Module | UL 1703 | 130 | 116.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.98287 | 36 | 1 | N | 8.11 | 21.96 | 7.44 | 17.48 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.4958 | 17.47 | 5.9637 | 15.9683 | Rack | Flat Plate | 0.657 | 1.496 | 1 | 0.20101
Gintung Energy | ASEC-135G6M | 135 W Polycrystalline Module | UL 1703 | 135 | 120.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 0.98287 | 36 | 1 | N | 8.26 | 22.1 | 7.64 | 17.68 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.53 | 17.4596 | 6.11 | 16.1073 | Rack | Flat Plate | 0.657 | 1.496 | 1 | 0.19787
Gintung Energy | ASEC-135G6S | 135 W Monocrystalline Module | UL 1703 | 135 | 120.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.98287 | 36 | 1 | N | 8.27 | 22.15 | 7.7 | 17.54 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.5501 | 17.244 | 6.1701 | 16.0208 | Rack | Flat Plate | 0.657 | 1.496 | 1 | 0.198
Gintung Energy | ASEC-140G6M | 140 W Polycrystalline Module | UL 1703 | 140 | 125.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 0.98287 | 36 | 1 | N | 8.57 | 22.25 | 7.89 | 17.75 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.58 | 17.5288 | 6.31 | 16.1711 | Rack | Flat Plate | 0.657 | 1.496 | 1 | 0.19783
Gintung Energy | ASEC-140G6S | 140 W Monocrystalline Module | UL 1703 | 140 | 125.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.98287 | 36 | 1 | N | 8.47 | 22.25 | 7.95 | 17.62 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6004 | 17.3227 | 6.3704 | 16.0939 | Rack | Flat Plate | 0.657 | 1.496 | 1 | 0.19802
Gintung Energy | ASEC-145G6M49 | 145 W Polycrystalline Module | UL 1703 | 145 | 127.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 0.98635 | 36 | 1 | N | 8.66 | 22.32 | 8.14 | 17.81 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.6973 | 17.7882 | 6.572 | 16.0243 | Rack | Flat Plate | 0.666 | 1.481 | 1 | 0.20822
Gintung Energy | ASEC-145G6S49 | 145 W Monocrystalline Module | UL 1703 | 145 | 126.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.98635 | 36 | 1 | N | 8.64 | 22.38 | 8.2 | 17.68 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7009 | 17.6607 | 6.6029 | 15.7086 | Rack | Flat Plate | 0.666 | 1.481 | 1 | 0.20717
Gintung Energy | ASEC-150G6M49 | 150 W Polycrystalline Module | UL 1703 | 150 | 131.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 0.98635 | 36 | 1 | N | 8.81 | 22.4 | 8.37 | 17.92 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7452 | 17.8981 | 6.7577 | 16.1232 | Rack | Flat Plate | 0.666 | 1.481 | 1 | 0.20824
Gintung Energy | ASEC-150G6S49 | 150 W Monocrystalline Module | UL 1703 | 150 | 131.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.98635 | 36 | 1 | N | 8.78 | 22.48 | 8.43 | 17.79 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7486 | 17.7705 | 6.7881 | 15.8063 | Rack | Flat Plate | 0.666 | 1.481 | 1 | 0.20716
Gintung Energy | ASEC-155G6M49 | 155 W Polycrystalline Module | UL 1703 | 155 | 136.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 0.98635 | 36 | 1 | N | 8.98 | 22.53 | 8.58 | 18.07 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.789 | 18.0479 | 6.9273 | 16.2582 | Rack | Flat Plate | 0.666 | 1.481 | 1 | 0.20831
Gintung Energy | ASEC-155G6S49 | 155 W Monocrystalline Module | UL 1703 | 155 | 135.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.98635 | 36 | 1 | N | 8.96 | 22.58 | 8.64 | 17.94 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7922 | 17.9204 | 6.9572 | 15.9396 | Rack | Flat Plate | 0.666 | 1.481 | 1 | 0.2072
Gintung Energy | ASEC-175G6M | 175 W Polycrystalline Module | UL 1703 | 175 | 155.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.03 | 29.29 | 7.48 | 23.41 | 45.9 | -0.483 | 0.089 | -0.35 | 0.035 | -0.511 | 1.3357 | 24.9918 | 5.521 | 21.7228 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19075
Gintung Energy | ASEC-175G6S | 175 W Monocrystalline Module | UL 1703 | 175 | 155.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.24 | 29.57 | 7.46 | 23.51 | 45.1 | -0.522 | 0.091 | -0.357 | 0.058 | -0.57 | 1.3646 | 25.0914 | 5.5495 | 21.6123 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19566
Gintung Energy | ASEC-180G6M | 180 W Polycrystalline Module | UL 1703 | 180 | 160.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.15 | 29.51 | 7.61 | 23.68 | 45.9 | -0.483 | 0.089 | -0.35 | 0.035 | -0.511 | 1.3589 | 25.28 | 5.6169 | 21.9733 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19085
Gintung Energy | ASEC-180G6S | 180 W Monocrystalline Module | UL 1703 | 180 | 159.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.3 | 29.73 | 7.58 | 23.82 | 45.1 | -0.522 | 0.091 | -0.357 | 0.058 | -0.57 | 1.3866 | 25.4222 | 5.6388 | 21.8973 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19583
Gintung Energy | ASEC-185G6M | 185 W Polycrystalline Module | UL 1703 | 185 | 165.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.23 | 29.76 | 7.79 | 23.75 | 45.9 | -0.483 | 0.089 | -0.35 | 0.035 | -0.511 | 1.3911 | 25.3547 | 5.7498 | 22.0383 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19065
Gintung Energy | ASEC-185G6S | 185 W Monocrystalline Module | UL 1703 | 185 | 164.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.33 | 29.9 | 7.63 | 24.28 | 45.1 | -0.522 | 0.091 | -0.357 | 0.058 | -0.57 | 1.3957 | 25.9132 | 5.676 | 22.3202 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.1955
Gintung Energy | ASEC-190G6M | 190 W Polycrystalline Module | UL 1703 | 190 | 167.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.407 | 54 | 1 | N | 7.87 | 32.85 | 7.56 | 25.18 | 43.9 | -0.572 | 0.183 | -0.415 | 0.019 | -0.588 | 1.4377 | 25.6291 | 6.2006 | 23.3835 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.19393
Gintung Energy | ASEC-190G6M68 | 190 W Polycrystalline Module | UL 1703 | 190 | 170 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.35 | 29.81 | 7.97 | 23.84 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.57 | 23.397 | 6.38 | 21.7258 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19333
Gintung Energy | ASEC-190G6S | 190 W Monocrystalline Module | UL 1703 | 190 | 169.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.407 | 54 | 1 | N | 8.01 | 32.83 | 7.53 | 25.25 | 44.2 | -0.514 | 0.136 | -0.371 | -0.022 | -0.495 | 1.4596 | 25.4167 | 6.1574 | 23.4948 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.19525
Gintung Energy | ASEC-190G6S68 | 190 W Monocrystalline Module | UL 1703 | 190 | 170.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.51 | 29.71 | 8.05 | 23.61 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.5999 | 23.6501 | 6.4603 | 21.5639 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19914
Gintung Energy | GTEC-190G6M68 | 190 W Polycrystalline Module | UL 1703 | 190 | 170 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.35 | 29.81 | 7.97 | 23.84 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.57 | 23.4 | 6.38 | 21.73 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19336
Gintung Energy | GTEC-190G6S68 | 190 W Monocrystalline Module | UL 1703 | 190 | 170.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.51 | 29.71 | 8.05 | 23.61 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6 | 23.65 | 6.46 | 21.56 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19916
Gintung Energy | ASEC-195G6M | 195 W Polycrystalline Module | UL 1703 | 195 | 172.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.407 | 54 | 1 | N | 8.11 | 32.94 | 7.63 | 25.59 | 43.9 | -0.572 | 0.19 | -0.42 | 0.29 | -0.588 | 1.451 | 26.0464 | 6.258 | 23.7643 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.19381
Gintung Energy | ASEC-195G6M68 | 195 W Polycrystalline Module | UL 1703 | 195 | 174.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.48 | 29.87 | 8.16 | 23.9 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.6074 | 23.4559 | 6.5321 | 21.7805 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19335
Gintung Energy | ASEC-195G6S | 195 W Monocrystalline Module | UL 1703 | 195 | 174.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.407 | 54 | 1 | N | 8.21 | 32.95 | 7.71 | 25.31 | 44.2 | -0.514 | 0.136 | -0.371 | -0.022 | -0.495 | 1.4945 | 25.4771 | 6.3046 | 23.5506 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.19526
Gintung Energy | ASEC-195G6S68 | 195 W Monocrystalline Module | UL 1703 | 195 | 175 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.63 | 29.82 | 8.24 | 23.67 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6376 | 23.7102 | 6.6127 | 21.6187 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19912
Gintung Energy | GTEC-195G6M68 | 195 W Polycrystalline Module | UL 1703 | 195 | 174.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.48 | 29.87 | 8.16 | 23.9 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.61 | 23.46 | 6.53 | 21.78 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.1937
Gintung Energy | GTEC-195G6S68 | 195 W Monocrystalline Module | UL 1703 | 195 | 175 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.63 | 29.82 | 8.24 | 23.67 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.64 | 23.71 | 6.61 | 21.62 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.19941
Gintung Energy | ASEC-200G6M | 200 W Polycrystalline Module | UL 1703 | 200 | 176.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.407 | 54 | 1 | N | 8.31 | 33.03 | 7.85 | 25.5 | 43.9 | -0.572 | 0.19 | -0.42 | 0.29 | -0.588 | 1.4928 | 25.9548 | 6.4384 | 23.6807 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.19373
Gintung Energy | ASEC-200G6M68 | 200 W Polycrystalline Module | UL 1703 | 200 | 175.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.65 | 29.95 | 8.31 | 24.07 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7261 | 24.0871 | 6.7009 | 21.6375 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20788
Gintung Energy | ASEC-200G6S | 200 W Monocrystalline Module | UL 1703 | 200 | 179 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.407 | 54 | 1 | N | 8.24 | 33.53 | 7.89 | 25.38 | 44.2 | -0.514 | 0.136 | -0.371 | -0.022 | -0.495 | 1.5294 | 25.5476 | 6.4518 | 23.6157 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.19536
Gintung Energy | ASEC-200G6S68 | 200 W Monocrystalline Module | UL 1703 | 200 | 175.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.77 | 29.93 | 8.39 | 23.84 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7324 | 23.7335 | 6.763 | 21.1609 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20558
Gintung Energy | GTEC-200G6M68 | 200 W Polycrystalline Module | UL 1703 | 200 | 175.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.65 | 29.95 | 8.31 | 24.07 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.73 | 24.09 | 6.7 | 21.64 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20838
Gintung Energy | GTEC-200G6S68 | 200 W Monocrystalline Module | UL 1703 | 200 | 175.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.77 | 29.93 | 8.39 | 23.84 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.73 | 23.73 | 6.76 | 21.16 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20526
Gintung Energy | ASEC-205G6M | 205 W Polycrystalline Module | UL 1703 | 205 | 181.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.407 | 54 | 1 | N | 8.61 | 33.58 | 7.93 | 25.87 | 43.9 | -0.572 | 0.19 | -0.42 | 0.29 | -0.588 | 1.508 | 26.3314 | 6.504 | 24.0243 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.1937
Gintung Energy | ASEC-205G6M68 | 205 W Polycrystalline Module | UL 1703 | 205 | 180.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.83 | 30.03 | 8.46 | 24.23 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7572 | 24.2472 | 6.8218 | 21.7814 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20785
Gintung Energy | ASEC-205G6S | 205 W Monocrystalline Module | UL 1703 | 205 | 183.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.407 | 54 | 1 | N | 8.32 | 33.64 | 7.93 | 25.87 | 44.2 | -0.514 | 0.136 | -0.371 | -0.022 | -0.495 | 1.5371 | 26.0408 | 6.4845 | 24.0717 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.19526
Gintung Energy | ASEC-205G6S68 | 205 W Monocrystalline Module | UL 1703 | 205 | 179.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.91 | 30.04 | 8.54 | 24 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7634 | 23.8928 | 6.8839 | 21.303 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20552
Gintung Energy | GTEC-205G6M68 | 205 W Polycrystalline Module | UL 1703 | 205 | 180.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.83 | 30.03 | 8.46 | 24.23 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.76 | 24.25 | 6.82 | 21.78 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.2082
Gintung Energy | GTEC-205G6S68 | 205 W Monocrystalline Module | UL 1703 | 205 | 179.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 8.91 | 30.04 | 8.54 | 24 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.76 | 23.89 | 6.88 | 21.3 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.2051
Gintung Energy | ASEC-210G6M | 210 W Polycrystalline Module | UL 1703 | 210 | 186.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.407 | 54 | 1 | N | 8.65 | 33.61 | 8.02 | 26.19 | 43.9 | -0.572 | 0.19 | -0.42 | 0.29 | -0.588 | 1.5251 | 26.6571 | 6.5779 | 24.3215 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.1936
Gintung Energy | ASEC-210G6M68 | 210 W Polycrystalline Module | UL 1703 | 210 | 185 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.99 | 30.14 | 8.63 | 24.33 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7926 | 24.3472 | 6.9589 | 21.8712 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20783
Gintung Energy | ASEC-210G6S | 210 W Monocrystalline Module | UL 1703 | 210 | 188.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.407 | 54 | 1 | N | 8.35 | 33.68 | 7.98 | 26.33 | 44.2 | -0.514 | 0.136 | -0.371 | -0.022 | -0.495 | 1.5468 | 26.5038 | 6.5254 | 24.4997 | Rack | Flat Plate | 0.965 | 1.458 | 1 | 0.19522
Gintung Energy | ASEC-210G6S68 | 210 W Monocrystalline Module | UL 1703 | 210 | 184.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 9.05 | 30.14 | 8.71 | 24.11 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7985 | 24.0023 | 7.0209 | 21.4006 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20556
Gintung Energy | GTEC-210G6M68 | 210 W Polycrystalline Module | UL 1703 | 210 | 185 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 8.99 | 30.14 | 8.63 | 24.33 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.79 | 24.35 | 6.96 | 21.87 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20755
Gintung Energy | GTEC-210G6S68 | 210 W Monocrystalline Module | UL 1703 | 210 | 184.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 9.05 | 30.14 | 8.71 | 24.11 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.8 | 24 | 7.02 | 21.4 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20571
Gintung Energy | ASEC-215G6M | 215 W Polycrystalline Module | UL 1703 | 215 | 192 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 7.96 | 36.39 | 7.41 | 29.02 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.4706 | 28.7724 | 6.0058 | 26.3557 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.19681
Gintung Energy | ASEC-215G6M68 | 215 W Polycrystalline Module | UL 1703 | 215 | 189.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 9.14 | 30.27 | 8.79 | 24.46 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8258 | 24.4773 | 7.0879 | 21.9881 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20786
Gintung Energy | ASEC-215G6M69 | 215 W Polycrystalline Module | UL 1703 | 215 | 192.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 8.71 | 33.69 | 8.08 | 26.61 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.6283 | 25.6029 | 6.462 | 24.2403 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.1939
Gintung Energy | ASEC-215G6S | 215 W Monocrystalline Module | UL 1703 | 215 | 192.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.07 | 36.4 | 7.45 | 28.88 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.5185 | 28.8304 | 5.96 | 26.4783 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20362
Gintung Energy | ASEC-215G6S68 | 215 W Monocrystalline Module | UL 1703 | 215 | 188.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 9.18 | 30.26 | 8.87 | 24.24 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.8315 | 24.1317 | 7.1499 | 21.516 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20557
Gintung Energy | ASEC-215G6S69 | 215 W Monocrystalline Module | UL 1703 | 215 | 192.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 8.47 | 33.77 | 8.09 | 26.58 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6281 | 26.1926 | 6.5023 | 24.2061 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.19835
Gintung Energy | GTEC-215G6M68 | 215 W Polycrystalline Module | UL 1703 | 215 | 189.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 9.14 | 30.27 | 8.79 | 24.46 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.83 | 24.48 | 7.09 | 21.99 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20836
Gintung Energy | GTEC-215G6M69 | 215 W Polycrystalline Module | UL 1703 | 215 | 192.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 8.71 | 33.69 | 8.08 | 26.61 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.63 | 25.6 | 6.46 | 24.24 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.19408
Gintung Energy | GTEC-215G6S68 | 215 W Monocrystalline Module | UL 1703 | 215 | 188.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 9.18 | 30.26 | 8.87 | 24.24 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.83 | 24.13 | 7.15 | 21.52 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20539
Gintung Energy | GTEC-215G6S69 | 215 W Monocrystalline Module | UL 1703 | 215 | 192.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 8.47 | 33.77 | 8.09 | 26.58 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.63 | 26.19 | 6.5 | 24.21 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.19856
Gintung Energy | ASEC-220G6M | 220 W Polycrystalline Module | UL 1703 | 220 | 196.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.1 | 36.57 | 7.56 | 29.11 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.5004 | 28.8616 | 6.1274 | 26.4374 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.19683
Gintung Energy | ASEC-220G6M68 | 220 W Polycrystalline Module | UL 1703 | 220 | 194.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 9.29 | 30.4 | 8.95 | 24.58 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.859 | 24.5974 | 7.217 | 22.096 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20785
Gintung Energy | ASEC-220G6M69 | 220 W Polycrystalline Module | UL 1703 | 220 | 197.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 8.75 | 33.75 | 8.24 | 26.71 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.6605 | 25.6991 | 6.5899 | 24.3314 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.19397
Gintung Energy | ASEC-220G6S | 220 W Monocrystalline Module | UL 1703 | 220 | 197 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.21 | 36.53 | 7.59 | 28.99 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.547 | 28.9402 | 6.072 | 26.5791 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.2035
Gintung Energy | ASEC-220G6S68 | 220 W Monocrystalline Module | UL 1703 | 220 | 193.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 9.32 | 30.34 | 9.03 | 24.36 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.8646 | 24.2512 | 7.2789 | 21.6225 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20553
Gintung Energy | ASEC-220G6S69 | 220 W Monocrystalline Module | UL 1703 | 220 | 197.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 8.61 | 33.86 | 8.25 | 26.67 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6603 | 26.2813 | 6.6309 | 24.288 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.19834
Gintung Energy | GTEC-220G6M68 | 220 W Polycrystalline Module | UL 1703 | 220 | 194.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3045 | 48 | 1 | N | 9.29 | 30.4 | 8.95 | 24.58 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.86 | 24.6 | 7.22 | 22.1 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20798
Gintung Energy | GTEC-220G6M69 | 220 W Polycrystalline Module | UL 1703 | 220 | 197.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 8.75 | 33.75 | 8.24 | 26.71 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.66 | 25.7 | 6.59 | 24.33 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.19392
Gintung Energy | GTEC-220G6S68 | 220 W Monocrystalline Module | UL 1703 | 220 | 193.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.3045 | 48 | 1 | N | 9.32 | 30.34 | 9.03 | 24.36 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.86 | 24.25 | 7.28 | 21.62 | Rack | Flat Plate | 0.989 | 1.319 | 1 | 0.20502
Gintung Energy | GTEC-220G6S69 | 220 W Monocrystalline Module | UL 1703 | 220 | 197.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 8.61 | 33.86 | 8.25 | 26.67 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.66 | 26.28 | 6.63 | 24.29 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.19829
Gintung Energy | ASEC-225G6M | 225 W Polycrystalline Module | UL 1703 | 225 | 201.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.21 | 36.75 | 7.71 | 29.19 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.5302 | 28.9409 | 6.249 | 26.5101 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.19682
Gintung Energy | ASEC-225G6M69 | 225 W Polycrystalline Module | UL 1703 | 225 | 197.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 8.81 | 33.83 | 8.37 | 26.88 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7407 | 26.5954 | 6.7477 | 24.1268 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20575
Gintung Energy | ASEC-225G6S | 225 W Monocrystalline Module | UL 1703 | 225 | 201.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.33 | 36.65 | 7.74 | 29.08 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.5776 | 29.03 | 6.192 | 26.6617 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20354
Gintung Energy | ASEC-225G6S69 | 225 W Monocrystalline Module | UL 1703 | 225 | 197.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 8.75 | 33.92 | 8.38 | 26.85 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7365 | 26.5625 | 6.7727 | 23.7801 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20501
Gintung Energy | GTEC-225G6M69 | 225 W Polycrystalline Module | UL 1703 | 225 | 197.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 8.81 | 33.83 | 8.37 | 26.88 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.74 | 26.6 | 6.75 | 24.13 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20571
Gintung Energy | GTEC-225G6S69 | 225 W Monocrystalline Module | UL 1703 | 225 | 197.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 8.75 | 33.92 | 8.38 | 26.85 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.74 | 26.56 | 6.77 | 23.78 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.2054
Gintung Energy | ASEC-230G6M | 230 W Polycrystalline Module | UL 1703 | 230 | 205.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.32 | 36.87 | 7.85 | 29.3 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.5523 | 28.7734 | 6.2682 | 26.8857 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.1942
Gintung Energy | ASEC-230G6M69 | 230 W Polycrystalline Module | UL 1703 | 230 | 202.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 8.92 | 33.93 | 8.51 | 27.03 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7698 | 26.7438 | 6.8606 | 24.2614 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20579
Gintung Energy | ASEC-230G6S | 230 W Monocrystalline Module | UL 1703 | 230 | 206.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.46 | 36.75 | 7.88 | 29.19 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6057 | 28.2912 | 6.3833 | 26.5719 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.19751
Gintung Energy | ASEC-230G6S69 | 230 W Monocrystalline Module | UL 1703 | 230 | 201.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 8.88 | 34.08 | 8.52 | 27 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7655 | 26.7109 | 6.8859 | 23.913 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20504
Gintung Energy | GTEC-230G6M69 | 230 W Polycrystalline Module | UL 1703 | 230 | 202.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 8.92 | 33.93 | 8.51 | 27.03 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.77 | 26.74 | 6.86 | 24.26 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20578
Gintung Energy | GTEC-230G6S69 | 230 W Monocrystalline Module | UL 1703 | 230 | 201.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 8.88 | 34.08 | 8.52 | 27 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.77 | 26.71 | 6.89 | 23.91 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20555
Gintung Energy | ASEC-235G6M | 235 W Polycrystalline Module | UL 1703 | 235 | 210.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.45 | 37.06 | 8.01 | 29.34 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.584 | 28.8127 | 6.396 | 26.9224 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.1942
Gintung Energy | ASEC-235G6M69 | 235 W Polycrystalline Module | UL 1703 | 235 | 207 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 9.02 | 34.06 | 8.64 | 27.2 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7969 | 26.912 | 6.9654 | 24.414 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20578
Gintung Energy | ASEC-235G6S | 235 W Monocrystalline Module | UL 1703 | 235 | 210.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.58 | 36.88 | 8.03 | 29.27 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6363 | 28.3688 | 6.5048 | 26.6447 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.19753
Gintung Energy | ASEC-235G6S69 | 235 W Monocrystalline Module | UL 1703 | 235 | 206.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 9 | 34.13 | 8.65 | 27.17 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7925 | 26.8791 | 6.991 | 24.0635 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20502
Gintung Energy | GTEC-235G6M69 | 235 W Polycrystalline Module | UL 1703 | 235 | 207 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 9.02 | 34.06 | 8.64 | 27.2 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8 | 26.91 | 6.97 | 24.41 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20612
Gintung Energy | GTEC-235G6S69 | 235 W Monocrystalline Module | UL 1703 | 235 | 206.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 9 | 34.13 | 8.65 | 27.17 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.79 | 26.88 | 6.99 | 24.06 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20475
Gintung Energy | ASEC-240G6M69 | 240 W Polycrystalline Module | UL 1703 | 240 | 211.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 9.14 | 34.19 | 8.77 | 27.37 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8239 | 27.0802 | 7.0702 | 24.5666 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.2058
Gintung Energy | ASEC-240G6M6A | 240 W Polycrystalline Module | UL 1703 | 240 | 214.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.18 | 8.16 | 29.42 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.6632 | 29.3695 | 6.528 | 26.9734 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20353
Gintung Energy | ASEC-240G6S69 | 240 W Monocrystalline Module | UL 1703 | 240 | 210.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 9.14 | 34.19 | 8.78 | 27.33 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.8194 | 27.0374 | 7.096 | 24.2052 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20497
Gintung Energy | ASEC-240G6S6A | 240 W Monocrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.01 | 8.17 | 29.38 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6652 | 29.3295 | 6.536 | 26.9367 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.2035
Gintung Energy | GTEC-240G6M69 | 240 W Polycrystalline Module | UL 1703 | 240 | 211.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 9.14 | 34.19 | 8.77 | 27.37 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.82 | 27.08 | 7.07 | 24.57 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20536
Gintung Energy | GTEC-240G6M6A | 240 W Polycrystalline Module | UL 1703 | 240 | 214.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.55 | 37.18 | 8.16 | 29.42 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.66 | 29.37 | 6.53 | 26.97 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20314
Gintung Energy | GTEC-240G6S69 | 240 W Monocrystalline Module | UL 1703 | 240 | 210.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 9.14 | 34.19 | 8.78 | 27.33 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.82 | 27.04 | 7.1 | 24.21 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20505
Gintung Energy | GTEC-240G6S6A | 240 W Monocrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.68 | 37.01 | 8.17 | 29.38 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.67 | 29.33 | 6.54 | 26.94 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20409
Gintung Energy | ASEC-245G6M | 245 W Polycrystalline Module | UL 1703 | 245 | 218.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 7.68 | 43.39 | 7.18 | 34.13 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.4397 | 33.5937 | 5.7683 | 31.2664 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19741
Gintung Energy | ASEC-245G6M69 | 245 W Polycrystalline Module | UL 1703 | 245 | 216.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 9.26 | 34.36 | 8.92 | 27.47 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8551 | 27.1792 | 7.1911 | 24.6564 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.2058
Gintung Energy | ASEC-245G6M6A | 245 W Polycrystalline Module | UL 1703 | 245 | 219.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.67 | 37.31 | 8.29 | 29.56 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.6897 | 29.5092 | 6.632 | 27.1017 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20351
Gintung Energy | ASEC-245G6S69 | 245 W Monocrystalline Module | UL 1703 | 245 | 215.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 9.28 | 34.29 | 8.93 | 27.44 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.8505 | 27.1462 | 7.2173 | 24.3027 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20504
Gintung Energy | ASEC-245G6S6A | 245 W Monocrystalline Module | UL 1703 | 245 | 220 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.81 | 37.14 | 8.31 | 29.49 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6938 | 29.4393 | 6.648 | 27.0376 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20352
Gintung Energy | GTEC-245G6M69 | 245 W Polycrystalline Module | UL 1703 | 245 | 216.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4647 | 54 | 1 | N | 9.26 | 34.36 | 8.92 | 27.47 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.86 | 27.18 | 7.19 | 24.66 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20635
Gintung Energy | GTEC-245G6M6A | 245 W Polycrystalline Module | UL 1703 | 245 | 219.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.67 | 37.31 | 8.29 | 29.56 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.69 | 29.51 | 6.63 | 27.1 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20356
Gintung Energy | GTEC-245G6S69 | 245 W Monocrystalline Module | UL 1703 | 245 | 215.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4647 | 54 | 1 | N | 9.28 | 34.29 | 8.93 | 27.44 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.85 | 27.15 | 7.22 | 24.3 | Rack | Flat Plate | 0.989 | 1.481 | 1 | 0.20501
Gintung Energy | GTEC-245G6S6A | 245 W Monocrystalline Module | UL 1703 | 245 | 220 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.81 | 37.14 | 8.31 | 29.49 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.69 | 29.44 | 6.65 | 27.04 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20308
Gintung Energy | ASEC-250G6M | 250 W Polycrystalline Module | UL 1703 | 250 | 223 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 7.78 | 43.53 | 7.29 | 34.3 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.4618 | 33.761 | 5.8567 | 31.4222 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19741
Gintung Energy | ASEC-250G6M6A | 250 W Polycrystalline Module | UL 1703 | 250 | 220 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.43 | 8.41 | 29.68 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7432 | 29.3166 | 6.7715 | 26.4891 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20442
Gintung Energy | ASEC-250G6M6B | 250 W Polycrystalline Module | UL 1703 | 250 | 219.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.25 | 40.95 | 7.81 | 32.01 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.6185 | 31.498 | 6.2945 | 28.5316 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20391
Gintung Energy | ASEC-250G6S6A | 250 W Monocrystalline Module | UL 1703 | 250 | 219.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.91 | 37.27 | 8.45 | 29.59 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7086 | 29.5476 | 6.7849 | 25.9223 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20194
Gintung Energy | ASEC-250G6S6B | 250 W Monocrystalline Module | UL 1703 | 250 | 218.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.37 | 40.36 | 7.85 | 31.85 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.6345 | 31.4514 | 6.3323 | 28.0196 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20563
Gintung Energy | GTEC-250G6M6A | 250 W Polycrystalline Module | UL 1703 | 250 | 220 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.78 | 37.43 | 8.41 | 29.68 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.74 | 29.32 | 6.77 | 26.49 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20407
Gintung Energy | GTEC-250G6S6A | 250 W Monocrystalline Module | UL 1703 | 250 | 219.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 8.91 | 37.27 | 8.45 | 29.59 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.71 | 29.55 | 6.78 | 25.92 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20212
Gintung Energy | ASEC-255G6M | 255 W Polycrystalline Module | UL 1703 | 255 | 227.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 7.89 | 43.69 | 7.4 | 34.46 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.4839 | 33.9185 | 5.9451 | 31.5688 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19737
Gintung Energy | ASEC-255G6M6A | 255 W Polycrystalline Module | UL 1703 | 255 | 224.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.9 | 37.6 | 8.54 | 29.86 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7702 | 29.4944 | 6.8761 | 26.6498 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20475
Gintung Energy | ASEC-255G6M6B | 255 W Polycrystalline Module | UL 1703 | 255 | 223.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.37 | 41.06 | 7.93 | 32.16 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.6433 | 31.6456 | 6.3913 | 28.6653 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20394
Gintung Energy | ASEC-255G6S | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 7.98 | 43.85 | 7.42 | 34.37 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.4764 | 33.707 | 5.8007 | 32.2932 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19515
Gintung Energy | ASEC-255G6S6A | 255 W Monocrystalline Module | UL 1703 | 255 | 223.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.02 | 37.35 | 8.58 | 29.72 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7349 | 29.6774 | 6.8892 | 26.0362 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20191
Gintung Energy | ASEC-255G6S6B | 255 W Monocrystalline Module | UL 1703 | 255 | 222.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.46 | 40.62 | 7.95 | 32.08 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.6554 | 31.6785 | 6.4129 | 28.2219 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20564
Gintung Energy | GTEC-255G6M6A | 255 W Polycrystalline Module | UL 1703 | 255 | 224.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 8.9 | 37.6 | 8.54 | 29.86 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.77 | 29.49 | 6.88 | 26.65 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.2047
Gintung Energy | GTEC-255G6S6A | 255 W Monocrystalline Module | UL 1703 | 255 | 223.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.02 | 37.35 | 8.58 | 29.72 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.73 | 29.68 | 6.89 | 26.04 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20136
Gintung Energy | ASEC-260G6M | 260 W Polycrystalline Module | UL 1703 | 260 | 232.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.01 | 43.84 | 7.53 | 34.53 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.5099 | 33.9874 | 6.0495 | 31.6329 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19738
Gintung Energy | ASEC-260G6M6A | 260 W Polycrystalline Module | UL 1703 | 260 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.02 | 37.78 | 8.66 | 30.02 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7951 | 29.6524 | 6.9727 | 26.7926 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20472
Gintung Energy | ASEC-260G6M6B | 260 W Polycrystalline Module | UL 1703 | 260 | 228.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.48 | 41.21 | 8.04 | 32.34 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.6661 | 31.8227 | 6.4799 | 28.8257 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20393
Gintung Energy | ASEC-260G6S | 260 W Monocrystalline Module | UL 1703 | 260 | 232.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.09 | 43.98 | 7.54 | 34.49 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.5003 | 33.8247 | 5.8946 | 32.4059 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19518
Gintung Energy | ASEC-260G6S6A | 260 W Monocrystalline Module | UL 1703 | 260 | 228.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.13 | 37.42 | 8.7 | 29.89 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7591 | 29.8472 | 6.9856 | 26.1851 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20194
Gintung Energy | ASEC-260G6S6B | 260 W Monocrystalline Module | UL 1703 | 260 | 227.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.58 | 40.73 | 8.06 | 32.26 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.6783 | 31.8562 | 6.5017 | 28.3803 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20563
Gintung Energy | GTEC-260G6M6A | 260 W Polycrystalline Module | UL 1703 | 260 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.02 | 37.78 | 8.66 | 30.02 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8 | 29.65 | 6.97 | 26.79 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20527
Gintung Energy | GTEC-260G6M6B | 260 W Polycrystalline Module | UL 1703 | 260 | 228.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.48 | 41.21 | 8.04 | 32.34 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.67 | 31.82 | 6.48 | 28.83 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20438
Gintung Energy | GTEC-260G6S6A | 260 W Monocrystalline Module | UL 1703 | 260 | 228.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.13 | 37.42 | 8.7 | 29.89 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.76 | 29.85 | 6.99 | 26.19 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20206
Gintung Energy | GTEC-260G6S6B | 260 W Monocrystalline Module | UL 1703 | 260 | 227.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.58 | 40.73 | 8.06 | 32.26 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.68 | 31.86 | 6.5 | 28.38 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20586
Gintung Energy | ASEC-265G6M | 265 W Polycrystalline Module | UL 1703 | 265 | 236.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.1 | 43.99 | 7.65 | 34.65 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.534 | 34.1055 | 6.1459 | 31.7428 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19742
Gintung Energy | ASEC-265G6M6A | 265 W Polycrystalline Module | UL 1703 | 265 | 233.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.15 | 37.91 | 8.78 | 30.18 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8199 | 29.8104 | 7.0694 | 26.9354 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20473
Gintung Energy | ASEC-265G6M6B | 265 W Polycrystalline Module | UL 1703 | 265 | 232.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.59 | 41.35 | 8.12 | 32.64 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.6827 | 32.1179 | 6.5444 | 29.0931 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20394
Gintung Energy | ASEC-265G6S | 265 W Monocrystalline Module | UL 1703 | 265 | 237.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.21 | 44.12 | 7.67 | 34.56 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.5261 | 33.8933 | 5.9962 | 32.4717 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19519
Gintung Energy | ASEC-265G6S6A | 265 W Monocrystalline Module | UL 1703 | 265 | 232.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.24 | 37.49 | 8.82 | 30.05 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7834 | 30.007 | 7.0819 | 26.3253 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20194
Gintung Energy | ASEC-265G6S6B | 265 W Monocrystalline Module | UL 1703 | 265 | 231.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.69 | 40.88 | 8.15 | 32.52 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.697 | 32.113 | 6.5743 | 28.609 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20564
Gintung Energy | GTEC-265G6M6A | 265 W Polycrystalline Module | UL 1703 | 265 | 233.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.15 | 37.91 | 8.78 | 30.18 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.82 | 29.81 | 7.07 | 26.94 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20473
Gintung Energy | GTEC-265G6M6B | 265 W Polycrystalline Module | UL 1703 | 265 | 232.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.59 | 41.35 | 8.12 | 32.64 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.68 | 32.12 | 6.54 | 29.09 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20363
Gintung Energy | GTEC-265G6S6A | 265 W Monocrystalline Module | UL 1703 | 265 | 232.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.24 | 37.49 | 8.82 | 30.05 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.78 | 30.01 | 7.08 | 26.33 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20158
Gintung Energy | GTEC-265G6S6B | 265 W Monocrystalline Module | UL 1703 | 265 | 231.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.69 | 40.88 | 8.15 | 32.52 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7 | 32.11 | 6.57 | 28.61 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20599
Gintung Energy | ASEC-270G6M | 270 W Polycrystalline Module | UL 1703 | 270 | 241.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.19 | 44.15 | 7.75 | 34.87 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.5262 | 34.0797 | 6.1841 | 32.1535 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19264
Gintung Energy | ASEC-270G6M6A | 270 W Polycrystalline Module | UL 1703 | 270 | 238.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.28 | 38.03 | 8.9 | 30.34 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8448 | 29.9685 | 7.166 | 27.0782 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20476
Gintung Energy | ASEC-270G6M6B | 270 W Polycrystalline Module | UL 1703 | 270 | 237.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.71 | 41.44 | 8.25 | 32.73 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7096 | 32.2065 | 6.6492 | 29.1733 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20393
Gintung Energy | ASEC-270G6S | 270 W Monocrystalline Module | UL 1703 | 270 | 241.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.34 | 44.27 | 7.8 | 34.62 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.5697 | 34.5214 | 6.1425 | 32.8353 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.2007
Gintung Energy | ASEC-270G6S6A | 270 W Monocrystalline Module | UL 1703 | 270 | 237.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.34 | 37.59 | 8.94 | 30.2 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.8077 | 30.1567 | 7.1783 | 26.4567 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.2019
Gintung Energy | ASEC-270G6S6B | 270 W Monocrystalline Module | UL 1703 | 270 | 236.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.81 | 40.97 | 8.3 | 32.53 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7282 | 32.1229 | 6.6953 | 28.6178 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20561
Gintung Energy | GTEC-270G6M6A | 270 W Polycrystalline Module | UL 1703 | 270 | 238.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6111 | 60 | 1 | N | 9.28 | 38.03 | 8.9 | 30.34 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.84 | 29.97 | 7.17 | 27.08 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20424
Gintung Energy | GTEC-270G6M6B | 270 W Polycrystalline Module | UL 1703 | 270 | 237.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.71 | 41.44 | 8.25 | 32.73 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.71 | 32.21 | 6.65 | 29.17 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.204
Gintung Energy | GTEC-270G6S6A | 270 W Monocrystalline Module | UL 1703 | 270 | 237.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6111 | 60 | 1 | N | 9.34 | 37.59 | 8.94 | 30.2 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.81 | 30.16 | 7.18 | 26.46 | Rack | Flat Plate | 0.989 | 1.629 | 1 | 0.20218
Gintung Energy | GTEC-270G6S6B | 270 W Monocrystalline Module | UL 1703 | 270 | 236.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.81 | 40.97 | 8.3 | 32.53 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.73 | 32.12 | 6.7 | 28.62 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20581
Gintung Energy | ASEC-275G6M | 275 W Polycrystalline Module | UL 1703 | 275 | 245.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.31 | 44.31 | 7.87 | 34.96 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.5498 | 34.1677 | 6.2799 | 32.2365 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19256
Gintung Energy | ASEC-275G6M6B | 275 W Polycrystalline Module | UL 1703 | 275 | 242 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.83 | 41.53 | 8.38 | 32.82 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.741 | 32.3248 | 6.7368 | 29.493 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20465
Gintung Energy | ASEC-275G6S | 275 W Monocrystalline Module | UL 1703 | 275 | 246.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.4 | 44.36 | 7.89 | 34.86 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.5879 | 34.7607 | 6.2134 | 33.0629 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20071
Gintung Energy | ASEC-275G6S6B | 275 W Monocrystalline Module | UL 1703 | 275 | 241 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.93 | 41.06 | 8.42 | 32.66 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.685 | 32.6822 | 6.7995 | 29.0494 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20025
Gintung Energy | GTEC-275G6M6B | 275 W Polycrystalline Module | UL 1703 | 275 | 242 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.83 | 41.53 | 8.38 | 32.82 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.74 | 32.32 | 6.74 | 29.49 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.2045
Gintung Energy | GTEC-275G6S6B | 275 W Monocrystalline Module | UL 1703 | 275 | 241 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 8.93 | 41.06 | 8.42 | 32.66 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.69 | 32.68 | 6.8 | 29.05 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20083
Gintung Energy | ASEC-280G6M | 280 W Polycrystalline Module | UL 1703 | 280 | 250.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.42 | 44.39 | 7.99 | 35.05 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.5735 | 34.2557 | 6.3757 | 32.3195 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.1925
Gintung Energy | ASEC-280G6M6B | 280 W Polycrystalline Module | UL 1703 | 280 | 246.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.93 | 41.64 | 8.49 | 32.98 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7639 | 32.4824 | 6.8252 | 29.6368 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20462
Gintung Energy | ASEC-280G6S | 280 W Monocrystalline Module | UL 1703 | 280 | 251 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.52 | 44.55 | 8.01 | 34.96 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.612 | 34.8604 | 6.3079 | 33.1577 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.2007
Gintung Energy | ASEC-280G6S6B | 280 W Monocrystalline Module | UL 1703 | 280 | 245.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 9.03 | 41.18 | 8.53 | 32.83 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.707 | 32.8523 | 6.8884 | 29.2006 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20028
Gintung Energy | GTEC-280G6M | 280 W Polycrystalline Module | UL 1703 | 280 | 250.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.42 | 44.39 | 7.99 | 35.05 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.57 | 34.26 | 6.38 | 32.32 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.1921
Gintung Energy | GTEC-280G6M6B | 280 W Polycrystalline Module | UL 1703 | 280 | 246.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 8.93 | 41.64 | 8.49 | 32.98 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.76 | 32.48 | 6.83 | 29.64 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20416
Gintung Energy | GTEC-280G6S | 280 W Monocrystalline Module | UL 1703 | 280 | 251 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.52 | 44.55 | 8.01 | 34.96 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.61 | 34.86 | 6.31 | 33.16 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20045
Gintung Energy | GTEC-280G6S6B | 280 W Monocrystalline Module | UL 1703 | 280 | 245.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 9.03 | 41.18 | 8.53 | 32.83 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.71 | 32.85 | 6.89 | 29.2 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20062
Gintung Energy | ASEC-285G6M | 285 W Polycrystalline Module | UL 1703 | 285 | 255.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.51 | 44.53 | 8.12 | 35.1 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.5991 | 34.3045 | 6.4794 | 32.3656 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19248
Gintung Energy | ASEC-285G6M6B | 285 W Polycrystalline Module | UL 1703 | 285 | 251.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 9.03 | 41.75 | 8.61 | 33.1 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7888 | 32.6006 | 6.9217 | 29.7446 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20462
Gintung Energy | ASEC-285G6S | 285 W Monocrystalline Module | UL 1703 | 285 | 255.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.64 | 44.69 | 8.13 | 35.06 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6362 | 34.9601 | 6.4024 | 33.2526 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.2007
Gintung Energy | ASEC-285G6S6B | 285 W Monocrystalline Module | UL 1703 | 285 | 250 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 9.13 | 41.29 | 8.65 | 32.95 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.731 | 32.9724 | 6.9853 | 29.3073 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20027
Gintung Energy | GTEC-285G6M | 285 W Polycrystalline Module | UL 1703 | 285 | 255.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.51 | 44.53 | 8.12 | 35.1 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.6 | 34.3 | 6.48 | 32.37 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19256
Gintung Energy | GTEC-285G6M6B | 285 W Polycrystalline Module | UL 1703 | 285 | 251.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 9.03 | 41.75 | 8.61 | 33.1 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.79 | 32.6 | 6.92 | 29.74 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20475
Gintung Energy | GTEC-285G6S | 285 W Monocrystalline Module | UL 1703 | 285 | 255.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.64 | 44.69 | 8.13 | 35.06 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.64 | 34.96 | 6.4 | 33.25 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20117
Gintung Energy | GTEC-285G6S6B | 285 W Monocrystalline Module | UL 1703 | 285 | 250 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 9.13 | 41.29 | 8.65 | 32.95 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.73 | 32.97 | 6.99 | 29.31 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20013
Gintung Energy | ASEC-290G6M | 290 W Polycrystalline Module | UL 1703 | 290 | 259.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.62 | 44.61 | 8.24 | 35.2 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.6227 | 34.4023 | 6.5751 | 32.4578 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.1925
Gintung Energy | ASEC-290G6M6B | 290 W Polycrystalline Module | UL 1703 | 290 | 255.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 9.12 | 41.89 | 8.74 | 33.18 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8158 | 32.6793 | 7.0262 | 29.8165 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20462
Gintung Energy | ASEC-290G6S | 290 W Monocrystalline Module | UL 1703 | 290 | 260.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.75 | 44.84 | 8.25 | 35.16 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.6603 | 35.0599 | 6.4969 | 33.3474 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20073
Gintung Energy | ASEC-290G6S6B | 290 W Monocrystalline Module | UL 1703 | 290 | 254.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 9.22 | 41.44 | 8.78 | 33.03 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7571 | 33.0525 | 7.0902 | 29.3785 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20026
Gintung Energy | GTEC-290G6M | 290 W Polycrystalline Module | UL 1703 | 290 | 259.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.62 | 44.61 | 8.24 | 35.2 | 46.1 | -0.4702 | 0.0214 | -0.3299 | 0.0102 | -0.4233 | 1.62 | 34.4 | 6.58 | 32.46 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.19217
Gintung Energy | GTEC-290G6M6B | 290 W Polycrystalline Module | UL 1703 | 290 | 255.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 9.12 | 41.89 | 8.74 | 33.18 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.82 | 32.68 | 7.03 | 29.82 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.2051
Gintung Energy | GTEC-290G6S | 290 W Monocrystalline Module | UL 1703 | 290 | 260.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.75 | 44.84 | 8.25 | 35.16 | 45.8 | -0.4684 | 0.0423 | -0.3397 | 0.0115 | -0.4125 | 1.66 | 35.06 | 6.5 | 33.35 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20069
Gintung Energy | GTEC-290G6S6B | 290 W Monocrystalline Module | UL 1703 | 290 | 254.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 9.22 | 41.44 | 8.78 | 33.03 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.76 | 33.05 | 7.09 | 29.38 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20058
Gintung Energy | ASEC-295G6M | 295 W Polycrystalline Module | UL 1703 | 295 | 259.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.72 | 44.69 | 8.34 | 35.37 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.737 | 34.8679 | 6.7524 | 31.5507 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20531
Gintung Energy | ASEC-295G6M6B | 295 W Polycrystalline Module | UL 1703 | 295 | 260.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 9.22 | 41.99 | 8.85 | 33.33 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8387 | 32.8271 | 7.1146 | 29.9513 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.2046
Gintung Energy | ASEC-295G6S | 295 W Monocrystalline Module | UL 1703 | 295 | 258.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.83 | 44.96 | 8.35 | 35.33 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.6948 | 35.1095 | 6.7453 | 31.2333 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20171
Gintung Energy | ASEC-295G6S6B | 295 W Monocrystalline Module | UL 1703 | 295 | 259.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 9.32 | 41.54 | 8.89 | 33.18 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7791 | 33.2026 | 7.1791 | 29.5119 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20024
Gintung Energy | GTEC-295G6M | 295 W Polycrystalline Module | UL 1703 | 295 | 259.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.72 | 44.69 | 8.34 | 35.37 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.74 | 34.87 | 6.75 | 31.55 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20567
Gintung Energy | GTEC-295G6M6B | 295 W Polycrystalline Module | UL 1703 | 295 | 260.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7733 | 66 | 1 | N | 9.22 | 41.99 | 8.85 | 33.33 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.84 | 32.83 | 7.11 | 29.95 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20477
Gintung Energy | GTEC-295G6S | 295 W Monocrystalline Module | UL 1703 | 295 | 258.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.83 | 44.96 | 8.35 | 35.33 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.69 | 35.11 | 6.75 | 31.23 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20114
Gintung Energy | GTEC-295G6S6B | 295 W Monocrystalline Module | UL 1703 | 295 | 259.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7733 | 66 | 1 | N | 9.32 | 41.54 | 8.89 | 33.18 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.78 | 33.2 | 7.18 | 29.51 | Rack | Flat Plate | 0.989 | 1.793 | 1 | 0.20033
Gintung Energy | ASEC-300G6M | 300 W Polycrystalline Module | UL 1703 | 300 | 263.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.83 | 44.78 | 8.45 | 35.5 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7599 | 34.9961 | 6.8415 | 31.6667 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.2053
Gintung Energy | ASEC-300G6S | 300 W Monocrystalline Module | UL 1703 | 300 | 262.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.91 | 45.07 | 8.46 | 35.46 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7172 | 35.2387 | 6.8342 | 31.3483 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.2017
Gintung Energy | GTEC-300G6M | 300 W Polycrystalline Module | UL 1703 | 300 | 263.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.83 | 44.78 | 8.45 | 35.5 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.76 | 35 | 6.84 | 31.67 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20533
Gintung Energy | GTEC-300G6S | 300 W Monocrystalline Module | UL 1703 | 300 | 262.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.91 | 45.07 | 8.46 | 35.46 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.72 | 35.24 | 6.83 | 31.35 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20204
Gintung Energy | ASEC-305G6M | 305 W Polycrystalline Module | UL 1703 | 305 | 268.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.95 | 44.88 | 8.57 | 35.59 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.7849 | 35.0848 | 6.9386 | 31.7469 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20532
Gintung Energy | ASEC-305G6S | 305 W Monocrystalline Module | UL 1703 | 305 | 267.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.99 | 45.18 | 8.58 | 35.55 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7415 | 35.3281 | 6.9311 | 31.4278 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20172
Gintung Energy | GTEC-305G6M | 305 W Polycrystalline Module | UL 1703 | 305 | 268.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 8.95 | 44.88 | 8.57 | 35.59 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.78 | 35.08 | 6.94 | 31.75 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20473
Gintung Energy | GTEC-305G6S | 305 W Monocrystalline Module | UL 1703 | 305 | 267.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 8.99 | 45.18 | 8.58 | 35.55 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.74 | 35.33 | 6.93 | 31.43 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20155
Gintung Energy | ASEC-310G6M | 310 W Polycrystalline Module | UL 1703 | 310 | 273 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 9.05 | 44.97 | 8.67 | 35.76 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8057 | 35.2524 | 7.0196 | 31.8986 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20534
Gintung Energy | ASEC-310G6S | 310 W Monocrystalline Module | UL 1703 | 310 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.08 | 45.22 | 8.68 | 35.71 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7618 | 35.4871 | 7.0119 | 31.5693 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20168
Gintung Energy | GTEC-310G6M | 310 W Polycrystalline Module | UL 1703 | 310 | 273 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 9.05 | 44.97 | 8.67 | 35.76 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.81 | 35.25 | 7.02 | 31.9 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20581
Gintung Energy | GTEC-310G6S | 310 W Monocrystalline Module | UL 1703 | 310 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.08 | 45.22 | 8.68 | 35.71 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.76 | 35.49 | 7.01 | 31.57 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20149
Gintung Energy | ASEC-315G6M | 315 W Polycrystalline Module | UL 1703 | 315 | 277.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 9.15 | 45.09 | 8.78 | 35.88 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8286 | 35.3707 | 7.1087 | 32.0056 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20534
Gintung Energy | ASEC-315G6S | 315 W Monocrystalline Module | UL 1703 | 315 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.18 | 45.27 | 8.79 | 35.84 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.7842 | 35.6163 | 7.1008 | 31.6842 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20173
Gintung Energy | GTEC-315G6M | 315 W Polycrystalline Module | UL 1703 | 315 | 277.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 9.15 | 45.09 | 8.78 | 35.88 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.83 | 35.37 | 7.11 | 32.01 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20548
Gintung Energy | GTEC-315G6S | 315 W Monocrystalline Module | UL 1703 | 315 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.18 | 45.27 | 8.79 | 35.84 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.78 | 35.62 | 7.1 | 31.68 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20128
Gintung Energy | ASEC-320G6M | 320 W Polycrystalline Module | UL 1703 | 320 | 282.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 9.27 | 45.18 | 8.9 | 35.96 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8536 | 35.4496 | 7.2058 | 32.077 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20535
Gintung Energy | ASEC-320G6S | 320 W Monocrystalline Module | UL 1703 | 320 | 280.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.28 | 45.31 | 8.91 | 35.91 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.8085 | 35.6859 | 7.1977 | 31.7461 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20168
Gintung Energy | GTEC-320G6M | 320 W Polycrystalline Module | UL 1703 | 320 | 282.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 9.27 | 45.18 | 8.9 | 35.96 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.85 | 35.45 | 7.21 | 32.08 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20495
Gintung Energy | GTEC-320G6S | 320 W Monocrystalline Module | UL 1703 | 320 | 280.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.28 | 45.31 | 8.91 | 35.91 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.81 | 35.69 | 7.2 | 31.75 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20187
Gintung Energy | ASEC-325G6M | 325 W Polycrystalline Module | UL 1703 | 325 | 286.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 9.38 | 45.35 | 9.01 | 36.07 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.8766 | 35.558 | 7.2949 | 32.1751 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20531
Gintung Energy | ASEC-325G6S | 325 W Monocrystalline Module | UL 1703 | 325 | 285.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.39 | 45.48 | 9.03 | 35.99 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.8329 | 35.7654 | 7.2946 | 31.8168 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.2017
Gintung Energy | GTEC-325G6M | 325 W Polycrystalline Module | UL 1703 | 325 | 286.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.956 | 72 | 1 | N | 9.38 | 45.35 | 9.01 | 36.07 | 50 | -0.4607 | 0.06581 | -0.3427 | -0.003265 | -0.456 | 1.88 | 35.56 | 7.29 | 32.18 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.2057
Gintung Energy | GTEC-325G6S | 325 W Monocrystalline Module | UL 1703 | 325 | 285.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.39 | 45.48 | 9.03 | 35.99 | 51.4 | -0.4502 | 0.0729 | -0.343 | 0.005458 | -0.4549 | 1.83 | 35.77 | 7.29 | 31.82 | Rack | Flat Plate | 1 | 1.956 | 1 | 0.20141
Goldi Solar Private Limited | GOLDI060F260PY24 | 260 W, 60 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 260 | 238.9 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5714 | 60 | 1 | N | 8.9 | 38.12 | 8.57 | 30.4 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.714 | 29.6424 | 6.9242 | 27.4183 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F265PY24 | 265 W, 60 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 265 | 243.6 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5714 | 60 | 1 | N | 8.97 | 38.32 | 8.64 | 30.7 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.728 | 29.935 | 6.9807 | 27.6888 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F270PY24 | 270 W, 60 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 270 | 248.3 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5714 | 60 | 1 | N | 9.03 | 38.52 | 8.72 | 31 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.744 | 30.2275 | 7.0454 | 27.9594 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F275PY24 | 275 W, 60 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 275 | 253 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5714 | 60 | 1 | N | 9.1 | 38.82 | 8.8 | 31.3 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.76 | 30.52 | 7.11 | 28.23 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F280PY24 | 280 W, 60 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 280 | 257.7 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5714 | 60 | 1 | N | 9.18 | 39.12 | 8.88 | 31.6 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.776 | 30.8125 | 7.1746 | 28.5006 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F285PY24 | 285 W, 60 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 285 | 262.4 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5714 | 60 | 1 | N | 9.25 | 39.42 | 8.95 | 31.85 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.79 | 31.0563 | 7.2312 | 28.7261 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F290PRC24B | 295 W, 60 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 290 | 269 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.36 | 39.65 | 9.04 | 32.1 | 46.82 | -0.3349 | 0.001 | -0.2363 |  |  | 1.7827 | 31.641 | 7.0722 | 29.6488 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F295PRC24 | 295 W, 60 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 295 | 273.4 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.45 | 39.85 | 9.12 | 32.35 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.8182 | 31.7823 | 7.2046 | 29.8246 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F295PRC24B | 290 W, 60 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 295 | 273.7 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.45 | 39.85 | 9.12 | 32.35 | 46.82 | -0.3349 | 0.001 | -0.2363 |  |  | 1.7984 | 31.8874 | 7.1348 | 29.8797 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F300PRC24 | 300 W, 60 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 300 | 278.2 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.53 | 40.1 | 9.19 | 32.65 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.8321 | 32.077 | 7.2599 | 30.1012 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F300PRC24B | 300 W, 60 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 300 | 278.5 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.53 | 40.1 | 9.19 | 32.65 | 46.82 | -0.3349 | 0.001 | -0.2363 |  |  | 1.8123 | 32.1831 | 7.1896 | 30.1568 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F305PRC24 | 305 W, 60 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 305 | 283 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.62 | 40.4 | 9.28 | 32.87 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.8501 | 32.2932 | 7.331 | 30.3041 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F305PRC24B | 305 W, 60 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 305 | 283.2 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.62 | 40.4 | 9.28 | 32.87 | 46.82 | -0.3349 | 0.001 | -0.2363 |  |  | 1.83 | 32.4 | 7.26 | 30.36 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F310PRC24 | 310 W, 60 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 310 | 287.7 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.71 | 40.6 | 9.38 | 33.05 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.87 | 32.47 | 7.41 | 30.47 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F310PRC24B | 310 W, 60 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 310 | 288 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.71 | 40.6 | 9.38 | 33.05 | 46.82 | -0.3349 | 0.001 | -0.2363 |  |  | 1.8497 | 32.5774 | 7.3382 | 30.5263 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F315PRC24 | 315 W, 60 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 315 | 292.5 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.82 | 40.85 | 9.45 | 33.35 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.884 | 32.7647 | 7.4653 | 30.7466 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F315PRC24B | 315 W, 60 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 315 | 292.8 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.82 | 40.85 | 9.45 | 33.35 | 46.82 | -0.3349 | 0.001 | -0.2363 |  |  | 1.8635 | 32.8731 | 7.393 | 30.8033 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F320PRC24 | 320 W, 60 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 297.3 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.9 | 41.15 | 9.53 | 33.6 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.8999 | 33.0103 | 7.5285 | 30.9771 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F320PRC24B | 320 W, 60 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 320 | 300.1 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.57 | 60 | 1 | N | 9.9 | 41.15 | 9.53 | 33.6 | 44.9 | -0.3253 | 0.0277 | -0.2392 |  |  | 1.9 | 33.21 | 7.55 | 31.55 | [6 empty] | 2020-08-21 | 2021-01-04
Goldi Solar Private Limited | GOLDI072F320PY24 | 320 W, 72 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 294.2 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8789 | 72 | 1 | N | 9.05 | 45.7 | 8.68 | 36.9 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.7165 | 35.6765 | 6.905 | 33.4058 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F325PRC24 | 325 W, 60 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 325 | 302 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5714 | 60 | 1 | N | 9.98 | 41.35 | 9.63 | 33.75 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.9198 | 33.1577 | 7.6075 | 31.1154 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI060F325PRC24B | 325 W, 60 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 325 | 304.9 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.57 | 60 | 1 | N | 9.98 | 41.35 | 9.63 | 33.75 | 44.9 | -0.3253 | 0.0277 | -0.2392 |  |  | 1.9199 | 33.3583 | 7.6292 | 31.6908 | [6 empty] | 2021-01-04
Goldi Solar Private Limited | GOLDI072F325PY24 | 325 W, 72 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 325 | 298.9 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8789 | 72 | 1 | N | 9.12 | 45.9 | 8.75 | 37.2 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.7303 | 35.9666 | 6.9607 | 33.6773 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F330PY24 | 330 W, 72 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 330 | 303.6 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8789 | 72 | 1 | N | 9.19 | 46.2 | 8.83 | 37.4 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.7462 | 36.1599 | 7.0243 | 33.8584 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F335PY24 | 335 W, 72 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 335 | 308.3 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8789 | 72 | 1 | N | 9.26 | 46.5 | 8.9 | 37.7 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.76 | 36.45 | 7.08 | 34.13 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F340PY24 | 340 W, 72 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 340 | 313.1 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8789 | 72 | 1 | N | 9.32 | 46.8 | 8.98 | 37.9 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.7758 | 36.6434 | 7.1436 | 34.3111 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F345PY24 | 345 W, 72 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 345 | 317.8 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8789 | 72 | 1 | N | 9.4 | 47.1 | 9.06 | 38.1 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.7916 | 36.8367 | 7.2073 | 34.4921 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F350PRC24B | 350 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 350 | 324.7 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.48 | 47.3 | 9.12 | 38.4 | 46.82 | -0.3349 | 0.001 | -0.2363 |  |  | 1.762 | 37.9505 | 6.9707 | 35.8986 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F350PY24 | 350 W, 72 cell polycrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 322.5 |  | 2019-12-05 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8789 | 72 | 1 | N | 9.48 | 47.3 | 9.12 | 38.4 | 46.43 | -0.3702 | 0.0091 | -0.2616 |  |  | 1.8035 | 37.1268 | 7.255 | 34.7637 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F355PRC24B | 355 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 355 | 329.5 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.56 | 47.5 | 9.2 | 38.6 | 46.82 | -0.3349 | 0.001 | -0.2363 |  |  | 1.7775 | 38.1482 | 7.0318 | 36.0856 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F360PRC24 | 360 W, 72 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 333.9 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.64 | 47.7 | 9.28 | 38.8 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.8091 | 38.4269 | 7.2167 | 35.9725 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F360PRC24B | 360 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 360 | 334.2 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.64 | 47.7 | 9.28 | 38.8 | 46.82 | -0.3349 | 0.001 | -0.2425 |  |  | 1.793 | 38.3459 | 7.093 | 36.2726 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F365PRC24 | 365 W, 72 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 338.6 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.72 | 47.9 | 9.34 | 39.1 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.8208 | 38.724 | 7.2634 | 36.2506 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F365PRC24B | 365 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 365 | 339 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.72 | 47.9 | 9.34 | 39.1 | 46.82 | -0.3349 | 0.001 | -0.2425 |  |  | 1.8045 | 38.6423 | 7.1389 | 36.553 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F370PRC24 | 370 W, 72 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 343.4 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.78 | 48.1 | 9.42 | 39.3 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.8364 | 38.9221 | 7.3256 | 36.436 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F370PRC24B | 370 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 370 | 343.7 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.78 | 48.1 | 9.42 | 39.3 | 46.82 | -0.3349 | 0.001 | -0.2425 |  |  | 1.82 | 38.84 | 7.2 | 36.74 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F375PRC24 | 375 W, 72 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 348.2 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.84 | 48.4 | 9.49 | 39.52 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.85 | 39.14 | 7.38 | 36.64 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F375PRC24B | 375 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 375 | 348.5 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.84 | 48.4 | 9.49 | 39.52 | 46.82 | -0.3349 | 0.001 | -0.2425 |  |  | 1.8335 | 39.0574 | 7.2535 | 36.9457 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F380PRC24 | 380 W, 72 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 352.9 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.92 | 48.7 | 9.56 | 39.75 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.8636 | 39.3678 | 7.4344 | 36.8532 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F380PRC24B | 380 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 380 | 353.3 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.92 | 48.7 | 9.56 | 39.75 | 46.82 | -0.3349 | 0.001 | -0.2425 |  |  | 1.847 | 39.2847 | 7.307 | 37.1607 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F385PRC24 | 385 W, 72 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 357.7 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8789 | 72 | 1 | N | 9.98 | 48.9 | 9.64 | 39.95 | 46.31 | -0.3474 | 0.0015 | -0.2425 |  |  | 1.8792 | 39.5659 | 7.4966 | 37.0387 | [6 empty] | 2020-08-21
Goldi Solar Private Limited | GOLDI072F385PRC24B | 385 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 385 | 361.1 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 9.98 | 48.9 | 9.64 | 39.95 | 44.9 | -0.3253 | 0.0277 | -0.2392 |  |  | 1.91 | 39.64 | 7.55 | 37.69 | [6 empty] | 2020-08-21 | 2021-01-04
Goldi Solar Private Limited | GOLDI072F390PRC24 | 390 W, 72 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 364.1 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 10.07 | 49.15 | 9.72 | 40.14 | 46.14 | -0.3292 | 0.0266 | -0.2374 |  |  | 1.95 | 39.69 | 7.72 | 37.38 | [6 empty] | 2020-08-21 | 2021-01-04
Goldi Solar Private Limited | GOLDI072F390PRC24B | 390 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 390 | 366 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 10.07 | 49.15 | 9.72 | 40.14 | 44.9 | -0.3253 | 0.0277 | -0.2392 |  |  | 1.9259 | 39.8285 | 7.6127 | 37.8693 | [6 empty] | 2021-01-04
Goldi Solar Private Limited | GOLDI072F395PRC24 | 395 W, 72 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 368.9 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 10.15 | 49.35 | 9.8 | 40.32 | 46.14 | -0.3292 | 0.0266 | -0.2374 |  |  | 1.966 | 39.868 | 7.7835 | 37.5476 | [6 empty] | 2021-01-04
Goldi Solar Private Limited | GOLDI072F395PRC24B | 395 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 395 | 370.8 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 10.15 | 49.35 | 9.8 | 40.32 | 44.9 | -0.3253 | 0.0277 | -0.2392 |  |  | 1.9417 | 40.0071 | 7.6753 | 38.0391 | [6 empty] | 2021-01-04
Goldi Solar Private Limited | GOLDI072F400PRC24 | 400 W, 72 cell monocrytalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 373.7 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 10.21 | 49.65 | 9.88 | 40.48 | 46.14 | -0.3292 | 0.0266 | -0.2374 |  |  | 1.9821 | 40.0262 | 7.8471 | 37.6966 | [6 empty] | 2021-01-04
Goldi Solar Private Limited | GOLDI072F400PRC24B | 400 W, 72 cell monocrytalline module, black backsheet, 1500V max system Vdc | UL 61730 | 400 | 375.6 |  | 2019-12-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 10.21 | 49.65 | 9.88 | 40.48 | 44.9 | -0.3253 | 0.0277 | -0.2392 |  |  | 1.9576 | 40.1659 | 7.738 | 38.19 | [6 empty] | 2021-01-04
Grape Solar | GS-P-160-EUG | 160 W Polycrystalline Module | UL 1703 | 160 | 143.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 7.6 | 28.6 | 6.87 | 23.3 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.2994 | 23.6196 | 5.5031 | 21.5872 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.19183
Grape Solar | GS-S-160-Fab8 | 160 W Monocrystalline Module | UL 1703 | 160 | 143.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 4.85 | 43.84 | 4.53 | 35.26 | 45.8 | -0.458 | 0.048 | -0.299 | -0.0035 | -0.435 | 0.81461 | 33.7339 | 3.7651 | 32.4173 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17175
Grape Solar | GS-P-165-EUG | 165 W Polycrystalline Module | UL 1703 | 165 | 148 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 7.7 | 28.8 | 7.02 | 23.5 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.3278 | 23.8223 | 5.6233 | 21.7725 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.19171
Grape Solar | GS-S-165-Fab8 | 165 W Monocrystalline Module | UL 1703 | 165 | 147.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 4.92 | 43.99 | 4.6 | 35.85 | 45.8 | -0.458 | 0.048 | -0.299 | -0.0035 | -0.435 | 0.82719 | 34.2984 | 3.8232 | 32.9597 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17195
Grape Solar | GS-P-170-EUG | 170 W Polycrystalline Module | UL 1703 | 170 | 152.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 7.82 | 29 | 7.15 | 23.8 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.411 | 24.4188 | 5.7544 | 21.9467 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.20267
Grape Solar | GS-S-170-Fab3 | 170 W Monocrystalline Module | UL 1703 | 170 | 150.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.12 | 44.5 | 4.74 | 35.9 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 0.93698 | 34.7168 | 3.7847 | 33.0381 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19135
Grape Solar | GS-S-175-Fab8 | 170 W Monocrystalline Module | UL 1703 | 170 | 152.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 4.97 | 44.13 | 4.64 | 36.57 | 45.8 | -0.458 | 0.048 | -0.299 | -0.0035 | -0.435 | 0.83439 | 34.9872 | 3.8565 | 33.6216 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17172
Grape Solar | GS-P-175-EUG | 175 W Polycrystalline Module | UL 1703 | 175 | 157.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 7.96 | 29.2 | 7.29 | 24 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4386 | 24.624 | 5.8671 | 22.1311 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.20242
Grape Solar | GS-S-175-EUG | 175 W Monocrystalline Module | UL 1703 | 175 | 158.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2823 | 72 | 1 | N | 5.28 | 43.8 | 4.83 | 36.2 | 45.8 | -0.416 | 0.0479 | -0.307 | -0.0236 | -0.396 | 0.92958 | 35.6032 | 3.9004 | 33.3376 | Rack | Flat Plate | 0.807 | 1.589 | 1 | 0.18912
Grape Solar | GS-S-175-Fab3 | 175 W Monocrystalline Module | UL 1703 | 175 | 155.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.17 | 44.8 | 4.86 | 36 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 0.9607 | 34.8135 | 3.8805 | 33.1301 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19112
Grape Solar | GS-P-180-EUG | 180 W Polycrystalline Module | UL 1703 | 180 | 161.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 8.1 | 29.4 | 7.47 | 24.1 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4741 | 24.7266 | 6.012 | 22.2233 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.2025
Grape Solar | GS-S-180-EUG | 180 W Monocrystalline Module | UL 1703 | 180 | 163.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2823 | 72 | 1 | N | 5.35 | 44.2 | 4.93 | 36.5 | 45.8 | -0.416 | 0.0479 | -0.307 | -0.0236 | -0.396 | 0.94883 | 35.8983 | 3.9812 | 33.6139 | Rack | Flat Plate | 0.807 | 1.589 | 1 | 0.18923
Grape Solar | GS-S-180-Fab3 | 180 W Monocrystalline Module | UL 1703 | 180 | 160 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.2 | 45 | 5 | 36 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 0.98837 | 34.8135 | 3.9922 | 33.1301 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19116
Grape Solar | GS-S-180-Fab8 | 180 W Monocrystalline Module | UL 1703 | 180 | 161.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.1 | 44.71 | 4.77 | 37.22 | 45.8 | -0.458 | 0.048 | -0.299 | -0.0035 | -0.435 | 0.90949 | 35.1769 | 3.7928 | 33.1238 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17774
Grape Solar | GS-S-185-Fab3 | 185 W Monocrystalline Module | UL 1703 | 185 | 164.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.32 | 45.2 | 5.11 | 36.2 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 1.0004 | 35.364 | 4.1292 | 32.4632 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19124
Grape Solar | GS-S-185-Fab8 | 185 W Monocrystalline Module | UL 1703 | 185 | 166.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.21 | 45 | 4.87 | 38.02 | 45.8 | -0.458 | 0.048 | -0.299 | -0.0035 | -0.435 | 0.92856 | 35.933 | 3.8723 | 33.8357 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18036
Grape Solar | GS-P-190-EUG | 190 W Polycrystalline Module | UL 1703 | 190 | 170.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.8 | 32.6 | 7.12 | 26.7 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4105 | 27.1633 | 5.7248 | 24.6318 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.20165
Grape Solar | GS-S-190-Fab3 | 190 W Monocrystalline Module | UL 1703 | 190 | 169 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.44 | 45.4 | 5.25 | 36.2 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 1.0278 | 35.364 | 4.2423 | 32.4632 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19131
Grape Solar | GS-P-195-EUG | 195 W Polycrystalline Module | UL 1703 | 195 | 175.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.92 | 32.8 | 7.25 | 26.9 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4363 | 27.3667 | 5.8293 | 24.8163 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.20157
Grape Solar | GS-S-195-Fab3 | 195 W Monocrystalline Module | UL 1703 | 195 | 173.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.58 | 45.5 | 5.38 | 36.2 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 1.0533 | 35.364 | 4.3474 | 32.4632 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19102
Grape Solar | GS-P-200-CSPE | 200 W Polycrystalline Module | UL 1703 | 200 | 177.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 7.68 | 36.2 | 6.93 | 28.9 | 49.1 | -0.434 | 0.13 | -0.37 | 0.131 | -0.539 | 1.1378 | 28.999 | 5.5854 | 26.8216 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.16497
Grape Solar | GS-P-200-EUG | 200 W Polycrystalline Module | UL 1703 | 200 | 179.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.02 | 33 | 7.38 | 27.1 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.462 | 27.5702 | 5.9339 | 25.0009 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.20154
Grape Solar | GS-P-200-Fab1 | 200 W Polycrystalline Module | UL 1703 | 200 | 178.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9032 | 72 | 1 | N | 7.58 | 36.1 | 6.98 | 28.7 | 47 | -0.4347 | 0.0782 | -0.3707 | 0.1622 | -0.4558 | 1.3855 | 28.2839 | 5.4084 | 26.4313 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19594
Grape Solar | GS-S-200-Fab1 | 200 W Monocrystalline Module | UL 1703 | 200 | 178.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 7.58 | 36.1 | 6.98 | 28.7 | 46.8 | -0.4385 | 0.0998 | -0.3669 | 0.1715 | -0.4586 | 1.402 | 28.4425 | 5.5268 | 26.135 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19938
Grape Solar | GS-P-205-EUG | 205 W Polycrystalline Module | UL 1703 | 205 | 184.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.15 | 33.2 | 7.54 | 27.2 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4937 | 27.6719 | 6.0625 | 25.0931 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.20163
Grape Solar | GS-P-205-Fab1 | 205 W Polycrystalline Module | UL 1703 | 205 | 183 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9032 | 72 | 1 | N | 7.69 | 36.3 | 7.1 | 28.9 | 47 | -0.4347 | 0.0782 | -0.3707 | 0.1622 | -0.4558 | 1.4093 | 28.481 | 5.5014 | 26.6155 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.1958
Grape Solar | GS-S-205-Fab1 | 205 W Monocrystalline Module | UL 1703 | 205 | 183 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 7.69 | 36.3 | 7.1 | 28.9 | 46.8 | -0.4385 | 0.0998 | -0.3669 | 0.1715 | -0.4586 | 1.4261 | 28.6407 | 5.6218 | 26.3171 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19924
Grape Solar | GS-P-210-Fab1 | 210 W Polycrystalline Module | UL 1703 | 210 | 187.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9032 | 72 | 1 | N | 7.8 | 36.4 | 7.22 | 29.1 | 47 | -0.4347 | 0.0782 | -0.3707 | 0.1622 | -0.4558 | 1.4331 | 28.6781 | 5.5944 | 26.7997 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19571
Grape Solar | GS-P-210-Fab5 | 210 W Polycrystalline Module | UL 1703 | 210 | 188.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 7.61 | 36.18 | 7.11 | 29.52 | 46.9 | -0.439 | 0.045 | -0.286 | -0.0034 | -0.435 | 1.416 | 28.1546 | 5.694 | 25.9322 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18984
Grape Solar | GS-S-210-Fab1 | 210 W Monocrystalline Module | UL 1703 | 210 | 187.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 7.8 | 36.4 | 7.22 | 29.1 | 46.8 | -0.4385 | 0.0998 | -0.3669 | 0.1715 | -0.4586 | 1.4502 | 28.8389 | 5.7168 | 26.4993 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19915
Grape Solar | GS-P-215-Fab1 | 215 W Polycrystalline Module | UL 1703 | 215 | 192.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9032 | 72 | 1 | N | 7.9 | 36.6 | 7.34 | 29.3 | 47 | -0.4347 | 0.0782 | -0.3707 | 0.1622 | -0.4558 | 1.457 | 28.8752 | 5.6874 | 26.9839 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19567
Grape Solar | GS-P-215-Fab5 | 215 W Polycrystalline Module | UL 1703 | 215 | 192.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 7.66 | 36.24 | 7.16 | 30 | 46.9 | -0.439 | 0.045 | -0.286 | -0.0034 | -0.435 | 1.426 | 28.6124 | 5.734 | 26.3538 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18977
Grape Solar | GS-S-215-Fab1 | 215 W Monocrystalline Module | UL 1703 | 215 | 192.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 7.9 | 36.6 | 7.34 | 29.3 | 46.8 | -0.4385 | 0.0998 | -0.3669 | 0.1715 | -0.4586 | 1.4743 | 29.0371 | 5.8118 | 26.6814 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19911
Grape Solar | GS-P-220-CS | 220 W Polycrystalline Module | UL 1703 | 220 | 201.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.09 | 36.6 | 7.52 | 29.3 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.4962 | 28.5107 | 5.9847 | 26.9322 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.1939
Grape Solar | GS-P-220-EUG | 220 W Polycrystalline Module | UL 1703 | 220 | 198.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 7.98 | 36.6 | 7.33 | 30 | 46.3 | -0.427 | 0.0457 | -0.309 | 0.0283 | -0.392 | 1.4181 | 28.6359 | 5.9395 | 27.3545 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18459
Grape Solar | GS-P-220-Fab1 | 220 W Polycrystalline Module | UL 1703 | 220 | 196.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9032 | 72 | 1 | N | 8.02 | 36.7 | 7.46 | 29.5 | 47 | -0.4347 | 0.0782 | -0.3707 | 0.1622 | -0.4558 | 1.4808 | 29.0723 | 5.7804 | 27.1681 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19568
Grape Solar | GS-P-220-Fab5 | 220 W Polycrystalline Module | UL 1703 | 220 | 197.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 7.81 | 36.3 | 7.31 | 30.12 | 46.9 | -0.439 | 0.045 | -0.286 | -0.0034 | -0.435 | 1.4558 | 28.7269 | 5.8542 | 26.4592 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.1901
Grape Solar | GS-S-220-CS | 220 W Monocrystalline Module | UL 1703 | 220 | 200.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6997 | 96 | 1 | N | 5.1 | 59.4 | 4.69 | 46.9 | 42.4 | -0.476 | 0.089 | -0.374 | 0.051 | -0.516 | 0.81565 | 46.7021 | 3.5685 | 43.4369 | Rack | Flat Plate | 1.061 | 1.602 | 1 | 0.17315
Grape Solar | GS-S-220-Fab1 | 220 W Monocrystalline Module | UL 1703 | 220 | 196.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 8.02 | 36.7 | 7.46 | 29.5 | 46.8 | -0.4385 | 0.0998 | -0.3669 | 0.1715 | -0.4586 | 1.4984 | 29.2353 | 5.9068 | 26.8635 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19912
Grape Solar | GS-S-220-Fab3 | 220 W Monocrystalline Module | UL 1703 | 220 | 196.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.01 | 58.8 | 4.68 | 47 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 0.90669 | 46.2145 | 3.7733 | 43.0129 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19047
Grape Solar | GS-S-220-Fab8 | 220 W Monocrystalline Module | UL 1703 | 220 | 195.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6896 | 96 | 1 | N | 4.92 | 58.65 | 4.6 | 47.8 | 46.9 | -0.468 | 0.065 | -0.305 | -0.0038 | -0.424 | 0.84449 | 43.4248 | 3.8251 | 42.633 | Rack | Flat Plate | 1.056 | 1.6 | 1 | 0.16669
Grape Solar | GS-P-225-EUG | 225 W Polycrystalline Module | UL 1703 | 225 | 203.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.1 | 36.8 | 7.48 | 30.1 | 46.3 | -0.427 | 0.0457 | -0.309 | 0.0283 | -0.392 | 1.4471 | 28.7313 | 6.0611 | 27.4456 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18479
Grape Solar | GS-P-225-Fab1 | 225 W Polycrystalline Module | UL 1703 | 225 | 202.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.41 | 36.21 | 7.85 | 28.66 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.51 | 27.71 | 6.23 | 25.87 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18596
Grape Solar | GS-P-225-Fab5 | 225 W Polycrystalline Module | UL 1703 | 225 | 201.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 7.97 | 36.33 | 7.46 | 30.18 | 46.9 | -0.439 | 0.045 | -0.286 | -0.0034 | -0.435 | 1.4769 | 29.4406 | 6.0021 | 26.9967 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19324
Grape Solar | GS-S-225-Fab1 | 225 W Monocrystalline Module | UL 1703 | 225 | 201.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 8.13 | 36.8 | 7.58 | 29.7 | 46.8 | -0.4385 | 0.0998 | -0.3669 | 0.1715 | -0.4586 | 1.5435 | 29.4248 | 6.0789 | 27.2131 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.20186
Grape Solar | GS-S-225-Fab3 | 225 W Monocrystalline Module | UL 1703 | 225 | 200.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.09 | 59 | 4.74 | 47.4 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 0.91832 | 46.6078 | 3.8217 | 43.379 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19023
Grape Solar | GS-S-225-Fab8 | 225 W Monocrystalline Module | UL 1703 | 225 | 200.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6896 | 96 | 1 | N | 4.93 | 58.84 | 4.61 | 48.76 | 46.9 | -0.468 | 0.065 | -0.305 | -0.0038 | -0.424 | 0.84633 | 44.297 | 3.8334 | 43.4892 | Rack | Flat Plate | 1.056 | 1.6 | 1 | 0.16662
Grape Solar | GS-P-230-CS | 230 W Polycrystalline Module | UL 1703 | 230 | 211 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6085 | 60 | 1 | N | 8.34 | 36.8 | 7.71 | 29.8 | 43.6 | -0.417 | 0.036 | -0.347 | 0.011 | -0.462 | 1.534 | 28.9973 | 6.1359 | 27.3918 | Rack | Flat Plate | 0.982 | 1.638 | 1 | 0.1934
Grape Solar | GS-P-230-EUG | 230 W Polycrystalline Module | UL 1703 | 230 | 207.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.2 | 37 | 7.6 | 30.3 | 46.3 | -0.427 | 0.0457 | -0.309 | 0.0283 | -0.392 | 1.4704 | 28.9223 | 6.1583 | 27.628 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1849
Grape Solar | GS-P-230-Fab1 | 230 W Polycrystalline Module | UL 1703 | 230 | 207.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.49 | 36.52 | 7.94 | 28.97 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.53 | 28.01 | 6.3 | 26.15 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18633
Grape Solar | GS-P-230-Fab5 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.11 | 36.42 | 7.58 | 30.36 | 46.9 | -0.439 | 0.045 | -0.286 | -0.0034 | -0.435 | 1.5006 | 29.6162 | 6.0986 | 27.1577 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19323
Grape Solar | GS-S-230-CS | 230 W Monocrystalline Module | UL 1703 | 230 | 209.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6997 | 96 | 1 | N | 5.25 | 58.8 | 4.84 | 47.5 | 42.4 | -0.476 | 0.089 | -0.374 | 0.051 | -0.516 | 0.84174 | 47.2996 | 3.6826 | 43.9926 | Rack | Flat Plate | 1.061 | 1.602 | 1 | 0.1731
Grape Solar | GS-S-230-Fab1 | 230 W Monocrystalline Module | UL 1703 | 230 | 205.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 8.24 | 37 | 7.69 | 29.9 | 46.8 | -0.4385 | 0.0998 | -0.3669 | 0.1715 | -0.4586 | 1.5659 | 29.623 | 6.1671 | 27.3964 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.20168
Grape Solar | GS-S-230-Fab3 | 230 W Monocrystalline Module | UL 1703 | 230 | 205.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.18 | 59.1 | 4.84 | 47.5 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 0.93769 | 46.7062 | 3.9023 | 43.4705 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19042
Grape Solar | GS-S-230-Fab8 | 230 W Monocrystalline Module | UL 1703 | 230 | 204.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6896 | 96 | 1 | N | 5 | 58.94 | 4.67 | 49.15 | 46.9 | -0.468 | 0.065 | -0.305 | -0.0038 | -0.424 | 0.85734 | 44.6513 | 3.8833 | 43.837 | Rack | Flat Plate | 1.056 | 1.6 | 1 | 0.16644
Grape Solar | GS-P-235-Fab1 | 235 W Polycrystalline Module | UL 1703 | 235 | 212 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.57 | 36.83 | 8.03 | 29.27 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.54 | 28.3 | 6.37 | 26.42 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18546
Grape Solar | GS-P-235-Fab5 | 235 W Polycrystalline Module | UL 1703 | 235 | 211 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.22 | 36.54 | 7.68 | 30.6 | 46.9 | -0.439 | 0.045 | -0.286 | -0.0034 | -0.435 | 1.5204 | 29.8504 | 6.1791 | 27.3724 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19313
Grape Solar | GS-S-235-Fab1 | 235 W Monocrystalline Module | UL 1703 | 235 | 210.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 8.35 | 37.2 | 7.81 | 30.1 | 46.8 | -0.4385 | 0.0998 | -0.3669 | 0.1715 | -0.4586 | 1.5904 | 29.8211 | 6.2633 | 27.5796 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.20182
Grape Solar | GS-S-235-Fab3 | 235 W Monocrystalline Module | UL 1703 | 235 | 210 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.27 | 59.2 | 4.93 | 47.7 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 0.95513 | 46.9028 | 3.9749 | 43.6535 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19063
Grape Solar | GS-S-235-Fab8 | 235 W Monocrystalline Module | UL 1703 | 235 | 209.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6896 | 96 | 1 | N | 5.05 | 59.04 | 4.72 | 49.72 | 46.9 | -0.468 | 0.065 | -0.305 | -0.0038 | -0.424 | 0.86652 | 45.1691 | 3.9248 | 44.3454 | Rack | Flat Plate | 1.056 | 1.6 | 1 | 0.16655
Grape Solar | GS-P-240-Fab1 | 240 W Polycrystalline Module | UL 1703 | 240 | 216.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.65 | 37.14 | 8.12 | 29.57 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.56 | 28.59 | 6.44 | 26.69 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18584
Grape Solar | GS-S-240-CS | 240 W Monocrystalline Module | UL 1703 | 240 | 218.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6997 | 96 | 1 | N | 5.4 | 59.3 | 4.99 | 48.8 | 42.4 | -0.476 | 0.089 | -0.374 | 0.051 | -0.516 | 0.86783 | 48.5941 | 3.7967 | 45.1966 | Rack | Flat Plate | 1.061 | 1.602 | 1 | 0.17571
Grape Solar | GS-S-240-Fab1 | 240 W Monocrystalline Module | UL 1703 | 240 | 214.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 8.47 | 37.3 | 7.92 | 30.3 | 46.8 | -0.4385 | 0.0998 | -0.3669 | 0.1715 | -0.4586 | 1.6128 | 30.0193 | 6.3516 | 27.7629 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.20173
Grape Solar | GS-S-240-Fab3 | 240 W Monocrystalline Module | UL 1703 | 240 | 214.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.34 | 59.4 | 4.99 | 48.1 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 0.99031 | 46.8538 | 4.0285 | 43.9788 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19333
Grape Solar | GS-S-240-Fab8 | 240 W Monocrystalline Module | UL 1703 | 240 | 213.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6896 | 96 | 1 | N | 5.1 | 59.61 | 4.77 | 50.3 | 46.9 | -0.468 | 0.065 | -0.305 | -0.0038 | -0.424 | 0.88264 | 47.138 | 3.7653 | 44.7354 | Rack | Flat Plate | 1.056 | 1.6 | 1 | 0.17336
Grape Solar | GS-P-245-Fab1 | 245 W Polycrystalline Module | UL 1703 | 245 | 221.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.73 | 37.45 | 8.21 | 29.85 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.58 | 28.86 | 6.51 | 26.94 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18612
Grape Solar | GS-S-245-Fab3 | 245 W Monocrystalline Module | UL 1703 | 245 | 219.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.43 | 59.5 | 5.06 | 48.4 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 1.0042 | 47.1461 | 4.085 | 44.2531 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19324
Grape Solar | GS-S-245-Fab8 | 245 W Monocrystalline Module | UL 1703 | 245 | 218.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6896 | 96 | 1 | N | 5.18 | 59.76 | 4.84 | 50.54 | 46.9 | -0.468 | 0.065 | -0.305 | -0.0038 | -0.424 | 0.89559 | 47.363 | 3.8206 | 44.9488 | Rack | Flat Plate | 1.056 | 1.6 | 1 | 0.17313
Grape Solar | GS-P-250-EUG | 250 W Polycrystalline Module | UL 1703 | 250 | 224.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 7.75 | 43.3 | 7.06 | 35.4 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4102 | 35.1163 | 5.7523 | 32.3094 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19808
Grape Solar | GS-P-250-Fab1 | 250 W Polycrystalline Module | UL 1703 | 250 | 225.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.81 | 37.76 | 8.3 | 30.13 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.63 | 29.17 | 6.61 | 27.52 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19019
Grape Solar | GS-S-250-Fab3 | 250 W Monocrystalline Module | UL 1703 | 250 | 223.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.49 | 59.6 | 5.14 | 48.7 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 1.0201 | 47.4383 | 4.1496 | 44.5274 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19356
Grape Solar | GS-S-250-Fab5 | 250 W Monocrystalline Module | UL 1703 | 250 | 222.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 7.71 | 43.77 | 7.21 | 34.71 | 46.9 | -0.468 | 0.065 | -0.305 | -0.0038 | -0.424 | 1.3341 | 32.5281 | 5.6914 | 30.8701 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.17359
Grape Solar | GS-S-250-Fab8 | 250 W Monocrystalline Module | UL 1703 | 250 | 223 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6896 | 96 | 1 | N | 5.26 | 59.9 | 4.92 | 50.78 | 46.9 | -0.468 | 0.065 | -0.305 | -0.0038 | -0.424 | 0.91039 | 47.5879 | 3.8837 | 45.1623 | Rack | Flat Plate | 1.056 | 1.6 | 1 | 0.17329
Grape Solar | GS-P-255-EUG | 255 W Polycrystalline Module | UL 1703 | 255 | 228.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 7.84 | 43.5 | 7.16 | 35.6 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4301 | 35.3146 | 5.8337 | 32.4919 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19806
Grape Solar | GS-P-255-Fab1 | 255 W Polycrystalline Module | UL 1703 | 255 | 230.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.89 | 38.07 | 8.39 | 30.4 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.65 | 29.44 | 6.68 | 27.77 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19049
Grape Solar | GS-P60-255-Fab2 | 255 W Polycrystalline Module | UL 1703 | 255 | 230.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.98 | 37.82 | 8.42 | 30.29 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.67 | 29.39 | 6.73 | 27.36 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19248
Grape Solar | GS-S-255-Fab3 | 255 W Monocrystalline Module | UL 1703 | 255 | 228.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9032 | 72 | 1 | N | 5.57 | 59.7 | 5.2 | 49 | 46.1 | -0.46 | 0.053 | -0.344 | -0.035 | -0.427 | 1.032 | 47.7305 | 4.1981 | 44.8017 | Rack | Flat Plate | 0.978 | 1.946 | 1 | 0.19317
Grape Solar | GS-S-255-Fab5 | 255 W Monocrystalline Module | UL 1703 | 255 | 226.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 7.73 | 43.85 | 7.23 | 35.28 | 46.9 | -0.468 | 0.065 | -0.305 | -0.0038 | -0.424 | 1.3378 | 33.0622 | 5.7071 | 31.377 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.17346
Grape Solar | GS-P-260-EUG | 260 W Polycrystalline Module | UL 1703 | 260 | 233.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 7.92 | 43.7 | 7.26 | 35.8 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4501 | 35.513 | 5.9152 | 32.6744 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19807
Grape Solar | GS-P-260-Fab1 | 260 W Polycrystalline Module | UL 1703 | 260 | 235.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.97 | 38.38 | 8.48 | 30.67 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.67 | 29.7 | 6.75 | 28.01 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19077
Grape Solar | GS-P60-260-Fab2 | 260 W Polycrystalline Module | UL 1703 | 260 | 234.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.04 | 37.98 | 8.49 | 30.63 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.68 | 29.72 | 6.79 | 27.67 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19204
Grape Solar | GS-P72-260-Fab2 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.24 | 42.81 | 7.62 | 34.12 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.5 | 33.09 | 6.11 | 30.89 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1909
Grape Solar | GS-S-260-Fab1 | 260 W Monocrystalline Module | UL 1703 | 260 | 232.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.968 | 72 | 1 | N | 7.88 | 44.5 | 7.26 | 35.8 | 46.4 | -0.46 | 0.06 | -0.33 | -0.01 | -0.45 | 1.4611 | 50.0712 | 5.8263 | 46.4998 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.28139
Grape Solar | GS-S-260-Fab5 | 260 W Monocrystalline Module | UL 1703 | 260 | 231.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 7.82 | 43.92 | 7.31 | 35.57 | 46.7 | -0.467 | 0.064 | -0.322 | 0.0028 | -0.456 | 1.5843 | 28.5632 | 6.197 | 29.0098 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.17405
Grape Solar | GS-P-265-Fab1 | 265 W Polycrystalline Module | UL 1703 | 265 | 239.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.05 | 38.69 | 8.57 | 30.93 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.69 | 29.95 | 6.82 | 28.25 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.191
Grape Solar | GS-P60-265-Fab2 | 265 W Polycrystalline Module | UL 1703 | 265 | 239.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.1 | 38.14 | 8.56 | 30.96 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.7 | 30.04 | 6.84 | 27.97 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19271
Grape Solar | GS-P72-265-Fab2 | 265 W Polycrystalline Module | UL 1703 | 265 | 240.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.31 | 43.11 | 7.71 | 34.37 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.51 | 33.33 | 6.18 | 31.12 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18992
Grape Solar | GS-S-265-Fab1 | 265 W Monocrystalline Module | UL 1703 | 265 | 236.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.968 | 72 | 1 | N | 8.02 | 44.5 | 7.4 | 35.8 | 46.4 | -0.46 | 0.06 | -0.33 | -0.01 | -0.45 | 1.4893 | 50.0712 | 5.9386 | 46.4998 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.2814
Grape Solar | GS-S-265-Fab5 | 265 W Monocrystalline Module | UL 1703 | 265 | 236.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 7.91 | 43.99 | 7.39 | 35.86 | 46.7 | -0.467 | 0.064 | -0.322 | 0.0028 | -0.456 | 1.6017 | 28.7961 | 6.2648 | 29.2463 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.17404
Grape Solar | GS-P-270-EUG | 270 W Polycrystalline Module | UL 1703 | 270 | 242.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.1 | 44.1 | 7.48 | 36.1 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4782 | 36.5937 | 6.0401 | 33.1801 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20035
Grape Solar | GS-P-270-Fab1 | 270 W Polycrystalline Module | UL 1703 | 270 | 244.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.13 | 39 | 8.66 | 31.19 | 47.5 | -0.411 | 0.0527 | -0.213 | -0.0074 | -0.405 | 1.71 | 30.2 | 6.9 | 28.49 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19127
Grape Solar | GS-P72-270-Fab2 | 270 W Polycrystalline Module | UL 1703 | 270 | 245.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.38 | 43.41 | 7.8 | 34.62 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.53 | 33.57 | 6.25 | 31.34 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19023
Grape Solar | GS-S-270-Fab1 | 270 W Monocrystalline Module | UL 1703 | 270 | 241.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.968 | 72 | 1 | N | 8.16 | 44.6 | 7.54 | 35.8 | 46.4 | -0.46 | 0.06 | -0.33 | -0.01 | -0.45 | 1.5175 | 50.0712 | 6.051 | 46.4998 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.28142
Grape Solar | GS-S-270-Fab5 | 270 W Monocrystalline Module | UL 1703 | 270 | 240.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 7.96 | 44.07 | 7.44 | 36.29 | 46.7 | -0.467 | 0.064 | -0.322 | 0.0028 | -0.456 | 1.6125 | 29.1414 | 6.3072 | 29.597 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.17404
Grape Solar | GS-P-275-EUG | 275 W Polycrystalline Module | UL 1703 | 275 | 247.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.2 | 44.3 | 7.6 | 36.2 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.5019 | 36.6951 | 6.137 | 33.2721 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20042
Grape Solar | GS-P-275-Fab1 | 275 W Polycrystalline Module | UL 1703 | 275 | 246.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.968 | 72 | 1 | N | 8.28 | 44.5 | 7.68 | 35.8 | 46.6 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.4992 | 49.1295 | 6.2098 | 45.3938 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.26784
Grape Solar | GS-P60-275-Fab2 | 275 W Polycrystalline Module | UL 1703 | 275 | 248.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.22 | 38.46 | 8.7 | 31.61 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.72 | 30.67 | 6.96 | 28.56 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19183
Grape Solar | GS-P72-275-Fab2 | 275 W Polycrystalline Module | UL 1703 | 275 | 250.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.45 | 43.7 | 7.89 | 34.85 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.55 | 33.8 | 6.32 | 31.55 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19051
Grape Solar | GS-S-275-Fab1 | 275 W Monocrystalline Module | UL 1703 | 275 | 246.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.968 | 72 | 1 | N | 8.28 | 44.5 | 7.68 | 35.8 | 46.4 | -0.46 | 0.06 | -0.33 | -0.01 | -0.45 | 1.5457 | 50.0712 | 6.1633 | 46.4998 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.28143
Grape Solar | GS-S-275-Fab5 | 275 W Monocrystalline Module | UL 1703 | 275 | 245.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.04 | 44.14 | 7.52 | 36.58 | 46.7 | -0.467 | 0.064 | -0.322 | 0.0028 | -0.456 | 1.6267 | 30.347 | 6.2926 | 31.9208 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.17951
Grape Solar | GS-P-280-EUG | 280 W Polycrystalline Module | UL 1703 | 280 | 252 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.28 | 44.5 | 7.7 | 36.4 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.5217 | 36.8978 | 6.2177 | 33.4559 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20053
Grape Solar | GS-P-280-Fab1 | 280 W Polycrystalline Module | UL 1703 | 280 | 251 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.968 | 72 | 1 | N | 8.46 | 44.5 | 7.82 | 35.8 | 46.6 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.5542 | 48.6484 | 6.2757 | 45.3231 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.27003
Grape Solar | GS-P72-280-Fab2 | 280 W Polycrystalline Module | UL 1703 | 280 | 254.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.52 | 44 | 7.98 | 35.09 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.57 | 34.03 | 6.39 | 31.77 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19081
Grape Solar | GS-S-280-Fab1 | 280 W Monocrystalline Module | UL 1703 | 280 | 250.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.968 | 72 | 1 | N | 8.86 | 44.5 | 7.82 | 35.8 | 46.4 | -0.46 | 0.06 | -0.33 | -0.01 | -0.45 | 1.5699 | 48.9271 | 6.3867 | 44.4399 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.27432
Grape Solar | GS-S-280-Fab5 | 280 W Monocrystalline Module | UL 1703 | 280 | 249.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.13 | 44.21 | 7.6 | 36.86 | 46.7 | -0.467 | 0.064 | -0.322 | 0.0028 | -0.456 | 1.644 | 30.5793 | 6.3596 | 32.1651 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.17955
Grape Solar | GS-M60-285-Fab1-USA | 285 W Monocrystalline Module | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.48 | 39.43 | 8.97 | 31.76 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7859 | 30.4884 | 7.1841 | 28.7062 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19105
Grape Solar | GS-P-285-Fab1 | 285 W Polycrystalline Module | UL 1703 | 285 | 255.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.968 | 72 | 1 | N | 8.56 | 44.6 | 7.92 | 36 | 46.6 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.574 | 48.9202 | 6.3559 | 45.5763 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.27018
Grape Solar | GS-P72-285-Fab2 | 285 W Polycrystalline Module | UL 1703 | 285 | 259.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.6 | 44.3 | 8.07 | 35.4 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.59 | 34.42 | 6.44 | 32.08 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19203
Grape Solar | GS-S-285-Fab1 | 285 W Monocrystalline Module | UL 1703 | 285 | 255.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.968 | 72 | 1 | N | 8.56 | 44.6 | 7.92 | 36 | 46.4 | -0.46 | 0.06 | -0.33 | -0.01 | -0.45 | 1.5899 | 49.2005 | 6.4683 | 44.6882 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.27447
Grape Solar | GS-M60-290-Fab1-USA | 290 W Monocrystalline Module | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.62 | 39.77 | 9.06 | 32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8038 | 30.7188 | 7.2562 | 28.9231 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19107
Grape Solar | GS-P-290-Fab1 | 290 W Polycrystalline Module | UL 1703 | 290 | 260.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.968 | 72 | 1 | N | 8.76 | 44.8 | 8.05 | 36 | 46.6 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.5999 | 48.9202 | 6.4603 | 45.5763 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.26988
Grape Solar | GS-P72-290-Fab2 | 290 W Polycrystalline Module | UL 1703 | 290 | 264.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.67 | 44.6 | 8.16 | 35.65 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.61 | 34.67 | 6.51 | 32.31 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19248
Grape Solar | GS-S-290-Fab1 | 290 W Monocrystalline Module | UL 1703 | 290 | 259.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.968 | 72 | 1 | N | 8.76 | 44.8 | 8.05 | 36 | 46.4 | -0.46 | 0.06 | -0.33 | -0.01 | -0.45 | 1.616 | 49.2005 | 6.5745 | 44.6882 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.27417
Grape Solar | GS-M60-295-Fab1-USA | 295 W Monocrystalline Module | UL 1703 | 295 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.814 | 31.2838 | 7.323 | 29.5803 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
Grape Solar | GS-P-295-Fab1 | 295 W Polycrystalline Module | UL 1703 | 295 | 264.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.968 | 72 | 1 | N | 8.81 | 44.8 | 8.19 | 36 | 46.6 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.6277 | 48.9202 | 6.5726 | 45.5763 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.26992
Grape Solar | GS-P72-295-Fab2 | 295 W Polycrystalline Module | UL 1703 | 295 | 268.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.75 | 44.9 | 8.25 | 35.76 | 45.6 | -0.412 | 0.0459 | -0.308 | -0.0098 | -0.404 | 1.62 | 34.77 | 6.59 | 32.41 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19094
Grape Solar | GS-S-295-Fab1 | 295 W Monocrystalline Module | UL 1703 | 295 | 264.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.968 | 72 | 1 | N | 8.71 | 44.8 | 8.19 | 36 | 46.4 | -0.46 | 0.06 | -0.33 | -0.01 | -0.45 | 1.6441 | 49.2005 | 6.6888 | 44.6882 | Rack | Flat Plate | 1 | 1.968 | 1 | 0.27421
Grape Solar | GS-M60-300-Fab1-USA | 300 W Monocrystalline Module | UL 1703 | 300 | 275.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8319 | 31.5167 | 7.395 | 29.8005 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19245
Grape Solar | GS-P72-300-Fab2 | 300 W Polycrystalline Module | UL 1703 | 300 | 270.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.73 | 45.2 | 8.24 | 36.41 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.64 | 35.2 | 6.59 | 33.02 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19243
Grape Solar | GS-P72-305-Fab2 | 305 W Polycrystalline Module | UL 1703 | 305 | 275.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.79 | 45.35 | 8.31 | 36.71 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.65 | 35.49 | 6.65 | 33.29 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.192
Grape Solar | GS-P72-310-Fab2 | 310 W Polycrystalline Module | UL 1703 | 310 | 279.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.85 | 45.45 | 8.38 | 37 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.67 | 35.77 | 6.7 | 33.56 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.1927
Grape Solar | GS-P72-315-Fab2 | 315 W Polycrystalline Module | UL 1703 | 315 | 284.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.91 | 45.6 | 8.45 | 37.28 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.68 | 36.04 | 6.76 | 33.81 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19221
Grape Solar | GS-P72-320-Fab2 | 320 W Polycrystalline Module | UL 1703 | 320 | 289.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.97 | 45.75 | 8.52 | 37.56 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.69 | 36.31 | 6.82 | 34.07 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19176
Grape Solar | GS-P72-325-Fab2 | 325 W Polycrystalline Module | UL 1703 | 325 | 293.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.03 | 45.9 | 8.59 | 37.84 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.71 | 36.58 | 6.87 | 34.32 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19247
Grape Solar | GS-P72-330-Fab2 | 330 W Polycrystalline Module | UL 1703 | 330 | 298.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.09 | 46.05 | 8.66 | 38.11 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.72 | 36.85 | 6.93 | 34.56 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19207
Grape Solar | GS-M72-340-Fab1-USA | 340 W Monocrystalline Module | UL 1703 | 340 | 311.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.64 | 47.18 | 8.96 | 38.32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7738 | 36.8198 | 7.1761 | 34.6753 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19209
Grape Solar | GS-M72-345-Fab1-USA | 345 W Monocrystalline Module | UL 1703 | 345 | 315.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.72 | 47.28 | 8.98 | 38.4 | 44.6 | -0.43 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7777 | 36.8967 | 7.1921 | 34.7477 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19012
Grape Solar | GS-M72-350-Fab1-USA | 350 W Monocrystalline Module | UL 1703 | 350 | 320.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.81 | 47.37 | 9.1 | 38.48 | 44.6 | -0.43 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8015 | 36.9736 | 7.2882 | 34.8201 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19031
Grape Solar | GS-M72-355-Fab1-USA | 355 W Monocrystalline Module | UL 1703 | 355 | 325.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.8985 | 47.4657 | 9.2082 | 38.5524 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8182 | 37.5082 | 7.381 | 35.3921 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
Grape Solar | GS-M72-360-Fab1-USA | 360 W Monocrystalline Module | UL 1703 | 360 | 330.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.9876 | 47.5606 | 9.3193 | 38.6295 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8401 | 37.5832 | 7.47 | 35.4629 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
Greenlite Solar Canada | GLS-200 | 200 W Polycrystalline Module | UL 1703 | 200 | 180 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4593 | 54 | 1 | N | 7.95 | 33.37 | 7.45 | 27.54 | 46.2 | -0.44 | 0.13 | -0.3 | -0.01 | -0.4 | 1.5972 | 28.0596 | 6.2168 | 25.6495 | Rack | Flat Plate | 0.982 | 1.486 | 1 | 0.22408
Greenlite Solar Canada | GLS-220 | 220 W Polycrystalline Module | UL 1703 | 220 | 197.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6144 | 60 | 1 | N | 7.95 | 37.08 | 7.45 | 30.6 | 46.2 | -0.44 | 0.13 | -0.3 | -0.01 | -0.4 | 1.5752 | 32.0657 | 6.0828 | 28.5414 | Rack | Flat Plate | 0.982 | 1.644 | 1 | 0.22959
Greenlite Solar Canada | GLS-270 | 270 W Polycrystalline Module | UL 1703 | 270 | 243.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9247 | 72 | 1 | N | 7.95 | 44.49 | 7.45 | 36.72 | 46.2 | -0.44 | 0.13 | -0.3 | -0.01 | -0.4 | 1.61 | 37.6418 | 6.14 | 34.174 | Rack | Flat Plate | 0.982 | 1.96 | 1 | 0.22446
Guangdong Golden Glass Technologies | GG160M2-24/1324x992 | 160 W Polycrystalline Module | UL 1703 | 160 | 143.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 7.6 | 28.6 | 6.87 | 23.3 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.2994 | 23.6196 | 5.5031 | 21.5872 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.19183
Guangdong Golden Glass Technologies | GG165M2-24/1324x992 | 165 W Polycrystalline Module | UL 1703 | 165 | 148 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 7.7 | 28.8 | 7.02 | 23.5 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.3278 | 23.8223 | 5.6233 | 21.7725 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.19171
Guangdong Golden Glass Technologies | GG170M2-24/1324x992 | 170 W Polycrystalline Module | UL 1703 | 170 | 152.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 7.82 | 29 | 7.15 | 23.8 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.411 | 24.4188 | 5.7544 | 21.9467 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.20267
Guangdong Golden Glass Technologies | GG175M2-24/1324x992 | 175 W Polycrystalline Module | UL 1703 | 175 | 157.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 7.96 | 29.2 | 7.29 | 24 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4386 | 24.624 | 5.8671 | 22.1311 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.20242
Guangdong Golden Glass Technologies | GG175S1-36/1589x807 | 175 W Monocrystalline Module | UL 1703 | 175 | 158.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2823 | 72 | 1 | N | 5.28 | 43.8 | 4.83 | 36.2 | 45.8 | -0.416 | 0.0479 | -0.307 | -0.0236 | -0.396 | 0.92958 | 35.6032 | 3.9004 | 33.3376 | Rack | Flat Plate | 0.807 | 1.589 | 1 | 0.18912
Guangdong Golden Glass Technologies | GG180M2-24/1324x992 | 180 W Polycrystalline Module | UL 1703 | 180 | 161.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3134 | 48 | 1 | N | 8.1 | 29.4 | 7.47 | 24.1 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4741 | 24.7266 | 6.012 | 22.2233 | Rack | Flat Plate | 0.992 | 1.324 | 1 | 0.2025
Guangdong Golden Glass Technologies | GG180S1-36/1589x807 | 180 W Monocrystalline Module | UL 1703 | 180 | 163.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2823 | 72 | 1 | N | 5.35 | 44.2 | 4.93 | 36.5 | 45.8 | -0.416 | 0.0479 | -0.307 | -0.0236 | -0.396 | 0.94883 | 35.8983 | 3.9812 | 33.6139 | Rack | Flat Plate | 0.807 | 1.589 | 1 | 0.18923
Guangdong Golden Glass Technologies | GG190M2-27/1482x992 | 190 W Polycrystalline Module | UL 1703 | 190 | 170.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.8 | 32.6 | 7.12 | 26.7 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4105 | 27.1633 | 5.7248 | 24.6318 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.20165
Guangdong Golden Glass Technologies | GG195M2-27/1482x992 | 195 W Polycrystalline Module | UL 1703 | 195 | 175.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 7.92 | 32.8 | 7.25 | 26.9 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4363 | 27.3667 | 5.8293 | 24.8163 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.20157
Guangdong Golden Glass Technologies | GG200M2-27/1482x992 | 200 W Polycrystalline Module | UL 1703 | 200 | 179.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.02 | 33 | 7.38 | 27.1 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.462 | 27.5702 | 5.9339 | 25.0009 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.20154
Guangdong Golden Glass Technologies | GG205M2-27/1482x992 | 205 W Polycrystalline Module | UL 1703 | 205 | 184.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4701 | 54 | 1 | N | 8.15 | 33.2 | 7.54 | 27.2 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4937 | 27.6719 | 6.0625 | 25.0931 | Rack | Flat Plate | 0.992 | 1.482 | 1 | 0.20163
Guangdong Golden Glass Technologies | GG220M2-30/1640x992 | 220 W Polycrystalline Module | UL 1703 | 220 | 198.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 7.98 | 36.6 | 7.33 | 30 | 46.3 | -0.427 | 0.0457 | -0.309 | 0.0283 | -0.392 | 1.4181 | 28.6359 | 5.9395 | 27.3545 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18459
Guangdong Golden Glass Technologies | GG225M2-30/1640x992 | 225 W Polycrystalline Module | UL 1703 | 225 | 203.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.1 | 36.8 | 7.48 | 30.1 | 46.3 | -0.427 | 0.0457 | -0.309 | 0.0283 | -0.392 | 1.4471 | 28.7313 | 6.0611 | 27.4456 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18479
Guangdong Golden Glass Technologies | GG230M2-30/1640x992 | 230 W Polycrystalline Module | UL 1703 | 230 | 207.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.2 | 37 | 7.6 | 30.3 | 46.3 | -0.427 | 0.0457 | -0.309 | 0.0283 | -0.392 | 1.4704 | 28.9223 | 6.1583 | 27.628 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1849
Guangdong Golden Glass Technologies | GG250M2-35/1956x992 | 250 W Polycrystalline Module | UL 1703 | 250 | 224.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 7.75 | 43.3 | 7.06 | 35.4 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4102 | 35.1163 | 5.7523 | 32.3094 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19808
Guangdong Golden Glass Technologies | GG255M2-35/1956x992 | 255 W Polycrystalline Module | UL 1703 | 255 | 228.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 7.84 | 43.5 | 7.16 | 35.6 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4301 | 35.3146 | 5.8337 | 32.4919 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19806
Guangdong Golden Glass Technologies | GG260M2-35/1956x992 | 260 W Polycrystalline Module | UL 1703 | 260 | 233.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 7.92 | 43.7 | 7.26 | 35.8 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4501 | 35.513 | 5.9152 | 32.6744 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19807
Guangdong Golden Glass Technologies | GG270M2-36/1956x992 | 270 W Polycrystalline Module | UL 1703 | 270 | 242.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.1 | 44.1 | 7.48 | 36.1 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.4782 | 36.5937 | 6.0401 | 33.1801 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20035
Guangdong Golden Glass Technologies | GG275M2-36/1956x992 | 275 W Polycrystalline Module | UL 1703 | 275 | 247.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.2 | 44.3 | 7.6 | 36.2 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.5019 | 36.6951 | 6.137 | 33.2721 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20042
Guangdong Golden Glass Technologies | GG280M2-36/1956x992 | 280 W Polycrystalline Module | UL 1703 | 280 | 252 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.28 | 44.5 | 7.7 | 36.4 | 46.7 | -0.435 | 0.041 | -0.303 | -0.015 | -0.422 | 1.5217 | 36.8978 | 6.2177 | 33.4559 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20053
Hansol Technics Co., Ltd. | HS240ME-V01 | 240 W Polycrystalline Module | UL 1703 | 240 | 214.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.31 | 37.7 | 7.93 | 30.3 | 48.1 | -0.44 | 0.05 | -0.32 | -0.01 | -0.43 | 1.57 | 29.62 | 6.37 | 27.51 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19376 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS245ME-V01 | 245 W Polycrystalline Module | UL 1703 | 245 | 219 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.44 | 37.8 | 8.07 | 30.4 | 48.1 | -0.44 | 0.05 | -0.32 | -0.01 | -0.43 | 1.6 | 29.71 | 6.48 | 27.6 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19402 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS250ME-V01 | 250 W Polycrystalline Module | UL 1703 | 250 | 223.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.57 | 37.9 | 8.2 | 30.5 | 48.1 | -0.44 | 0.05 | -0.32 | -0.01 | -0.43 | 1.63 | 29.81 | 6.58 | 27.69 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19436 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS250NB-AN3 | 250 W Polycrystalline Module | UL 1703 | 250 | 228.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.96 | 36.8 | 8.43 | 29.7 | 44.11 | -0.42 | 0.04 | -0.3 | -0.02 | -0.4 | 1.69 | 28.885 | 6.7598 | 27.449 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19526 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS255ME-V01 | 255 W Polycrystalline Module | UL 1703 | 255 | 228.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.71 | 38 | 8.34 | 30.6 | 48.1 | -0.44 | 0.05 | -0.32 | -0.01 | -0.43 | 1.65 | 29.91 | 6.7 | 27.78 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19354 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS255NB-AN3 | 255 W Polycrystalline Module | UL 1703 | 255 | 233.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.01 | 37.2 | 8.49 | 30.1 | 44.11 | -0.42 | 0.04 | -0.3 | -0.02 | -0.4 | 1.702 | 29.274 | 6.8079 | 27.8187 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19539 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS255NB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 255 | 233.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.01 | 37.2 | 8.49 | 30.1 | 45.6 | -0.394 | 0.046 | -0.304 | 0.005 | -0.399 | 1.724 | 30.078 | 7.014 | 28.671 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS255SE-V01 | 255 W Monocrystalline Module | UL 1703 | 255 | 230.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6007 | 60 | 1 | N | 8.74 | 37.9 | 8.23 | 31 | 45.8 | -0.451 | 0.048 | -0.328 | -0.018 | -0.436 | 1.66 | 29.77 | 6.58 | 27.87 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.1938 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS260ME-V01 | 260 W Polycrystalline Module | UL 1703 | 260 | 233.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.85 | 38.1 | 8.48 | 30.7 | 47.94 | -0.42 | 0.05 | -0.31 | -0.01 | -0.41 | 6.1185 | 29.649 | 24.5815 | 27.9173 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.69772 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS260NB-AN3 | 260 W Polycrystalline Module | UL 1703 | 260 | 238.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.07 | 37.6 | 8.54 | 30.5 | 44.11 | -0.42 | 0.04 | -0.3 | -0.02 | -0.4 | 1.712 | 29.663 | 6.848 | 28.1883 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19532 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS260NB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 260 | 238.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.07 | 37.6 | 8.54 | 30.5 | 45.6 | -0.394 | 0.046 | -0.304 | 0.005 | -0.399 | 1.724 | 30.078 | 7.014 | 28.671 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS260PB-AN1 | 260 W, 60 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 260 | 239.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.61 | 60 |  | N | 9.03 | 37.3 | 8.54 | 30.5 | 44.77 | -0.388 | 0.047 | -0.303 | 0.005 | -0.393 | 1.7031 | 29.1738 | 6.8112 | 28.1574 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS260SE-V01 | 260 W Monocrystalline Module | UL 1703 | 260 | 234.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6007 | 60 | 1 | N | 8.88 | 38 | 8.37 | 31.1 | 45.8 | -0.451 | 0.048 | -0.328 | -0.018 | -0.436 | 1.69 | 29.86 | 6.69 | 27.96 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19409 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS265ME-V01 | 265 W Polycrystalline Module | UL 1703 | 265 | 238.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.98 | 38.2 | 8.61 | 30.8 | 47.94 | -0.42 | 0.05 | -0.31 | -0.01 | -0.41 | 6.1385 | 29.7455 | 24.6615 | 28.0082 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.68903 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS265NB-AN3 | 265 W Polycrystalline Module | UL 1703 | 265 | 242.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.12 | 38 | 8.59 | 30.9 | 44.11 | -0.42 | 0.04 | -0.3 | -0.02 | -0.4 | 1.722 | 30.052 | 6.8881 | 28.558 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19528 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS265NB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 265 | 242.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.12 | 38 | 8.59 | 30.9 | 45.6 | -0.394 | 0.046 | -0.304 | 0.005 | -0.399 | 1.724 | 30.078 | 7.014 | 28.671 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS265PB-AN1 | 265 W, 60 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 265 | 244.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.61 | 60 |  | N | 9.08 | 37.7 | 8.59 | 30.9 | 44.77 | -0.388 | 0.047 | -0.303 | 0.005 | -0.393 | 1.713 | 29.5564 | 6.8511 | 28.5267 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS265SE-V01 | 265 W Monocrystalline Module | UL 1703 | 265 | 239.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6007 | 60 | 1 | N | 9.01 | 38.1 | 8.5 | 31.2 | 45.8 | -0.451 | 0.048 | -0.328 | -0.018 | -0.436 | 1.72 | 29.96 | 6.79 | 28.05 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19446 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS270ME-V01 | 270 W Polycrystalline Module | UL 1703 | 270 | 243.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.12 | 38.3 | 8.75 | 30.9 | 47.94 | -0.42 | 0.05 | -0.31 | -0.01 | -0.41 | 6.1584 | 29.8421 | 24.7416 | 28.0992 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.68066 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS270NB-AN3 | 270 W Polycrystalline Module | UL 1703 | 270 | 247.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.16 | 38.4 | 8.63 | 31.3 | 44.11 | -0.42 | 0.04 | -0.3 | -0.02 | -0.4 | 1.73 | 30.4411 | 6.9202 | 28.9277 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19505 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS270NB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 270 | 247.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.16 | 38.4 | 8.63 | 31.3 | 45.6 | -0.394 | 0.046 | -0.304 | 0.005 | -0.399 | 1.724 | 30.078 | 7.014 | 28.671 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS270PB-AN1 | 270 W, 60 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 270 | 248.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.61 | 60 |  | N | 9.13 | 38.1 | 8.64 | 31.3 | 44.77 | -0.388 | 0.047 | -0.303 | 0.005 | -0.393 | 1.723 | 29.939 | 6.891 | 28.896 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS270SE-V01 | 270 W Monocrystalline Module | UL 1703 | 270 | 244.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6007 | 60 | 1 | N | 9.14 | 38.2 | 8.63 | 31.3 | 45.8 | -0.451 | 0.048 | -0.328 | -0.018 | -0.436 | 1.74 | 30.05 | 6.9 | 28.14 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19366 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS275NB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 275 | 252.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.21 | 38.8 | 8.68 | 31.7 | 45.6 | -0.394 | 0.046 | -0.304 | 0.005 | -0.399 | 1.724 | 30.078 | 7.014 | 28.671 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS275PB-AN1 | 275 W, 60 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 275 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.61 | 60 |  | N | 9.18 | 38.5 | 8.69 | 31.7 | 44.77 | -0.388 | 0.047 | -0.303 | 0.005 | -0.393 | 1.733 | 30.3216 | 6.9309 | 29.2653 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS275SE-V01 | 275 W Monocrystalline Module | UL 1703 | 275 | 248.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6007 | 60 | 1 | N | 9.28 | 38.3 | 8.77 | 31.4 | 45.8 | -0.451 | 0.048 | -0.328 | -0.018 | -0.436 | 1.77 | 30.15 | 7.01 | 28.23 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19406 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS275TB-AN3 | 275 W Monocrystalline Module | UL 1703 | 275 | 246.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.41 | 38.3 | 8.88 | 31 | 46.17 | -0.48 | 0.04 | -0.34 | -0.02 | -0.46 | 1.7702 | 29.93 | 7.1292 | 27.8952 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19266 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS280PB-AN1 | 280 W, 60 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 280 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.61 | 60 |  | N | 9.22 | 38.9 | 8.73 | 32.1 | 44.77 | -0.388 | 0.047 | -0.303 | 0.005 | -0.393 | 1.7409 | 30.7042 | 6.9628 | 29.6346 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS280SE-V01 | 280 W Monocrystalline Module | UL 1703 | 280 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6007 | 60 | 1 | N | 9.41 | 38.4 | 8.9 | 31.5 | 45.8 | -0.451 | 0.048 | -0.328 | -0.018 | -0.436 | 1.8 | 30.25 | 7.11 | 28.32 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19446 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS280TB-AN3 | 280 W Monocrystalline Module | UL 1703 | 280 | 250.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.45 | 38.7 | 8.92 | 31.4 | 46.17 | -0.48 | 0.04 | -0.34 | -0.02 | -0.46 | 1.7782 | 30.3162 | 7.1613 | 28.2552 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19253 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS280TB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 280 | 255.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.45 | 38.7 | 8.92 | 31.4 | 47 | -0.394 | 0.036 | -0.29 | -0.004 | -0.391 | 1.831 | 31.186 | 7.362 | 29.331 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS285TB-AN3 | 285 W Monocrystalline Module | UL 1703 | 285 | 255.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.5 | 39.1 | 8.97 | 31.8 | 46.17 | -0.48 | 0.04 | -0.34 | -0.02 | -0.46 | 1.7881 | 30.7024 | 7.2014 | 28.6151 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19263 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS285TB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 285 | 260.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.5 | 39.1 | 8.97 | 31.8 | 47 | -0.394 | 0.036 | -0.29 | -0.004 | -0.391 | 1.831 | 31.186 | 7.362 | 29.331 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS285UB-AN1 [Wht] | 285 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 285 | 262.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.62 | 39.1 | 9.11 | 31.3 | 45.6 | -0.373 | 0.045 | -0.279 | 0.007 | -0.381 | 1.817 | 31.901 | 7.353 | 30.127 | [6 empty] | 2017-10-01 | 2018-02-01
Hansol Technics Co., Ltd. | HS290TB-AN3 | 290 W Monocrystalline Module | UL 1703 | 290 | 260.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.54 | 39.5 | 9.01 | 32.2 | 46.17 | -0.48 | 0.04 | -0.34 | -0.02 | -0.46 | 1.7961 | 31.0886 | 7.2335 | 28.975 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19255 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS290TB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 290 | 264.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.54 | 39.5 | 9.01 | 32.2 | 47 | -0.394 | 0.036 | -0.29 | -0.004 | -0.391 | 1.831 | 31.186 | 7.362 | 29.331 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS290UB-AN1 [Blk] | 290 W, 60 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.67 | 39.5 | 9.16 | 31.7 | 46.06 | -0.379 | 0.043 | -0.282 | -0.002 | -0.378 | 1.8063 | 30.618 | 7.1957 | 28.9809 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS290UB-AN1 [Wht] | 290 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 290 | 265.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.67 | 39.5 | 9.16 | 31.7 | 47.1 | -0.387 | 0.042 | -0.282 | 0 | -0.387 | 1.8458 | 30.6064 | 7.3329 | 28.6793 | [6 empty] | 2017-10-01 | 2018-07-02
Hansol Technics Co., Ltd. | HS295ME-V01 | 295 W Polycrystalline Module | UL 1703 | 295 | 264.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 8.61 | 45 | 8.09 | 36.5 | 46.7 | -0.45 | 0.05 | -0.33 | -0.01 | -0.162 | 1.6 | 35.39 | 6.48 | 33.14 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19195 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS295TB-AN3 | 295 W Monocrystalline Module | UL 1703 | 295 | 264.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.59 | 39.9 | 9.05 | 32.6 | 46.17 | -0.48 | 0.04 | -0.34 | -0.02 | -0.46 | 1.8041 | 31.4748 | 7.2656 | 29.335 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19249 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS295TB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 295 | 269.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.59 | 39.9 | 9.05 | 32.6 | 47 | -0.394 | 0.036 | -0.29 | -0.004 | -0.391 | 1.831 | 31.186 | 7.362 | 29.331 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS295UB-AN1 [Blk] | 295 W, 60 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.71 | 39.9 | 9.2 | 32.1 | 46.06 | -0.379 | 0.043 | -0.282 | -0.002 | -0.378 | 1.8142 | 31.0043 | 7.2272 | 29.3466 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS295UB-AN1 [Wht] | 295 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 295 | 269.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.71 | 39.9 | 9.2 | 32.1 | 47.1 | -0.387 | 0.042 | -0.282 | 0 | -0.387 | 1.8539 | 30.9926 | 7.365 | 29.0412 | [6 empty] | 2017-10-01 | 2018-07-02
Hansol Technics Co., Ltd. | HS295UB-JH2 [Blk] | 295 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 295 | 274 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.44 | 39.6 | 8.81 | 33.5 | 44.96 | -0.359 | 0.04 | -0.28 |  |  | 1.7756 | 31.32 | 7.2058 | 30.3494 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS300ME-V01 | 300 W Polycrystalline Module | UL 1703 | 300 | 269.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 8.72 | 45.1 | 8.2 | 36.6 | 46.7 | -0.45 | 0.05 | -0.33 | -0.01 | -0.162 | 1.62 | 35.49 | 6.57 | 33.23 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19165 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS300ND-AN3 | 300 W Polycrystalline Module | UL 1703 | 300 | 270.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 8.97 | 44.5 | 8.46 | 35.5 | 47.29 | -0.42 | 0.05 | -0.31 | -0.01 | -0.4 | 1.6841 | 34.4315 | 6.7858 | 32.3716 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19328 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS300TB-AN3 | 300 W Monocrystalline Module | UL 1703 | 300 | 269.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.64 | 40.3 | 9.1 | 33 | 46.17 | -0.48 | 0.04 | -0.34 | -0.02 | -0.46 | 1.8141 | 31.861 | 7.3058 | 29.6949 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19266 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS300TB-AN4 | 60 Cell Poly c-Si PV Module | UL 1703 | 300 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 |  | N | 9.64 | 40.3 | 9.1 | 33 | 47 | -0.394 | 0.036 | -0.29 | -0.004 | -0.391 | 1.831 | 31.186 | 7.362 | 29.331 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS300UB-AN1 [Blk] | 300 W, 60 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.75 | 40.3 | 9.24 | 32.5 | 46.06 | -0.379 | 0.043 | -0.282 | -0.002 | -0.378 | 1.8221 | 31.3907 | 7.2586 | 29.7123 | [6 empty] | 2018-07-02 | 2018-08-01
Hansol Technics Co., Ltd. | HS300UB-AN1 [Wht] | 300 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 300 | 274.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.75 | 40.3 | 9.24 | 32.5 | 47.1 | -0.387 | 0.042 | -0.282 | 0 | -0.387 | 1.8619 | 31.3788 | 7.397 | 29.4031 | [6 empty] | 2017-10-01 | 2018-07-02
Hansol Technics Co., Ltd. | HS300UB-JH2 [Blk] | 300 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 300 | 278.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.54 | 39.8 | 8.91 | 33.7 | 44.96 | -0.359 | 0.04 | -0.28 |  |  | 1.7957 | 31.507 | 7.2876 | 30.5306 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS305ME-V01 | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 8.84 | 45.2 | 8.32 | 36.7 | 46.7 | -0.45 | 0.05 | -0.33 | -0.01 | -0.162 | 1.64 | 35.59 | 6.67 | 33.32 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19137 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS305ND-AN3 | 305 W Polycrystalline Module | UL 1703 | 305 | 275.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.02 | 44.9 | 8.5 | 35.9 | 47.29 | -0.42 | 0.05 | -0.31 | -0.01 | -0.4 | 1.704 | 34.9148 | 6.8159 | 33.1791 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19506 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS305ND-AN4 | 72 Cell Poly c-Si PV Module | UL 1703 | 305 | 279.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 |  | N | 9.02 | 44.9 | 8.5 | 35.9 | 45.57 | -0.397 | 0.045 | -0.307 | 0.007 | -0.404 | 1.704 | 35.933 | 6.946 | 34.364 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS305SE-V01 | 305 W Monocrystalline Module | UL 1703 | 305 | 272.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9129 | 72 | 1 | N | 8.76 | 45.9 | 8.18 | 37.3 | 47.7 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.65 | 35.86 | 6.54 | 32.81 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.194 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS305UB-AN1 [Blk] | 305 W, 60 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 305 | 281 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.79 | 40.7 | 9.28 | 32.9 | 46.06 | -0.379 | 0.043 | -0.282 | -0.002 | -0.378 | 1.83 | 31.777 | 7.29 | 30.078 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS305UB-AN1 [Wht] | 305 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 305 | 279.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.79 | 40.7 | 9.28 | 32.9 | 47.1 | -0.387 | 0.042 | -0.282 | 0 | -0.387 | 1.87 | 31.765 | 7.429 | 29.765 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS305UB-JH2 [Blk] | 305 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 305 | 283.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.63 | 40 | 9 | 33.9 | 44.96 | -0.359 | 0.04 | -0.28 |  |  | 1.8138 | 31.694 | 7.3612 | 30.7118 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS305UB-JH2 [Wht] | 305 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 305 | 285.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.63 | 40 | 9 | 33.9 | 43.35 | -0.357 | 0.045 | -0.28 |  |  | 1.8272 | 31.3462 | 7.3784 | 30.5925 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS310ME-V01 | 310 W Polycrystalline Module | UL 1703 | 310 | 278.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 8.95 | 45.3 | 8.43 | 36.8 | 46.7 | -0.45 | 0.05 | -0.33 | -0.01 | -0.162 | 1.67 | 35.68 | 6.75 | 33.41 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19221 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS310ND-AN3 | 310 W Polycrystalline Module | UL 1703 | 310 | 279.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.07 | 45.3 | 8.55 | 36.3 | 47.29 | -0.42 | 0.05 | -0.31 | -0.01 | -0.4 | 1.714 | 35.3039 | 6.856 | 33.5487 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.1952 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS310ND-AN4 | 72 Cell Poly c-Si PV Module | UL 1703 | 310 | 283.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 |  | N | 9.07 | 45.3 | 8.55 | 36.3 | 45.57 | -0.397 | 0.045 | -0.307 | 0.007 | -0.404 | 1.704 | 35.933 | 6.946 | 34.364 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS310SE-V01 | 310 W Monocrystalline Module | UL 1703 | 310 | 277.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9129 | 72 | 1 | N | 8.88 | 46 | 8.3 | 37.4 | 47.7 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.68 | 35.95 | 6.63 | 32.9 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19483 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS310UB-AN1 [Blk] | 310 W, 60 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.83 | 41.1 | 9.32 | 33.3 | 46.06 | -0.379 | 0.043 | -0.282 | -0.002 | -0.378 | 1.8379 | 32.1633 | 7.3214 | 30.4437 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS310UB-AN1 [Wht] | 310 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 310 | 284.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.83 | 41.1 | 9.32 | 33.3 | 47.1 | -0.387 | 0.042 | -0.282 | 0 | -0.387 | 1.8781 | 32.1512 | 7.461 | 30.1269 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS310UB-JH2 [Blk] | 310 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 310 | 288.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.73 | 40.2 | 9.1 | 34.1 | 44.96 | -0.359 | 0.04 | -0.28 |  |  | 1.834 | 31.881 | 7.443 | 30.893 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS310UB-JH2 [Wht] | 310 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 310 | 290.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.73 | 40.2 | 9.1 | 34.1 | 43.35 | -0.357 | 0.045 | -0.28 |  |  | 1.8475 | 31.5311 | 7.4604 | 30.773 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS315ME-V01 | 315 W Polycrystalline Module | UL 1703 | 315 | 283.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 9.06 | 45.4 | 8.54 | 36.9 | 46.7 | -0.45 | 0.05 | -0.33 | -0.01 | -0.162 | 1.69 | 35.78 | 6.84 | 33.5 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19196 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS315ND-AN3 | 315 W Polycrystalline Module | UL 1703 | 315 | 284.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.12 | 45.7 | 8.59 | 36.7 | 47.29 | -0.42 | 0.05 | -0.31 | -0.01 | -0.4 | 1.722 | 35.6929 | 6.8881 | 33.9184 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19512 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS315ND-AN4 | 72 Cell Poly c-Si PV Module | UL 1703 | 315 | 288.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 |  | N | 9.12 | 45.7 | 8.59 | 36.7 | 45.57 | -0.397 | 0.045 | -0.307 | 0.007 | -0.404 | 1.704 | 35.933 | 6.946 | 34.364 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS315PD-AN1 | 315 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 315 | 289.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 |  | N | 9.08 | 44.9 | 8.71 | 36.2 | 45.72 | -0.379 | 0.056 | -0.298 | 0.011 | -0.389 | 1.6996 | 34.6349 | 6.8378 | 33.3272 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS315SE-V01 | 315 W Monocrystalline Module | UL 1703 | 315 | 282 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9129 | 72 | 1 | N | 8.99 | 46.1 | 8.41 | 37.5 | 47.7 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.7 | 36.05 | 6.72 | 32.98 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19456 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS315UB-AN1 [Blk] | 315 W, 60 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.86 | 41.5 | 9.35 | 33.7 | 46.06 | -0.379 | 0.043 | -0.282 | -0.002 | -0.378 | 1.8438 | 32.5497 | 7.345 | 30.8094 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS315UB-AN1 [Wht] | 315 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 315 | 288.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.86 | 41.5 | 9.35 | 33.7 | 47.1 | -0.387 | 0.042 | -0.282 | 0 | -0.387 | 1.8841 | 32.5374 | 7.485 | 30.4888 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS315UB-HH2 | 315 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 315 | 293.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.658 | 60 | 2 | N | 9.68 | 40.8 | 9.08 | 34.7 | 45.06 | -0.346 | 0.039 | -0.268 |  |  | 1.8578 | 32.1157 | 7.5388 | 31.1022 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS315UB-JH2 [Blk] | 315 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 315 | 293 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.82 | 40.4 | 9.19 | 34.3 | 44.96 | -0.359 | 0.04 | -0.28 |  |  | 1.8521 | 32.068 | 7.5166 | 31.0742 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS315UB-JH2 [Wht] | 315 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 315 | 294.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.82 | 40.4 | 9.19 | 34.3 | 43.35 | -0.357 | 0.045 | -0.28 |  |  | 1.8657 | 31.7161 | 7.5342 | 30.9535 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS320ME-V01 | 320 W Polycrystalline Module | UL 1703 | 320 | 288.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 9.17 | 45.5 | 8.65 | 37 | 46.7 | -0.45 | 0.05 | -0.33 | -0.01 | -0.162 | 1.71 | 35.88 | 6.93 | 33.6 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19173 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS320ND-AN3 | 320 W Polycrystalline Module | UL 1703 | 320 | 289 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.16 | 46.1 | 8.63 | 37.1 | 47.29 | -0.42 | 0.05 | -0.31 | -0.01 | -0.4 | 1.73 | 36.0819 | 6.9202 | 34.2881 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19507 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS320ND-AN4 | 72 Cell Poly c-Si PV Module | UL 1703 | 320 | 293.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 |  | N | 9.16 | 46.1 | 8.63 | 37.1 | 45.57 | -0.397 | 0.045 | -0.307 | 0.007 | -0.404 | 1.704 | 35.933 | 6.946 | 34.364 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS320PD-AN1 | 320 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 320 | 294.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 |  | N | 9.12 | 45.3 | 8.75 | 36.6 | 45.72 | -0.379 | 0.056 | -0.298 | 0.011 | -0.389 | 1.7074 | 35.0176 | 6.8692 | 33.6955 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS320SE-V01 | 320 W Monocrystalline Module | UL 1703 | 320 | 286.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9129 | 72 | 1 | N | 9.1 | 46.2 | 8.52 | 37.6 | 47.7 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.72 | 36.14 | 6.81 | 33.07 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19425 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS320UB-AN1 [Blk] | 320 W, 60 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 320 | 295.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.9 | 41.9 | 9.39 | 34.1 | 46.06 | -0.379 | 0.043 | -0.282 | -0.002 | -0.378 | 1.8517 | 32.936 | 7.3764 | 31.1751 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS320UB-AN1 [Wht] | 320 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 320 | 293.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 |  | N | 9.9 | 41.9 | 9.39 | 34.1 | 47.1 | -0.387 | 0.042 | -0.282 | 0 | -0.387 | 1.8922 | 32.9236 | 7.5171 | 30.8507 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS320UB-HH2 | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 298.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.658 | 60 | 2 | N | 9.77 | 41 | 9.17 | 34.9 | 45.06 | -0.346 | 0.039 | -0.268 |  |  | 1.8762 | 32.3008 | 7.6136 | 31.2815 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS320UB-JH2 [Blk] | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 320 | 297.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.91 | 40.6 | 9.28 | 34.5 | 44.96 | -0.359 | 0.04 | -0.28 |  |  | 1.8703 | 32.255 | 7.5902 | 31.2554 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS320UB-JH2 [Wht] | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 320 | 299.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 9.91 | 40.6 | 9.28 | 34.5 | 43.35 | -0.357 | 0.045 | -0.28 |  |  | 1.884 | 31.901 | 7.608 | 31.134 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS325ME-V01 | 325 W Polycrystalline Module | UL 1703 | 325 | 292.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 9.29 | 45.6 | 8.77 | 37.1 | 46.7 | -0.45 | 0.05 | -0.33 | -0.01 | -0.162 | 1.73 | 35.98 | 7.03 | 33.69 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19152 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS325ND-AN3 | 325 W Polycrystalline Module | UL 1703 | 325 | 293.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.2 | 46.5 | 8.67 | 37.5 | 47.29 | -0.42 | 0.05 | -0.31 | -0.01 | -0.4 | 1.7381 | 36.4709 | 6.9523 | 34.6578 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19504 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS325ND-AN4 | 72 Cell Poly c-Si PV Module | UL 1703 | 325 | 297.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 |  | N | 9.2 | 46.5 | 8.67 | 37.5 | 45.57 | -0.397 | 0.045 | -0.307 | 0.007 | -0.404 | 1.704 | 35.933 | 6.946 | 34.364 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS325PD-AN1 | 325 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 325 | 299 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 |  | N | 9.16 | 45.7 | 8.79 | 37 | 45.72 | -0.379 | 0.056 | -0.298 | 0.011 | -0.389 | 1.7152 | 35.4003 | 6.9006 | 34.0637 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS325SE-V01 | 325 W Monocrystalline Module | UL 1703 | 325 | 291.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9129 | 72 | 1 | N | 9.21 | 46.3 | 8.63 | 37.7 | 47.7 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.74 | 36.24 | 6.9 | 33.16 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19402 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS325TD-AN3 | 325 W Monocrystalline Module | UL 1703 | 325 | 293.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.2 | 46.5 | 8.67 | 37.5 | 46.1 | -0.44 | 0.04 | -0.31 | -0.02 | -0.43 | 1.7321 | 36.1075 | 6.9665 | 33.8094 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19244 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS325UB-HH2 | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 325 | 303.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.658 | 60 | 2 | N | 9.86 | 41.2 | 9.26 | 35.1 | 45.06 | -0.346 | 0.039 | -0.268 |  |  | 1.8946 | 32.4859 | 7.6883 | 31.4607 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS325UB-JH2 [Blk] | 325 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 325 | 302.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 10 | 40.8 | 9.37 | 34.7 | 44.96 | -0.359 | 0.04 | -0.28 |  |  | 1.8884 | 32.442 | 7.6638 | 31.4366 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS325UB-JH2 [Wht] | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 325 | 304.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 10 | 40.8 | 9.37 | 34.7 | 43.35 | -0.357 | 0.045 | -0.28 |  |  | 1.9023 | 32.0859 | 7.6818 | 31.3145 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS330ND-AN4 | 72 Cell Poly c-Si PV Module | UL 1703 | 330 | 302.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 |  | N | 9.24 | 46.9 | 8.71 | 37.9 | 45.57 | -0.397 | 0.045 | -0.307 | 0.007 | -0.404 | 1.704 | 35.933 | 6.946 | 34.364 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS330PD-AN1 | 330 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 330 | 303.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 |  | N | 9.2 | 46.1 | 8.83 | 37.4 | 45.72 | -0.379 | 0.056 | -0.298 | 0.011 | -0.389 | 1.723 | 35.783 | 6.932 | 34.432 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS330SE-V01 | 330 W Monocrystalline Module | UL 1703 | 330 | 295.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9129 | 72 | 1 | N | 9.32 | 46.4 | 8.74 | 37.8 | 47.7 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.76 | 36.34 | 6.99 | 33.25 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19381 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS330TD-AN3 | 330 W Monocrystalline Module | UL 1703 | 330 | 298.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.24 | 46.9 | 8.71 | 37.9 | 46.1 | -0.44 | 0.04 | -0.31 | -0.02 | -0.43 | 1.7401 | 36.4927 | 6.9986 | 34.17 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19243 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS330TD-AN4 | 72 Cell Mono c-Si PV Module | UL 1703 | 330 | 305.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 |  | N | 9.46 | 45.8 | 8.88 | 37.2 | 44.49 | -0.38 | 0.038 | -0.281 | 0 | -0.38 | 1.833 | 37.908 | 7.357 | 36.072 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS330UB-HH2 | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 330 | 307.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.658 | 60 | 2 | N | 9.95 | 41.4 | 9.35 | 35.3 | 45.06 | -0.346 | 0.039 | -0.268 |  |  | 1.913 | 32.671 | 7.763 | 31.64 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS330UB-JH2 [Wht] | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 330 | 309.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 10.09 | 41 | 9.46 | 34.9 | 43.35 | -0.357 | 0.045 | -0.28 |  |  | 1.9205 | 32.2709 | 7.7556 | 31.495 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS335ND-AN4 | 72 Cell Poly c-Si PV Module | UL 1703 | 335 | 307.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9345 | 72 |  | N | 9.28 | 47.3 | 8.75 | 38.3 | 45.57 | -0.397 | 0.045 | -0.307 | 0.007 | -0.404 | 1.704 | 35.933 | 6.946 | 34.364 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS335PD-AN1 | 335 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 335 | 308.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 |  | N | 9.24 | 46.5 | 8.87 | 37.8 | 45.72 | -0.379 | 0.056 | -0.298 | 0.011 | -0.389 | 1.7308 | 36.1657 | 6.9634 | 34.8003 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS335SE-V01 | 335 W Monocrystalline Module | UL 1703 | 335 | 300.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9129 | 72 | 1 | N | 9.43 | 46.5 | 8.85 | 37.9 | 47.7 | -0.45 | 0.05 | -0.33 | -0.02 | -0.44 | 1.79 | 36.43 | 7.07 | 33.34 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19466 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS335TD-AN3 | 335 W Monocrystalline Module | UL 1703 | 335 | 303.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.5 | 46.2 | 8.92 | 37.6 | 46.1 | -0.44 | 0.04 | -0.31 | -0.02 | -0.43 | 1.782 | 36.2038 | 7.1673 | 33.8996 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19259 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS335TD-AN4 | 72 Cell Mono c-Si PV Module | UL 1703 | 335 | 309.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 |  | N | 9.5 | 46.2 | 8.92 | 37.6 | 44.49 | -0.38 | 0.038 | -0.281 | 0 | -0.38 | 1.833 | 37.908 | 7.357 | 36.072 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS335UB-HH2 | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 335 | 312.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.658 | 60 | 2 | N | 10.04 | 41.6 | 9.44 | 35.5 | 45.06 | -0.346 | 0.039 | -0.268 |  |  | 1.9314 | 32.8561 | 7.8377 | 31.8193 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS335UB-JH2 [Wht] | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 335 | 314.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.611 | 60 | 2 | N | 10.18 | 41.2 | 9.55 | 35.1 | 43.35 | -0.357 | 0.045 | -0.28 |  |  | 1.9388 | 32.4558 | 7.8294 | 31.6755 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS340PD-AN1 | 340 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 340 | 313.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 |  | N | 9.28 | 46.9 | 8.91 | 38.2 | 45.72 | -0.379 | 0.056 | -0.298 | 0.011 | -0.389 | 1.7386 | 36.5484 | 6.9948 | 35.1685 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS340TD-AN3 | 340 W Monocrystalline Module | UL 1703 | 340 | 307.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.54 | 46.6 | 8.95 | 38 | 46.1 | -0.44 | 0.04 | -0.31 | -0.02 | -0.43 | 1.788 | 36.5889 | 7.1914 | 34.2602 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19242 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS340TD-AN4 | 72 Cell Mono c-Si PV Module | UL 1703 | 340 | 314.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 |  | N | 9.54 | 46.6 | 8.95 | 38 | 44.49 | -0.38 | 0.038 | -0.281 | 0 | -0.38 | 1.833 | 37.908 | 7.357 | 36.072 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS340UD-AN1 [Wht] | 340 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 340 | 310.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.934 | 72 |  | N | 9.5 | 46.1 | 8.88 | 38.3 | 47.3 | -0.385 | 0.041 | -0.281 | -0.006 | -0.38 | 1.8114 | 37.4346 | 7.2867 | 35.0577 | [6 empty] | 2017-11-15 | 2018-07-02
Hansol Technics Co., Ltd. | HS345PD-AN1 | 345 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 345 | 317.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 72 |  | N | 9.31 | 47.3 | 8.94 | 38.6 | 45.72 | -0.379 | 0.056 | -0.298 | 0.011 | -0.389 | 1.7445 | 36.9311 | 7.0184 | 35.5368 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS345TD-AN3 | 345 W Monocrystalline Module | UL 1703 | 345 | 312.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.58 | 47 | 8.99 | 38.4 | 46.1 | -0.44 | 0.04 | -0.31 | -0.02 | -0.43 | 1.796 | 36.9741 | 7.2236 | 34.6208 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19248 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS345TD-AN4 | 72 Cell Mono c-Si PV Module | UL 1703 | 345 | 319.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 |  | N | 9.58 | 47 | 8.99 | 38.4 | 44.49 | -0.38 | 0.038 | -0.281 | 0 | -0.38 | 1.833 | 37.908 | 7.357 | 36.072 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS345UD-AN1 [Blk] | 345 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 345 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.55 | 46.4 | 8.94 | 38.6 | 45.73 | -0.376 | 0.044 | -0.281 | 0.006 | -0.382 | 1.8038 | 37.1649 | 7.2161 | 35.1046 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS345UD-AN1 [Wht] | 345 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 345 | 315.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.55 | 46.4 | 8.94 | 38.6 | 47.3 | -0.385 | 0.041 | -0.281 | -0.006 | -0.38 | 1.844 | 38.412 | 7.418 | 35.973 | [6 empty] | 2017-11-15 | 2018-07-02
Hansol Technics Co., Ltd. | HS350TD-AN3 | 350 W Monocrystalline Module | UL 1703 | 350 | 317.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.62 | 47.4 | 9.03 | 38.8 | 46.1 | -0.44 | 0.04 | -0.31 | -0.02 | -0.43 | 1.804 | 37.3592 | 7.2557 | 34.9815 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19256 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS350TD-AN4 | 72 Cell Mono c-Si PV Module | UL 1703 | 350 | 324.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 |  | N | 9.62 | 47.4 | 9.03 | 38.8 | 44.49 | -0.38 | 0.038 | -0.281 | 0 | -0.38 | 1.833 | 37.908 | 7.357 | 36.072 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS350UD-AN1 [Blk] | 350 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 350 | 322.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.6 | 46.7 | 9 | 38.9 | 45.73 | -0.376 | 0.044 | -0.281 | 0.006 | -0.382 | 1.8159 | 37.4537 | 7.2645 | 35.3774 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS350UD-AN1 [Wht] | 350 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 350 | 320 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.6 | 46.7 | 9 | 38.9 | 47.3 | -0.385 | 0.041 | -0.281 | -0.006 | -0.38 | 1.844 | 38.412 | 7.418 | 35.973 | [6 empty] | 2017-11-15 | 2018-07-02
Hansol Technics Co., Ltd. | HS355TD-AN3 | 355 W Monocrystalline Module | UL 1703 | 355 | 321.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.65 | 47.8 | 9.06 | 39.2 | 46.1 | -0.44 | 0.04 | -0.31 | -0.02 | -0.43 | 1.81 | 37.7444 | 7.2798 | 35.3421 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19244 |  | 2018-07-02
Hansol Technics Co., Ltd. | HS355TD-AN4 | 72 Cell Mono c-Si PV Module | UL 1703 | 355 | 328.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 |  | N | 9.65 | 47.8 | 9.06 | 39.2 | 44.49 | -0.38 | 0.038 | -0.281 | 0 | -0.38 | 1.833 | 37.908 | 7.357 | 36.072 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS355UD-AN1 [Blk] | 355 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 355 | 327.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.64 | 47 | 9.04 | 39.3 | 45.73 | -0.376 | 0.044 | -0.281 | 0.006 | -0.382 | 1.8239 | 37.8389 | 7.2968 | 35.7412 | [6 empty] | 2018-07-02 | 2018-08-01
Hansol Technics Co., Ltd. | HS355UD-AN1 [Wht] | 355 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 329 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.64 | 47 | 9.04 | 39.3 | 44.32 | -0.382 | 0.046 | -0.283 | 0.005 | -0.386 | 1.8446 | 36.8207 | 7.3596 | 34.9411 | [6 empty] | 2017-11-15 | 2018-07-02
Hansol Technics Co., Ltd. | HS360TD-AN4 | 72 Cell Mono c-Si PV Module | UL 1703 | 360 | 333.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9345 | 72 |  | N | 9.69 | 48.2 | 9.1 | 39.6 | 44.49 | -0.38 | 0.038 | -0.281 | 0 | -0.38 | 1.833 | 37.908 | 7.357 | 36.072 | [6 empty] | 2017-09-01
Hansol Technics Co., Ltd. | HS360UD-AN1 [Blk] | 360 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 360 | 332.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.67 | 47.4 | 9.07 | 39.7 | 45.73 | -0.376 | 0.044 | -0.281 | 0.006 | -0.382 | 1.83 | 38.224 | 7.321 | 36.105 | [6 empty] | 2018-07-02 | 2018-08-01
Hansol Technics Co., Ltd. | HS360UD-AN1 [Wht] | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 333.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.67 | 47.4 | 9.07 | 39.7 | 44.32 | -0.382 | 0.046 | -0.283 | 0.005 | -0.386 | 1.8507 | 37.1955 | 7.384 | 35.2967 | [6 empty] | 2017-11-15 | 2018-07-02
Hansol Technics Co., Ltd. | HS365UD-AH2 | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 339.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.95 | 47.1 | 9.49 | 38.5 | 44.59 | -0.363 | 0.047 | -0.27 |  |  | 1.8901 | 37.5118 | 7.593 | 35.868 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS365UD-AN1 [Blk] | 365 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 365 | 337 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.71 | 47.8 | 9.11 | 40.1 | 45.73 | -0.376 | 0.044 | -0.281 | 0.006 | -0.382 | 1.8381 | 38.6091 | 7.3533 | 36.4688 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS365UD-AN1 [Wht] | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 338.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.71 | 47.8 | 9.11 | 40.1 | 44.32 | -0.382 | 0.046 | -0.283 | 0.005 | -0.386 | 1.8589 | 37.5702 | 7.4166 | 35.6524 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS370UD-AH2 | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 344.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.98 | 47.5 | 9.52 | 38.9 | 44.59 | -0.363 | 0.047 | -0.27 |  |  | 1.8961 | 37.9015 | 7.617 | 36.2407 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS370UD-AN1 [Blk] | 370 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 370 | 341.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.74 | 48.2 | 9.14 | 40.5 | 45.73 | -0.376 | 0.044 | -0.281 | 0.006 | -0.382 | 1.8441 | 38.9943 | 7.3775 | 36.8326 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS370UD-AN1 [Wht] | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 343.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.74 | 48.2 | 9.14 | 40.5 | 44.32 | -0.382 | 0.046 | -0.283 | 0.005 | -0.386 | 1.865 | 37.945 | 7.441 | 36.008 | [6 empty] | 2018-07-02
Hansol Technics Co., Ltd. | HS370UD-JH2 | 370 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 346.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.929 | 72 | 2 | N | 9.83 | 47.5 | 9.28 | 39.9 | 43.36 | -0.353 | 0.048 | -0.278 |  |  | 1.8433 | 37.642 | 7.468 | 36.7681 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS375UD-AH2 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 349 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.01 | 47.9 | 9.55 | 39.3 | 44.59 | -0.363 | 0.047 | -0.27 |  |  | 1.902 | 38.2913 | 7.641 | 36.6133 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS375UD-JH2 | 375 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 351.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.929 | 72 | 2 | N | 9.91 | 47.7 | 9.36 | 40.1 | 43.36 | -0.353 | 0.048 | -0.278 |  |  | 1.8592 | 37.8306 | 7.5323 | 36.9524 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS380UD-AH2 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 353.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.04 | 48.3 | 9.58 | 39.7 | 44.59 | -0.363 | 0.047 | -0.27 |  |  | 1.908 | 38.681 | 7.665 | 36.986 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS380UD-HH2 | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 352.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.978 | 72 | 2 | N | 9.85 | 48.3 | 9.33 | 40.7 | 46.73 | -0.341 | 0.042 | -0.268 |  |  | 1.8718 | 38.7034 | 7.5995 | 37.2183 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS380UD-JH2 | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 356.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.929 | 72 | 2 | N | 9.98 | 47.9 | 9.43 | 40.3 | 43.36 | -0.353 | 0.048 | -0.278 |  |  | 1.8731 | 38.0193 | 7.5887 | 37.1367 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS380UE-AN1 | 380W 78 Cell Mono c-Si PV Module, White Backsheet, 1000V or 1500V max system Vdc | UL 1703 | 380 | 350.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 |  | N | 10.36 | 49.7 | 9.48 | 40.1 | 45.8 | -0.379 | 0.042 | -0.281 | 0.008 | -0.386 | 1.8377 | 39.8625 | 7.3648 | 37.6469 | [6 empty] | 2018-10-01
Hansol Technics Co., Ltd. | HS385UD-AH2 | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 358.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.07 | 48.7 | 9.61 | 40.1 | 44.59 | -0.363 | 0.047 | -0.27 |  |  | 1.914 | 39.0707 | 7.689 | 37.3587 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS385UD-HH2 | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 357.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.978 | 72 | 2 | N | 9.93 | 48.5 | 9.41 | 40.9 | 46.73 | -0.341 | 0.042 | -0.268 |  |  | 1.8879 | 38.8936 | 7.6647 | 37.4012 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS385UD-JH2 | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 360.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.929 | 72 | 2 | N | 10.05 | 48.1 | 9.5 | 40.5 | 43.36 | -0.353 | 0.048 | -0.278 |  |  | 1.887 | 38.208 | 7.645 | 37.321 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS385UE-AN1 | 385W 78 Cell Mono c-Si PV Module, White Backsheet, 1000V or 1500V max system Vdc | UL 1703 | 385 | 354.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 |  | N | 10.39 | 50.1 | 9.51 | 40.5 | 45.8 | -0.379 | 0.042 | -0.281 | 0.008 | -0.386 | 1.8436 | 40.2601 | 7.3881 | 38.0224 | [6 empty] | 2018-10-01
Hansol Technics Co., Ltd. | HS390UD-AH2 | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 363.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.1 | 49.1 | 9.64 | 40.5 | 44.59 | -0.363 | 0.047 | -0.27 |  |  | 1.9199 | 39.4605 | 7.713 | 37.7313 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS390UD-HH2 | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.978 | 72 | 2 | N | 10.01 | 48.7 | 9.49 | 41.1 | 46.73 | -0.341 | 0.042 | -0.268 |  |  | 1.9039 | 39.0838 | 7.7298 | 37.5841 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS390UD-JH2 | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 365.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.929 | 72 | 2 | N | 10.13 | 48.3 | 9.58 | 40.7 | 43.36 | -0.353 | 0.048 | -0.278 |  |  | 1.9029 | 38.3967 | 7.7094 | 37.5053 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS390UE-AN1 | 390W 78 Cell Mono c-Si PV Module, White Backsheet, 1000V or 1500V max system Vdc | UL 1703 | 390 | 359.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 |  | N | 10.42 | 50.5 | 9.54 | 40.9 | 45.8 | -0.379 | 0.042 | -0.281 | 0.008 | -0.386 | 1.8494 | 40.6577 | 7.4114 | 38.3979 | [6 empty] | 2018-10-01
Hansol Technics Co., Ltd. | HS395UD-AH2 | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 368.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.13 | 49.5 | 9.67 | 40.9 | 44.59 | -0.363 | 0.047 | -0.27 |  |  | 1.9259 | 39.8502 | 7.737 | 38.104 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS395UD-HH2 | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.978 | 72 | 2 | N | 10.09 | 48.9 | 9.57 | 41.3 | 46.73 | -0.341 | 0.042 | -0.268 |  |  | 1.92 | 39.274 | 7.795 | 37.767 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS395UD-JH2 | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 370.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.929 | 72 | 2 | N | 10.21 | 48.5 | 9.66 | 40.9 | 43.36 | -0.353 | 0.048 | -0.278 |  |  | 1.9188 | 38.5854 | 7.7738 | 37.6896 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS395UE-AN1 | 395W 78 Cell Mono c-Si PV Module, White Backsheet, 1000V or 1500V max system Vdc | UL 1703 | 395 | 364.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 |  | N | 10.45 | 50.9 | 9.57 | 41.3 | 45.8 | -0.379 | 0.042 | -0.281 | 0.008 | -0.386 | 1.8552 | 41.0554 | 7.4347 | 38.7735 | [6 empty] | 2018-10-01
Hansol Technics Co., Ltd. | HS395UE-JH2 | 395 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 395 | 371 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 | 2 | N | 9.48 | 52 | 8.8 | 44.9 | 42.54 | -0.352 | 0.043 | -0.278 |  |  | 1.8249 | 40.7922 | 7.3846 | 40.0347 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS400UD-HH2 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 371.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.978 | 72 | 2 | N | 10.16 | 49.1 | 9.64 | 41.5 | 46.73 | -0.341 | 0.042 | -0.268 |  |  | 1.934 | 39.4642 | 7.852 | 37.9499 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS400UD-JH2 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 375.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.929 | 72 | 2 | N | 10.29 | 48.7 | 9.74 | 41.1 | 43.36 | -0.353 | 0.048 | -0.278 |  |  | 1.9347 | 38.774 | 7.8381 | 37.8739 | [6 empty] | 2019-07-01
Hansol Technics Co., Ltd. | HS400UE-AN1 | 400W 78 Cell Mono c-Si PV Module, White Backsheet, 1000V or 1500V max system Vdc | UL 1703 | 400 | 369.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 |  | N | 10.48 | 51.3 | 9.6 | 41.7 | 45.8 | -0.379 | 0.042 | -0.281 | 0.008 | -0.386 | 1.861 | 41.453 | 7.458 | 39.149 | [6 empty] | 2018-10-01
Hansol Technics Co., Ltd. | HS400UE-JH2 | 400 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 400 | 375.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 | 2 | N | 9.55 | 52.2 | 8.87 | 45.1 | 42.54 | -0.352 | 0.043 | -0.278 |  |  | 1.8394 | 40.9739 | 7.4434 | 40.213 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS405UD-HH2 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 376.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.978 | 72 | 2 | N | 10.24 | 49.3 | 9.72 | 41.7 | 46.73 | -0.341 | 0.042 | -0.268 |  |  | 1.9501 | 39.6544 | 7.9172 | 38.1328 | [6 empty] | 2020-10-12
Hansol Technics Co., Ltd. | HS405UE-AN1 | 405W 78 Cell Mono c-Si PV Module, White Backsheet, 1000V or 1500V max system Vdc | UL 1703 | 405 | 373.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 |  | N | 10.51 | 51.7 | 9.63 | 42.1 | 45.8 | -0.379 | 0.042 | -0.281 | 0.008 | -0.386 | 1.8668 | 41.8506 | 7.4813 | 39.5245 | [6 empty] | 2018-10-01
Hansol Technics Co., Ltd. | HS405UE-JH2 | 405 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 405 | 380.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 | 2 | N | 9.63 | 52.4 | 8.95 | 45.3 | 42.54 | -0.352 | 0.043 | -0.278 |  |  | 1.856 | 41.1556 | 7.5105 | 40.3913 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS410UE-AN1 | 410W 78 Cell Mono c-Si PV Module, White Backsheet, 1000V or 1500V max system Vdc | UL 1703 | 410 | 378.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 |  | N | 10.54 | 52.1 | 9.64 | 42.5 | 45.8 | -0.379 | 0.042 | -0.281 | 0.008 | -0.386 | 1.8688 | 42.2483 | 7.4891 | 39.9001 | [6 empty] | 2018-10-01
Hansol Technics Co., Ltd. | HS410UE-JH2 | 410 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 410 | 385.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 | 2 | N | 9.7 | 52.6 | 9.02 | 45.5 | 42.54 | -0.352 | 0.043 | -0.278 |  |  | 1.8705 | 41.3373 | 7.5693 | 40.5697 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS415UE-AN1 | 415W 78 Cell Mono c-Si PV Module, White Backsheet, 1000V or 1500V max system Vdc | UL 1703 | 415 | 383.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 |  | N | 10.58 | 52.5 | 9.68 | 42.9 | 45.8 | -0.379 | 0.042 | -0.281 | 0.008 | -0.386 | 1.8765 | 42.6459 | 7.5202 | 40.2756 | [6 empty] | 2018-10-01
Hansol Technics Co., Ltd. | HS415UE-JH2 | 415 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 415 | 390.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 | 2 | N | 9.77 | 52.8 | 9.09 | 45.7 | 42.54 | -0.352 | 0.043 | -0.278 |  |  | 1.885 | 41.519 | 7.628 | 40.748 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS420UE-AN1 | 420W 78 Cell Mono c-Si PV Module, White Backsheet, 1000V or 1500V max system Vdc | UL 1703 | 420 | 388.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 |  | N | 10.61 | 52.9 | 9.71 | 43.3 | 45.8 | -0.379 | 0.042 | -0.281 | 0.008 | -0.386 | 1.8823 | 43.0435 | 7.5435 | 40.6511 | [6 empty] | 2018-10-01
Hansol Technics Co., Ltd. | HS420UE-JH2 | 420 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 420 | 395 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 | 2 | N | 9.84 | 53 | 9.16 | 45.9 | 42.54 | -0.352 | 0.043 | -0.278 |  |  | 1.8995 | 41.7007 | 7.6867 | 40.9263 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS425UE-JH2 | 425 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 425 | 399.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 | 2 | N | 9.9 | 53.2 | 9.22 | 46.1 | 42.54 | -0.352 | 0.043 | -0.278 |  |  | 1.912 | 41.8824 | 7.7371 | 41.1047 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS430UE-JH2 | 430 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 430 | 404.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 | 2 | N | 9.97 | 53.4 | 9.29 | 46.3 | 42.54 | -0.352 | 0.043 | -0.278 |  |  | 1.9265 | 42.0641 | 7.7958 | 41.283 | [6 empty] | 2019-08-01
Hansol Technics Co., Ltd. | HS435UE-JH2 | 435 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 435 | 409.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 78 | 2 | N | 10.04 | 53.6 | 9.36 | 46.5 | 42.54 | -0.352 | 0.043 | -0.278 |  |  | 1.941 | 42.2458 | 7.8546 | 41.4613 | [6 empty] | 2019-08-01
Hanwha Q CELLS | Q.PRO-G3 240 | 240 W Polycrystalline Module | UL 1703 | 240 | 217.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 8.76 | 37.35 | 8.2 | 29.57 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.67 | 29.07 | 6.6 | 26.95 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.20228
Hanwha Q CELLS | Q.PRO BFR - G3 245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 8.85 | 37.56 | 8.32 | 29.73 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.67 | 29.07 | 6.67 | 25.89 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.19815
Hanwha Q CELLS | Q.PRO-G3 245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 8.85 | 37.56 | 8.32 | 29.73 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.67 | 29.07 | 6.67 | 25.89 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.19815
Hanwha Q CELLS | Q.PRO BFR - G3 250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 8.94 | 37.78 | 8.45 | 29.89 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.7 | 29.22 | 6.77 | 26.03 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.1987
Hanwha Q CELLS | Q.PRO-G3 250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 8.94 | 37.78 | 8.45 | 29.89 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.7 | 29.22 | 6.77 | 26.03 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.1987
Hanwha Q CELLS | Q.PRO BFR - G3 255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 9.03 | 37.99 | 8.57 | 30.04 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.72 | 29.37 | 6.87 | 26.16 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.1981
Hanwha Q CELLS | Q.PRO BFR G4 255 | 255 W Polycrystalline Module, Black frame | UL 1703 | 255 | 230.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5273 | 60 | 1 | N | 9.07 | 37.54 | 8.45 | 30.18 | 47.2 | -0.419 | 0.05 | -0.302 | -0.017 | -0.404 | 1.7 | 30.58 | 6.77 | 28.29 | Rack | Flat Plate | 0.951 | 1.606 | 1 | 0.20387
Hanwha Q CELLS | Q.PRO BFR-G4.1 255 | 255 W Polycrystalline Module | UL 1703 | 255 | 232.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.99 | 37.47 | 8.37 | 30.45 | 47 | -0.39 | 0.05 | -0.29 | -0.01 | -0.38 | 1.65 | 29.36 | 6.7 | 27.81 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.18998
Hanwha Q CELLS | Q.PRO G4.1/SC 255 | 255 W Polycrystalline Module | UL 1703 | 255 | 232.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.99 | 37.47 | 8.37 | 30.45 | 46.9 | -0.39 | 0.05 | -0.29 | -0.01 | -0.38 | 1.65 | 29.36 | 6.7 | 27.81 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.18998
Hanwha Q CELLS | Q.PRO-G3 255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 9.03 | 37.99 | 8.57 | 30.04 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.72 | 29.37 | 6.87 | 26.16 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.1981
Hanwha Q CELLS | Q.PRO-G4 255 | 255 W Polycrystalline Module | UL 1703 | 255 | 230.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5273 | 60 | 1 | N | 9.07 | 37.54 | 8.45 | 30.18 | 47.2 | -0.419 | 0.05 | -0.302 | -0.017 | -0.404 | 1.7 | 30.58 | 6.77 | 28.29 | Rack | Flat Plate | 0.951 | 1.606 | 1 | 0.20387
Hanwha Q CELLS | Q.PRO-G4/SC 255 | 255 W Polycrystalline Module | UL 1703 | 255 | 232 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5986 | 60 | 1 | N | 9.07 | 37.54 | 8.45 | 30.18 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.7 | 29.51 | 6.77 | 26.28 | Rack | Flat Plate | 0.973 | 1.643 | 1 | 0.19673
Hanwha Q CELLS | Q.PRO BFR - G3 260 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 9.12 | 38.21 | 8.7 | 30.18 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.75 | 29.51 | 6.97 | 26.28 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.19863
Hanwha Q CELLS | Q.PRO BFR G4 260 | 260 W Polycrystalline Module, Black frame | UL 1703 | 260 | 235.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5273 | 60 | 1 | N | 9.15 | 37.77 | 8.53 | 30.46 | 47.2 | -0.419 | 0.05 | -0.302 | -0.017 | -0.404 | 1.72 | 30.86 | 6.83 | 28.55 | Rack | Flat Plate | 0.951 | 1.606 | 1 | 0.20415
Hanwha Q CELLS | Q.PRO BFR-G4.1 260 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.07 | 37.7 | 8.46 | 30.74 | 47 | -0.39 | 0.05 | -0.29 | -0.01 | -0.38 | 1.67 | 29.64 | 6.77 | 28.07 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19038
Hanwha Q CELLS | Q.PRO BFR-G4.3 260 | 260 W Polycrystalline Module | UL 1703 | 260 | 233.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.85 | 38.1 | 8.48 | 30.7 | 47.94 | -0.42 | 0.05 | -0.31 | -0.01 | -0.41 | 6.1185 | 29.649 | 24.5815 | 27.9173 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.69772
Hanwha Q CELLS | Q.PRO G4.1/SC 260 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.07 | 37.7 | 8.46 | 30.74 | 46.9 | -0.39 | 0.05 | -0.29 | -0.01 | -0.38 | 1.67 | 29.64 | 6.77 | 28.07 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19038
Hanwha Q CELLS | Q.PRO-G3 260 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 9.12 | 38.21 | 8.7 | 30.18 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.75 | 29.51 | 6.97 | 26.28 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.19863
Hanwha Q CELLS | Q.PRO-G4 260 | 260 W Polycrystalline Module | UL 1703 | 260 | 235.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5273 | 60 | 1 | N | 9.15 | 37.77 | 8.53 | 30.46 | 47.2 | -0.419 | 0.05 | -0.302 | -0.017 | -0.404 | 1.72 | 30.86 | 6.83 | 28.55 | Rack | Flat Plate | 0.951 | 1.606 | 1 | 0.20415
Hanwha Q CELLS | Q.PRO-G4/SC 260 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5986 | 60 | 1 | N | 9.15 | 37.77 | 8.53 | 30.46 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.71 | 29.78 | 6.84 | 26.53 | Rack | Flat Plate | 0.973 | 1.643 | 1 | 0.19586
Hanwha Q CELLS | Q.PEAK BLK-G3 265 | 265 W Monocrystalline Module | UL 1703 | 265 | 237.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.08 | 38.22 | 8.6 | 31.1 | 49.1 | -0.421 | 0.097 | -0.342 | 0.063 | -0.474 | 1.74 | 30.12 | 7.03 | 27.94 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.19777
Hanwha Q CELLS | Q.PEAK-G3 265 | 265 W Monocrystalline Module | UL 1703 | 265 | 237.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.15 | 37.91 | 8.65 | 30.94 | 46.8 | -0.454 | 0.099 | -0.349 | 0.039 | -0.487 | 1.76 | 36 | 7 | 28.43 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.23909
Hanwha Q CELLS | Q.PRO BFR - G3 265 | 265 W Polycrystalline Module | UL 1703 | 265 | 241.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 9.21 | 38.43 | 8.82 | 30.32 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.77 | 29.64 | 7.07 | 26.4 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.19797
Hanwha Q CELLS | Q.PRO BFR G4 265 | 265 W Polycrystalline Module, Black frame | UL 1703 | 265 | 240.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5273 | 60 | 1 | N | 9.23 | 38.01 | 8.62 | 30.75 | 47.2 | -0.419 | 0.05 | -0.302 | -0.017 | -0.404 | 1.74 | 31.15 | 6.9 | 28.82 | Rack | Flat Plate | 0.951 | 1.606 | 1 | 0.20453
Hanwha Q CELLS | Q.PRO BFR-G4.1 265 | 265 W Polycrystalline Module | UL 1703 | 265 | 241.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.15 | 37.93 | 8.54 | 31.03 | 47 | -0.39 | 0.05 | -0.29 | -0.01 | -0.38 | 1.69 | 29.92 | 6.83 | 28.34 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19081
Hanwha Q CELLS | Q.PRO BFR-G4.3 265 | 265 W Polycrystalline Module | UL 1703 | 265 | 238.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.98 | 38.2 | 8.61 | 30.8 | 47.94 | -0.42 | 0.05 | -0.31 | -0.01 | -0.41 | 6.1385 | 29.7455 | 24.6615 | 28.0082 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.68903
Hanwha Q CELLS | Q.PRO G4.1/SC 265 | 265 W Polycrystalline Module | UL 1703 | 265 | 241.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.15 | 37.93 | 8.54 | 31.03 | 46.9 | -0.39 | 0.05 | -0.29 | -0.01 | -0.38 | 1.69 | 29.92 | 6.83 | 28.34 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19081
Hanwha Q CELLS | Q.PRO-G3 265 | 265 W Polycrystalline Module | UL 1703 | 265 | 241.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.653 | 60 | 1 | N | 9.21 | 38.43 | 8.82 | 30.32 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.77 | 29.64 | 7.07 | 26.4 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.19797
Hanwha Q CELLS | Q.PRO-G4 265 | 265 W Polycrystalline Module | UL 1703 | 265 | 240.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5273 | 60 | 1 | N | 9.23 | 38.01 | 8.62 | 30.75 | 47.2 | -0.419 | 0.05 | -0.302 | -0.017 | -0.404 | 1.74 | 31.15 | 6.9 | 28.82 | Rack | Flat Plate | 0.951 | 1.606 | 1 | 0.20453
Hanwha Q CELLS | Q.PRO-G4/SC 265 | 265 W Polycrystalline Module | UL 1703 | 265 | 241.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5986 | 60 | 1 | N | 9.23 | 38.01 | 8.62 | 30.75 | 44.8 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.73 | 30.06 | 6.91 | 26.78 | Rack | Flat Plate | 0.973 | 1.643 | 1 | 0.19624
Hanwha Q CELLS | Q.PEAK BLK-G3 270 | 270 W Monocrystalline Module | UL 1703 | 270 | 241.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.14 | 38.51 | 8.67 | 31.42 | 49.1 | -0.421 | 0.097 | -0.342 | 0.063 | -0.474 | 1.76 | 30.33 | 7.11 | 28.14 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.19771
Hanwha Q CELLS | Q.PEAK-G3 270 | 270 W Monocrystalline Module | UL 1703 | 270 | 242.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.25 | 38.21 | 8.75 | 31.16 | 46.8 | -0.454 | 0.099 | -0.349 | 0.039 | -0.487 | 1.78 | 36.26 | 7.08 | 28.63 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.23905
Hanwha Q CELLS | Q.PLUS BFR G3.1 270 | 270 W Polycrystalline Module | UL 1703 | 270 | 247.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.29 | 38.46 | 8.7 | 31.04 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.7322 | 30.2363 | 6.9678 | 28.6093 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19398
Hanwha Q CELLS | Q.PLUS BFR G4.1 270 | 270 W Polycrystalline Module | UL 1703 | 270 | 247.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.29 | 38.46 | 8.7 | 31.04 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.7322 | 30.2363 | 6.9678 | 28.6093 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19398
Hanwha Q CELLS | Q.PLUS G4 270 | 270 W Polycrystalline Module, Black Frame | UL 1703 | 270 | 246.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.665 | 60 | 1 | N | 9.43 | 38.65 | 8.84 | 30.53 | 46.5 | -0.4 | 0.04 | -0.29 | -0.015 | -0.39 | 1.83 | 30.09 | 7.08 | 28.65 | Rack | Flat Plate | 1 | 1.665 | 1 | 0.20394
Hanwha Q CELLS | Q.PLUS-G3 270 | 270 W Polycrystalline Module | UL 1703 | 270 | 246.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5344 | 60 | 1 | N | 9.48 | 38.86 | 8.85 | 30.78 | 46.6 | -0.407 | 0.006 | -0.319 | 0.063 | -0.463 | 1.79 | 30.16 | 7.08 | 28.17 | Rack | Flat Plate | 0.959 | 1.6 | 1 | 0.19995
Hanwha Q CELLS | Q.PLUS-G4.1/SC 270 | 270 W Polycrystalline Module, Black Frame | UL 1703 | 270 | 247 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.3 | 38.53 | 8.72 | 30.98 | 45.83 | -0.4 | 0.04 | -0.28 | -0.02 | -0.38 | 1.7341 | 30.2334 | 6.9659 | 28.6102 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19418
Hanwha Q CELLS | Q.PEAK BLK-G3 275 | 275 W Monocrystalline Module | UL 1703 | 275 | 246.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.21 | 38.8 | 8.74 | 31.73 | 49.1 | -0.421 | 0.097 | -0.342 | 0.063 | -0.474 | 1.78 | 30.54 | 7.19 | 28.33 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.19768
Hanwha Q CELLS | Q.PEAK-G3 275 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.35 | 38.51 | 8.85 | 31.37 | 46.8 | -0.454 | 0.099 | -0.349 | 0.039 | -0.487 | 1.8 | 36.5 | 7.17 | 28.82 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.23891
Hanwha Q CELLS | Q.PLUS BFR G3.1 275 | 275 W Polycrystalline Module | UL 1703 | 275 | 252 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.35 | 38.72 | 8.77 | 31.36 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.7462 | 30.548 | 7.0238 | 28.9043 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19397
Hanwha Q CELLS | Q.PLUS BFR G4.1 275 | 275 W Polycrystalline Module | UL 1703 | 275 | 252 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.35 | 38.72 | 8.77 | 31.36 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.7462 | 30.548 | 7.0238 | 28.9043 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19397
Hanwha Q CELLS | Q.PLUS G4 275 | 275 W Polycrystalline Module, Black Frame | UL 1703 | 275 | 250.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.665 | 60 | 1 | N | 9.49 | 38.9 | 8.91 | 30.85 | 46.5 | -0.4 | 0.04 | -0.29 | -0.015 | -0.39 | 1.85 | 30.41 | 7.14 | 28.95 | Rack | Flat Plate | 1 | 1.665 | 1 | 0.20458
Hanwha Q CELLS | Q.PLUS-G3 275 | 275 W Polycrystalline Module | UL 1703 | 275 | 250.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5344 | 60 | 1 | N | 9.55 | 39.14 | 8.93 | 31.08 | 46.6 | -0.407 | 0.006 | -0.319 | 0.063 | -0.463 | 1.81 | 30.45 | 7.14 | 28.45 | Rack | Flat Plate | 0.959 | 1.6 | 1 | 0.20042
Hanwha Q CELLS | Q.PLUS-G4.1/SC 275 | 275 W Polycrystalline Module, Black Frame | UL 1703 | 275 | 251.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.36 | 38.78 | 8.79 | 31.3 | 45.83 | -0.4 | 0.04 | -0.28 | -0.02 | -0.38 | 1.748 | 30.5451 | 7.022 | 28.9051 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19416
Hanwha Q CELLS | B.LINE PEAK BLK-G4.1 280 | 280 W Monocrystalline Module | UL 1703 | 280 | 256.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.49 | 38.62 | 8.89 | 31.5 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.7896 | 30.7905 | 7.1274 | 29.0518 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.1968
Hanwha Q CELLS | Q.PEAK-G3 280 | 280 W Monocrystalline Module | UL 1703 | 280 | 251.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.45 | 38.81 | 8.95 | 31.58 | 46.8 | -0.454 | 0.099 | -0.349 | 0.039 | -0.487 | 1.82 | 36.75 | 7.25 | 29.01 | Rack | Flat Plate | 0.994 | 1.663 | 1 | 0.23888
Hanwha Q CELLS | Q.PLUS BFR G3.1 280 | 280 W Polycrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.41 | 38.97 | 8.84 | 31.67 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.7601 | 30.85 | 7.0799 | 29.19 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19392
Hanwha Q CELLS | Q.PLUS BFR G4.1 280 | 280 W Polycrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.41 | 38.97 | 8.84 | 31.67 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.7601 | 30.85 | 7.0799 | 29.19 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19392
Hanwha Q CELLS | Q.PLUS BFR-G4.1/TAA 280 | 280 W Polycrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.41 | 38.97 | 8.84 | 31.67 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.7601 | 30.85 | 7.0799 | 29.19 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19392
Hanwha Q CELLS | Q.PLUS G4 280 | 280 W Polycrystalline Module, Black Frame | UL 1703 | 280 | 255.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.665 | 60 | 1 | N | 9.55 | 39.16 | 8.99 | 31.16 | 46.5 | -0.4 | 0.04 | -0.29 | -0.015 | -0.39 | 1.86 | 30.71 | 7.2 | 29.24 | Rack | Flat Plate | 1 | 1.665 | 1 | 0.204
Hanwha Q CELLS | Q.PLUS-G3 280 | 280 W Polycrystalline Module | UL 1703 | 280 | 255.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5344 | 60 | 1 | N | 9.62 | 39.41 | 9 | 31.38 | 46.6 | -0.407 | 0.006 | -0.319 | 0.063 | -0.463 | 1.82 | 30.74 | 7.2 | 28.72 | Rack | Flat Plate | 0.959 | 1.6 | 1 | 0.19981
Hanwha Q CELLS | Q.PLUS-G4.1/SC 280 | 280 W Polycrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.41 | 38.97 | 8.84 | 31.67 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.7601 | 30.85 | 7.0799 | 29.19 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19392
Hanwha Q CELLS | Q.PLUS-G4.3 280 | 280 W, 60 cell polycrystalline module, white backsheet, silver frame, 1500V or 1000V max system Vdc | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.41 | 38.97 | 8.84 | 31.67 | 45.39 | -0.4 | 0.04 | -0.29 |  |  | 1.78 | 30.85 | 7.16 | 29.19 | [6 empty] | 2019-12-02
Hanwha Q CELLS | Q.PLUS BFR-G4.1 282 | 282 W, 60 cell polycrystalline module, white backsheet, black frame, 1000V or 1500V max system Vdc | UL 61730 | 282 | 258.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.5 | 39.1 | 9 | 31.4 | 45.39 | -0.4 | 0.04 | -0.29 |  |  | 1.78 | 30.85 | 7.16 | 29.19 | [6 empty] | 2020-08-21
Hanwha Q CELLS | B.LINE PEAK BLK-G4.1 285 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.56 | 38.91 | 8.98 | 31.73 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.8078 | 31.0154 | 7.1996 | 29.2639 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19673
Hanwha Q CELLS | B.LINE PEAK BLK-G4.1/SC 285 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.56 | 38.91 | 8.98 | 31.73 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.8078 | 31.0154 | 7.1996 | 29.2639 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19673
Hanwha Q CELLS | Q.PEAK BLK-G4.1 285 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.56 | 38.91 | 8.98 | 31.73 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.8078 | 31.0154 | 7.1996 | 29.2639 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19673
Hanwha Q CELLS | Q.PEAK BLK-G4.1/SC 285 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.56 | 38.91 | 8.98 | 31.73 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.8078 | 31.0154 | 7.1996 | 29.2639 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19673
Hanwha Q CELLS | Q.PEAK BLK-G4.1/TAA 285 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.56 | 38.91 | 8.98 | 31.73 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.8078 | 31.0154 | 7.1996 | 29.2639 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19673
Hanwha Q CELLS | Q.PLUS BFR-G4.1 285 | 285 W, 60 cell polycrystalline module, white backsheet, black frame, 1000V or 1500V max system Vdc | UL 61730 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.46 | 39.22 | 8.91 | 31.99 | 45.39 | -0.4 | 0.04 | -0.29 |  |  | 1.7622 | 31.4297 | 7.0884 | 29.7385 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PLUS BFR-G4.1/TAA 285 | 285 W Polycrystalline Module | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.46 | 39.22 | 8.91 | 31.99 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.774 | 31.1617 | 7.136 | 29.4849 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19397
Hanwha Q CELLS | Q.PLUS-G4.1/SC 285 | 285 W Polycrystalline Module | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.46 | 39.22 | 8.91 | 31.99 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.774 | 31.1617 | 7.136 | 29.4849 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19397
Hanwha Q CELLS | Q.PLUS-G4.3 285 | 285 W, 60 cell polycrystalline module, white backsheet, silver frame, 1500V or 1000V max system Vdc | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.46 | 39.22 | 8.91 | 31.99 | 45.39 | -0.4 | 0.04 | -0.29 |  |  | 1.7941 | 31.1617 | 7.2167 | 29.4849 | [6 empty] | 2019-12-02
Hanwha Q CELLS | Q.PEAK BLK-G3.1 290 | 290 W Monocrystalline Module | UL 1703 | 290 | 265.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 9.63 | 39.19 | 9.07 | 31.96 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.7825 | 31.2857 | 7.2974 | 29.0645 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.1923
Hanwha Q CELLS | Q.PEAK BLK-G4.1 290 | 290 W Monocrystalline Module, Black Frame, Black backsheet, Q.ANTUM Cells | UL 1703 | 290 | 265.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.63 | 38.19 | 9.07 | 31.96 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.784 | 31.291 | 7.105 | 29.524 | [6 empty] | 2017-09-01
Hanwha Q CELLS | Q.PEAK BLK-G4.1/SC 290 | 290 W Monocrystalline Module , Black Frame, Black backsheet, Q.ANTUM Cells | UL 1703 | 290 | 265.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.63 | 39.19 | 9.07 | 31.96 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.784 | 31.291 | 7.105 | 29.524 | [6 empty] | 2017-09-01
Hanwha Q CELLS | Q.PEAK BLK-G4.1/TAA 290 | 290 W Monocrystalline Module, Black Frame, Black backsheet, Q.ANTUM Cells | UL 1703 | 290 | 265.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.63 | 39.19 | 9.07 | 31.96 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.784 | 31.291 | 7.105 | 29.524 | [6 empty] | 2017-09-01
Hanwha Q CELLS | Q.PEAK DUO BLK-G5 290 | 290 W Monocrystalline module, 120 Q.ANTUM solar half-cells | UL 1703 | 290 | 266.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.621 | 120 |  | N | 9.61 | 38.94 | 9.14 | 31.71 | 47.39 | -0.366 | 0.047 | -0.285 | 0.018 | -0.383 | 1.806 | 31.693 | 7.298 | 29.987 | [6 empty] | 2017-12-01
Hanwha Q CELLS | Q.PEAK-G4.1 290 | 290 W, 60 Cells Monocrystalline Module | UL 1703 | 290 | 267.9 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.63 | 39.19 | 9.07 | 31.96 | 44.89 | -0.379 | 0.045 | -0.28 | -0.002 | -0.377 | 1.839 | 31.896 | 7.382 | 30.158 | [6 empty] | 2018-02-01
Hanwha Q CELLS | Q.PLUS BFR-G4.1 290 | 290 W, 60 cell polycrystalline module, white backsheet, black frame, 1000V or 1500V max system Vdc | UL 61730 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.52 | 39.48 | 8.98 | 32.29 | 45.39 | -0.4 | 0.04 | -0.29 |  |  | 1.776 | 31.7244 | 7.1441 | 30.0174 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PLUS-BFR G4.1/TAA 290 | 290 W Polycrystalline Module | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.52 | 39.48 | 8.98 | 32.29 | 45.39 | -0.4 | 0.04 | -0.29 | -0.02 | -0.39 | 1.788 | 31.4539 | 7.192 | 29.7614 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19393
Hanwha Q CELLS | Q.PLUS-G4.3 290 | 290 W, 60 cell polycrystalline module, white backsheet, silver frame, 1500V or 1000V max system Vdc | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.52 | 39.48 | 8.98 | 32.29 | 45.39 | -0.4 | 0.04 | -0.29 |  |  | 1.8082 | 31.4539 | 7.2734 | 29.7614 | [6 empty] | 2019-12-02
Hanwha Q CELLS | Q.PRO L 290 | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.58 | 35.07 | 6.61 | 32.09 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19107
Hanwha Q CELLS | Q.PEAK BLK-G3.1 295 | 295 W Monocrystalline Module | UL 1703 | 295 | 269.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 9.7 | 39.48 | 9.17 | 32.19 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8021 | 31.5108 | 7.3778 | 29.2736 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.1925
Hanwha Q CELLS | Q.PEAK BLK-G4.1 295 | 295 W Monocrystalline Module , Black Frame, Black backsheet, Q.ANTUM Cells | UL 1703 | 295 | 270.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.7 | 39.48 | 9.17 | 32.19 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.784 | 31.291 | 7.105 | 29.524 | [6 empty] | 2017-09-01
Hanwha Q CELLS | Q.PEAK BLK-G4.1/SC 295 | 295 W Monocrystalline Module , Black Frame, Black backsheet, Q.ANTUM Cells | UL 1703 | 295 | 270.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.7 | 39.48 | 9.17 | 32.19 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.784 | 31.291 | 7.105 | 29.524 | [6 empty] | 2017-09-01
Hanwha Q CELLS | Q.PEAK BLK-G4.1/TAA 295 | 295 W Monocrystalline Module, Black Frame, Black backsheet, Q.ANTUM Cells | UL 1703 | 295 | 270.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.7 | 39.48 | 9.17 | 32.19 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.784 | 31.291 | 7.105 | 29.524 | [6 empty] | 2017-09-01
Hanwha Q CELLS | Q.PEAK G3.1 295 | 295 W Monocrystalline Module | UL 1703 | 295 | 269.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.7 | 39.48 | 9.17 | 32.19 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8021 | 31.5108 | 7.3778 | 29.2736 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.1925
Hanwha Q CELLS | Q.PEAK G4.1/SC 295 | 295 W Monocrystalline Module | UL 1703 | 295 | 269.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.7 | 39.48 | 9.17 | 32.19 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8021 | 31.5108 | 7.3778 | 29.2736 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.1925
Hanwha Q CELLS | Q.PEAK-G4.1 295 | 295 W, 60 Cells Monocrystalline Module | UL 1703 | 295 | 272.6 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.7 | 39.48 | 9.17 | 32.19 | 44.89 | -0.379 | 0.045 | -0.28 | -0.002 | -0.377 | 1.839 | 31.896 | 7.382 | 30.158 | [7 empty] | 2018-02-01
Hanwha Q CELLS | Q.PLUS BFR-G4.1 295 | 295 W, 60 cell polycrystalline module, white backsheet, black frame, 1000V or 1500V max system Vdc | UL 61730 | 295 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.58 | 39.73 | 9.05 | 32.59 | 45.39 | -0.4 | 0.04 | -0.29 |  |  | 1.7899 | 32.0192 | 7.1998 | 30.2962 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PRO L 295 | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6 | 35.27 | 6.68 | 32.27 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha Q CELLS | Q.PEAK BLK-G4.1 300 | Black Frame, Black backsheet, Q.ANTUM Cells | UL 1703 | 300 | 275.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.77 | 39.76 | 9.26 | 32.41 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.784 | 31.291 | 7.105 | 29.524 | [6 empty] | 2017-08-01 | 2017-09-01
Hanwha Q CELLS | Q.PEAK BLK-G4.1/TAA 300 | 300 W Monocrystalline Module, Black Frame, Black backsheet, Q.ANTUM Cells | UL 1703 | 300 | 275.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.77 | 39.76 | 9.26 | 32.41 | 45.97 | -0.392 | 0.039 | -0.288 | -0.006 | -0.386 | 1.784 | 31.291 | 7.105 | 29.524 | [6 empty] | 2017-09-01
Hanwha Q CELLS | Q.PEAK DUO BLK-G5 300 | 300 W, 120 half cell Monocrystalline module, black backsheet | UL 1703 | 300 | 277.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 120 |  | N | 9.72 | 39.48 | 9.25 | 32.43 | 45.57 | -0.361 | 0.038 | -0.277 | 0 | -0.361 | 1.7927 | 31.3402 | 7.2162 | 30.1799 | [6 empty] | 2018-04-02
Hanwha Q CELLS | Q.PEAK G3.1 300 | 300 W Monocrystalline Module | UL 1703 | 300 | 274.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.77 | 39.76 | 9.26 | 32.41 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8198 | 31.7262 | 7.4502 | 29.4737 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19245
Hanwha Q CELLS | Q.PEAK G4.1/ Max 300 | 300 W Monocrystalline Module | UL 1703 | 300 | 274.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6414 | 60 | 1 | N | 9.77 | 35 | 9.26 | 32.41 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8198 | 31.7262 | 7.4502 | 29.4737 | Rack | Flat Plate | 0.996 | 1.648 | 1 | 0.19245
Hanwha Q CELLS | Q.PEAK G4.1/SC 300 | 300 W Monocrystalline Module | UL 1703 | 300 | 274.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.77 | 39.76 | 9.26 | 32.41 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8198 | 31.7262 | 7.4502 | 29.4737 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19245
Hanwha Q CELLS | Q.PEAK G4.1/TAA 300 | 300 W Monocrystalline Module | UL 1703 | 300 | 274.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.77 | 39.76 | 9.26 | 32.41 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8198 | 31.7262 | 7.4502 | 29.4737 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19245
Hanwha Q CELLS | Q.PEAK-G4.1 300 | 300 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 300 | 277.6 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.77 | 39.76 | 9.26 | 32.41 | 44.89 | -0.379 | 0.045 | -0.28 | 1.839 | 31.896 | 1.839 | 31.896 | 7.382 | 30.158 | [7 empty] | 2019-09-16
Hanwha Q CELLS | Q.PRO L 300 | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.61 | 35.46 | 6.75 | 32.45 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1903
Hanwha Q CELLS | Q.PRO L-G3 300 | 300 W Polycrystalline Module, Silver Frame | UL 1703 | 300 | 272.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.972 | 72 | 1 | N | 8.92 | 44.9 | 8.31 | 36.09 | 46.6 | -0.41 | 0.05 | -0.3 | -0.02 | -0.39 | 1.65 | 35.34 | 6.67 | 32.8 | Rack | Flat Plate | 1 | 1.972 | 1 | 0.19437
Hanwha Q CELLS | Q.PEAK BLK-G4.1 305 | 305 W, 60 cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 1703 | 305 | 281.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.84 | 40.05 | 9.35 | 32.62 | 46.52 | -0.367 | 0.042 | -0.274 |  |  | 1.774 | 32.276 | 7.184 | 30.43 | [6 empty] | 2020-02-03
Hanwha Q CELLS | Q.PEAK DUO BLK-G5 305 | 305 W Monocrystalline module, 120 Q.ANTUM solar half-cells | UL 1703 | 305 | 280.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.621 | 120 |  | N | 9.78 | 39.75 | 9.31 | 32.78 | 47.39 | -0.366 | 0.047 | -0.285 | 0.018 | -0.383 | 1.806 | 31.693 | 7.298 | 29.987 | [6 empty] | 2017-12-01
Hanwha Q CELLS | Q.PEAK DUO-G5 305 | 305 W, 120 Half Cells PERC-Mono PV Module | UL 1703 | 305 | 281.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 120 |  | N | 9.93 | 39.35 | 9.44 | 32.3 | 45.48 | -0.378 | 0.04 | -0.282 | -0.01 | -0.37 | 1.86 | 31.83 | 7.48 | 30.52 | [6 empty] | 2017-11-15 | 2018-12-17
Hanwha Q CELLS | Q.PEAK G3.1 305 | 305 W Monocrystalline Module | UL 1703 | 305 | 279.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.84 | 40.05 | 9.35 | 32.62 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8375 | 31.9318 | 7.5226 | 29.6647 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19238
Hanwha Q CELLS | Q.PEAK G4.1/ Max 305 | 305 W Monocrystalline Module | UL 1703 | 305 | 279.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6414 | 60 | 1 | N | 9.84 | 35 | 9.35 | 32.62 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8375 | 31.9318 | 7.5226 | 29.6647 | Rack | Flat Plate | 0.996 | 1.648 | 1 | 0.19238
Hanwha Q CELLS | Q.PEAK G4.1/SC 305 | 305 W Monocrystalline Module | UL 1703 | 305 | 279.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.84 | 40.05 | 9.35 | 32.62 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8375 | 31.9318 | 7.5226 | 29.6647 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19238
Hanwha Q CELLS | Q.PEAK G4.1/TAA 305 | 305 W Monocrystalline Module | UL 1703 | 305 | 279.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.84 | 40.05 | 9.35 | 32.62 | 45.84 | -0.408 | 0.044 | -0.29 | -0.01 | -0.4 | 1.8375 | 31.9318 | 7.5226 | 29.6647 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19238
Hanwha Q CELLS | Q.PEAK-G4.1 305 | 305 W, 60 Cells Monocrystalline Module | UL 1703 | 305 | 282.1 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 9.84 | 40.05 | 9.35 | 32.62 | 44.89 | -0.379 | 0.045 | -0.28 | -0.002 | -0.377 | 1.839 | 31.896 | 7.382 | 30.158 | [7 empty] | 2018-02-01
Hanwha Q CELLS | Q.PRO L 305 | 305 W Polycrystalline Module | UL 1703 | 305 | 272.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.63 | 35.76 | 6.81 | 32.72 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19111
Hanwha Q CELLS | Q.PRO L-G2 305 | 305 W Polycrystalline Module | UL 1703 | 305 | 274.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7372 | 72 | 1 | N | 8.99 | 45.14 | 8.38 | 36.39 | 46.5 | -0.46 | 0.035 | -0.333 | -0.01 | -0.452 | 1.7 | 35.62 | 6.68 | 33.18 | Rack | Flat Plate | 0.932 | 1.864 | 1 | 0.19854
Hanwha Q CELLS | Q.PRO L-G2.3 305 | 305 W Polycrystalline Module | UL 1703 | 305 | 276 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 8.92 | 45.06 | 8.32 | 36.66 | 46.9 | -0.42 | 0.05 | -0.31 | -0.02 | -0.4 | 1.65 | 35.66 | 6.66 | 33.38 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19291
Hanwha Q CELLS | Q.PRO L-G3 305 | 305 W Polycrystalline Module, Silver Frame | UL 1703 | 305 | 276.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.972 | 72 | 1 | N | 8.99 | 45.14 | 8.38 | 36.39 | 46.6 | -0.41 | 0.05 | -0.3 | -0.02 | -0.39 | 1.67 | 35.63 | 6.72 | 33.08 | Rack | Flat Plate | 1 | 1.972 | 1 | 0.19509
Hanwha Q CELLS | B.LINE PRO L-G4.1 307 | 307W Polycrystalline Module | UL 1703 | 308 | 284.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 8.96 | 45.2 | 8.35 | 36.8 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.6852 | 34.8606 | 6.6743 | 33.9745 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19074
Hanwha Q CELLS | Q.PEAK DUO BLK-G5 310 | 310 W, 120 half cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 287.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.83 | 40.02 | 9.36 | 33.12 | 45.57 | -0.361 | 0.038 | -0.277 | 0 | -0.361 | 1.814 | 32.007 | 7.302 | 30.822 | [6 empty] | 2018-04-02 | 2018-12-17
Hanwha Q CELLS | Q.PEAK DUO BLK-G5/SC 310 | 310 W, 120 half cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 287.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.83 | 40.02 | 9.36 | 33.12 | 45.57 | -0.361 | 0.038 | -0.277 | 0 | -0.361 | 1.814 | 32.007 | 7.302 | 30.822 | [6 empty] | 2018-12-17
Hanwha Q CELLS | Q.PEAK DUO-G5 310 | 310 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 310 | 286.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.98 | 39.61 | 9.5 | 32.64 | 45.48 | -0.378 | 0.04 | -0.282 | -0.01 | -0.37 | 1.86 | 31.83 | 7.48 | 30.52 | [6 empty] | 2017-11-15 | 2018-12-17
Hanwha Q CELLS | Q.PEAK-G4.1 310 | 310 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 310 | 287.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.91 | 40.33 | 9.44 | 32.83 | 44.89 | -0.379 | 0.045 | -0.28 | 1.8747 | 32.3093 | 1.8747 | 32.3093 | 7.5255 | 30.5488 | [6 empty] | 2019-09-16
Hanwha Q CELLS | Q.PRO L 310 | 310 W Polycrystalline Module | UL 1703 | 310 | 283.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 9.08 | 45.75 | 8.65 | 36.15 | 43.6 | -0.44 | 0.05 | -0.32 | -0.01 | -0.42 | 1.74 | 35.22 | 6.92 | 31.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19769
Hanwha Q CELLS | Q.PRO L G4 310 | 310 W Polycrystalline Module, Silver Frame | UL 1703 | 310 | 283.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 8.99 | 45.29 | 8.39 | 36.96 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.69 | 35.73 | 6.71 | 35.87 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19479
Hanwha Q CELLS | Q.PRO L G4.1 310 | 310 W Polycrystalline Module | UL 1703 | 310 | 283.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 8.99 | 45.29 | 8.39 | 36.96 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.69 | 35.73 | 6.71 | 35.87 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19479
Hanwha Q CELLS | Q.PRO L-G2 310 | 310 W Polycrystalline Module | UL 1703 | 310 | 279.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.7372 | 72 | 1 | N | 9.06 | 45.37 | 8.45 | 36.68 | 46.5 | -0.46 | 0.035 | -0.333 | -0.01 | -0.452 | 1.71 | 35.9 | 6.74 | 33.45 | Rack | Flat Plate | 0.932 | 1.864 | 1 | 0.19803
Hanwha Q CELLS | Q.PRO L-G2.3 310 | 310 W Polycrystalline Module | UL 1703 | 310 | 280.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 8.99 | 45.29 | 8.39 | 36.96 | 46.9 | -0.42 | 0.05 | -0.31 | -0.02 | -0.4 | 1.67 | 35.95 | 6.71 | 33.65 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19367
Hanwha Q CELLS | Q.PRO L-G3 310 | 310 W Polycrystalline Module, Silver Frame | UL 1703 | 310 | 281.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.972 | 72 | 1 | N | 9.06 | 45.37 | 8.45 | 36.68 | 46.6 | -0.41 | 0.05 | -0.3 | -0.02 | -0.39 | 1.68 | 35.92 | 6.78 | 33.34 | Rack | Flat Plate | 1 | 1.972 | 1 | 0.19466
Hanwha Q CELLS | Q.PRO L-G3.1 310 | 310 W Polycrystalline Module, Silver frame | UL 1703 | 310 | 283.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 8.99 | 45.29 | 8.39 | 36.96 | 44.8 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.72 | 35.79 | 6.73 | 34.66 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19858
Hanwha Q CELLS | Q.PEAK DUO BLK-G5 315 | 315 W, 120 half cell Monocrystalline module, black backsheet | UL 1703 | 315 | 292.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 120 |  | N | 9.89 | 40.29 | 9.41 | 33.46 | 45.57 | -0.361 | 0.038 | -0.277 | 0 | -0.361 | 1.8237 | 32.3356 | 7.341 | 31.1384 | [6 empty] | 2018-04-02
Hanwha Q CELLS | Q.PEAK DUO BLK-G5/SC 315 | 315 W, 120 half cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 315 | 292.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.89 | 40.29 | 9.41 | 33.46 | 45.57 | -0.361 | 0.038 | -0.277 | 0 | -0.361 | 1.8237 | 32.3356 | 7.341 | 31.1384 | [6 empty] | 2018-12-17
Hanwha Q CELLS | Q.PEAK DUO-G5 315 | 315 W, 120 Half Cells PERC-Mono PV Module | UL 1703 | 315 | 291.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 120 |  | N | 10.04 | 39.87 | 9.55 | 32.98 | 45.48 | -0.378 | 0.04 | -0.282 | -0.01 | -0.37 | 1.86 | 31.83 | 7.48 | 30.52 | [6 empty] | 2017-11-15 | 2018-12-17
Hanwha Q CELLS | Q.PEAK DUO-G7 315 | 315 W, 120 half-cut cell monocrystalline module, 12 busbars, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 292.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 9.99 | 39.84 | 9.51 | 33.14 | 45.85 | -0.356 | 0.038 | -0.272 |  |  | 1.8735 | 31.4723 | 7.5765 | 30.3473 | [6 empty] | 2019-10-01
Hanwha Q CELLS | Q.PEAK-G4.1 315 | 315 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 291.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 1 | N | 9.98 | 40.62 | 9.53 | 33.04 | 44.89 | -0.379 | 0.045 | -0.28 | 1.8926 | 32.516 | 1.8926 | 32.516 | 7.5972 | 30.7442 | [6 empty] | 2019-09-16
Hanwha Q CELLS | Q.PRO L G2 315 | 315 W Polycrystalline Module | UL 1703 | 315 | 288.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 9.12 | 45.61 | 8.52 | 36.97 | 43.6 | -0.44 | 0.04 | -0.32 | -0.02 | -0.42 | 1.71 | 46.16 | 6.82 | 45 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.25058
Hanwha Q CELLS | Q.PRO L G4 315 | 315 W Polycrystalline Module, Silver Frame | UL 1703 | 315 | 288 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.06 | 45.53 | 8.46 | 36.96 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.71 | 35.73 | 6.76 | 35.87 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19396
Hanwha Q CELLS | Q.PRO L G4.1 315 | 315 W Polycrystalline Module | UL 1703 | 315 | 288 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.06 | 45.53 | 8.46 | 36.96 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.71 | 35.73 | 6.76 | 35.87 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19396
Hanwha Q CELLS | Q.PRO L-G2.3 315 | 315 W Polycrystalline Module | UL 1703 | 315 | 285.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9129 | 72 | 1 | N | 9.06 | 45.53 | 8.46 | 37.24 | 46.9 | -0.42 | 0.05 | -0.31 | -0.02 | -0.4 | 1.68 | 36.22 | 6.77 | 33.91 | Rack | Flat Plate | 0.982 | 1.948 | 1 | 0.19317
Hanwha Q CELLS | Q.PRO L-G3 315 | 315 W Polycrystalline Module, Silver Frame | UL 1703 | 315 | 286.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.972 | 72 | 1 | N | 9.12 | 45.61 | 8.52 | 36.97 | 46.6 | -0.41 | 0.05 | -0.3 | -0.02 | -0.39 | 1.69 | 36.2 | 6.84 | 33.6 | Rack | Flat Plate | 1 | 1.972 | 1 | 0.19422
Hanwha Q CELLS | Q.PRO L-G3.1 315 | 315 W Polycrystalline Module, Silver frame | UL 1703 | 315 | 288.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.06 | 45.53 | 8.46 | 37.24 | 44.8 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.73 | 36.06 | 6.79 | 34.92 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19804
Hanwha Q CELLS | B.LINE PLUS L-G4.2 317 | 317 W Polycrystalline Module | UL 1703 | 317 | 293.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.36 | 46 | 8.76 | 36.2 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.768 | 34.2922 | 7.002 | 33.4206 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19126
Hanwha Q CELLS | Q.PEAK DUO BLK-G5 320 | 320 W, 120 half cell Monocrystalline module, black backsheet | UL 1703 | 320 | 297 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 120 |  | N | 9.94 | 40.56 | 9.47 | 33.8 | 45.57 | -0.361 | 0.038 | -0.277 | 0 | -0.361 | 1.8353 | 32.6641 | 7.3878 | 31.4548 | [6 empty] | 2018-04-02
Hanwha Q CELLS | Q.PEAK DUO BLK-G5/SC 320 | 320 W, 120 half cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 297 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.94 | 40.56 | 9.47 | 33.8 | 45.57 | -0.361 | 0.038 | -0.277 | 0 | -0.361 | 1.8353 | 32.6641 | 7.3878 | 31.4548 | [6 empty] | 2018-12-17
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+ 320 | 320 W, 120 half-cut cell monocrystalline module, black backsheet and frame, 1000V max system Vdc | UL 1703 | 320 | 298.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.734 | 60 | 2 | N | 10.3 | 39.65 | 9.8 | 32.64 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.8981 | 31.4837 | 7.6965 | 30.4837 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO-G5 320 | 320 W, 120 Half Cells PERC-Mono PV Module | UL 1703 | 320 | 295.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 120 |  | N | 10.09 | 40.13 | 9.6 | 33.32 | 45.48 | -0.378 | 0.04 | -0.282 | -0.01 | -0.37 | 1.86 | 31.83 | 7.48 | 30.52 | [6 empty] | 2017-11-15 | 2018-12-17
Hanwha Q CELLS | Q.PEAK DUO-G5/SC 320 | 320 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 320 | 296 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.09 | 40.13 | 9.6 | 33.32 | 45.48 | -0.378 | 0.04 | -0.282 | -0.01 | -0.37 | 1.8796 | 32.4931 | 7.5587 | 31.1558 | [6 empty] | 2018-12-17
Hanwha Q CELLS | Q.PEAK DUO-G7 320 | 320 W, 120 half-cut cell monocrystalline module, 12 busbars, white backsheet, 1000V max system Vdc | UL 1703 | 320 | 296.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.04 | 40.1 | 9.56 | 33.47 | 45.85 | -0.356 | 0.038 | -0.272 |  |  | 1.8833 | 31.7857 | 7.6164 | 30.6495 | [6 empty] | 2019-10-01
Hanwha Q CELLS | Q.PLUS L-G4 320 | 320 W Polycrystalline Module, Silver frame | UL 1703 | 320 | 292.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.39 | 46.17 | 8.76 | 36.39 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.77 | 35.18 | 7 | 35.32 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19459
Hanwha Q CELLS | Q.PLUS L-G4.1 320 | 320 W Polycrystalline Module, Silver frame | UL 1703 | 320 | 292.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.39 | 46.17 | 8.76 | 36.39 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.77 | 35.18 | 7 | 35.32 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19459
Hanwha Q CELLS | Q.PLUS L-G4.2 320 | 320 W Polycrystalline Module | UL 1703 | 320 | 295.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.39 | 46.17 | 8.79 | 36.39 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.77 | 34.47 | 7.03 | 33.6 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19066
Hanwha Q CELLS | Q.PRO L G4 320 | 320 W Polycrystalline Module, Silver Frame | UL 1703 | 320 | 292.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.13 | 45.76 | 8.53 | 37.53 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.72 | 36.28 | 6.82 | 36.42 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19501
Hanwha Q CELLS | Q.PRO L G4.1 320 | 320 W Polycrystalline Module | UL 1703 | 320 | 292.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.13 | 45.76 | 8.53 | 37.53 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.72 | 36.28 | 6.82 | 36.42 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19501
Hanwha Q CELLS | Q.PRO L-G3.1 320 | 320 W Polycrystalline Module, Silver frame | UL 1703 | 320 | 293.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.13 | 45.76 | 8.53 | 37.53 | 44.8 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.75 | 36.34 | 6.84 | 35.19 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19873
Hanwha Q CELLS | B.LINE PLUS L-G4.1 322 | 322W Polycrystalline Module | UL 1703 | 323 | 298.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.16 | 45.9 | 8.56 | 37.7 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.7276 | 35.7131 | 6.8421 | 34.8054 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19102
Hanwha Q CELLS | B.LINE PRO L-G4.1 322 | 322W Polycrystalline Module | UL 1703 | 323 | 298.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.16 | 45.9 | 8.56 | 37.7 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.7276 | 35.7131 | 6.8421 | 34.8054 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19102
Hanwha Q CELLS | B.LINE PLUS L-G4.2 325 | 325 W Polycrystalline Module | UL 1703 | 325 | 300.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.44 | 46.3 | 8.85 | 36.7 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.7861 | 34.7658 | 7.0739 | 33.8822 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19107
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+ 325 | 325 W, 120 half-cut cell monocrystalline module, black backsheet and frame, 1000V max system Vdc | UL 1703 | 325 | 303.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.734 | 60 | 2 | N | 10.36 | 39.9 | 9.86 | 32.97 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9097 | 31.802 | 7.7436 | 30.7919 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO-G5 325 | 325 W, 120 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 325 | 303.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.636 | 60 | 2 | N | 10.14 | 40.4 | 9.66 | 33.65 | 44.73 | -0.352 | 0.044 | -0.269 |  |  | 1.892 | 32.324 | 7.584 | 31.105 | [6 empty] | 2017-11-15 | 2019-06-03
Hanwha Q CELLS | Q.PEAK DUO-G5/SC 325 | 325 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 325 | 300.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.14 | 40.4 | 9.66 | 33.65 | 45.48 | -0.378 | 0.04 | -0.282 | -0.01 | -0.37 | 1.8913 | 32.8149 | 7.606 | 31.4644 | [6 empty] | 2018-12-17
Hanwha Q CELLS | Q.PEAK DUO-G7 325 | 325 W, 120 half-cut cell monocrystalline module, 12 busbars, white backsheet, 1000V max system Vdc | UL 1703 | 325 | 301.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.1 | 40.36 | 9.61 | 33.81 | 45.85 | -0.356 | 0.038 | -0.272 |  |  | 1.8932 | 32.1086 | 7.6562 | 30.9608 | [6 empty] | 2019-10-01
Hanwha Q CELLS | Q.PLUS L-G4 325 | 325 W Polycrystalline Module, Silver frame | UL 1703 | 325 | 297.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.44 | 46.43 | 8.85 | 36.7 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.78 | 35.48 | 7.08 | 35.62 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19432
Hanwha Q CELLS | Q.PLUS L-G4.1 325 | 325 W Polycrystalline Module, Silver frame | UL 1703 | 325 | 297.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.44 | 46.43 | 8.85 | 36.7 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.78 | 35.48 | 7.08 | 35.62 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19432
Hanwha Q CELLS | Q.PLUS L-G4.2 325 | 325 W Polycrystalline Module | UL 1703 | 325 | 300.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.44 | 46.43 | 8.85 | 36.7 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.79 | 34.77 | 7.07 | 33.88 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.1915
Hanwha Q CELLS | B.LINE PLUS L-G4.2 330 | 330 W Polycrystalline Module | UL 1703 | 330 | 305.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.49 | 46.55 | 8.91 | 37.02 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.7983 | 35.069 | 7.1219 | 34.1776 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.1911
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+ 330 | 330 W, 120 half-cut cell monocrystalline module, black backsheet and frame, 1000V max system Vdc | UL 1703 | 330 | 308.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.734 | 60 | 2 | N | 10.41 | 40.15 | 9.91 | 33.29 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9194 | 32.1107 | 7.7829 | 31.0908 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/HL 330 | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 330 | 308.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.41 | 40.15 | 9.91 | 33.29 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9194 | 32.1107 | 7.7829 | 31.0908 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/SC 330 | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 330 | 308.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.41 | 40.15 | 9.91 | 33.29 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9194 | 32.1107 | 7.7829 | 31.0908 | [6 empty] | 2020-01-13 | 2021-04-12
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/TS 330 | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 330 | 308.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.41 | 40.15 | 9.91 | 33.29 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9194 | 32.1107 | 7.7829 | 31.0908 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO BLK-G8 330 | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 330 | 305.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.41 | 39.96 | 10.01 | 33.61 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9006 | 32.1881 | 7.7196 | 30.9604 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G8+ 330 | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 330 | 305.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.41 | 39.96 | 10.01 | 33.61 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9006 | 32.1881 | 7.7196 | 30.9604 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO-G5 330 | 330 W, 120 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 330 | 307.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.636 | 60 | 2 | N | 10.2 | 40.66 | 9.71 | 33.98 | 44.73 | -0.352 | 0.044 | -0.269 |  |  | 1.9018 | 32.641 | 7.6233 | 31.41 | [6 empty] | 2019-06-03
Hanwha Q CELLS | Q.PEAK DUO-G6 330 | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 330 | 305.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.738 | 60 | 2 | N | 10.57 | 39.74 | 10.06 | 32.81 | 45.7 | -0.364 | 0.042 | -0.273 |  |  | 1.983 | 32.144 | 7.948 | 30.632 | [6 empty] | 2019-06-17
Hanwha Q CELLS | Q.PEAK DUO-G7 330 | 330 W, 120 half-cut cell monocrystalline module, 12 busbars, white backsheet, 1000V max system Vdc | UL 1703 | 330 | 306.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.15 | 40.62 | 9.67 | 34.14 | 45.85 | -0.356 | 0.038 | -0.272 |  |  | 1.905 | 32.422 | 7.704 | 31.263 | [6 empty] | 2019-10-01
Hanwha Q CELLS | Q.PEAK DUO-G8 330 | 330W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 330 | 308.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.52 | 39.71 | 10.01 | 32.97 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 1.9941 | 31.6218 | 7.9273 | 30.679 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO-G8+ 330 | 330W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 330 | 308.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.52 | 39.71 | 10.01 | 32.97 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 1.9941 | 31.6218 | 7.9273 | 30.679 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PLUS L-G4 330 | 330 W Polycrystalline Module, Silver frame | UL 1703 | 330 | 302.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.49 | 46.68 | 8.91 | 37.02 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.8 | 35.79 | 7.12 | 35.93 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19522
Hanwha Q CELLS | Q.PLUS L-G4.1 330 | 330 W Polycrystalline Module, Silver frame | UL 1703 | 330 | 302.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.49 | 46.68 | 8.91 | 37.02 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.8 | 35.79 | 7.12 | 35.93 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19522
Hanwha Q CELLS | Q.PLUS L-G4.2 330 | 330 W Polycrystalline Module | UL 1703 | 330 | 305.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.49 | 46.68 | 8.91 | 37.02 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.8 | 35.07 | 7.12 | 34.18 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19129
Hanwha Q CELLS | B.LINE PLUS L-G4.2 332 | 332W Polycrystalline Module | UL 1703 | 332 | 307.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.51 | 46.8 | 8.94 | 37.2 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.8043 | 35.2395 | 7.1459 | 34.3438 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19151
Hanwha Q CELLS | B.LINE PLUS L-G4.2 335 | 335 W Polycrystalline Module | UL 1703 | 335 | 310.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.54 | 46.81 | 8.97 | 37.33 | 43.2 | -0.4 | 0.04 | -0.29 | -0.01 | -0.39 | 1.8104 | 35.3626 | 7.1699 | 34.4638 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.1911
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+ 335 | 335 W, 120 half-cut cell monocrystalline module, black backsheet and frame, 1000V max system Vdc | UL 1703 | 335 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.734 | 60 | 2 | N | 10.47 | 40.41 | 9.97 | 33.62 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.931 | 32.429 | 7.83 | 31.399 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/HL 335 | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 335 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.47 | 40.41 | 9.97 | 33.62 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.931 | 32.429 | 7.83 | 31.399 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/SC 335 | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 335 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.47 | 40.41 | 9.97 | 33.62 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.931 | 32.429 | 7.83 | 31.399 | [6 empty] | 2020-01-13 | 2021-04-12
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/TS 335 | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 335 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.47 | 40.41 | 9.97 | 33.62 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.931 | 32.429 | 7.83 | 31.399 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO BLK-G8 335 | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 335 | 310.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.57 | 39.96 | 10.01 | 33.61 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9006 | 32.1881 | 7.7196 | 30.9604 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G8+ 335 | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 335 | 310.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.47 | 39.96 | 10.01 | 33.61 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9006 | 32.1881 | 7.7196 | 30.9604 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO-G5 335 | 335 W, 120 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 335 | 312.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.636 | 60 | 2 | N | 10.25 | 40.92 | 9.76 | 34.31 | 44.73 | -0.352 | 0.044 | -0.269 |  |  | 1.9116 | 32.958 | 7.6625 | 31.7151 | [6 empty] | 2019-06-03
Hanwha Q CELLS | Q.PEAK DUO-G8 335 | 335W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 335 | 313.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.57 | 39.96 | 10.06 | 33.29 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.0041 | 31.9288 | 7.9669 | 30.9768 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO-G8+ 335 | 335W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 335 | 313.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.57 | 39.96 | 10.06 | 33.29 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.0041 | 31.9288 | 7.9669 | 30.9768 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PLUS L-G4 335 | 335 W Polycrystalline Module, Silver frame | UL 1703 | 335 | 306.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.54 | 46.94 | 8.97 | 37.33 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.81 | 36.09 | 7.17 | 36.23 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19499
Hanwha Q CELLS | Q.PLUS L-G4.1 335 | 335 W Polycrystalline Module, Silver frame | UL 1703 | 335 | 306.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.54 | 46.94 | 8.97 | 37.33 | 45.1 | -0.41 | 0.04 | -0.31 | -0.01 | -0.4 | 1.81 | 36.09 | 7.17 | 36.23 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19499
Hanwha Q CELLS | Q.PLUS L-G4.2 335 | 335 W, 72 cell polycrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 1703 | 335 | 307.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.54 | 46.81 | 8.97 | 37.33 | 45.22 | -0.398 | 0.05 | -0.294 | -0.01 | -0.39 | 1.762 | 36.201 | 7.09 | 34.367 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19041 |  | 2019-12-23
Hanwha Q CELLS | Q.PLUS L-G4.2/TAA 335 | 335 W Polycrystalline Module | UL 1703 | 335 | 307.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.54 | 46.81 | 8.97 | 37.33 | 45.22 | -0.398 | 0.05 | -0.294 | 0 | -0.398 | 1.791 | 36.2078 | 7.2065 | 34.3734 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19357
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+ 340 | 340 W, 120 half-cut cell monocrystalline module, black backsheet and frame, 1000V max system Vdc | UL 1703 | 340 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.734 | 60 | 2 | N | 10.52 | 40.66 | 10.02 | 33.94 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9407 | 32.7377 | 7.8693 | 31.6979 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/AC 340 | 340 W, 120 half-cut cell monocrystalline ACPV module, black backsheet. DC module:Q.PEAK DUO BLK-G6+ 340. Microinverter: IQ7PLUS-72-x-ACM-US-y | UL 1741 | 340 | 318 | This component is specific to ACPV modules and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.52 | 40.66 | 10.02 | 33.94 | 44.4 | -0.343 | 0.044 | -0.269 |  |  | 1.94 | 32.74 | 7.87 | 31.7 | [6 empty] | 2020-07-13
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/HL 340 | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 340 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.52 | 40.66 | 10.02 | 33.94 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9407 | 32.7377 | 7.8693 | 31.6979 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/SC 340 | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 340 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.52 | 40.66 | 10.02 | 33.94 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9407 | 32.7377 | 7.8693 | 31.6979 | [6 empty] | 2020-01-13 | 2021-04-12
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/TS 340 | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 340 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.52 | 40.66 | 10.02 | 33.94 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9407 | 32.7377 | 7.8693 | 31.6979 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO BLK-G8 340 | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 340 | 315.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.63 | 40.2 | 10.12 | 33.61 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9215 | 32.1881 | 7.8044 | 30.9604 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G8+ 340 | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 340 | 315.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.63 | 40.2 | 10.12 | 33.61 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9215 | 32.1881 | 7.8044 | 30.9604 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO-G6 340 | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 340 | 315.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.738 | 60 | 2 | N | 10.68 | 40.24 | 10.16 | 33.45 | 45.7 | -0.364 | 0.042 | -0.273 |  |  | 2.0027 | 32.771 | 8.027 | 31.2295 | [6 empty] | 2019-06-17
Hanwha Q CELLS | Q.PEAK DUO-G6+ 340 | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 340 | 316 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.68 | 40.24 | 10.16 | 33.45 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 1.9763 | 31.7101 | 8.0177 | 30.3497 | [6 empty] | 2020-02-03
Hanwha Q CELLS | Q.PEAK DUO-G6+/SC 340 | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 340 | 316 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.68 | 40.24 | 10.16 | 33.45 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 1.9763 | 31.7101 | 8.0177 | 30.3497 | [6 empty] | 2020-02-03
Hanwha Q CELLS | Q.PEAK DUO-G8 340 | 340W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 340 | 318 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.63 | 40.2 | 10.12 | 33.61 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.016 | 32.2357 | 8.0144 | 31.2745 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO-G8+ 340 | 340W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 340 | 318 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.63 | 40.2 | 10.12 | 33.61 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.016 | 32.2357 | 8.0144 | 31.2745 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PLUS L-G4.2 340 | 340 W Polycrystalline Module | UL 1703 | 340 | 312.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.59 | 47.07 | 9.03 | 37.63 | 45.22 | -0.398 | 0.05 | -0.294 | 0 | -0.398 | 1.8029 | 36.4988 | 7.2547 | 34.6497 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19354
Hanwha Q CELLS | Q.PLUS L-G4.2/TAA 340 | 340 W Polycrystalline Module | UL 1703 | 340 | 312.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.59 | 47.07 | 9.03 | 37.63 | 45.22 | -0.398 | 0.05 | -0.294 | 0 | -0.398 | 1.8029 | 36.4988 | 7.2547 | 34.6497 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19354
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+ 345 | 345 W, 120 half-cut cell monocrystalline module, black backsheet and frame, 1000V max system Vdc | UL 1703 | 345 | 322.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.734 | 60 | 2 | N | 10.58 | 40.92 | 10.07 | 34.25 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9504 | 33.0367 | 7.9085 | 31.9874 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/AC 345 | 345 W, 120 half-cut cell monocrystalline ACPV module, black backsheet. DC module:Q.PEAK DUO BLK-G6+ 345. Microinverter: IQ7PLUS-72-x-ACM-US-y | UL 1741 | 345 | 322.8 | This component is specific to ACPV modules and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.58 | 40.92 | 10.07 | 34.25 | 44.4 | -0.343 | 0.044 | -0.269 |  |  | 1.95 | 33.04 | 7.91 | 32 | [6 empty] | 2020-07-13
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/HL 345 | 345 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 345 | 322.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.58 | 40.92 | 10.07 | 34.25 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9504 | 33.0367 | 7.9085 | 31.9874 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/SC 345 | 345 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 345 | 322.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.58 | 40.92 | 10.07 | 34.25 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9504 | 33.0367 | 7.9085 | 31.9874 | [6 empty] | 2020-01-13 | 2021-04-12
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/TS 345 | 345 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 345 | 322.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.58 | 40.92 | 10.07 | 34.25 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.9504 | 33.0367 | 7.9085 | 31.9874 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO BLK-G8 345 | 345 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 345 | 320 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.68 | 40.45 | 10.17 | 33.92 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.931 | 32.485 | 7.843 | 31.246 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G8+ 345 | 345 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 345 | 320 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.68 | 40.45 | 10.17 | 33.92 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.931 | 32.485 | 7.843 | 31.246 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO-G6 345 | 345 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 345 | 320.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.73 | 40.49 | 10.22 | 33.76 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 1.988 | 32.004 | 8.065 | 30.631 | [6 empty] | 2019-06-17 | 2021-08-23
Hanwha Q CELLS | Q.PEAK DUO-G6+ 345 | 345 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 345 | 320.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.73 | 40.49 | 10.22 | 33.76 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 1.988 | 32.004 | 8.065 | 30.631 | [6 empty] | 2020-02-03
Hanwha Q CELLS | Q.PEAK DUO-G6+/SC 345 | 345 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 345 | 320.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.73 | 40.49 | 10.22 | 33.76 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 1.988 | 32.004 | 8.065 | 30.631 | [6 empty] | 2020-02-03
Hanwha Q CELLS | Q.PEAK DUO-G8 345 | 345W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 345 | 322.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.68 | 40.45 | 10.17 | 33.92 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.026 | 32.533 | 8.054 | 31.563 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO-G8+ 345 | 345W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 345 | 322.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.68 | 40.45 | 10.17 | 33.92 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.026 | 32.533 | 8.054 | 31.563 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK L-G4.1 345 | Silver frame, white backsheet Q.ANTUM Mono Cells | UL 1703 | 345 | 316.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.994 | 72 |  | N | 9.6 | 46.86 | 9.03 | 38.22 | 45.51 | -0.394 | 0.038 | -0.289 | -0.361 | -0.391 | 1.815 | 37.569 | 7.272 | 35.348 | [6 empty] | 2017-08-01
Hanwha Q CELLS | Q.PLUS L-G4.2 345 | 345 W Polycrystalline Module | UL 1703 | 345 | 316.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.64 | 47.32 | 9.09 | 37.93 | 45.22 | -0.398 | 0.05 | -0.294 | 0 | -0.398 | 1.8149 | 36.7898 | 7.3029 | 34.9259 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19354
Hanwha Q CELLS | Q.PLUS L-G4.2/TAA 345 | 345 W Polycrystalline Module | UL 1703 | 345 | 316.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.64 | 47.46 | 9.09 | 37.93 | 45.22 | -0.398 | 0.05 | -0.294 | 0 | -0.398 | 1.8149 | 36.7898 | 7.3029 | 34.9259 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19354
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+ 350 | 350 W, 120 half-cut cell monocrystalline module, black backsheet and frame, 1000V max system Vdc | UL 1703 | 350 | 327.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.734 | 60 | 2 | N | 10.63 | 41.17 | 10.13 | 34.56 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.962 | 33.3357 | 7.9557 | 32.2769 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/HL 350 | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 350 | 327.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.63 | 41.17 | 10.13 | 34.56 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.962 | 33.3357 | 7.9557 | 32.2769 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/SC 350 | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 350 | 327.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.63 | 41.17 | 10.13 | 34.56 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.962 | 33.3357 | 7.9557 | 32.2769 | [6 empty] | 2021-04-12
Hanwha Q CELLS | Q.PEAK DUO BLK-G6+/TS 350 | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 350 | 327.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.63 | 41.17 | 10.13 | 34.56 | 44.36 | -0.343 | 0.044 | -0.269 |  |  | 1.962 | 33.3357 | 7.9557 | 32.2769 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO BLK-G8 350 | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 350 | 324.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.74 | 40.7 | 10.22 | 34.24 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9405 | 32.7915 | 7.8816 | 31.5408 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G8+ 350 | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 350 | 324.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.74 | 40.7 | 10.22 | 34.24 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9405 | 32.7915 | 7.8816 | 31.5408 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO-G6 350 | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 350 | 325.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.79 | 40.73 | 10.27 | 34.07 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 1.9977 | 32.2979 | 8.1045 | 30.9123 | [6 empty] | 2021-08-23
Hanwha Q CELLS | Q.PEAK DUO-G6+ 350 | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 350 | 325.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.79 | 40.73 | 10.27 | 34.07 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 1.9977 | 32.2979 | 8.1045 | 30.9123 | [6 empty] | 2020-02-03
Hanwha Q CELLS | Q.PEAK DUO-G6+/SC 350 | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 350 | 325.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.79 | 40.73 | 10.27 | 34.07 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 1.9977 | 32.2979 | 8.1045 | 30.9123 | [6 empty] | 2020-02-03
Hanwha Q CELLS | Q.PEAK DUO-G8 350 | 350W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 350 | 327.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.74 | 40.7 | 10.22 | 34.24 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.036 | 32.8399 | 8.0936 | 31.8608 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO-G8+ 350 | 350W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 350 | 327.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.74 | 40.7 | 10.22 | 34.24 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.036 | 32.8399 | 8.0936 | 31.8608 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK L-G4.1 350 | Silver frame, white backsheet Q.ANTUM Mono Cells | UL 1703 | 350 | 321.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.994 | 72 |  | N | 9.65 | 47.14 | 9.1 | 38.44 | 45.51 | -0.394 | 0.038 | -0.289 | -0.361 | -0.391 | 1.815 | 37.569 | 7.272 | 35.348 | [6 empty] | 2017-08-01
Hanwha Q CELLS | Q.PLUS L-G4.2 350 | 350 W, 72 cell polycrystalline module, white backsheet, 1500V or 1000V max system Vdc | UL 1703 | 350 | 321.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.64 | 46.82 | 9.16 | 38.2 | 45.22 | -0.398 | 0.05 | -0.294 |  |  | 1.7993 | 37.0447 | 7.2402 | 35.1679 | [6 empty] | 2020-01-21
Hanwha Q CELLS | Q.PLUS L-G4.2/TAA 350 | 350 W Polycrystalline Module | UL 1703 | 350 | 321.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.994 | 72 | 1 | N | 9.69 | 47.71 | 9.15 | 38.23 | 45.22 | -0.398 | 0.05 | -0.294 | 0 | -0.398 | 1.8269 | 37.0807 | 7.3511 | 35.2022 | Rack | Flat Plate | 1 | 1.994 | 1 | 0.19355
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9 355 | 355 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 355 | 328.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.49 | 44.81 | 9.85 | 36.03 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 1.972 | 35.6327 | 7.7804 | 33.336 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9+ 355 | 355 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 355 | 328.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.49 | 44.81 | 9.85 | 36.03 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 1.972 | 35.6327 | 7.7804 | 33.336 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK-G8 355 | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 355 | 329.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.79 | 40.95 | 10.28 | 34.55 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9519 | 33.0883 | 7.9278 | 31.8263 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G8+ 355 | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 355 | 329.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.79 | 40.95 | 10.28 | 34.55 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9519 | 33.0883 | 7.9278 | 31.8263 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO ML-G9 355 | 355 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 355 | 327.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.49 | 44.81 | 9.85 | 36.03 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 1.9622 | 35.5395 | 7.8198 | 32.8271 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 355 | 355 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 355 | 327.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.49 | 44.81 | 9.85 | 36.03 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 1.9622 | 35.5395 | 7.8198 | 32.8271 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO-G6 355 | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 355 | 330.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.84 | 40.98 | 10.33 | 34.38 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 2.0094 | 32.5918 | 8.1518 | 31.1935 | [6 empty] | 2021-08-23
Hanwha Q CELLS | Q.PEAK DUO-G6+ 355 | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 355 | 330.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.84 | 40.98 | 10.33 | 34.38 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 2.0094 | 32.5918 | 8.1518 | 31.1935 | [6 empty] | 2020-02-03
Hanwha Q CELLS | Q.PEAK DUO-G6+/SC 355 | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 355 | 330.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.84 | 40.98 | 10.33 | 34.38 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 2.0094 | 32.5918 | 8.1518 | 31.1935 | [6 empty] | 2020-02-03
Hanwha Q CELLS | Q.PEAK DUO-G8 355 | 355W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 355 | 332.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.79 | 40.95 | 10.28 | 34.55 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.0479 | 33.1372 | 8.1411 | 32.1492 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO-G8+ 355 | 355W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 355 | 332.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.79 | 40.95 | 10.28 | 34.55 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.0479 | 33.1372 | 8.1411 | 32.1492 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK L-G4.1 355 | Silver frame, white backsheet Q.ANTUM Mono Cells | UL 1703 | 355 | 326.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.994 | 72 |  | N | 9.71 | 47.43 | 9.18 | 38.67 | 45.51 | -0.394 | 0.038 | -0.289 | -0.361 | -0.391 | 1.815 | 37.569 | 7.272 | 35.348 | [6 empty] | 2017-08-01
Hanwha Q CELLS | Q.PLUS DUO L-G5.2 355 | 355 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 328.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.951 | 72 | 2 | N | 9.82 | 46.57 | 9.28 | 38.24 | 45.36 | -0.362 | 0.05 | -0.274 |  |  | 1.808 | 37.437 | 7.308 | 36.089 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PLUS DUO L-G5.3 355 | 355 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 328.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.951 | 72 | 2 | N | 9.82 | 46.57 | 9.28 | 38.24 | 45.36 | -0.362 | 0.05 | -0.274 |  |  | 1.808 | 37.437 | 7.308 | 36.089 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9 360 | 360 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 360 | 333 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.52 | 44.85 | 9.91 | 36.32 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 1.984 | 35.9195 | 7.8278 | 33.6043 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9+ 360 | 360 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 360 | 333 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.52 | 44.85 | 9.91 | 36.32 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 1.984 | 35.9195 | 7.8278 | 33.6043 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK-G8 360 | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 360 | 334.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.84 | 41.19 | 10.33 | 34.85 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9614 | 33.3757 | 7.9664 | 32.1027 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO BLK-G8+ 360 | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V or 1000V max system Vdc | UL 61730 | 360 | 334.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.84 | 41.19 | 10.33 | 34.85 | 46.71 | -0.345 | 0.039 | -0.272 |  |  | 1.9614 | 33.3757 | 7.9664 | 32.1027 | [6 empty] | 2021-02-11
Hanwha Q CELLS | Q.PEAK DUO ML-G9 360 | 360 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 360 | 332.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.52 | 44.85 | 9.91 | 36.32 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 1.9742 | 35.8255 | 7.8674 | 33.0913 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 360 | 360 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 360 | 332.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.52 | 44.85 | 9.91 | 36.32 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 1.9742 | 35.8255 | 7.8674 | 33.0913 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO-G6 360 | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 360 | 335.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.73 | 60 | 2 | N | 10.9 | 41.23 | 10.38 | 34.69 | 45.15 | -0.36 | 0.047 | -0.276 |  |  | 2.0191 | 32.8856 | 8.1913 | 31.4748 | [6 empty] | 2021-08-23
Hanwha Q CELLS | Q.PEAK DUO-G8 360 | 360W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 360 | 337.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.84 | 41.19 | 10.33 | 34.85 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.0579 | 33.425 | 8.1807 | 32.4284 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK DUO-G8+ 360 | 360W, 120 half-cell Mono c-Si PV Module, Q.ANTUM | UL 61730 | 360 | 337.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.732 | 60 | 2 | N | 10.84 | 41.19 | 10.33 | 34.85 | 44.4 | -0.343 | 0.043 | -0.27 |  |  | 2.0579 | 33.425 | 8.1807 | 32.4284 | [6 empty] | 2020-08-21
Hanwha Q CELLS | Q.PEAK L-G4.1 360 | Silver frame, white backsheet Q.ANTUM Mono Cells | UL 1703 | 360 | 330.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.994 | 72 |  | N | 9.77 | 47.71 | 9.26 | 38.89 | 45.51 | -0.394 | 0.038 | -0.289 | -0.361 | -0.391 | 1.815 | 37.569 | 7.272 | 35.348 | [6 empty] | 2017-08-01
Hanwha Q CELLS | Q.PEAK L-G4.2 360 | 360 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V or 1000V max system Vdc | UL 1703 | 360 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.927 | 72 | 1 | N | 9.77 | 47.71 | 9.26 | 38.89 | 45.51 | -0.394 | 0.038 | -0.289 | -0.361 | -0.391 | 1.815 | 37.569 | 7.253 | 35.518 | [6 empty] | 2017-08-01 | 2019-12-02
Hanwha Q CELLS | Q.PLUS DUO L-G5.2 360 | 360 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 333.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.951 | 72 | 2 | N | 9.87 | 46.8 | 9.35 | 38.52 | 45.36 | -0.362 | 0.05 | -0.274 |  |  | 1.8216 | 37.7111 | 7.3631 | 36.3533 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PLUS DUO L-G5.3 360 | 360 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 333.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.951 | 72 | 2 | N | 9.87 | 46.8 | 9.35 | 38.52 | 45.36 | -0.362 | 0.05 | -0.274 |  |  | 1.8216 | 37.7111 | 7.3631 | 36.3533 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9 365 | 365 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 365 | 337.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.55 | 44.89 | 9.97 | 36.61 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 1.996 | 36.2063 | 7.8752 | 33.8726 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9+ 365 | 365 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 365 | 337.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.55 | 44.89 | 9.97 | 36.61 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 1.996 | 36.2063 | 7.8752 | 33.8726 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9 365 | 365 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 365 | 337 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.55 | 44.89 | 9.97 | 36.61 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 1.9861 | 36.1116 | 7.915 | 33.3556 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 365 | 365 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 365 | 337 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.55 | 44.89 | 9.97 | 36.61 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 1.9861 | 36.1116 | 7.915 | 33.3556 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK L-G4.2 365 | 365 W Monocrystalline Module | UL 1703 | 365 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9464 | 72 | 1 | N | 9.83 | 48 | 9.33 | 39.1 | 45.51 | -0.394 | 0.038 | -0.289 | -0.361 | -0.391 | 1.8703 | 38.228 | 7.4937 | 35.968 | Rack | Flat Plate | 0.988 | 1.97 | 1 | 0.19589
Hanwha Q CELLS | Q.PLUS DUO L-G5.2 365 | 365 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 338.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.951 | 72 | 2 | N | 9.92 | 47.03 | 9.41 | 38.79 | 45.36 | -0.362 | 0.05 | -0.274 |  |  | 1.8333 | 37.9755 | 7.4104 | 36.6081 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PLUS DUO L-G5.3 365 | 365 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 338.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.951 | 72 | 2 | N | 9.92 | 47.03 | 9.41 | 38.79 | 45.36 | -0.362 | 0.05 | -0.274 |  |  | 1.8333 | 37.9755 | 7.4104 | 36.6081 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9 370 | 370 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 370 | 342.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.58 | 44.92 | 10.03 | 36.9 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.008 | 36.4931 | 7.9226 | 34.1409 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9+ 370 | 370 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 370 | 342.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.58 | 44.92 | 10.03 | 36.9 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.008 | 36.4931 | 7.9226 | 34.1409 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9 370 | 370 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 370 | 341.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.58 | 44.92 | 10.03 | 36.9 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 1.9981 | 36.3976 | 7.9627 | 33.6198 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 370 | 370 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 370 | 341.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.58 | 44.92 | 10.03 | 36.9 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 1.9981 | 36.3976 | 7.9627 | 33.6198 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK L-G4.2 370 | 370 W Monocrystalline Module | UL 1703 | 370 | 340.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9464 | 72 | 1 | N | 9.89 | 48.28 | 9.41 | 39.32 | 45.51 | -0.394 | 0.038 | -0.289 | -0.361 | -0.391 | 1.8864 | 38.4431 | 7.5579 | 36.1704 | Rack | Flat Plate | 0.988 | 1.97 | 1 | 0.19599
Hanwha Q CELLS | Q.PLUS DUO L-G5.2 370 | 370 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 343.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.951 | 72 | 2 | N | 9.96 | 47.26 | 9.47 | 39.05 | 45.36 | -0.362 | 0.05 | -0.274 |  |  | 1.845 | 38.23 | 7.4576 | 36.8534 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PLUS DUO L-G5.3 370 | 370 W, 144 half cut cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 343.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.951 | 72 | 2 | N | 9.96 | 47.26 | 9.47 | 39.05 | 45.36 | -0.362 | 0.05 | -0.274 |  |  | 1.845 | 38.23 | 7.4576 | 36.8534 | [6 empty] | 2019-09-03
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9 375 | 375 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 375 | 347.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.62 | 44.96 | 10.09 | 37.18 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.02 | 36.77 | 7.97 | 34.4 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9+ 375 | 375 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 375 | 347.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.62 | 44.96 | 10.09 | 37.18 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.02 | 36.77 | 7.97 | 34.4 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9 375 | 375 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 375 | 346.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.62 | 44.96 | 10.09 | 37.18 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.01 | 36.6738 | 8.0103 | 33.8749 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 375 | 375 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 375 | 346.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.62 | 44.96 | 10.09 | 37.18 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.01 | 36.6738 | 8.0103 | 33.8749 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK L-G4.2 375 | 375 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V or 1000V max system Vdc | UL 1703 | 375 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.927 | 72 | 1 | N | 10 | 48.17 | 9.52 | 39.4 | 45.51 | -0.394 | 0.038 | -0.289 |  |  | 1.866 | 38.0617 | 7.4566 | 35.9838 | [6 empty] | 2019-12-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10 380 | 380 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 352.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.01 | 45.16 | 10.53 | 36.09 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0566 | 35.5972 | 8.2065 | 34.2076 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a 380 | 380 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 352.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.01 | 45.16 | 10.53 | 36.09 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0566 | 35.5972 | 8.2065 | 34.2076 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a+ 380 | 380 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 352.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.01 | 45.16 | 10.53 | 36.09 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0566 | 35.5972 | 8.2065 | 34.2076 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10+ 380 | 380 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 352.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.01 | 45.16 | 10.53 | 36.09 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0566 | 35.5972 | 8.2065 | 34.2076 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9 380 | 380 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 352 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.65 | 44.99 | 10.14 | 37.46 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.03 | 37.0469 | 8.0095 | 34.6591 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9+ 380 | 380 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 352 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.65 | 44.99 | 10.14 | 37.46 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.03 | 37.0469 | 8.0095 | 34.6591 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO L-G5.2 380 | 380 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 351.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.015 | 72 | 2 | N | 10.05 | 47.95 | 9.57 | 39.71 | 46.35 | -0.354 | 0.04 | -0.272 | 1.892 | 38.835 | 1.892 | 38.835 | 7.547 | 36.887 | [6 empty] | 2018-06-15 | 2019-06-03
Hanwha Q CELLS | Q.PEAK DUO L-G5.3 380 | 380 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 351.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.015 | 72 | 2 | N | 10.05 | 47.95 | 9.57 | 39.71 | 46.35 | -0.354 | 0.04 | -0.272 | 1.892 | 38.835 | 1.892 | 38.835 | 7.547 | 36.887 | 36.887 | [5 empty] | 2019-06-03
Hanwha Q CELLS | Q.PEAK DUO ML-G10 380 | 380 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.01 | 45.16 | 10.53 | 36.09 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0647 | 34.9451 | 8.249 | 33.8099 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a 380 | 380 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.01 | 45.16 | 10.53 | 36.09 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0647 | 34.9451 | 8.249 | 33.8099 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a+ 380 | 380 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.01 | 45.16 | 10.53 | 36.09 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0647 | 34.9451 | 8.249 | 33.8099 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10+ 380 | 380 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.01 | 45.16 | 10.53 | 36.09 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0647 | 34.9451 | 8.249 | 33.8099 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G9 380 | 380 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 351.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.65 | 44.99 | 10.14 | 37.46 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.02 | 36.95 | 8.09 | 34.13 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 380 | 380 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 351.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.65 | 44.99 | 10.14 | 37.46 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.02 | 36.95 | 8.09 | 34.13 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10 385 | 385 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 357.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.04 | 45.19 | 10.59 | 36.36 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0683 | 35.8635 | 8.2532 | 34.4636 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a 385 | 385 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 357.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.04 | 45.19 | 10.59 | 36.36 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0683 | 35.8635 | 8.2532 | 34.4636 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a+ 385 | 385 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 357.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.04 | 45.19 | 10.59 | 36.36 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0683 | 35.8635 | 8.2532 | 34.4636 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10+ 385 | 385 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 357.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.04 | 45.19 | 10.59 | 36.36 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0683 | 35.8635 | 8.2532 | 34.4636 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9 385 | 385 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 356.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.68 | 45.03 | 10.2 | 37.74 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.042 | 37.3238 | 8.0569 | 34.9181 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9+ 385 | 385 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 356.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.68 | 45.03 | 10.2 | 37.74 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.042 | 37.3238 | 8.0569 | 34.9181 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO L-G5.2 385 | 385 W, 144 half cells monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 356.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 144 |  | N | 10.1 | 48.21 | 9.61 | 40.05 | 46.35 | -0.354 | 0.04 | -0.272 | -0.001 | -0.354 | 1.8999 | 39.1675 | 7.5785 | 37.2028 | [6 empty] | 2018-06-15 | 2018-08-01
Hanwha Q CELLS | Q.PEAK DUO L-G5.3 385 | 385 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 356.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.015 | 72 | 2 | N | 10.1 | 48.21 | 9.61 | 40.05 | 46.35 | -0.354 | 0.04 | -0.272 | 1.8999 | 39.1675 | 1.8999 | 39.1675 | 7.5785 | 37.2028 | 37.2028 | [5 empty] | 2019-06-03
Hanwha Q CELLS | Q.PEAK DUO L-G7 385 | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 385 | 358.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.05 | 48.17 | 9.57 | 40.24 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8645 | 38.2939 | 7.5559 | 37.1044 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.2 385 | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730, UL 1703 | 385 | 358.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.05 | 48.17 | 9.57 | 40.24 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8645 | 38.2939 | 7.5559 | 37.1044 | [6 empty] | 2020-01-13 | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.3 385 | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 358.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.05 | 48.17 | 9.57 | 40.24 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8645 | 38.2939 | 7.5559 | 37.1044 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO ML-G10 385 | 385 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 359.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.04 | 45.19 | 10.59 | 36.36 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0765 | 35.2065 | 8.296 | 34.0629 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a 385 | 385 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 359.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.04 | 45.19 | 10.59 | 36.36 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0765 | 35.2065 | 8.296 | 34.0629 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a+ 385 | 385 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 359.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.04 | 45.19 | 10.59 | 36.36 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0765 | 35.2065 | 8.296 | 34.0629 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10+ 385 | 385 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 359.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.04 | 45.19 | 10.59 | 36.36 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0765 | 35.2065 | 8.296 | 34.0629 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G9 385 | 385 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 356.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.68 | 45.03 | 10.2 | 37.74 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.032 | 37.2262 | 8.0976 | 34.3851 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 385 | 385 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 385 | 356.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.68 | 45.03 | 10.2 | 37.74 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.032 | 37.2262 | 8.0976 | 34.3851 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10 390 | 390 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.07 | 45.23 | 10.65 | 36.62 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.08 | 36.12 | 8.3 | 34.71 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a 390 | 390 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.07 | 45.23 | 10.65 | 36.62 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.08 | 36.12 | 8.3 | 34.71 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a+ 390 | 390 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.07 | 45.23 | 10.65 | 36.62 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.08 | 36.12 | 8.3 | 34.71 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10+ 390 | 390 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.07 | 45.23 | 10.65 | 36.62 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.08 | 36.12 | 8.3 | 34.71 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9 390 | 390 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 361.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.71 | 45.06 | 10.26 | 38.01 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.054 | 37.5908 | 8.1043 | 35.1679 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G9+ 390 | 390 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 361.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.71 | 45.06 | 10.26 | 38.01 | 46.3 | -0.3637 | 0.078 | -0.3039 |  |  | 2.054 | 37.5908 | 8.1043 | 35.1679 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO L-G5.2 390 | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 363.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.963 | 72 | 2 | N | 10.14 | 48.48 | 9.66 | 40.38 | 44.59 | -0.359 | 0.04 | -0.273 | -0.001 | -0.354 | 1.883 | 38.698 | 7.605 | 37.107 | [6 empty] | 2018-06-15 | 2019-08-15
Hanwha Q CELLS | Q.PEAK DUO L-G5.3 390 | 390 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 361.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.015 | 72 | 2 | N | 10.14 | 48.48 | 9.66 | 40.38 | 46.35 | -0.354 | 0.04 | -0.272 | 1.9098 | 39.4902 | 1.9098 | 39.4902 | 7.618 | 37.5094 | 37.5094 | [5 empty] | 2019-06-03
Hanwha Q CELLS | Q.PEAK DUO L-G7 390 | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 390 | 363.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.44 | 9.61 | 40.57 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8723 | 38.608 | 7.5875 | 37.4087 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.2 390 | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730, UL 1703 | 390 | 363.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.44 | 9.61 | 40.57 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8723 | 38.608 | 7.5875 | 37.4087 | [6 empty] | 2020-01-13 | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.3 390 | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 363.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.44 | 9.61 | 40.57 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8723 | 38.608 | 7.5875 | 37.4087 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO ML-G10 390 | 390 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 364 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.1 | 45.23 | 10.65 | 36.62 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0882 | 35.4582 | 8.343 | 34.3064 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a 390 | 390 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 364 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.1 | 45.23 | 10.65 | 36.62 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0882 | 35.4582 | 8.343 | 34.3064 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a+ 390 | 390 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 364 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.1 | 45.23 | 10.65 | 36.62 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0882 | 35.4582 | 8.343 | 34.3064 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10+ 390 | 390 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 364 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.1 | 45.23 | 10.65 | 36.62 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.0882 | 35.4582 | 8.343 | 34.3064 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G9 390 | 390 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 360.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.71 | 45.06 | 10.26 | 38.01 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.0439 | 37.4925 | 8.1453 | 34.6311 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 390 | 390 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 390 | 360.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.71 | 45.06 | 10.26 | 38.01 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.0439 | 37.4925 | 8.1453 | 34.6311 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10 395 | 395 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.1 | 45.27 | 10.71 | 36.88 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0917 | 36.3765 | 8.3468 | 34.9564 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a 395 | 395 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.1 | 45.27 | 10.71 | 36.88 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0917 | 36.3765 | 8.3468 | 34.9564 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a+ 395 | 395 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.1 | 45.27 | 10.71 | 36.88 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0917 | 36.3765 | 8.3468 | 34.9564 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10+ 395 | 395 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.1 | 45.27 | 10.71 | 36.88 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.0917 | 36.3765 | 8.3468 | 34.9564 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO L-G5.2 395 | 395 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 366 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.015 | 72 | 2 | N | 10.19 | 48.74 | 9.7 | 40.71 | 46.35 | -0.354 | 0.04 | -0.272 | 1.9177 | 39.813 | 1.9177 | 39.813 | 7.6495 | 37.8159 | [6 empty] | 2019-06-03
Hanwha Q CELLS | Q.PEAK DUO L-G5.3 395 | 395 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 366 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.015 | 72 | 2 | N | 10.19 | 48.74 | 9.7 | 40.71 | 46.35 | -0.354 | 0.04 | -0.272 | 1.9177 | 39.813 | 1.9177 | 39.813 | 7.6495 | 37.8159 | 37.8159 | [5 empty] | 2019-06-03
Hanwha Q CELLS | Q.PEAK DUO L-G7 395 | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 395 | 367.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.14 | 48.7 | 9.66 | 40.9 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.882 | 38.922 | 7.627 | 37.713 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.2 395 | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730, UL 1703 | 395 | 367.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.14 | 48.7 | 9.66 | 40.9 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.882 | 38.922 | 7.627 | 37.713 | [6 empty] | 2020-01-13 | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.3 395 | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 367.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.14 | 48.7 | 9.66 | 40.9 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.882 | 38.922 | 7.627 | 37.713 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO ML-G10 395 | 395 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 368.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.14 | 45.27 | 10.71 | 36.88 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1 | 35.71 | 8.39 | 34.55 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a 395 | 395 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 368.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.14 | 45.27 | 10.71 | 36.88 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1 | 35.71 | 8.39 | 34.55 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a+ 395 | 395 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 368.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.14 | 45.27 | 10.71 | 36.88 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1 | 35.71 | 8.39 | 34.55 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10+ 395 | 395 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 368.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.14 | 45.27 | 10.71 | 36.88 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1 | 35.71 | 8.39 | 34.55 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G9 395 | 395 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 365.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.74 | 45.1 | 10.32 | 38.29 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.0559 | 37.7687 | 8.1929 | 34.8862 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 395 | 395 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 395 | 365.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.74 | 45.1 | 10.32 | 38.29 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.0559 | 37.7687 | 8.1929 | 34.8862 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10 400 | 400 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 371.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.14 | 45.3 | 10.77 | 37.13 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1034 | 36.623 | 8.3935 | 35.1934 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a 400 | 400 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 371.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.14 | 45.3 | 10.77 | 37.13 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1034 | 36.623 | 8.3935 | 35.1934 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a+ 400 | 400 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 371.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.14 | 45.3 | 10.77 | 37.13 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1034 | 36.623 | 8.3935 | 35.1934 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10+ 400 | 400 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 371.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.14 | 45.3 | 10.77 | 37.13 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1034 | 36.623 | 8.3935 | 35.1934 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO L-G5.2 400 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 373 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.963 | 72 | 2 | N | 10.24 | 49 | 9.75 | 41.04 | 44.59 | -0.359 | 0.04 | -0.273 |  |  | 1.9005 | 39.3305 | 7.6759 | 37.7135 | [6 empty] | 2019-08-15
Hanwha Q CELLS | Q.PEAK DUO L-G5.3 400 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 373 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.963 | 72 | 2 | N | 10.24 | 49 | 9.75 | 41.04 | 44.59 | -0.359 | 0.04 | -0.273 |  |  | 1.9005 | 39.3305 | 7.6759 | 37.7135 | [6 empty] | 2019-08-15
Hanwha Q CELLS | Q.PEAK DUO L-G6 400 | 400 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 400 | 371.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.6 | 47.89 | 10.09 | 39.63 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 1.987 | 38.558 | 7.962 | 36.959 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.2 400 | 400 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 371.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.6 | 47.89 | 10.09 | 39.63 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 1.987 | 38.558 | 7.962 | 36.959 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BFG 400 | 400 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 400 | 373.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.6 | 47.89 | 10.09 | 39.63 | 45.5 | -0.334 | 0.041 | -0.263 | 1.9875 | 38.2993 | 1.9875 | 38.2993 | 8.0396 | 36.9977 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BGT 400 | 400 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 400 | 373.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.6 | 47.89 | 10.09 | 39.63 | 45.5 | -0.334 | 0.041 | -0.263 |  |  | 1.9875 | 38.2993 | 8.0396 | 36.9977 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G7 400 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 400 | 372.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.19 | 48.96 | 9.7 | 41.23 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8898 | 39.236 | 7.6586 | 38.0173 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.2 400 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730, UL 1703 | 400 | 372.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.19 | 48.96 | 9.7 | 41.23 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8898 | 39.236 | 7.6586 | 38.0173 | [6 empty] | 2020-01-13 | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.3 400 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 372.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.19 | 48.96 | 9.7 | 41.23 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8898 | 39.236 | 7.6586 | 38.0173 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G8 400 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 400 | 372.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.55 | 47.85 | 10.05 | 39.82 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 1.9863 | 38.3296 | 8.0518 | 36.9475 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.2 400 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 372.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.55 | 47.85 | 10.05 | 39.82 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 1.9863 | 38.3296 | 8.0518 | 36.9475 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3 400 | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 372.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.55 | 47.85 | 10.05 | 39.82 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 1.9863 | 38.3296 | 8.0518 | 36.9475 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO ML-G10 400 | 400 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 373.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.17 | 45.3 | 10.77 | 37.13 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1118 | 35.9521 | 8.437 | 34.7842 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a 400 | 400 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 373.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.17 | 45.3 | 10.77 | 37.13 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1118 | 35.9521 | 8.437 | 34.7842 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a+ 400 | 400 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 373.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.17 | 45.3 | 10.77 | 37.13 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1118 | 35.9521 | 8.437 | 34.7842 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10+ 400 | 400 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 373.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.17 | 45.3 | 10.77 | 37.13 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1118 | 35.9521 | 8.437 | 34.7842 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G9 400 | 400 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 370.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.77 | 45.14 | 10.38 | 38.55 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.0678 | 38.0252 | 8.2405 | 35.1231 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO ML-G9+ 400 | 400 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 400 | 370.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 66 | 2 | N | 10.77 | 45.14 | 10.38 | 38.55 | 46.3 | -0.373 | 0.0807 | -0.3113 |  |  | 2.0678 | 38.0252 | 8.2405 | 35.1231 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10 405 | 405 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 376.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.17 | 45.34 | 10.83 | 37.39 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1152 | 36.8795 | 8.4403 | 35.4398 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a 405 | 405 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 376.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.17 | 45.34 | 10.83 | 37.39 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1152 | 36.8795 | 8.4403 | 35.4398 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a+ 405 | 405 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 376.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.17 | 45.34 | 10.83 | 37.39 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1152 | 36.8795 | 8.4403 | 35.4398 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10+ 405 | 405 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 376.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.17 | 45.34 | 10.83 | 37.39 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1152 | 36.8795 | 8.4403 | 35.4398 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO L-G5.2 405 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 405 | 377.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.963 | 72 | 2 | N | 10.28 | 49.26 | 9.79 | 41.36 | 44.59 | -0.359 | 0.04 | -0.273 |  |  | 1.9083 | 39.6372 | 7.7073 | 38.0076 | [6 empty] | 2019-08-15
Hanwha Q CELLS | Q.PEAK DUO L-G6 405 | 405 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 405 | 376.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.65 | 48.14 | 10.14 | 39.95 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 1.9968 | 38.8693 | 8.0015 | 37.2574 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.2 405 | 405 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 405 | 376.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.65 | 48.14 | 10.14 | 39.95 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 1.9968 | 38.8693 | 8.0015 | 37.2574 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.3 405 | 405 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 405 | 376.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.65 | 48.14 | 10.14 | 39.95 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 1.9968 | 38.8693 | 8.0015 | 37.2574 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BFG 405 | 405 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 405 | 378 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.65 | 48.14 | 10.14 | 39.95 | 45.5 | -0.334 | 0.041 | -0.263 | 1.9974 | 38.6086 | 1.9974 | 38.6086 | 8.0794 | 37.2964 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BGT 405 | 405 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 405 | 378 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.65 | 48.14 | 10.14 | 39.95 | 45.5 | -0.334 | 0.041 | -0.263 |  |  | 1.9974 | 38.6086 | 8.0794 | 37.2964 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G7 405 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 405 | 377.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.23 | 49.22 | 9.75 | 41.56 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8995 | 39.5501 | 7.6981 | 38.3216 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.2 405 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730, UL 1703 | 405 | 377.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.23 | 49.22 | 9.75 | 41.56 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8995 | 39.5501 | 7.6981 | 38.3216 | [6 empty] | 2020-01-13 | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.3 405 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 377.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.23 | 49.22 | 9.75 | 41.56 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.8995 | 39.5501 | 7.6981 | 38.3216 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G8 405 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 405 | 377.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.6 | 48.1 | 10.09 | 40.14 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 1.9942 | 38.6376 | 8.0839 | 37.2444 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.2 405 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 377.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.6 | 48.1 | 10.09 | 40.14 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 1.9942 | 38.6376 | 8.0839 | 37.2444 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3 405 | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 377.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.6 | 48.1 | 10.09 | 40.14 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 1.9942 | 38.6376 | 8.0839 | 37.2444 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BFG 405 | 405 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 405 | 379.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.6 | 48.1 | 10.09 | 40.14 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 1.9797 | 38.406 | 8.018 | 37.1947 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BGT 405 | 405 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 405 | 379.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.6 | 48.1 | 10.09 | 40.14 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 1.9797 | 38.406 | 8.018 | 37.1947 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO ML-G10 405 | 405 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 378.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.2 | 45.34 | 10.83 | 37.39 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1235 | 36.2038 | 8.484 | 35.0278 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a 405 | 405 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 378.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.2 | 45.34 | 10.83 | 37.39 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1235 | 36.2038 | 8.484 | 35.0278 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a+ 405 | 405 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 378.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.2 | 45.34 | 10.83 | 37.39 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1235 | 36.2038 | 8.484 | 35.0278 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10+ 405 | 405 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 405 | 378.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.2 | 45.34 | 10.83 | 37.39 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1235 | 36.2038 | 8.484 | 35.0278 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10 410 | 410 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 381 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.2 | 45.37 | 10.89 | 37.64 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1269 | 37.1261 | 8.487 | 35.6768 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a 410 | 410 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 381 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.2 | 45.37 | 10.89 | 37.64 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1269 | 37.1261 | 8.487 | 35.6768 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10.a+ 410 | 410 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 381 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.2 | 45.37 | 10.89 | 37.64 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1269 | 37.1261 | 8.487 | 35.6768 | [6 empty] | 2021-07-12
Hanwha Q CELLS | Q.PEAK DUO BLK ML-G10+ 410 | 410 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 381 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.2 | 45.37 | 10.89 | 37.64 | 45.7 | -0.3621 | 0.0414 | -0.2695 |  |  | 2.1269 | 37.1261 | 8.487 | 35.6768 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO L-G6 410 | 410 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 410 | 381.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.7 | 48.38 | 10.18 | 40.27 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 2.0047 | 39.1807 | 8.033 | 37.5559 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.2 410 | 410 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 410 | 381.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.7 | 48.38 | 10.18 | 40.27 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 2.0047 | 39.1807 | 8.033 | 37.5559 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.3 410 | 410 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 410 | 381.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.7 | 48.38 | 10.18 | 40.27 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 2.0047 | 39.1807 | 8.033 | 37.5559 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BFG 410 | 410 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 410 | 382.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.7 | 48.39 | 10.18 | 40.27 | 45.5 | -0.334 | 0.041 | -0.263 | 2.0053 | 38.9178 | 2.0053 | 38.9178 | 8.1113 | 37.5952 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BGT 410 | 410 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 410 | 382.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.7 | 48.39 | 10.18 | 40.27 | 45.5 | -0.334 | 0.041 | -0.263 |  |  | 2.0053 | 38.9178 | 8.1113 | 37.5952 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G7 410 | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 410 | 382.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.28 | 49.48 | 9.79 | 41.88 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.9073 | 39.8546 | 7.7296 | 38.6166 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.2 410 | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 382.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.28 | 49.48 | 9.79 | 41.88 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.9073 | 39.8546 | 7.7296 | 38.6166 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.3 410 | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 382.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.28 | 49.48 | 9.79 | 41.88 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.9073 | 39.8546 | 7.7296 | 38.6166 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G8 410 | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 410 | 382.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.65 | 48.34 | 10.13 | 40.46 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0021 | 38.9456 | 8.1159 | 37.5414 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.2 410 | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 410 | 382.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.65 | 48.34 | 10.13 | 40.46 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0021 | 38.9456 | 8.1159 | 37.5414 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3 410 | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 410 | 382.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.65 | 48.34 | 10.13 | 40.46 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0021 | 38.9456 | 8.1159 | 37.5414 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BFG 410 | 410 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 410 | 384.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.65 | 48.34 | 10.13 | 40.46 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 1.9875 | 38.7122 | 8.0497 | 37.4912 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BGT 410 | 410 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 410 | 384.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.65 | 48.34 | 10.13 | 40.46 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 1.9875 | 38.7122 | 8.0497 | 37.4912 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO ML-G10 410 | 410 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 383.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.23 | 45.37 | 10.89 | 37.64 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1353 | 36.4459 | 8.531 | 35.262 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a 410 | 410 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 383.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.23 | 45.37 | 10.89 | 37.64 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1353 | 36.4459 | 8.531 | 35.262 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a+ 410 | 410 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 383.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.23 | 45.37 | 10.89 | 37.64 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1353 | 36.4459 | 8.531 | 35.262 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10+ 410 | 410 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 410 | 383.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.23 | 45.37 | 10.89 | 37.64 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1353 | 36.4459 | 8.531 | 35.262 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO L-G6 415 | 415 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 415 | 386 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.74 | 48.63 | 10.23 | 40.58 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 2.0146 | 39.4823 | 8.0725 | 37.845 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.2 415 | 415 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 415 | 386 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.74 | 48.63 | 10.23 | 40.58 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 2.0146 | 39.4823 | 8.0725 | 37.845 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.3 415 | 415 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 415 | 386 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.74 | 48.63 | 10.23 | 40.58 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 2.0146 | 39.4823 | 8.0725 | 37.845 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BFG 415 | 415 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 415 | 387.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.74 | 48.63 | 10.23 | 40.58 | 45.5 | -0.334 | 0.041 | -0.263 | 2.0151 | 39.2174 | 2.0151 | 39.2174 | 8.1511 | 37.8846 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BGT 415 | 415 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 415 | 387.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.74 | 48.63 | 10.23 | 40.58 | 45.5 | -0.334 | 0.041 | -0.263 |  |  | 2.0151 | 39.2174 | 8.1511 | 37.8846 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G7 415 | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 415 | 387.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.32 | 49.74 | 9.83 | 42.2 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.9151 | 40.1591 | 7.7612 | 38.9117 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.2 415 | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 415 | 387.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.32 | 49.74 | 9.83 | 42.2 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.9151 | 40.1591 | 7.7612 | 38.9117 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G7.3 415 | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 415 | 387.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.32 | 49.74 | 9.83 | 42.2 | 45.63 | -0.346 | 0.034 | -0.27 |  |  | 1.9151 | 40.1591 | 7.7612 | 38.9117 | [6 empty] | 2020-09-01
Hanwha Q CELLS | Q.PEAK DUO L-G8 415 | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 415 | 386.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.69 | 48.59 | 10.18 | 40.77 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.012 | 39.244 | 8.156 | 37.829 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.2 415 | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 415 | 386.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.69 | 48.59 | 10.18 | 40.77 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.012 | 39.244 | 8.156 | 37.829 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3 415 | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 415 | 386.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.69 | 48.59 | 10.18 | 40.77 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.012 | 39.244 | 8.156 | 37.829 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BFG 415 | 415 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 415 | 388.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.69 | 48.59 | 10.18 | 40.77 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 1.9973 | 39.0088 | 8.0895 | 37.7785 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BGT 415 | 415 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 415 | 388.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.69 | 48.59 | 10.18 | 40.77 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 1.9973 | 39.0088 | 8.0895 | 37.7785 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO ML-G10 415 | 415 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 415 | 387.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.27 | 45.41 | 10.95 | 37.89 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1471 | 36.688 | 8.578 | 35.4962 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a 415 | 415 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 415 | 387.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.27 | 45.41 | 10.95 | 37.89 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1471 | 36.688 | 8.578 | 35.4962 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10.a+ 415 | 415 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 415 | 387.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.27 | 45.41 | 10.95 | 37.89 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1471 | 36.688 | 8.578 | 35.4962 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO ML-G10+ 415 | 415 W, 132 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 415 | 387.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 66 | 2 | N | 11.27 | 45.41 | 10.95 | 37.89 | 45 | -0.3478 | 0.0557 | -0.2765 |  |  | 2.1471 | 36.688 | 8.578 | 35.4962 | [6 empty] | 2021-08-02
Hanwha Q CELLS | Q.PEAK DUO L-G6.2 420 | 420 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 420 | 390.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.79 | 48.88 | 10.27 | 40.89 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 2.0224 | 39.7839 | 8.104 | 38.1341 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.3 420 | 420 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 420 | 390.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.79 | 48.88 | 10.27 | 40.89 | 45.15 | -0.359 | 0.04 | -0.274 |  |  | 2.0224 | 39.7839 | 8.104 | 38.1341 | [6 empty] | 2019-05-15
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BFG 420 | 420 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 420 | 392.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.79 | 48.88 | 10.27 | 40.89 | 45.5 | -0.334 | 0.041 | -0.263 | 2.023 | 39.517 | 2.023 | 39.517 | 8.183 | 38.174 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BGT 420 | 420 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 420 | 392.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.79 | 48.88 | 10.27 | 40.89 | 45.5 | -0.334 | 0.041 | -0.263 |  |  | 2.023 | 39.517 | 8.183 | 38.174 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G8 420 | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 420 | 391.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.74 | 48.84 | 10.22 | 41.08 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0199 | 39.5424 | 8.188 | 38.1166 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.2 420 | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 391.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.74 | 48.84 | 10.22 | 41.08 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0199 | 39.5424 | 8.188 | 38.1166 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3 420 | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 391.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.74 | 48.84 | 10.22 | 41.08 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0199 | 39.5424 | 8.188 | 38.1166 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BFG 420 | 420 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 420 | 393.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.74 | 48.84 | 10.22 | 41.08 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 2.0052 | 39.3054 | 8.1213 | 38.0657 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BGT 420 | 420 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 420 | 393.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.74 | 48.84 | 10.22 | 41.08 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 2.0052 | 39.3054 | 8.1213 | 38.0657 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO L-G6 425 | 425 W, 144 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 425 | 393.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 72 | 2 | N | 10.83 | 49.13 | 10.32 | 41.2 | 46.4 | -0.359 | 0.0429 | -0.2652 |  |  | 2.05 | 36.93 | 8.26 | 37.74 | [6 empty] | 2020-12-11
Hanwha Q CELLS | Q.PEAK DUO L-G6.2 425 | 425 W, 144 half cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 393.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 72 | 2 | N | 10.83 | 49.13 | 10.32 | 41.2 | 46.4 | -0.359 | 0.0429 | -0.2652 |  |  | 2.05 | 36.93 | 8.26 | 37.74 | [6 empty] | 2020-12-11
Hanwha Q CELLS | Q.PEAK DUO L-G6.3 425 | 425 W, 144 half cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 393.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 72 | 2 | N | 10.83 | 49.13 | 10.32 | 41.2 | 46.4 | -0.359 | 0.0429 | -0.2652 |  |  | 2.05 | 36.93 | 8.26 | 37.74 | [6 empty] | 2020-12-11
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BFG 425 | 425 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 425 | 397.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.83 | 49.13 | 10.32 | 41.2 | 45.5 | -0.334 | 0.041 | -0.263 | 2.0328 | 39.8166 | 2.0328 | 39.8166 | 8.2228 | 38.4634 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BGT 425 | 425 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 425 | 397.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.83 | 49.13 | 10.32 | 41.2 | 45.5 | -0.334 | 0.041 | -0.263 |  |  | 2.0328 | 39.8166 | 8.2228 | 38.4634 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G8 425 | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 425 | 396.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.78 | 49.09 | 10.27 | 41.39 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0298 | 39.8408 | 8.2281 | 38.4043 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.2 425 | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 396.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.78 | 49.09 | 10.27 | 41.39 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0298 | 39.8408 | 8.2281 | 38.4043 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3 425 | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 396.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.78 | 49.09 | 10.27 | 41.39 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0298 | 39.8408 | 8.2281 | 38.4043 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BFG 425 | 425 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 425 | 398.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.78 | 49.09 | 10.27 | 41.39 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 2.015 | 39.602 | 8.161 | 38.353 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO L-G8.3/BGT 425 | 425 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 425 | 398.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.78 | 49.09 | 10.27 | 41.39 | 44.34 | -0.337 | 0.041 | -0.264 |  |  | 2.015 | 39.602 | 8.161 | 38.353 | [6 empty] | 2020-08-03
Hanwha Q CELLS | Q.PEAK DUO L-G6 430 | 430 W, 144 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 430 | 398.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 72 | 2 | N | 10.92 | 49.62 | 10.41 | 41.85 | 46.4 | -0.359 | 0.0429 | -0.2652 |  |  | 2.0679 | 37.5126 | 8.332 | 38.3354 | [6 empty] | 2020-12-11
Hanwha Q CELLS | Q.PEAK DUO L-G6.2 430 | 430 W, 144 half cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 398.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 72 | 2 | N | 10.92 | 49.62 | 10.41 | 41.85 | 46.4 | -0.359 | 0.0429 | -0.2652 |  |  | 2.0679 | 37.5126 | 8.332 | 38.3354 | [6 empty] | 2020-12-11
Hanwha Q CELLS | Q.PEAK DUO L-G6.3 430 | 430 W, 144 half cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 398.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 72 | 2 | N | 10.92 | 49.62 | 10.41 | 41.85 | 46.4 | -0.359 | 0.0429 | -0.2652 |  |  | 2.0679 | 37.5126 | 8.332 | 38.3354 | [6 empty] | 2020-12-11
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BFG 430 | 430 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 430 | 401.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.88 | 49.38 | 10.36 | 41.5 | 45.5 | -0.334 | 0.041 | -0.263 | 2.0407 | 40.1065 | 2.0407 | 40.1065 | 8.2547 | 38.7435 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BGT 430 | 430 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 430 | 401.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.88 | 49.38 | 10.36 | 41.5 | 45.5 | -0.334 | 0.041 | -0.263 |  |  | 2.0407 | 40.1065 | 8.2547 | 38.7435 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G8 430 | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 430 | 401.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.83 | 49.33 | 10.31 | 41.7 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0377 | 40.1392 | 8.2602 | 38.6919 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.2 430 | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 401.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.83 | 49.33 | 10.31 | 41.7 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0377 | 40.1392 | 8.2602 | 38.6919 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3 430 | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 401.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.83 | 49.33 | 10.31 | 41.7 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0377 | 40.1392 | 8.2602 | 38.6919 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO XL-G9 430 | 430 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 430 | 397.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.54 | 53.04 | 9.95 | 43.2 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0096 | 42.3231 | 7.9012 | 39.488 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.2 430 | 430 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 397.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.54 | 53.04 | 9.95 | 43.2 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0096 | 42.3231 | 7.9012 | 39.488 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3 430 | 430 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 397.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.54 | 53.04 | 9.95 | 43.2 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0096 | 42.3231 | 7.9012 | 39.488 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO L-G6 435 | 435 W, 144 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 435 | 403.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 72 | 2 | N | 10.97 | 49.87 | 10.45 | 42.17 | 46.4 | -0.359 | 0.0429 | -0.2652 |  |  | 2.0758 | 37.7995 | 8.3641 | 38.6285 | [6 empty] | 2020-12-11
Hanwha Q CELLS | Q.PEAK DUO L-G6.2 435 | 435 W, 144 half cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 403.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 72 | 2 | N | 10.97 | 49.87 | 10.45 | 42.17 | 46.4 | -0.359 | 0.0429 | -0.2652 |  |  | 2.0758 | 37.7995 | 8.3641 | 38.6285 | [6 empty] | 2020-12-11
Hanwha Q CELLS | Q.PEAK DUO L-G6.3 435 | 435 W, 144 half cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 403.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 72 | 2 | N | 10.97 | 49.87 | 10.45 | 42.17 | 46.4 | -0.359 | 0.0429 | -0.2652 |  |  | 2.0758 | 37.7995 | 8.3641 | 38.6285 | [6 empty] | 2020-12-11
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BFG 435 | 435 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 435 | 406.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.92 | 49.63 | 10.41 | 41.81 | 45.5 | -0.334 | 0.041 | -0.263 | 2.0506 | 40.4061 | 2.0506 | 40.4061 | 8.2946 | 39.0329 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BGT 435 | 435 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 435 | 406.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.92 | 49.63 | 10.41 | 41.81 | 45.5 | -0.334 | 0.041 | -0.263 |  |  | 2.0506 | 40.4061 | 8.2946 | 39.0329 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G8 435 | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 435 | 406 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.87 | 49.58 | 10.36 | 42 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0476 | 40.428 | 8.3002 | 38.9703 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.2 435 | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 406 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.87 | 49.58 | 10.36 | 42 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0476 | 40.428 | 8.3002 | 38.9703 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO L-G8.3 435 | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 406 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.085 | 72 | 2 | N | 10.87 | 49.58 | 10.36 | 42 | 45.73 | -0.338 | 0.04 | -0.267 |  |  | 2.0476 | 40.428 | 8.3002 | 38.9703 | [6 empty] | 2020-08-11
Hanwha Q CELLS | Q.PEAK DUO XL-G9 435 | 435 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 435 | 402.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.57 | 53.07 | 10 | 43.49 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0197 | 42.6073 | 7.9409 | 39.753 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.2 435 | 435 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 402.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.57 | 53.07 | 10 | 43.49 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0197 | 42.6073 | 7.9409 | 39.753 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3 435 | 435 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 402.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.57 | 53.07 | 10 | 43.49 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0197 | 42.6073 | 7.9409 | 39.753 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BFG 440 | 440 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 440 | 411.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.97 | 49.87 | 10.45 | 42.11 | 45.5 | -0.334 | 0.041 | -0.263 | 2.0585 | 40.696 | 2.0585 | 40.696 | 8.3264 | 39.313 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO L-G6.3/BGT 440 | 440 W, 144 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 440 | 411.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.076 | 72 | 2 | N | 10.97 | 49.87 | 10.45 | 42.11 | 45.5 | -0.334 | 0.041 | -0.263 |  |  | 2.0585 | 40.696 | 8.3264 | 39.313 | [6 empty] | 2021-02-01
Hanwha Q CELLS | Q.PEAK DUO XL-G9 440 | 440 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 440 | 407.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.59 | 53.11 | 10.05 | 43.77 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0298 | 42.8816 | 7.9806 | 40.009 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.2 440 | 440 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 407.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.59 | 53.11 | 10.05 | 43.77 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0298 | 42.8816 | 7.9806 | 40.009 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3 440 | 440 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 407.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.59 | 53.11 | 10.05 | 43.77 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0298 | 42.8816 | 7.9806 | 40.009 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3/BFG 440 | 440 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 440 | 408.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 78 | 2 | N | 10.46 | 52.65 | 9.96 | 44.18 | 46.1 | -0.3575 | 0.0267 | -0.2687 |  |  | 1.9762 | 42.8095 | 7.9542 | 40.6068 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO XL-G9 445 | 445 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 445 | 411.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.62 | 53.15 | 10.1 | 44.06 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0399 | 43.1657 | 8.0203 | 40.2741 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.2 445 | 445 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 411.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.62 | 53.15 | 10.1 | 44.06 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0399 | 43.1657 | 8.0203 | 40.2741 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3 445 | 445 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 411.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.62 | 53.15 | 10.1 | 44.06 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0399 | 43.1657 | 8.0203 | 40.2741 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3/BFG 445 | 445 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 445 | 413 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 78 | 2 | N | 10.54 | 53.15 | 10.04 | 44.82 | 46.1 | -0.3575 | 0.0267 | -0.2687 |  |  | 1.9921 | 43.4296 | 8.0181 | 41.1951 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO XL-G9 450 | 450 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 450 | 416.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.65 | 53.18 | 10.15 | 44.34 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.05 | 43.44 | 8.06 | 40.53 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.2 450 | 450 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 416.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.65 | 53.18 | 10.15 | 44.34 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.05 | 43.44 | 8.06 | 40.53 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3 450 | 450 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 416.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.65 | 53.18 | 10.15 | 44.34 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.05 | 43.44 | 8.06 | 40.53 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3/BFG 450 | 450 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 450 | 417.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 78 | 2 | N | 10.54 | 53.15 | 10.04 | 44.82 | 46.1 | -0.3575 | 0.0267 | -0.2687 |  |  | 1.9921 | 43.4296 | 8.0181 | 41.1951 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO XL-G9 455 | 455 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 455 | 421.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.67 | 53.22 | 10.2 | 44.61 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0601 | 43.7045 | 8.0997 | 40.7768 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.2 455 | 455 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 421.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.67 | 53.22 | 10.2 | 44.61 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0601 | 43.7045 | 8.0997 | 40.7768 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3 455 | 455 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 421.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.67 | 53.22 | 10.2 | 44.61 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0601 | 43.7045 | 8.0997 | 40.7768 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3/BFG 455 | 455 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 455 | 422.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 78 | 2 | N | 10.58 | 53.41 | 10.08 | 45.13 | 46.1 | -0.3575 | 0.0267 | -0.2687 |  |  | 2 | 43.73 | 8.05 | 41.48 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 460 | 460 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 460 | 428 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.16 | 53.48 | 10.52 | 43.73 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0726 | 42.1783 | 8.3394 | 40.5291 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 460 | 460 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 460 | 428 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.16 | 53.48 | 10.52 | 43.73 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0726 | 42.1783 | 8.3394 | 40.5291 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3/BFG 460 | 460 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 460 | 430.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 10.95 | 52.44 | 10.43 | 44.11 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1157 | 42.2782 | 8.3737 | 40.6815 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 460 | 460 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 460 | 428 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.16 | 53.48 | 10.52 | 43.73 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0726 | 42.1783 | 8.3394 | 40.5291 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 460 | 460 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 460 | 428 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.16 | 53.48 | 10.52 | 43.73 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0726 | 42.1783 | 8.3394 | 40.5291 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d/BFG 460 | 460 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 460 | 430.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 10.95 | 52.44 | 10.43 | 44.11 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1157 | 42.2782 | 8.3737 | 40.6815 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G9 460 | 460 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 460 | 426.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.7 | 53.25 | 10.25 | 44.89 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0702 | 43.9788 | 8.1394 | 41.0327 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.2 460 | 460 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 460 | 426.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.7 | 53.25 | 10.25 | 44.89 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0702 | 43.9788 | 8.1394 | 41.0327 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3 460 | 460 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 460 | 426.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.7 | 53.25 | 10.25 | 44.89 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0702 | 43.9788 | 8.1394 | 41.0327 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3/BFG 460 | 460 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 460 | 427.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 78 | 2 | N | 10.63 | 53.66 | 10.12 | 45.44 | 46.1 | -0.3575 | 0.0267 | -0.2687 |  |  | 2.0079 | 44.0304 | 8.0819 | 41.7649 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 465 | 465 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 465 | 432.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.18 | 53.51 | 10.57 | 44 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0824 | 42.4387 | 8.379 | 40.7793 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 465 | 465 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 465 | 432.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.18 | 53.51 | 10.57 | 44 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0824 | 42.4387 | 8.379 | 40.7793 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3/BFG 465 | 465 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 465 | 435.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11 | 52.68 | 10.47 | 44.42 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1238 | 42.5753 | 8.4058 | 40.9674 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 465 | 465 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 465 | 432.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.18 | 53.51 | 10.57 | 44 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0824 | 42.4387 | 8.379 | 40.7793 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 465 | 465 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 465 | 432.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.18 | 53.51 | 10.57 | 44 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0824 | 42.4387 | 8.379 | 40.7793 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d/BFG 465 | 465 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 465 | 435.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11 | 52.68 | 10.47 | 44.42 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1238 | 42.5753 | 8.4058 | 40.9674 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G9 465 | 465 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 465 | 430.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.73 | 53.29 | 10.3 | 45.16 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0803 | 44.2434 | 8.1791 | 41.2795 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.2 465 | 465 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 465 | 430.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.73 | 53.29 | 10.3 | 45.16 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0803 | 44.2434 | 8.1791 | 41.2795 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3 465 | 465 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 465 | 430.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.73 | 53.29 | 10.3 | 45.16 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0803 | 44.2434 | 8.1791 | 41.2795 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3/BFG 465 | 465 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 465 | 432.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 78 | 2 | N | 10.67 | 53.91 | 10.16 | 45.75 | 46.1 | -0.3575 | 0.0267 | -0.2687 |  |  | 2.0159 | 44.3308 | 8.1139 | 42.0499 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 470 | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 470 | 437.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.21 | 53.54 | 10.62 | 44.27 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0923 | 42.6992 | 8.4187 | 41.0295 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 470 | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 470 | 437.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.21 | 53.54 | 10.62 | 44.27 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0923 | 42.6992 | 8.4187 | 41.0295 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3/BFG 470 | 470 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 470 | 439.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.04 | 52.91 | 10.51 | 44.73 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1319 | 42.8725 | 8.4379 | 41.2533 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 470 | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 470 | 437.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.21 | 53.54 | 10.62 | 44.27 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0923 | 42.6992 | 8.4187 | 41.0295 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 470 | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 470 | 437.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.21 | 53.54 | 10.62 | 44.27 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.0923 | 42.6992 | 8.4187 | 41.0295 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d/BFG 470 | 470 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 470 | 439.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.04 | 52.91 | 10.51 | 44.73 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1319 | 42.8725 | 8.4379 | 41.2533 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G9 470 | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 470 | 435.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.75 | 53.33 | 10.35 | 45.43 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0904 | 44.5079 | 8.2188 | 41.5263 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.2 470 | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 470 | 435.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.75 | 53.33 | 10.35 | 45.43 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0904 | 44.5079 | 8.2188 | 41.5263 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3 470 | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 470 | 435.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 78 | 2 | N | 10.75 | 53.33 | 10.35 | 45.43 | 46.5 | -0.3642 | 0.0165 | -0.2593 |  |  | 2.0904 | 44.5079 | 8.2188 | 41.5263 | [6 empty] | 2020-10-12
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3/BFG 470 | 470 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 470 | 436.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 78 | 2 | N | 10.71 | 54.17 | 10.2 | 46.06 | 46.1 | -0.3575 | 0.0267 | -0.2687 |  |  | 2.0238 | 44.6312 | 8.1458 | 42.3348 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 475 | 475 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 475 | 442.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.24 | 53.58 | 10.66 | 44.54 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1001 | 42.9596 | 8.4504 | 41.2798 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 475 | 475 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 475 | 442.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.24 | 53.58 | 10.66 | 44.54 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1001 | 42.9596 | 8.4504 | 41.2798 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3/BFG 475 | 475 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 475 | 444.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.08 | 53.15 | 10.55 | 45.03 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.14 | 43.16 | 8.47 | 41.53 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 475 | 475 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 475 | 442.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.24 | 53.58 | 10.66 | 44.54 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1001 | 42.9596 | 8.4504 | 41.2798 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 475 | 475 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 475 | 442.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.24 | 53.58 | 10.66 | 44.54 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1001 | 42.9596 | 8.4504 | 41.2798 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d/BFG 475 | 475 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 475 | 444.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.08 | 53.15 | 10.55 | 45.03 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.14 | 43.16 | 8.47 | 41.53 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G9.3/BFG 475 | 475 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 475 | 441.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 78 | 2 | N | 10.75 | 54.42 | 10.24 | 46.36 | 46.1 | -0.3575 | 0.0267 | -0.2687 |  |  | 2.0317 | 44.9218 | 8.1778 | 42.6105 | [6 empty] | 2021-06-11
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 480 | 480 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 480 | 447.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.26 | 53.61 | 10.71 | 44.81 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.11 | 43.22 | 8.49 | 41.53 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 480 | 480 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 480 | 447.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.26 | 53.61 | 10.71 | 44.81 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.11 | 43.22 | 8.49 | 41.53 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3/BFG 480 | 480 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 480 | 449.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.12 | 53.39 | 10.59 | 45.33 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1481 | 43.4475 | 8.5021 | 41.8067 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 480 | 480 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 480 | 447.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.26 | 53.61 | 10.71 | 44.81 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.11 | 43.22 | 8.49 | 41.53 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 480 | 480 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 480 | 447.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.26 | 53.61 | 10.71 | 44.81 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.11 | 43.22 | 8.49 | 41.53 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d/BFG 480 | 480 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 480 | 449.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.12 | 53.39 | 10.59 | 45.33 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1481 | 43.4475 | 8.5021 | 41.8067 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 485 | 485 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 485 | 451.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.29 | 53.64 | 10.76 | 45.07 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1199 | 43.4708 | 8.5296 | 41.771 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 485 | 485 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 485 | 451.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.29 | 53.64 | 10.76 | 45.07 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1199 | 43.4708 | 8.5296 | 41.771 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3/BFG 485 | 485 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 485 | 454.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.16 | 53.63 | 10.63 | 45.63 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1562 | 43.7351 | 8.5342 | 42.0834 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 485 | 485 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 485 | 451.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.29 | 53.64 | 10.76 | 45.07 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1199 | 43.4708 | 8.5296 | 41.771 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 485 | 485 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 485 | 451.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.29 | 53.64 | 10.76 | 45.07 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1199 | 43.4708 | 8.5296 | 41.771 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d/BFG 485 | 485 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 485 | 454.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.16 | 53.63 | 10.63 | 45.63 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1562 | 43.7351 | 8.5342 | 42.0834 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 490 | 490 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 490 | 456.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.31 | 53.68 | 10.81 | 45.33 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1297 | 43.7215 | 8.5693 | 42.0119 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 490 | 490 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 490 | 456.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.31 | 53.68 | 10.81 | 45.33 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1297 | 43.7215 | 8.5693 | 42.0119 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3/BFG 490 | 490 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 490 | 459.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.2 | 53.86 | 10.67 | 45.93 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1643 | 44.0226 | 8.5663 | 42.36 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 490 | 490 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 490 | 456.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.31 | 53.68 | 10.81 | 45.33 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1297 | 43.7215 | 8.5693 | 42.0119 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 490 | 490 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 490 | 456.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.31 | 53.68 | 10.81 | 45.33 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1297 | 43.7215 | 8.5693 | 42.0119 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d/BFG 490 | 490 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 490 | 459.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.2 | 53.86 | 10.67 | 45.93 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1643 | 44.0226 | 8.5663 | 42.36 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 495 | 495 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 495 | 461.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.34 | 53.71 | 10.86 | 45.59 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1396 | 43.9723 | 8.6089 | 42.2529 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 495 | 495 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 495 | 461.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.34 | 53.71 | 10.86 | 45.59 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1396 | 43.9723 | 8.6089 | 42.2529 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3/BFG 495 | 495 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 495 | 463.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.24 | 54.1 | 10.71 | 46.22 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1725 | 44.3006 | 8.5985 | 42.6275 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 495 | 495 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 495 | 461.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.34 | 53.71 | 10.86 | 45.59 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1396 | 43.9723 | 8.6089 | 42.2529 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 495 | 495 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 495 | 461.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.34 | 53.71 | 10.86 | 45.59 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1396 | 43.9723 | 8.6089 | 42.2529 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d/BFG 495 | 495 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 495 | 463.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.24 | 54.1 | 10.71 | 46.22 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1725 | 44.3006 | 8.5985 | 42.6275 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 500 | 500 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 500 | 466.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.36 | 53.75 | 10.91 | 45.85 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1494 | 44.2231 | 8.6485 | 42.4939 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 500 | 500 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 500 | 466.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.36 | 53.75 | 10.91 | 45.85 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1494 | 44.2231 | 8.6485 | 42.4939 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3/BFG 500 | 500 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 500 | 468.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.28 | 54.34 | 10.75 | 46.51 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1806 | 44.5785 | 8.6306 | 42.895 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 500 | 500 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 500 | 466.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.36 | 53.75 | 10.91 | 45.85 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1494 | 44.2231 | 8.6485 | 42.4939 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 500 | 500 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 500 | 466.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.36 | 53.75 | 10.91 | 45.85 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1494 | 44.2231 | 8.6485 | 42.4939 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d/BFG 500 | 500 W, 156 half-cut cell monocrystalline module, bifacial, 1500V max system Vdc | UL 61730 | 500 | 468.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.28 | 54.34 | 10.75 | 46.51 | 45 | -0.3389 | 0.0577 | -0.2681 |  |  | 2.1806 | 44.5785 | 8.6306 | 42.895 | [6 empty] | 2021-07-21
Hanwha Q CELLS | Q.PEAK DUO XL-G10.2 505 | 505 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 505 | 471.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.39 | 53.78 | 10.95 | 46.1 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1573 | 44.4642 | 8.6803 | 42.7256 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.3 505 | 505 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 505 | 471.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.39 | 53.78 | 10.95 | 46.1 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1573 | 44.4642 | 8.6803 | 42.7256 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.c 505 | 505 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 505 | 471.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.39 | 53.78 | 10.95 | 46.1 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1573 | 44.4642 | 8.6803 | 42.7256 | [6 empty] | 2021-07-01
Hanwha Q CELLS | Q.PEAK DUO XL-G10.d 505 | 505 W, 156 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 505 | 471.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 78 | 2 | N | 11.39 | 53.78 | 10.95 | 46.1 | 46.5 | -0.3397 | 0.01334 | -0.2639 |  |  | 2.1573 | 44.4642 | 8.6803 | 42.7256 | [6 empty] | 2021-07-01
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-230Q | 230 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 230 | 204.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19341
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-230QB | 230 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, BlackFrame | UL 1703 | 230 | 204.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19341
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-230QW | 230 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 230 | 204.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19341
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-230Q | 230 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 230 | 204.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19341
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-230QB | 230 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 230 | 204.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19341
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-230QW | 230 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 230 | 204.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19341
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-235T | 235 W Polycrystalline Module | UL 1703 | 235 | 208.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5523 | 27.7097 | 6.5077 | 25.9498 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18304
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-235TB | 235 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 235 | 211.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5664 | 28.9432 | 6.4561 | 26.474 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19292
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-235TW | 235 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 235 | 208.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5523 | 27.7097 | 6.5077 | 25.9498 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18304
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-235T | 235 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 235 | 211.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5664 | 28.9432 | 6.4561 | 26.474 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19292
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-235TB | 235 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 235 | 211.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5664 | 28.9432 | 6.4561 | 26.474 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19292
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-235TW | 235 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 235 | 211.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5664 | 28.9432 | 6.4561 | 26.474 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19292
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha Q CELLS (Qidong) | HSL60M6-HA-0-240T | 240 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19004
Hanwha Q CELLS (Qidong) | HSL60M6-HB-0-240T | 240 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-240T | 240 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-240TB | 240 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-240TW | 240 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-240T | 240 W Polycrystalline Module | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5677 | 28.0905 | 6.5723 | 26.3065 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18349
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-240TB | 240 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 215.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19163
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-240TW | 240 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5677 | 28.0905 | 6.5723 | 26.3065 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18349
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-240T | 240 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 240 | 215.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19163
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-240TB | 240 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 215.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19163
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-240TW | 240 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 215.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19163
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-240T | 240 W Polycrystalline Module | UL 1703 | 240 | 213.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5677 | 28.0905 | 6.5723 | 26.3065 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18349
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-240TB | 240 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19163
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-240TW | 240 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 213.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5677 | 28.0905 | 6.5723 | 26.3065 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18349
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-240T | 240 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19163
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-240TB | 240 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19163
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-240TW | 240 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19163
Hanwha Q CELLS (Qidong) | HSL60M6-HB-0-245TW | 245 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-245T | 245 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-245TB | 245 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-245TW | 245 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-245T | 245 W Polycrystalline Module | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5984 | 29.1861 | 6.6417 | 26.7745 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19041
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-245TB | 245 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 220.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19178
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-245TW | 245 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5984 | 29.1861 | 6.6417 | 26.7745 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19041
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-245T | 245 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 245 | 220.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19178
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-245TB | 245 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 220.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19178
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-245TW | 245 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 220.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19178
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-245T | 245 W Polycrystalline Module | UL 1703 | 245 | 218 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5984 | 29.1861 | 6.6417 | 26.7745 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19041
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-245TB | 245 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19178
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-245TW | 245 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 218 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5984 | 29.1861 | 6.6417 | 26.7745 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19041
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.8 | 37.5 | 8.25 | 29.7 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6284 | 28.9887 | 6.651 | 27.1863 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19268
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-245T | 245 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19178
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-245TB | 245 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19178
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-245TW | 245 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19178
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-245W | 245 W Polycrystalline Module | UL 1703 | 245 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.8 | 37.5 | 8.25 | 29.7 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6284 | 28.9887 | 6.651 | 27.1863 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19268
Hanwha Q CELLS (Qidong) | HSL60M6-HA-0-250T | 250 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 250 | 222.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19249
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-250T | 250 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 250 | 225.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19168
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-250TB | 250 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 225.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19168
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-250TW | 250 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 225.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19168
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-250T | 250 W Polycrystalline Module | UL 1703 | 250 | 222.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.6139 | 29.4809 | 6.7061 | 27.0449 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19031
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-250TB | 250 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19168
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-250TW | 250 W Polycrystalline module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 222.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.6139 | 29.4809 | 6.7061 | 27.0449 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19031
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.74 | 37.2 | 8.22 | 30.4 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6225 | 29.672 | 6.6268 | 27.827 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19257
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-250T | 250 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19168
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-250TB | 250 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19168
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-250TW | 250 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19168
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-250W | 250 W Polycrystalline Module | UL 1703 | 250 | 227.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.74 | 37.2 | 8.22 | 30.4 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6225 | 29.672 | 6.6268 | 27.827 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19257
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 226.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.72 | 37.6 | 8.2 | 30.5 | 45.5 | -0.4309 | 0.0552 | -0.3232 | -0.0049 | -0.5404 | 1.649 | 30.442 | 6.5613 | 28.0234 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.2008
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-250W | 250 W Polycrystalline Module | UL 1703 | 250 | 227.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.72 | 37.6 | 8.2 | 30.5 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.64 | 29.56 | 6.65 | 27.78 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19391
Hanwha Q CELLS (Qidong) | HSL60M6-HA-4-255T | 255 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19227
Hanwha Q CELLS (Qidong) | HSL60M6-HA-4-255TB | 255 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19227
Hanwha Q CELLS (Qidong) | HSL60M6-HA-4-255TW | 255 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19227
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-255T | 255 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 255 | 227.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19227
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-255TB | 255 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 255 | 227.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19227
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-255TW | 255 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 255 | 227.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19227
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-255T | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-255TB | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PA-0-255TW | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PA-2-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PA-3-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-255T | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-255TB | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PA-4-255TW | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-255T | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-255TB | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-255TW | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PB-2-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PB-3-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-255 | 255 W Polycrystalline Module | UL 1703 | 255 | 232.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.89 | 38 | 8.29 | 30.8 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6363 | 29.8156 | 6.6833 | 28.1932 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19132
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-255T | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-255TB | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-255TW | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-255W | 255 W Polycrystalline Module | UL 1703 | 255 | 232.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.89 | 38 | 8.29 | 30.8 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6363 | 30.0624 | 6.6833 | 28.1932 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19291
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-255 | 255 W Polycrystalline Module | UL 1703 | 255 | 231.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.86 | 37.8 | 8.31 | 30.7 | 45.5 | -0.4309 | 0.0552 | -0.3232 | -0.0049 | -0.5404 | 1.6711 | 30.6417 | 6.6493 | 28.2071 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.20081
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-255W | 255 W Polycrystalline Module | UL 1703 | 255 | 232.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.86 | 37.8 | 8.31 | 30.7 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.66 | 29.75 | 6.74 | 27.96 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19367
Hanwha Q CELLS (Qidong) | HSL60M6-HA-4-260T | 260 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 260 | 231.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19237
Hanwha Q CELLS (Qidong) | HSL60M6-HA-4-260TB | 260 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 260 | 231.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19237
Hanwha Q CELLS (Qidong) | HSL60M6-HA-4-260TW | 260 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 260 | 231.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19237
Hanwha Q CELLS (Qidong) | HSL60M6-HB-0-260T | 260 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-260T | 260 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-260TB | 260 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha Q CELLS (Qidong) | HSL60M6-HB-4-260TW | 260 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-260T | 260 W Polycrystalline Module | UL 1703 | 260 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.99 | 37.7 | 8.56 | 30.4 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.58 | 30.3 | 6.72 | 27.65 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18413
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-260TW | 260 W Polycrystalline Module | UL 1703 | 260 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.99 | 37.7 | 8.56 | 30.4 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.58 | 30.3 | 6.72 | 27.65 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18413
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-260 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.93 | 38.1 | 8.35 | 31.2 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6482 | 30.4528 | 6.7316 | 28.5593 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19304
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-260T | 260 W Polycrystalline Module | UL 1703 | 260 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.99 | 37.7 | 8.56 | 30.4 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.58 | 30.3 | 6.72 | 27.65 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18413
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-260TW | 260 W Polycrystalline Module | UL 1703 | 260 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.99 | 37.7 | 8.56 | 30.4 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.58 | 30.3 | 6.72 | 27.65 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18413
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-260W | 260 W Polycrystalline Module | UL 1703 | 260 | 236.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.93 | 38.1 | 8.35 | 31.2 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6482 | 30.4528 | 6.7316 | 28.5593 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19304
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-260 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.98 | 38.1 | 8.42 | 30.9 | 45.5 | -0.4309 | 0.0552 | -0.3232 | -0.0049 | -0.5404 | 1.6933 | 30.8413 | 6.7374 | 28.3909 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.20086
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-260W | 260 W Polycrystalline Module | UL 1703 | 260 | 236.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.98 | 38.1 | 8.42 | 30.9 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.68 | 29.94 | 6.83 | 28.15 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19346
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-265T | 265 W Polycrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.02 | 37.8 | 8.67 | 30.6 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 30.5 | 6.81 | 27.84 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18415
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-265TW | 265 W Polycrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.02 | 37.8 | 8.67 | 30.6 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 30.5 | 6.81 | 27.84 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18415
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-265T | 265 W Polycrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.02 | 37.8 | 8.67 | 30.6 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 30.5 | 6.81 | 27.84 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18415
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-265TW | 265 W Polycrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.02 | 37.8 | 8.67 | 30.6 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 30.5 | 6.81 | 27.84 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18415
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-265 | 265 W Polycrystalline Module | UL 1703 | 265 | 240.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.12 | 38.3 | 8.53 | 31.1 | 45.5 | -0.4309 | 0.0552 | -0.3232 | -0.0049 | -0.5404 | 1.7154 | 31.0409 | 6.8254 | 28.5747 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.20093
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-265W | 265 W Polycrystalline Module | UL 1703 | 265 | 241.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.12 | 38.3 | 8.53 | 31.1 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.71 | 30.14 | 6.91 | 28.33 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19449
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-270T | 270 W Polycrystalline Module | UL 1703 | 270 | 242.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.04 | 37.8 | 8.77 | 30.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.62 | 30.7 | 6.89 | 28.02 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.1842
Hanwha Q CELLS (Qidong) | HSL60P6-PB-0-270TW | 270 W Polycrystalline Module | UL 1703 | 270 | 242.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.04 | 37.8 | 8.77 | 30.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.62 | 30.7 | 6.89 | 28.02 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.1842
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-270T | 270 W Polycrystalline Module | UL 1703 | 270 | 242.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.04 | 37.8 | 8.77 | 30.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.62 | 30.7 | 6.89 | 28.02 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.1842
Hanwha Q CELLS (Qidong) | HSL60P6-PB-4-270TW | 270 W Polycrystalline Module | UL 1703 | 270 | 242.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.04 | 37.8 | 8.77 | 30.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.62 | 30.7 | 6.89 | 28.02 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.1842
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-270 | 270 W Polycrystalline Module | UL 1703 | 270 | 245.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.22 | 38.5 | 8.66 | 31.2 | 45.5 | -0.4309 | 0.0552 | -0.3232 | -0.0049 | -0.5404 | 1.7415 | 31.1407 | 6.9294 | 28.6665 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.20086
Hanwha Q CELLS (Qidong) | HSL60P6-PC-3-275 | 275 W Polycrystalline Module | UL 1703 | 275 | 250.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.31 | 38.7 | 8.79 | 31.3 | 45.5 | -0.4309 | 0.0552 | -0.3232 | -0.0049 | -0.5404 | 1.7677 | 31.2405 | 7.0334 | 28.7584 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.20081
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-275T | 275 W Polycrystalline Module | UL 1703 | 275 | 244.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5363 | 34.2411 | 6.3507 | 31.9101 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-275TB | 275 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5311 | 34.6997 | 6.2411 | 31.9329 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19319
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-275TW | 275 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 275 | 244.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5363 | 34.2411 | 6.3507 | 31.9101 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-275T | 275 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5311 | 34.6997 | 6.2411 | 31.9329 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19319
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-275TB | 275 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5311 | 34.6997 | 6.2411 | 31.9329 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19319
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-275TW | 275 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5311 | 34.6997 | 6.2411 | 31.9329 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19319
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-280T | 280 W Polycrystalline Module | UL 1703 | 280 | 248.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5541 | 34.3373 | 6.4244 | 31.9997 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19059
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-280TB | 280 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 280 | 251.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5489 | 34.7971 | 6.3136 | 32.0226 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19249
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-280TW | 280 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 280 | 248.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5541 | 34.3373 | 6.4244 | 31.9997 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19059
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-280T | 280 W Polycrystalline Module, 1000 V System Voltage | UL 1703 | 280 | 251.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5489 | 34.7971 | 6.3136 | 32.0226 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19249
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-280TB | 280 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 280 | 251.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5489 | 34.7971 | 6.3136 | 32.0226 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19249
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-280TW | 280 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 280 | 251.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5489 | 34.7971 | 6.3136 | 32.0226 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19249
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-285T | 285 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-285TB | 285 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-285TW | 285 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-285T | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-285TB | 285 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-285TW | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-285T | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-285TB | 285 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-285TW | 285 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-285T | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-285TB | 285 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-285TW | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-285T | 285 W Polycrystalline Module | UL 1703 | 285 | 253.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.55 | 35.87 | 6.51 | 33.42 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19508
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-285TB | 285 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 256.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19284
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-285TW | 285 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.55 | 35.87 | 6.51 | 33.42 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19508
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-285T | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 285 | 256.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.57 | 34.99 | 6.4 | 32.2 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19275
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-285TB | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 256.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.57 | 34.99 | 6.4 | 32.2 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19275
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-285TW | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 256.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.57 | 34.99 | 6.4 | 32.2 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19275
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-285T | 285 W Polycrystalline Module | UL 1703 | 285 | 253.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5488 | 35.87 | 6.509 | 33.4207 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19494
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-285TB | 285 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19284
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-285TW | 285 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5488 | 35.87 | 6.509 | 33.4207 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19494
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-285T | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 285 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19284
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-285TB | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19284
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-285TW | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19284
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-290T | 290 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-290TB | 290 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-290TW | 290 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-290T | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-290TB | 290 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-290TW | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-290T | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-290TB | 290 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-290TW | 290 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-290T | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-290TB | 290 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-290TW | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-290T | 290 W Polycrystalline Module | UL 1703 | 290 | 257.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5605 | 36.1698 | 6.5581 | 33.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19463
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-290TB | 290 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 260.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19026
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-290TW | 290 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 257.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5605 | 36.1698 | 6.5581 | 33.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19463
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-290T | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 290 | 260.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19026
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-290TB | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 260.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19026
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-290TW | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 260.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19026
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-290T | 290 W Polycrystalline Module | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5605 | 36.1698 | 6.5581 | 33.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19463
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-290TB | 290 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19026
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-290TW | 290 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5605 | 36.1698 | 6.5581 | 33.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19463
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-290T | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 290 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19026
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-290TB | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19026
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-290TW | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19026
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-290 | 290 W Polycrystalline Module | UL 1703 | 290 | 263.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.49 | 44.4 | 8.02 | 36.2 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.59 | 34.68 | 6.52 | 32.58 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19014
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-290W | 290 W Polycrystalline Module | UL 1703 | 290 | 263.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.49 | 44.4 | 8.02 | 36.2 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.59 | 34.68 | 6.52 | 32.58 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19014
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-295T | 295 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-295TB | 295 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-295TW | 295 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-295T | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-295TB | 295 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-295TW | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-295T | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-295TB | 295 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-295TW | 295 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-295T | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-295TB | 295 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-295TW | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-295T | 295 W Polycrystalline Module | UL 1703 | 295 | 262.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5819 | 36.3696 | 6.6482 | 33.8862 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19503
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-295TB | 295 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19066
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-295TW | 295 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5819 | 36.3696 | 6.6482 | 33.8862 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19503
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-295T | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 295 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19066
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-295TB | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19066
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-295TW | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19066
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-295T | 295 W Polycrystalline Module | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5819 | 36.3696 | 6.6482 | 33.8862 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19503
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-295TB | 295 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 265.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19066
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-295TW | 295 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5819 | 36.3696 | 6.6482 | 33.8862 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19503
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.55 | 44.9 | 8.11 | 36.4 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6007 | 35.2366 | 6.5481 | 33.2007 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19119
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-295T | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 295 | 265.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19066
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-295TB | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 265.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19066
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-295TW | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 265.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19066
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-295W | 295 W Polycrystalline Module | UL 1703 | 295 | 268.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.55 | 44.9 | 8.11 | 36.4 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6007 | 35.2366 | 6.5481 | 33.2007 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19119
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.6 | 44.6 | 8.11 | 36.4 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.61 | 34.87 | 6.6 | 32.76 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19031
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 265.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.42 | 45.1 | 8.11 | 36.4 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6241 | 36.1896 | 6.4661 | 33.2022 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19924
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-295QW | 295 W Polycrystalline Module, Black Frame | UL 1703 | 295 | 265.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.42 | 45.1 | 8.11 | 36.4 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6241 | 36.1896 | 6.4661 | 33.2022 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19924
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-295W | 295 W Polycrystalline Module | UL 1703 | 295 | 268.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.6 | 44.6 | 8.11 | 36.4 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.61 | 34.87 | 6.6 | 32.76 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19031
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-300T | 300 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-300TB | 300 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-300TW | 300 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-300T | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-300TB | 300 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-300TW | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-300T | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-300TB | 300 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-300TW | 300 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-300T | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-300TB | 300 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-300TW | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-300T | 300 W Polycrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 268.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.17974
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-300TW | 300 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 268.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.17974
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-300T | 300 W Polycrystalline Module, 1000 V System voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 268.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.17974
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-300TW | 300 W Polycrystalline Module, 1000 V System voltage, White Backsheet, Black Frame | UL 1703 | 300 | 268.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.17974
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-300T | 300 W Polycrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 268.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.17974
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-300TW | 300 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 268.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.17974
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-300 | 300 W Polycrystalline Module | UL 1703 | 300 | 273 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.6 | 45 | 8.22 | 36.5 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6224 | 35.3334 | 6.637 | 33.2919 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-300T | 300 W Monocrystalline Module, 1000 V System voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 268.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.5 | 35.88 | 6.56 | 32.99 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1794
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-300TW | 300 W Monocrystalline Module, 1000 V System voltage, White Backsheet, Black Frame | UL 1703 | 300 | 268.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.5 | 35.88 | 6.56 | 32.99 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1794
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-300W | 300 W Polycrystalline Module | UL 1703 | 300 | 273 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.6 | 45 | 8.22 | 36.5 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6224 | 35.3334 | 6.637 | 33.2919 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19108
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-300 | 300 W Polycrystalline Module | UL 1703 | 300 | 271.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.7 | 44.8 | 8.2 | 36.6 | 46.3 | -0.4303 | 0.0579 | -0.4177 | -0.0013 | -0.4182 | 1.645 | 36.5252 | 6.5579 | 33.6113 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.20027
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 269.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.57 | 45.3 | 8.2 | 36.6 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6421 | 36.3885 | 6.5379 | 33.3847 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19918
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-300QW | 300 W Polycrystalline Module, Black Frame | UL 1703 | 300 | 269.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.57 | 45.3 | 8.2 | 36.6 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6421 | 36.3885 | 6.5379 | 33.3847 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19918
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-300W | 300 W Polycrystalline Module | UL 1703 | 300 | 273.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.7 | 44.8 | 8.2 | 36.6 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.63 | 35.06 | 6.67 | 32.94 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19049
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-305T | 305 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-305TB | 305 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-305TW | 305 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-305T | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-305TB | 305 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-305TW | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-305T | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-305TB | 305 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-305TW | 305 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-305T | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-305TB | 305 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-305TW | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-305T | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-305TB | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PA-0-305TW | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PA-2-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PA-3-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-305T | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-305TB | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PA-4-305TW | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-305T | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-305TB | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-305TW | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PB-2-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PB-3-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-305 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.65 | 45.2 | 8.33 | 36.6 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6441 | 35.4302 | 6.7258 | 33.3832 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19098
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-305T | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-305TB | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-305TW | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-305W | 305 W Polycrystalline Module | UL 1703 | 305 | 277.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.65 | 45.2 | 8.33 | 36.6 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6441 | 35.4302 | 6.7258 | 33.3832 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19098
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-305 | 305 W Polycrystalline Module | UL 1703 | 305 | 275.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.81 | 45 | 8.29 | 36.8 | 46.3 | -0.4303 | 0.0579 | -0.4177 | -0.0013 | -0.4182 | 1.663 | 36.7248 | 6.6299 | 33.7949 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.20024
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.72 | 45.4 | 8.32 | 36.7 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6661 | 36.4879 | 6.6335 | 33.4759 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19932
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-305QW | 305 W Polycrystalline Module, Black Frame | UL 1703 | 305 | 274.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.72 | 45.4 | 8.32 | 36.7 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6661 | 36.4879 | 6.6335 | 33.4759 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19932
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-305W | 305 W Polycrystalline Module | UL 1703 | 305 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.81 | 45 | 8.29 | 36.8 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.64 | 35.25 | 6.74 | 33.12 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.18954
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-310T | 310 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-310TB | 310 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HA-0-310TW | 310 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-310T | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-310TB | 310 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HA-4-310TW | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-310T | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-310TB | 310 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HB-0-310TW | 310 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-310T | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-310TB | 310 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72M6-HB-4-310TW | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-310T | 310 W Polycrystalline Module | UL 1703 | 310 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.85 | 45.7 | 8.43 | 36.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.59 | 36.02 | 6.66 | 33.09 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18475
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-310TW | 310 W Polycrystalline Module | UL 1703 | 310 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.85 | 45.7 | 8.43 | 36.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.59 | 36.02 | 6.66 | 33.09 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18475
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-310 | 310 W Polycrystalline Module | UL 1703 | 310 | 282.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.91 | 45.2 | 8.48 | 36.6 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6737 | 35.4302 | 6.8469 | 33.3832 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-310T | 310 W Polycrystalline Module | UL 1703 | 310 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.85 | 45.7 | 8.43 | 36.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.59 | 36.02 | 6.66 | 33.09 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18475
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-310TW | 310 W Polycrystalline Module | UL 1703 | 310 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.85 | 45.7 | 8.43 | 36.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.59 | 36.02 | 6.66 | 33.09 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18475
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-310W | 310 W Polycrystalline Module | UL 1703 | 310 | 282.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.91 | 45.2 | 8.48 | 36.6 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6737 | 35.4302 | 6.8469 | 33.3832 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19129
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-310 | 310 W Polycrystalline Module | UL 1703 | 310 | 280.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.91 | 45.1 | 8.36 | 37.1 | 46.3 | -0.4303 | 0.0579 | -0.4177 | -0.0013 | -0.4182 | 1.677 | 37.0242 | 6.6859 | 34.0704 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.20029
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-310Q | 310 W Polycrystalline Module | UL 1703 | 310 | 278.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.87 | 45.6 | 8.41 | 36.9 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6842 | 36.6867 | 6.7053 | 33.6583 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19931
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-310QW | 310 W Polycrystalline Module, Black Frame | UL 1703 | 310 | 278.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.87 | 45.6 | 8.41 | 36.9 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6842 | 36.6867 | 6.7053 | 33.6583 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19931
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-310W | 310 W Polycrystalline Module | UL 1703 | 310 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.91 | 45.1 | 8.36 | 37.1 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.66 | 35.54 | 6.8 | 33.39 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19031
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-315T | 315 W Polycrystalline Module | UL 1703 | 315 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.9 | 45.8 | 8.52 | 37 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 36.21 | 6.73 | 33.27 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18392
Hanwha Q CELLS (Qidong) | HSL72P6-PB-0-315TW | 315 W Polycrystalline Module | UL 1703 | 315 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.9 | 45.8 | 8.52 | 37 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 36.21 | 6.73 | 33.27 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18392
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-315T | 315 W Polycrystalline Module | UL 1703 | 315 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.9 | 45.8 | 8.52 | 37 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 36.21 | 6.73 | 33.27 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18392
Hanwha Q CELLS (Qidong) | HSL72P6-PB-4-315TW | 315 W Polycrystalline Module | UL 1703 | 315 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.9 | 45.8 | 8.52 | 37 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 36.21 | 6.73 | 33.27 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18392
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-315 | 315 W Polycrystalline Module | UL 1703 | 315 | 285.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.02 | 45.3 | 8.45 | 37.3 | 46.3 | -0.4303 | 0.0579 | -0.4177 | -0.0013 | -0.4182 | 1.6951 | 37.2238 | 6.7578 | 34.2541 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.20031
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-315Q | 315 W Polycrystalline Module | UL 1703 | 315 | 283.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.02 | 45.7 | 8.48 | 37.2 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6982 | 36.985 | 6.7611 | 33.9319 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19939
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-315QW | 315 W Polycrystalline Module, Black Frame | UL 1703 | 315 | 283.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.02 | 45.7 | 8.48 | 37.2 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6982 | 36.985 | 6.7611 | 33.9319 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19939
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-320 | 320 W Polycrystalline Module | UL 1703 | 320 | 289.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.1 | 45.6 | 8.52 | 37.6 | 46.3 | -0.4303 | 0.0579 | -0.4177 | -0.0013 | -0.4182 | 1.7091 | 37.5231 | 6.8138 | 34.5296 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.20041
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-325 | 325 W Polycrystalline Module | UL 1703 | 325 | 294.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.19 | 45.8 | 8.6 | 37.8 | 46.3 | -0.4303 | 0.0579 | -0.4177 | -0.0013 | -0.4182 | 1.7252 | 37.7227 | 6.8778 | 34.7133 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.20024
Hanwha Q CELLS (Qidong) | HSL72P6-PC-3-330 | 330 W Polycrystalline Module | UL 1703 | 330 | 299.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.28 | 46 | 8.69 | 38 | 46.3 | -0.4303 | 0.0579 | -0.4177 | -0.0013 | -0.4182 | 1.7432 | 37.9223 | 6.9498 | 34.8969 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.20033
Hanwha Q CELLS (Qidong) Co., Ltd. | Q.PRIME L-G5.1.G 330 | 330 W, 72 cell Monocrystalline module | UL 1703 | 330 | 300.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.41 | 45.6 | 8.83 | 37.4 | 45.7 | -0.41812 | 0.052272 | -0.32414 | 0.01654 | -0.44766 | 1.6434 | 36.6873 | 6.9879 | 34.2922 | [6 empty] | 2018-05-15
Hanwha Q CELLS (Qidong) Co., Ltd. | Q.PRIME L-G5.2.G 330 | 330 W, 72 cell Monocrystalline module | UL 1703 | 330 | 301 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 |  | N | 9.29 | 45.7 | 8.76 | 37.7 | 45.6 | -0.41625 | 0.046506 | -0.34047 | 0.01229 | -0.43075 | 1.6409 | 37.0151 | 7.0247 | 34.2734 | [6 empty] | 2018-05-15
Hanwha Q CELLS (Qidong) Co., Ltd. | Q.PRIME L-G5.1.G 335 | 335 W, 72 cell Monocrystalline module | UL 1703 | 335 | 305.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.47 | 45.8 | 8.91 | 37.6 | 45.7 | -0.41812 | 0.052272 | -0.32414 | 0.01654 | -0.44766 | 1.6583 | 36.8835 | 7.0512 | 34.4755 | [6 empty] | 2018-05-15
Hanwha Q CELLS (Qidong) Co., Ltd. | Q.PRIME L-G5.2.G 335 | 335 W, 72 cell Monocrystalline module | UL 1703 | 335 | 305.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 |  | N | 9.35 | 46 | 8.84 | 37.9 | 45.6 | -0.41625 | 0.046506 | -0.34047 | 0.01229 | -0.43075 | 1.6559 | 37.2115 | 7.0889 | 34.4553 | [6 empty] | 2018-05-15
Hanwha Q CELLS (Qidong) Co., Ltd. | Q.PRIME L-G5.1.G 340 | 340 W, 72 cell Monocrystalline module | UL 1703 | 340 | 310.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.48 | 46.1 | 8.93 | 38.1 | 45.7 | -0.41812 | 0.052272 | -0.32414 | 0.01654 | -0.44766 | 1.662 | 37.374 | 7.067 | 34.934 | [6 empty] | 2018-05-15
Hanwha Q CELLS (Qidong) Co., Ltd. | Q.PRIME L-G5.2.G 340 | 340 W, 72 cell Monocrystalline module | UL 1703 | 340 | 310.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 |  | N | 9.41 | 46.1 | 8.91 | 38.2 | 45.6 | -0.41625 | 0.046506 | -0.34047 | 0.01229 | -0.43075 | 1.669 | 37.506 | 7.145 | 34.728 | [6 empty] | 2018-05-15
Hanwha Q CELLS (Qidong) Co., Ltd. | Q.PRIME L-G5.1.G 345 | 345 W, 72 cell Monocrystalline module | UL 1703 | 345 | 315 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.49 | 46.2 | 8.94 | 38.6 | 45.7 | -0.41812 | 0.052272 | -0.32414 | 0.01654 | -0.44766 | 1.6639 | 37.8645 | 7.0749 | 35.3925 | [6 empty] | 2018-05-15
Hanwha Q CELLS (Qidong) Co., Ltd. | Q.PRIME L-G5.2.G 345 | 345 W, 72 cell Monocrystalline module | UL 1703 | 345 | 315.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 |  | N | 9.46 | 46.3 | 8.99 | 38.4 | 45.6 | -0.41625 | 0.046506 | -0.34047 | 0.01229 | -0.43075 | 1.684 | 37.7024 | 7.2092 | 34.9098 | [6 empty] | 2018-05-15
Hanwha SolarOne (Qidong) | SF160-24-M155 | 155 W Monocrystalline Module | UL 1703 | 155 | 138.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 4.9 | 43.5 | 4.38 | 35.4 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 0.83749 | 32.5517 | 3.5329 | 31.8397 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17588
Hanwha SolarOne (Qidong) | SF160-24-M160 | 160 W Monocrystalline Module | UL 1703 | 160 | 142.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5 | 43.5 | 4.5 | 35.6 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 0.88085 | 33.7533 | 3.5809 | 32.2144 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18582
Hanwha SolarOne (Qidong) | SF160-24-M160B | 160 W Monocrystalline Module, Black Backsheet | UL 1703 | 160 | 144.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5 | 43.5 | 4.5 | 35.6 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 0.86922 | 35.527 | 3.5584 | 34.224 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.193
Hanwha SolarOne (Qidong) | SF160-24-M165 | 165 W Monocrystalline Module | UL 1703 | 165 | 147.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.1 | 44 | 4.61 | 35.8 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 0.90238 | 33.9429 | 3.6684 | 32.3954 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18563
Hanwha SolarOne (Qidong) | SF160-24-M165B | 165 W Monocrystalline Module, Black Backsheet | UL 1703 | 165 | 148.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.1 | 44 | 4.61 | 35.8 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 0.89046 | 35.7266 | 3.6453 | 34.4162 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19281
Hanwha SolarOne (Qidong) | SF160-24-P165 | 165 W Polycrystalline Module | UL 1703 | 165 | 145.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 5.14 | 43.7 | 4.65 | 35.5 | 47.7 | -0.4799 | 0.005 | -0.34 | -0.0177 | -0.4579 | 0.91082 | 34.26 | 3.6912 | 31.66 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18912
Hanwha SolarOne (Qidong) | SF160-24-M170 | 170 W Monocrystalline Module | UL 1703 | 170 | 151.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.12 | 44.5 | 4.74 | 35.9 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 0.9404 | 34.6933 | 3.7901 | 32.481 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19192
Hanwha SolarOne (Qidong) | SF160-24-M170B | 170 W Monocrystalline Module, Black Backsheet | UL 1703 | 170 | 153.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.12 | 44.5 | 4.74 | 35.9 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 0.91557 | 35.8264 | 3.7481 | 34.5124 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19295
Hanwha SolarOne (Qidong) | SF160-24-P170 | 170 W Polycrystalline Module | UL 1703 | 170 | 150 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 5.17 | 44.1 | 4.78 | 35.5 | 47.7 | -0.4799 | 0.005 | -0.34 | -0.0177 | -0.4579 | 0.93629 | 34.26 | 3.7944 | 31.66 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18869
Hanwha SolarOne (Qidong) | SF190-27-P170 | 170 W Polycrystalline Module | UL 1703 | 170 | 150.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.494 | 54 | 1 | N | 7.54 | 32.2 | 6.47 | 26.3 | 47 | -0.47 | 0.039 | -0.324 | -0.027 | -0.45 | 1.3013 | 24.6494 | 5.2053 | 23.8791 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.18869
Hanwha SolarOne (Qidong) | SF160-24-M175 | 175 W Monocrystalline Module | UL 1703 | 175 | 156.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.17 | 44.8 | 4.86 | 36 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 0.96421 | 34.7899 | 3.8861 | 32.5714 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19168
Hanwha SolarOne (Qidong) | SF160-24-M175B | 175 W Monocrystalline Module, Black Backsheet | UL 1703 | 175 | 158 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.17 | 44.8 | 4.86 | 36 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 0.97575 | 35.2462 | 3.8561 | 33.9698 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19652
Hanwha SolarOne (Qidong) | SF160-24-M175L | 175 W Monocrystalline Module | UL 1703 | 175 | 156.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.17 | 44.8 | 4.86 | 36 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 0.96421 | 34.7899 | 3.8861 | 32.5714 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19168
Hanwha SolarOne (Qidong) | SF160-24-M175L-B | 175 W Monocrystalline Module | UL 1703 | 175 | 158 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.17 | 44.8 | 4.86 | 36 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 0.97575 | 35.2462 | 3.8561 | 33.9698 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19652
Hanwha SolarOne (Qidong) | SF160-24-P175 | 175 W Polycrystalline Module | UL 1703 | 175 | 154.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 44.5 | 4.9 | 35.7 | 47.7 | -0.4799 | 0.005 | -0.34 | -0.0177 | -0.4579 | 0.95979 | 34.453 | 3.8897 | 31.8384 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18896
Hanwha SolarOne (Qidong) | SF190-27-P175 | 175 W Polycrystalline Module | UL 1703 | 175 | 155 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.494 | 54 | 1 | N | 7.64 | 32.3 | 6.63 | 26.4 | 47 | -0.47 | 0.039 | -0.324 | -0.027 | -0.45 | 1.3335 | 24.7431 | 5.3341 | 23.9699 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.18854
Hanwha SolarOne (Qidong) | SF160-24-M180 | 180 W Monocrystalline Module | UL 1703 | 180 | 161 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 45 | 5 | 36 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 0.99198 | 34.7899 | 3.998 | 32.5714 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19173
Hanwha SolarOne (Qidong) | SF160-24-M180B | 180 W Monocrystalline Module, Black Backsheet | UL 1703 | 180 | 162.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 45 | 5 | 36 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 1.0039 | 35.2462 | 3.9672 | 33.9698 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19657
Hanwha SolarOne (Qidong) | SF160-24-M180L | 180 W Monocrystalline Module | UL 1703 | 180 | 161 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 45 | 5 | 36 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 0.99198 | 34.7899 | 3.998 | 32.5714 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19173
Hanwha SolarOne (Qidong) | SF160-24-M180L-B | 180 W Monocrystalline Module | UL 1703 | 180 | 162.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 45 | 5 | 36 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 1.0039 | 35.2462 | 3.9672 | 33.9698 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19657
Hanwha SolarOne (Qidong) | SF190-27-M180 | 180 W Monocrystalline Module | UL 1703 | 180 | 159.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 7.78 | 32.6 | 6.84 | 26.3 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.3626 | 25.3607 | 5.4774 | 23.7712 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19198
Hanwha SolarOne (Qidong) | SF190-27-M180B | 180 W Monocrystalline Module, Black Backsheet | UL 1703 | 180 | 159.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 7.78 | 32.6 | 6.84 | 26.3 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.2808 | 27.494 | 5.4775 | 24.4614 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19563
Hanwha SolarOne (Qidong) | SF190-27-P180 | 180 W Polycrystalline Module | UL 1703 | 180 | 159.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.494 | 54 | 1 | N | 7.72 | 32.4 | 6.8 | 26.5 | 47 | -0.47 | 0.039 | -0.324 | -0.027 | -0.45 | 1.3007 | 25.572 | 5.4706 | 23.9222 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.18479
Hanwha SolarOne (Qidong) | SF160-24-M185 | 185 W Monocrystalline Module | UL 1703 | 185 | 165.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.23 | 45.3 | 5.12 | 36.1 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 1.02 | 34.8107 | 4.1 | 32.6288 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19192
Hanwha SolarOne (Qidong) | SF160-24-M185B | 185 W Monocrystalline Module, Black Backsheet | UL 1703 | 185 | 167.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.23 | 45.3 | 5.12 | 36.1 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 1.028 | 35.3441 | 4.0624 | 34.0642 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19639
Hanwha SolarOne (Qidong) | SF160-24-M185L | 185 W Monocrystalline Module | UL 1703 | 185 | 165.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.23 | 45.3 | 5.12 | 36.1 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 1.02 | 34.8107 | 4.1 | 32.6288 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19192
Hanwha SolarOne (Qidong) | SF160-24-M185L-B | 185 W Monocrystalline Module | UL 1703 | 185 | 167.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.23 | 45.3 | 5.12 | 36.1 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 1.028 | 35.3441 | 4.0624 | 34.0642 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19639
Hanwha SolarOne (Qidong) | SF190-27-M185 | 185 W Monocrystalline Module | UL 1703 | 185 | 164 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 7.86 | 32.7 | 7 | 26.4 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.3945 | 25.4571 | 5.6055 | 23.8615 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19189
Hanwha SolarOne (Qidong) | SF190-27-M185B | 185 W Monocrystalline Module, Black Backsheet | UL 1703 | 185 | 164 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 7.86 | 32.7 | 7 | 26.4 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.3108 | 27.5986 | 5.6056 | 24.5544 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19554
Hanwha SolarOne (Qidong) | SF190-27-P185 | 185 W Polycrystalline Module | UL 1703 | 185 | 164 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.494 | 54 | 1 | N | 7.8 | 32.5 | 6.96 | 26.6 | 47 | -0.47 | 0.039 | -0.324 | -0.027 | -0.45 | 1.3313 | 25.6685 | 5.5993 | 24.0125 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.18472
Hanwha SolarOne (Qidong) | SF160-24-M190 | 190 W Monocrystalline Module | UL 1703 | 190 | 170.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.78 | 44.8 | 5.33 | 35.8 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 1.0618 | 34.5214 | 4.2682 | 32.3577 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19292
Hanwha SolarOne (Qidong) | SF160-24-M190B | 190 W Monocrystalline Module | UL 1703 | 190 | 171.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.78 | 44.8 | 5.33 | 35.8 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 1.0701 | 35.0504 | 4.229 | 33.0615 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19741
Hanwha SolarOne (Qidong) | SF160-24-M190L | 190 W Monocrystalline Module | UL 1703 | 190 | 170.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.78 | 44.8 | 5.33 | 35.8 | 47.1 | -0.448 | 0.034 | -0.328 | -0.024 | -0.428 | 1.0618 | 34.5214 | 4.2682 | 32.3577 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19292
Hanwha SolarOne (Qidong) | SF160-24-M190L-B | 190 W Monocrystalline Module | UL 1703 | 190 | 171.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.78 | 44.8 | 5.33 | 35.8 | 45.9 | -0.434 | 0.041 | -0.324 | -0.026 | -0.414 | 1.0701 | 35.0504 | 4.229 | 33.0615 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19741
Hanwha SolarOne (Qidong) | SF190-27-M190 | 190 W Monocrystalline Module | UL 1703 | 190 | 168.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 7.93 | 32.8 | 7.17 | 26.5 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.4283 | 25.5536 | 5.7417 | 23.9519 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.1921
Hanwha SolarOne (Qidong) | SF190-27-M190B | 190 W Monocrystalline Module, Black Backsheet | UL 1703 | 190 | 168.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 7.93 | 32.8 | 7.17 | 26.5 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.3426 | 27.7031 | 5.7417 | 24.6474 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19576
Hanwha SolarOne (Qidong) | SF190-27-P190 | 190 W Polycrystalline Module | UL 1703 | 190 | 168.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.494 | 54 | 1 | N | 7.98 | 32.6 | 7.12 | 26.7 | 47 | -0.47 | 0.039 | -0.324 | -0.027 | -0.45 | 1.3974 | 26.0838 | 5.7226 | 24.2354 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19184
Hanwha SolarOne (Qidong) | SF190-27-M195 | 195 W Monocrystalline Module | UL 1703 | 195 | 173.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 8.12 | 32.9 | 7.33 | 26.6 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.4602 | 25.65 | 5.8698 | 24.0423 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19207
Hanwha SolarOne (Qidong) | SF190-27-M195B | 195 W Monocrystalline Module, Black Backsheet | UL 1703 | 195 | 173.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 8.12 | 32.9 | 7.33 | 26.6 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.4016 | 27.5782 | 5.8432 | 24.758 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19822
Hanwha SolarOne (Qidong) | SF190-27-P195 | 195 W Polycrystalline Module | UL 1703 | 195 | 173.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.494 | 54 | 1 | N | 8.06 | 32.7 | 7.28 | 26.8 | 47 | -0.47 | 0.039 | -0.324 | -0.027 | -0.45 | 1.4288 | 26.1815 | 5.8512 | 24.3262 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19183
Hanwha SolarOne (Qidong) | SF190-27-M200 | 200 W Monocrystalline Module | UL 1703 | 200 | 177.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 8.19 | 33 | 7.49 | 26.7 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.4921 | 25.7464 | 5.9979 | 24.1327 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19208
Hanwha SolarOne (Qidong) | SF190-27-M200B | 200 W Monocrystalline Module, Black Backsheet | UL 1703 | 200 | 177.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 8.19 | 33 | 7.49 | 26.7 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.4322 | 27.6819 | 5.9707 | 24.8511 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19823
Hanwha SolarOne (Qidong) | SF190-27-P200 | 200 W Polycrystalline Module | UL 1703 | 200 | 177.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.494 | 54 | 1 | N | 8.24 | 32.8 | 7.44 | 26.9 | 47 | -0.47 | 0.039 | -0.324 | -0.027 | -0.45 | 1.4602 | 26.2792 | 5.9798 | 24.4169 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19186
Hanwha SolarOne (Qidong) | SF220-30-M200 | 200 W Monocrystalline Module | UL 1703 | 200 | 179.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 7.5 | 36.2 | 6.76 | 29.6 | 45.4 | -0.447 | 0.037 | -0.339 | -0.01 | -0.441 | 1.3682 | 28.8704 | 5.4278 | 26.9944 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.1975
Hanwha SolarOne (Qidong) | SF220-30-M200B | 200 W Monocrystalline Module | UL 1703 | 200 | 178.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 7.8 | 35.2 | 7.17 | 27.9 | 46.1 | -0.454 | 0.022 | -0.339 | -0.01 | -0.446 | 1.3734 | 27.2147 | 5.6261 | 25.3547 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18688
Hanwha SolarOne (Qidong) | SF220-30-P200 | 200 W Polycrystalline Module | UL 1703 | 200 | 180 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 7.52 | 36 | 6.78 | 29.5 | 45.3 | -0.448 | 0.055 | -0.325 | -0.017 | -0.434 | 1.3018 | 28.7541 | 5.424 | 26.9352 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18715
Hanwha SolarOne (Qidong) | SF220-30-P200B | 200 W Polycrystalline Module | UL 1703 | 200 | 178.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 7.82 | 35.7 | 7.25 | 27.6 | 45.9 | -0.459 | 0.074 | -0.338 | -0.001 | -0.458 | 1.4084 | 27.3064 | 5.8132 | 25.3489 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19229
Hanwha SolarOne (Qidong) | SF190-27-M205 | 205 W Monocrystalline Module | UL 1703 | 205 | 182.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 8.26 | 33.1 | 7.65 | 26.8 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.524 | 25.8429 | 6.126 | 24.2231 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19212
Hanwha SolarOne (Qidong) | SF190-27-M205B | 205 W Monocrystalline Module, Black Backsheet | UL 1703 | 205 | 182.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 8.26 | 33.1 | 7.65 | 26.8 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.4628 | 27.7856 | 6.0983 | 24.9441 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19827
Hanwha SolarOne (Qidong) | SF190-27-P205 | 205 W Polycrystalline Module | UL 1703 | 205 | 182.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.494 | 54 | 1 | N | 8.35 | 32.9 | 7.6 | 27 | 47 | -0.47 | 0.039 | -0.324 | -0.027 | -0.45 | 1.4987 | 26.4886 | 6.0239 | 24.1364 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19365
Hanwha SolarOne (Qidong) | SF220-30-M205 | 205 W Monocrystalline Module | UL 1703 | 205 | 184.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 7.65 | 36.3 | 6.9 | 29.7 | 45.4 | -0.447 | 0.037 | -0.339 | -0.01 | -0.441 | 1.3965 | 28.968 | 5.5402 | 27.0856 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19734
Hanwha SolarOne (Qidong) | SF220-30-M205B | 205 W Monocrystalline Module | UL 1703 | 205 | 183.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 7.91 | 35.4 | 7.3 | 28.1 | 46.1 | -0.454 | 0.022 | -0.339 | -0.01 | -0.446 | 1.3983 | 27.4098 | 5.7281 | 25.5365 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18696
Hanwha SolarOne (Qidong) | SF220-30-P205 | 205 W Polycrystalline Module | UL 1703 | 205 | 184.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 7.67 | 36.1 | 6.93 | 29.6 | 45.3 | -0.448 | 0.055 | -0.325 | -0.017 | -0.434 | 1.3306 | 28.8515 | 5.544 | 27.0265 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18726
Hanwha SolarOne (Qidong) | SF220-30-P205B | 205 W Polycrystalline Module | UL 1703 | 205 | 183.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 7.94 | 35.9 | 7.38 | 27.8 | 45.9 | -0.459 | 0.074 | -0.338 | -0.001 | -0.458 | 1.4337 | 27.5043 | 5.9175 | 25.5326 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19235
Hanwha SolarOne (Qidong) | SF190-27-M210 | 210 W Monocrystalline Module | UL 1703 | 210 | 186.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 8.32 | 33.2 | 7.81 | 26.9 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.5558 | 25.9393 | 6.2542 | 24.3135 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19218
Hanwha SolarOne (Qidong) | SF190-27-M210B | 210 W Monocrystalline Module, Black Backsheet | UL 1703 | 210 | 186.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.494 | 54 | 1 | N | 8.32 | 33.2 | 7.81 | 26.9 | 46.7 | -0.478 | 0.04 | -0.328 | -0.055 | -0.434 | 1.4934 | 27.8893 | 6.2258 | 25.0372 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19833
Hanwha SolarOne (Qidong) | SF190-27-P210 | 210 W Polycrystalline Module | UL 1703 | 210 | 186.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.494 | 54 | 1 | N | 8.48 | 33 | 7.75 | 27.1 | 47 | -0.47 | 0.039 | -0.324 | -0.027 | -0.45 | 1.5283 | 26.5867 | 6.1428 | 24.2258 | Rack | Flat Plate | 1 | 1.494 | 1 | 0.19349
Hanwha SolarOne (Qidong) | SF220-30-M210 | 210 W Monocrystalline Module | UL 1703 | 210 | 189.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 7.8 | 36.4 | 7.05 | 29.8 | 45.4 | -0.447 | 0.037 | -0.339 | -0.01 | -0.441 | 1.4269 | 29.0655 | 5.6607 | 27.1768 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19749
Hanwha SolarOne (Qidong) | SF220-30-M210B | 210 W Monocrystalline Module | UL 1703 | 210 | 188.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.02 | 35.6 | 7.43 | 28.3 | 46.1 | -0.454 | 0.022 | -0.339 | -0.01 | -0.446 | 1.4232 | 27.6049 | 5.8301 | 25.7182 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18708
Hanwha SolarOne (Qidong) | SF220-30-P210 | 210 W Polycrystalline Module | UL 1703 | 210 | 189.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 7.82 | 36.2 | 7.08 | 29.7 | 45.3 | -0.448 | 0.055 | -0.325 | -0.017 | -0.434 | 1.3594 | 28.949 | 5.664 | 27.1178 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18739
Hanwha SolarOne (Qidong) | SF220-30-P210B | 210 W Polycrystalline Module | UL 1703 | 210 | 188 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.06 | 36.1 | 7.48 | 28.1 | 45.9 | -0.459 | 0.074 | -0.338 | -0.001 | -0.458 | 1.4531 | 27.8011 | 5.9977 | 25.8082 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19237
Hanwha SolarOne (Qidong) | SF220-30-M215 | 215 W Monocrystalline Module | UL 1703 | 215 | 193.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 7.95 | 36.5 | 7.2 | 29.9 | 45.4 | -0.447 | 0.037 | -0.339 | -0.01 | -0.441 | 1.4573 | 29.163 | 5.7811 | 27.268 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19767
Hanwha SolarOne (Qidong) | SF220-30-M215B | 215 W Monocrystalline Module | UL 1703 | 215 | 192.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.14 | 35.8 | 7.55 | 28.5 | 46.1 | -0.454 | 0.022 | -0.339 | -0.01 | -0.446 | 1.4462 | 27.8 | 5.9243 | 25.9 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18699
Hanwha SolarOne (Qidong) | SF220-30-P215 | 215 W Polycrystalline Module | UL 1703 | 215 | 193.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 7.97 | 36.4 | 7.24 | 29.7 | 45.3 | -0.448 | 0.055 | -0.325 | -0.017 | -0.434 | 1.3901 | 28.949 | 5.792 | 27.1178 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | SF220-30-P215B | 215 W Polycrystalline Module | UL 1703 | 215 | 192.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.17 | 36.3 | 7.6 | 28.3 | 45.9 | -0.459 | 0.074 | -0.338 | -0.001 | -0.458 | 1.4764 | 27.9989 | 6.0939 | 25.9918 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19227
Hanwha SolarOne (Qidong) | SF220-30-M220 | 220 W Monocrystalline Module | UL 1703 | 220 | 198.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.1 | 36.6 | 7.34 | 30 | 45.4 | -0.447 | 0.037 | -0.339 | -0.01 | -0.441 | 1.4856 | 29.2606 | 5.8935 | 27.3592 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19759
Hanwha SolarOne (Qidong) | SF220-30-M220B | 220 W Monocrystalline Module | UL 1703 | 220 | 197.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.24 | 36.1 | 7.64 | 28.8 | 46.1 | -0.454 | 0.022 | -0.339 | -0.01 | -0.446 | 1.4634 | 28.0926 | 5.9949 | 26.1726 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18687
Hanwha SolarOne (Qidong) | SF220-30-P220 | 220 W Polycrystalline Module | UL 1703 | 220 | 198.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.12 | 36.5 | 7.4 | 29.8 | 45.3 | -0.448 | 0.055 | -0.325 | -0.017 | -0.434 | 1.4208 | 29.0465 | 5.92 | 27.2091 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18759
Hanwha SolarOne (Qidong) | SF220-30-P220B | 220 W Polycrystalline Module | UL 1703 | 220 | 197.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.28 | 36.5 | 7.72 | 28.5 | 45.9 | -0.459 | 0.074 | -0.338 | -0.001 | -0.458 | 1.4997 | 28.1968 | 6.1901 | 26.1755 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19221
Hanwha SolarOne (Qidong) | SF220-30-M225 | 225 W Monocrystalline Module | UL 1703 | 225 | 202.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.16 | 36.8 | 7.48 | 30.1 | 45.4 | -0.447 | 0.037 | -0.339 | -0.01 | -0.441 | 1.3523 | 29.6848 | 5.8859 | 28.0241 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.17841
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-230Q | 230 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 230 | 204.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19341
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-230QB | 230 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 230 | 204.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19341
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-230QW | 230 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 230 | 204.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19341
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-230Q | 230 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 230 | 204.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19341
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-230QB | 230 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 230 | 204.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19341
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-230QW | 230 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 230 | 204.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.46 | 36.8 | 7.94 | 29 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5444 | 28.8043 | 6.3627 | 26.2173 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19341
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-235T | 235 W Polycrystalline Module | UL 1703 | 235 | 208.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5523 | 27.7097 | 6.5077 | 25.9498 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18304
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-235TB | 235 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 235 | 211.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5664 | 28.9432 | 6.4561 | 26.474 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19292
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-235TW | 235 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 235 | 208.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5523 | 27.7097 | 6.5077 | 25.9498 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18304
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-235T | 235 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 235 | 211.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5664 | 28.9432 | 6.4561 | 26.474 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19292
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-235TB | 235 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 235 | 211.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5664 | 28.9432 | 6.4561 | 26.474 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19292
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-235TW | 235 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 235 | 211.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.65 | 36.8 | 8.05 | 29.1 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5664 | 28.9432 | 6.4561 | 26.474 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19292
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-235Q | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-235QB | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-235QW | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.55 | 37 | 8.05 | 29.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5466 | 29.0389 | 6.4839 | 26.3205 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19112
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-240T | 240 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-240TW | 240 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-240T | 240 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-240TB | 240 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-240TW | 240 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-240T | 240 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-240TB | 240 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-240TW | 240 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-240T | 240 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-240TB | 240 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-240TW | 240 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 213.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.52 | 37.3 | 7.99 | 30 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5324 | 29.7636 | 6.3872 | 27.1915 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19004
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-240T | 240 W Polycrystalline Module | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5677 | 28.0905 | 6.5723 | 26.3065 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18349
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-240TB | 240 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 215.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19163
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-240TW | 240 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 213.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5677 | 28.0905 | 6.5723 | 26.3065 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18349
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-240T | 240 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 240 | 215.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19163
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-240TB | 240 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 215.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19163
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-240TW | 240 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 215.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19163
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-240T | 240 W Polycrystalline Module | UL 1703 | 240 | 213.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5677 | 28.0905 | 6.5723 | 26.3065 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18349
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-240TB | 240 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19163
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-240TW | 240 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 213.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5677 | 28.0905 | 6.5723 | 26.3065 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18349
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-240QB | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-240Q | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-240QW | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.64 | 37.3 | 8.17 | 29.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5697 | 29.2378 | 6.5806 | 26.5008 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19122
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-240T | 240 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19163
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-240TB | 240 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19163
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-240TW | 240 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.75 | 37.1 | 8.13 | 29.5 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5838 | 29.0372 | 6.5322 | 26.6672 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19163
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-245T | 245 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-245TW | 245 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-245T | 245 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-245TB | 245 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-245TW | 245 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-245T | 245 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-245TB | 245 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-245TW | 245 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-245T | 245 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-245TB | 245 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-245TW | 245 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 218.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.63 | 37.5 | 8.11 | 30.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5554 | 29.962 | 6.4832 | 27.3728 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19021
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-245T | 245 W Polycrystalline Module | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5984 | 29.1861 | 6.6417 | 26.7745 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19041
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-245TB | 245 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 220.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19178
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-245TW | 245 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5984 | 29.1861 | 6.6417 | 26.7745 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19041
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-245T | 245 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 245 | 220.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19178
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-245TB | 245 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 220.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19178
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-245TW | 245 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 220.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19178
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-245T | 245 W Polycrystalline Module | UL 1703 | 245 | 218 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5984 | 29.1861 | 6.6417 | 26.7745 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19041
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-245TB | 245 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19178
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-245TW | 245 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 218 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5984 | 29.1861 | 6.6417 | 26.7745 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19041
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-245 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.8 | 37.5 | 8.25 | 29.7 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6284 | 28.9887 | 6.651 | 27.1863 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19268
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-245Q | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-245QB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-245QW | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.5 | 8.28 | 29.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5908 | 29.4367 | 6.6692 | 26.6811 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19114
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-245T | 245 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19178
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-245TB | 245 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19178
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-245TW | 245 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.8 | 37.2 | 8.25 | 29.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6072 | 29.234 | 6.6287 | 26.848 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19178
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-245W | 245 W Polycrystalline Module | UL 1703 | 245 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.8 | 37.5 | 8.25 | 29.7 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6284 | 28.9887 | 6.651 | 27.1863 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19268
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-250T | 250 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 250 | 222.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-250TW | 250 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 222.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-250T | 250 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 250 | 222.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-250TB | 250 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 222.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-250TW | 250 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 222.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-250T | 250 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-250TB | 250 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-250TW | 250 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-250T | 250 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-250TB | 250 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-250TW | 250 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.73 | 37.6 | 8.22 | 30.4 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5916 | 30.2344 | 6.587 | 27.108 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-250T | 250 W Polycrystalline Module | UL 1703 | 250 | 222.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.6139 | 29.4809 | 6.7061 | 27.0449 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19031
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-250TB | 250 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 225.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19168
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-250TW | 250 W Polycrystalline module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 222.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.6139 | 29.4809 | 6.7061 | 27.0449 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19031
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-250T | 250 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 250 | 225.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19168
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-250TB | 250 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 225.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19168
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-250TW | 250 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 225.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19168
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-250T | 250 W Polycrystalline Module | UL 1703 | 250 | 222.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.6139 | 29.4809 | 6.7061 | 27.0449 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19031
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-250TB | 250 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19168
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-250TW | 250 W Polycrystalline module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 222.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.6139 | 29.4809 | 6.7061 | 27.0449 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19031
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.74 | 37.2 | 8.22 | 30.4 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6225 | 29.672 | 6.6268 | 27.827 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19257
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-250Q | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-250QB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-250QW | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.82 | 37.7 | 8.39 | 29.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6119 | 29.6356 | 6.7578 | 26.8613 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-250T | 250 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19168
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-250TB | 250 W Polycrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19168
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-250TW | 250 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.89 | 37.4 | 8.33 | 30 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.6228 | 29.5293 | 6.6929 | 27.1192 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19168
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-250W | 250 W Polycrystalline Module | UL 1703 | 250 | 227.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.74 | 37.2 | 8.22 | 30.4 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6225 | 29.672 | 6.6268 | 27.827 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19257
Hanwha SolarOne (Qidong) | HSL60P6-PC-3-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.72 | 37.6 | 8.2 | 30.5 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.64 | 29.56 | 6.65 | 27.78 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19391
Hanwha SolarOne (Qidong) | HSL60P6-PC-3-250W | 250 W Polycrystalline Module | UL 1703 | 250 | 227.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.72 | 37.6 | 8.2 | 30.5 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.64 | 29.56 | 6.65 | 27.78 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19391
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-255T | 255 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-255TW | 255 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-255T | 255 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-255TB | 255 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-255TW | 255 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-255T | 255 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 255 | 227.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-255TB | 255 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 255 | 227.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-255TW | 255 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 255 | 227.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-255T | 255 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 255 | 227.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-255TB | 255 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 255 | 227.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-255TW | 255 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 255 | 227.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.81 | 37.8 | 8.32 | 30.6 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.611 | 30.4333 | 6.6672 | 27.2864 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19227
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-255T | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-255TB | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PA-0-255TW | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PA-2-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PA-3-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-255T | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-255TB | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PA-4-255TW | 255 W Polycrystalline Module | UL 1703 | 255 | 228.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.652 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-255T | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-255TB | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-255TW | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PB-2-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PB-3-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-255 | 255 W Polycrystalline Module | UL 1703 | 255 | 232.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.89 | 38 | 8.29 | 30.8 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6363 | 29.8156 | 6.6833 | 28.1932 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19132
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-255Q | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-255QB | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-255QW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.91 | 37.9 | 8.51 | 30 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5899 | 30.0202 | 6.6786 | 27.1141 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18717
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-255T | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-255TB | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-255TW | 255 W Polycrystalline Module | UL 1703 | 255 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6164 | 60 | 1 | N | 8.95 | 37.5 | 8.48 | 30.1 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.597 | 29.911 | 6.5552 | 27.1434 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.18732
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-255W | 255 W Polycrystalline Module | UL 1703 | 255 | 232.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.89 | 38 | 8.29 | 30.8 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6363 | 30.0624 | 6.6833 | 28.1932 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19291
Hanwha SolarOne (Qidong) | HSL60P6-PC-3-255 | 255 W Polycrystalline Module | UL 1703 | 255 | 232.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.86 | 37.8 | 8.31 | 30.7 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.66 | 29.75 | 6.74 | 27.96 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19367
Hanwha SolarOne (Qidong) | HSL60P6-PC-3-255W | 255 W Polycrystalline Module | UL 1703 | 255 | 232.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.86 | 37.8 | 8.31 | 30.7 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.66 | 29.75 | 6.74 | 27.96 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19367
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-260T | 260 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 260 | 231.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HA-0-260TW | 260 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 260 | 231.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-260T | 260 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 260 | 231.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-260TB | 260 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 260 | 231.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HA-4-260TW | 260 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 260 | 231.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.652 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 1 | 1.652 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-260T | 260 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-260TB | 260 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HB-0-260TW | 260 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-260T | 260 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-260TB | 260 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60M6-HB-4-260TW | 260 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 260 | 231.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6164 | 60 | 1 | N | 8.92 | 37.9 | 8.46 | 30.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6381 | 30.5328 | 6.7793 | 27.3756 | Rack | Flat Plate | 0.988 | 1.636 | 1 | 0.19237
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-260T | 260 W Polycrystalline Module | UL 1703 | 260 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.99 | 37.7 | 8.56 | 30.4 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.58 | 30.3 | 6.72 | 27.65 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18413
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-260TW | 260 W Polycrystalline Module | UL 1703 | 260 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.99 | 37.7 | 8.56 | 30.4 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.58 | 30.3 | 6.72 | 27.65 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18413
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-260 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.93 | 38.1 | 8.35 | 31.2 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6482 | 30.4528 | 6.7316 | 28.5593 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19304
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-260T | 260 W Polycrystalline Module | UL 1703 | 260 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.99 | 37.7 | 8.56 | 30.4 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.58 | 30.3 | 6.72 | 27.65 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18413
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-260TW | 260 W Polycrystalline Module | UL 1703 | 260 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.99 | 37.7 | 8.56 | 30.4 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.58 | 30.3 | 6.72 | 27.65 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18413
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-260W | 260 W Polycrystalline Module | UL 1703 | 260 | 236.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 8.93 | 38.1 | 8.35 | 31.2 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6482 | 30.4528 | 6.7316 | 28.5593 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.19304
Hanwha SolarOne (Qidong) | HSL60P6-PC-3-260 | 260 W Polycrystalline Module | UL 1703 | 260 | 236.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.98 | 38.1 | 8.42 | 30.9 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.68 | 29.94 | 6.83 | 28.15 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19346
Hanwha SolarOne (Qidong) | HSL60P6-PC-3-260W | 260 W Polycrystalline Module | UL 1703 | 260 | 236.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 8.98 | 38.1 | 8.42 | 30.9 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.68 | 29.94 | 6.83 | 28.15 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19346
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-265T | 265 W Polycrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.02 | 37.8 | 8.67 | 30.6 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 30.5 | 6.81 | 27.84 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18415
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-265TW | 265 W Polycrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.02 | 37.8 | 8.67 | 30.6 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 30.5 | 6.81 | 27.84 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18415
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-265T | 265 W Polycrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.02 | 37.8 | 8.67 | 30.6 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 30.5 | 6.81 | 27.84 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18415
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-265TW | 265 W Polycrystalline Module | UL 1703 | 265 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.02 | 37.8 | 8.67 | 30.6 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 30.5 | 6.81 | 27.84 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.18415
Hanwha SolarOne (Qidong) | HSL60P6-PC-3-265 | 265 W Polycrystalline Module | UL 1703 | 265 | 241.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.12 | 38.3 | 8.53 | 31.1 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.71 | 30.14 | 6.91 | 28.33 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19449
Hanwha SolarOne (Qidong) | HSL60P6-PC-3-265W | 265 W Polycrystalline Module | UL 1703 | 265 | 241.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 1 | N | 9.12 | 38.3 | 8.53 | 31.1 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.71 | 30.14 | 6.91 | 28.33 | Rack | Flat Plate | 1 | 1.67 | 1 | 0.19449
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-270T | 270 W Polycrystalline Module | UL 1703 | 270 | 242.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.04 | 37.8 | 8.77 | 30.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.62 | 30.7 | 6.89 | 28.02 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.1842
Hanwha SolarOne (Qidong) | HSL60P6-PB-0-270TW | 270 W Polycrystalline Module | UL 1703 | 270 | 242.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.04 | 37.8 | 8.77 | 30.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.62 | 30.7 | 6.89 | 28.02 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.1842
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-270T | 270 W Polycrystalline Module | UL 1703 | 270 | 242.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.04 | 37.8 | 8.77 | 30.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.62 | 30.7 | 6.89 | 28.02 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.1842
Hanwha SolarOne (Qidong) | HSL60P6-PB-4-270TW | 270 W Polycrystalline Module | UL 1703 | 270 | 242.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6007 | 60 | 1 | N | 9.04 | 37.8 | 8.77 | 30.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.62 | 30.7 | 6.89 | 28.02 | Rack | Flat Plate | 0.982 | 1.63 | 1 | 0.1842
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-275T | 275 W Polycrystalline Module | UL 1703 | 275 | 244.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5363 | 34.2411 | 6.3507 | 31.9101 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-275TB | 275 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5311 | 34.6997 | 6.2411 | 31.9329 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19319
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-275TW | 275 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 275 | 244.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5363 | 34.2411 | 6.3507 | 31.9101 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-275T | 275 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5311 | 34.6997 | 6.2411 | 31.9329 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19319
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-275TB | 275 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5311 | 34.6997 | 6.2411 | 31.9329 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19319
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-275TW | 275 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 275 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.38 | 44.5 | 7.75 | 35.6 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5311 | 34.6997 | 6.2411 | 31.9329 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19319
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-280T | 280 W Polycrystalline Module | UL 1703 | 280 | 248.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5541 | 34.3373 | 6.4244 | 31.9997 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19059
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-280TB | 280 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 280 | 251.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5489 | 34.7971 | 6.3136 | 32.0226 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-280TW | 280 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 280 | 248.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5541 | 34.3373 | 6.4244 | 31.9997 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19059
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-280T | 280 W Polycrystalline Module, 1000 V System Voltage | UL 1703 | 280 | 251.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5489 | 34.7971 | 6.3136 | 32.0226 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-280TB | 280 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 280 | 251.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5489 | 34.7971 | 6.3136 | 32.0226 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-280TW | 280 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 280 | 251.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.43 | 44.6 | 7.84 | 35.7 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5489 | 34.7971 | 6.3136 | 32.0226 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19249
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-280Q | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-280QB | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-280QW | 280 W Polycrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.47 | 44.7 | 7.98 | 35.1 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5612 | 34.808 | 6.4276 | 31.4187 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19408
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-285T | 285 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-285TB | 285 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-285TW | 285 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-285T | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-285TB | 285 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-285TW | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-285T | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-285TB | 285 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-285TW | 285 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-285T | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-285TB | 285 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-285TW | 285 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.41 | 44.6 | 7.91 | 36 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 35.86 | 6.3 | 32.51 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19125
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-285T | 285 W Polycrystalline Module | UL 1703 | 285 | 253.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.55 | 35.87 | 6.51 | 33.42 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19508
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-285TB | 285 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 256.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19284
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-285TW | 285 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.55 | 35.87 | 6.51 | 33.42 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19508
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-285T | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 285 | 256.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.57 | 34.99 | 6.4 | 32.2 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19275
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-285TB | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 256.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.57 | 34.99 | 6.4 | 32.2 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19275
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-285TW | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 256.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.57 | 34.99 | 6.4 | 32.2 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19275
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-285T | 285 W Polycrystalline Module | UL 1703 | 285 | 253.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5488 | 35.87 | 6.509 | 33.4207 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19494
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-285TB | 285 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 285 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19284
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-285TW | 285 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 253.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5488 | 35.87 | 6.509 | 33.4207 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19494
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-285Q | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-285QB | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-285QW | 285 W Polycrystalline Module | UL 1703 | 285 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.56 | 44.8 | 8.1 | 35.2 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5847 | 34.9072 | 6.5243 | 31.5082 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19409
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-285T | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 285 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19284
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-285TB | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19284
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-285TW | 285 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 285 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 44.8 | 7.95 | 35.9 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5706 | 34.9921 | 6.4022 | 32.202 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19284
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-290T | 290 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-290TB | 290 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-290TW | 290 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-290T | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-290TB | 290 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-290TW | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 257.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-290T | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-290TB | 290 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-290TW | 290 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-290T | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-290TB | 290 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-290TW | 290 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.48 | 44.9 | 8.01 | 36.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 36.06 | 6.38 | 32.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19149
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-290T | 290 W Polycrystalline Module | UL 1703 | 290 | 257.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5605 | 36.1698 | 6.5581 | 33.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19463
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-290TB | 290 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 260.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19026
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-290TW | 290 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 257.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5605 | 36.1698 | 6.5581 | 33.7 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19463
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-290T | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 290 | 260.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19026
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-290TB | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 260.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19026
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-290TW | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 260.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19026
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-290T | 290 W Polycrystalline Module | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5605 | 36.1698 | 6.5581 | 33.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19463
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-290TB | 290 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 290 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19026
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-290TW | 290 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 258 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5605 | 36.1698 | 6.5581 | 33.7 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19463
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-290Q | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-290QB | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-290QW | 290 W Polycrystalline Module | UL 1703 | 290 | 258.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45 | 8.2 | 35.4 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.5777 | 35.0679 | 6.6053 | 32.0894 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19079
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-290T | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 290 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19026
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-290TB | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19026
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-290TW | 290 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 290 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.57 | 45.1 | 8.01 | 36.2 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5538 | 35.5119 | 6.4375 | 32.8655 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19026
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-290 | 290 W Polycrystalline Module | UL 1703 | 290 | 263.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.49 | 44.4 | 8.02 | 36.2 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.59 | 34.68 | 6.52 | 32.58 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19014
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-290W | 290 W Polycrystalline Module | UL 1703 | 290 | 263.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.49 | 44.4 | 8.02 | 36.2 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.59 | 34.68 | 6.52 | 32.58 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19014
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-295T | 295 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-295TB | 295 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-295TW | 295 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-295T | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-295TB | 295 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-295TW | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-295T | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-295TB | 295 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-295TW | 295 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-295T | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-295TB | 295 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-295TW | 295 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.53 | 45 | 8.08 | 36.5 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.52 | 37.06 | 6.44 | 32.97 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19095
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-295T | 295 W Polycrystalline Module | UL 1703 | 295 | 262.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5819 | 36.3696 | 6.6482 | 33.8862 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19503
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-295TB | 295 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19066
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-295TW | 295 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5819 | 36.3696 | 6.6482 | 33.8862 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19503
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-295T | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 295 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19066
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-295TB | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19066
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-295TW | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 265.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19066
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-295T | 295 W Polycrystalline Module | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5819 | 36.3696 | 6.6482 | 33.8862 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19503
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-295TB | 295 W Polycrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 295 | 265.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19066
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-295TW | 295 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 262.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.9 | -0.48 | 0.05 | -0.35 | -0.02 | -0.49 | 1.5819 | 36.3696 | 6.6482 | 33.8862 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19503
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.55 | 44.9 | 8.11 | 36.4 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6007 | 35.2366 | 6.5481 | 33.2007 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19119
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-295QB | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-295QW | 295 W Polycrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.73 | 45.2 | 8.29 | 35.6 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.595 | 35.2661 | 6.6778 | 32.2707 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19068
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-295T | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet | UL 1703 | 295 | 265.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19066
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-295TB | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 265.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19066
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-295TW | 295 W Polycrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 295 | 265.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.65 | 45.3 | 8.12 | 36.4 | 46.1 | -0.45 | 0.07 | -0.34 | 0.01 | -0.46 | 1.5751 | 35.7081 | 6.5259 | 33.0471 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19066
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-295W | 295 W Polycrystalline Module | UL 1703 | 295 | 268.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.55 | 44.9 | 8.11 | 36.4 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6007 | 35.2366 | 6.5481 | 33.2007 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19119
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-295 | 295 W Polycrystalline Module | UL 1703 | 295 | 268.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.6 | 44.6 | 8.11 | 36.4 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.61 | 34.87 | 6.6 | 32.76 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19031
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-295Q | 295 W Polycrystalline Module | UL 1703 | 295 | 265.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.42 | 45.1 | 8.11 | 36.4 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6241 | 36.1896 | 6.4661 | 33.2022 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19924
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-295QW | 295 W Polycrystalline Module, Black Frame | UL 1703 | 295 | 265.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.42 | 45.1 | 8.11 | 36.4 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6241 | 36.1896 | 6.4661 | 33.2022 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19924
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-295W | 295 W Polycrystalline Module | UL 1703 | 295 | 268.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.6 | 44.6 | 8.11 | 36.4 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.61 | 34.87 | 6.6 | 32.76 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19031
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-300T | 300 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-300TB | 300 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-300TW | 300 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-300T | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-300TB | 300 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-300TW | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 267.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-300T | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-300TB | 300 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-300TW | 300 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-300T | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-300TB | 300 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-300TW | 300 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.61 | 45.2 | 8.17 | 36.7 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.54 | 37.26 | 6.51 | 33.15 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19127
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-300T | 300 W Polycrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 268.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.17974
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-300TW | 300 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 268.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.17974
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-300T | 300 W Polycrystalline Module, 1000 V System voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 268.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.17974
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-300TW | 300 W Polycrystalline Module, 1000 V System voltage, White Backsheet, Black Frame | UL 1703 | 300 | 268.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.17974
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-300T | 300 W Polycrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 268.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.17974
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-300TW | 300 W Polycrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 300 | 268.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.503 | 35.8754 | 6.5619 | 32.9909 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.17974
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-300 | 300 W Polycrystalline Module | UL 1703 | 300 | 273 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.6 | 45 | 8.22 | 36.5 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6224 | 35.3334 | 6.637 | 33.2919 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-300QB | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-300QW | 300 W Polycrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.82 | 45.4 | 8.38 | 35.8 | 47.7 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.6124 | 35.4642 | 6.7503 | 32.452 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1906
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-300T | 300 W Monocrystalline Module, 1000 V System voltage, White Backsheet, Silver Frame | UL 1703 | 300 | 268.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.5 | 35.88 | 6.56 | 32.99 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1794
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-300TW | 300 W Monocrystalline Module, 1000 V System voltage, White Backsheet, Black Frame | UL 1703 | 300 | 268.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.72 | 45.5 | 8.22 | 36.5 | 47.1 | -0.46 | 0.06 | -0.36 | 0.02 | -0.47 | 1.5 | 35.88 | 6.56 | 32.99 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1794
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-300W | 300 W Polycrystalline Module | UL 1703 | 300 | 273 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.6 | 45 | 8.22 | 36.5 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6224 | 35.3334 | 6.637 | 33.2919 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19108
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-300 | 300 W Polycrystalline Module | UL 1703 | 300 | 273.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.7 | 44.8 | 8.2 | 36.6 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.63 | 35.06 | 6.67 | 32.94 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19049
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-300Q | 300 W Polycrystalline Module | UL 1703 | 300 | 269.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.57 | 45.3 | 8.2 | 36.6 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6421 | 36.3885 | 6.5379 | 33.3847 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19918
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-300QW | 300 W Polycrystalline Module, Black Frame | UL 1703 | 300 | 269.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.57 | 45.3 | 8.2 | 36.6 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6421 | 36.3885 | 6.5379 | 33.3847 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19918
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-300W | 300 W Polycrystalline Module | UL 1703 | 300 | 273.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.7 | 44.8 | 8.2 | 36.6 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.63 | 35.06 | 6.67 | 32.94 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19049
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-305T | 305 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-305TB | 305 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-305TW | 305 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-305T | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-305TB | 305 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-305TW | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 305 | 271.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-305T | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-305TB | 305 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-305TW | 305 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-305T | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-305TB | 305 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-305TW | 305 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 305 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.68 | 45.5 | 8.26 | 36.9 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.56 | 37.46 | 6.58 | 33.33 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.1916
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-305T | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-305TB | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PA-0-305TW | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PA-2-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PA-3-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-305T | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-305TB | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PA-4-305TW | 305 W Polycrystalline Module | UL 1703 | 305 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.966 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-305T | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-305TB | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-305TW | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PB-2-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PB-3-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-305 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.65 | 45.2 | 8.33 | 36.6 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6441 | 35.4302 | 6.7258 | 33.3832 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19098
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-305QB | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-305QW | 305 W Polycrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.9 | 45.5 | 8.45 | 36.1 | 46.5 | -0.453 | 0.063 | -0.322 | 0.021 | -0.471 | 1.5978 | 35.9164 | 6.6277 | 32.7007 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18815
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-305T | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-305TB | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-305TW | 305 W Polycrystalline Module | UL 1703 | 305 | 273.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9325 | 72 | 1 | N | 8.8 | 45.7 | 8.32 | 36.7 | 46.2 | -0.467 | 0.061 | -0.359 | 0.013 | -0.476 | 1.5562 | 36.016 | 6.5342 | 33.0554 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.18376
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-305W | 305 W Polycrystalline Module | UL 1703 | 305 | 277.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.65 | 45.2 | 8.33 | 36.6 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6441 | 35.4302 | 6.7258 | 33.3832 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19098
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-305 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.81 | 45 | 8.29 | 36.8 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.64 | 35.25 | 6.74 | 33.12 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.18954
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-305Q | 305 W Polycrystalline Module | UL 1703 | 305 | 274.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.72 | 45.4 | 8.32 | 36.7 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6661 | 36.4879 | 6.6335 | 33.4759 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19932
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-305QW | 305 W Polycrystalline Module, Black Frame | UL 1703 | 305 | 274.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.72 | 45.4 | 8.32 | 36.7 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6661 | 36.4879 | 6.6335 | 33.4759 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19932
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-305W | 305 W Polycrystalline Module | UL 1703 | 305 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.81 | 45 | 8.29 | 36.8 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.64 | 35.25 | 6.74 | 33.12 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.18954
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-310T | 310 W Monocrystalline Module, 600V System Voltage, White Backsheet, Silver Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-310TB | 310 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HA-0-310TW | 310 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-310T | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-310TB | 310 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HA-4-310TW | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 310 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.966 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 1 | 1.966 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-310T | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-310TB | 310 W Monocrystalline Module, 600V System Voltage, Black Backsheet, Black Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HB-0-310TW | 310 W Monocrystalline Module, 600V System Voltage, White Backsheet, Black Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-310T | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Silver Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-310TB | 310 W Monocrystalline Module, 1000 V System Voltage, Black Backsheet, Black Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72M6-HB-4-310TW | 310 W Monocrystalline Module, 1000 V System Voltage, White Backsheet, Black Frame | UL 1703 | 310 | 276.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9325 | 72 | 1 | N | 8.77 | 45.7 | 8.33 | 37.2 | 47.9 | -0.458 | 0.049 | -0.319 | 0.035 | -0.474 | 1.57 | 37.77 | 6.63 | 33.6 | Rack | Flat Plate | 0.988 | 1.956 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-310T | 310 W Polycrystalline Module | UL 1703 | 310 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.85 | 45.7 | 8.43 | 36.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.59 | 36.02 | 6.66 | 33.09 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18475
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-310TW | 310 W Polycrystalline Module | UL 1703 | 310 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.85 | 45.7 | 8.43 | 36.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.59 | 36.02 | 6.66 | 33.09 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18475
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-310 | 310 W Polycrystalline Module | UL 1703 | 310 | 282.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.91 | 45.2 | 8.48 | 36.6 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6737 | 35.4302 | 6.8469 | 33.3832 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-310T | 310 W Polycrystalline Module | UL 1703 | 310 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.85 | 45.7 | 8.43 | 36.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.59 | 36.02 | 6.66 | 33.09 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18475
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-310TW | 310 W Polycrystalline Module | UL 1703 | 310 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.85 | 45.7 | 8.43 | 36.8 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.59 | 36.02 | 6.66 | 33.09 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18475
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-310W | 310 W Polycrystalline Module | UL 1703 | 310 | 282.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.91 | 45.2 | 8.48 | 36.6 | 46.6 | -0.4 | 0.06 | -0.3 | 0.03 | -0.42 | 1.6737 | 35.4302 | 6.8469 | 33.3832 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.19129
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-310 | 310 W Polycrystalline Module | UL 1703 | 310 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.91 | 45.1 | 8.36 | 37.1 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.66 | 35.54 | 6.8 | 33.39 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19031
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-310Q | 310 W Polycrystalline Module | UL 1703 | 310 | 278.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.87 | 45.6 | 8.41 | 36.9 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6842 | 36.6867 | 6.7053 | 33.6583 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19931
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-310QW | 310 W Polycrystalline Module, Black Frame | UL 1703 | 310 | 278.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.87 | 45.6 | 8.41 | 36.9 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6842 | 36.6867 | 6.7053 | 33.6583 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19931
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-310W | 310 W Polycrystalline Module | UL 1703 | 310 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 8.91 | 45.1 | 8.36 | 37.1 | 45.8 | -0.41 | 0.05 | -0.3 | 0.03 | -0.43 | 1.66 | 35.54 | 6.8 | 33.39 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19031
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-315T | 315 W Polycrystalline Module | UL 1703 | 315 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.9 | 45.8 | 8.52 | 37 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 36.21 | 6.73 | 33.27 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18392
Hanwha SolarOne (Qidong) | HSL72P6-PB-0-315TW | 315 W Polycrystalline Module | UL 1703 | 315 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.9 | 45.8 | 8.52 | 37 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 36.21 | 6.73 | 33.27 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18392
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-315T | 315 W Polycrystalline Module | UL 1703 | 315 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.9 | 45.8 | 8.52 | 37 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 36.21 | 6.73 | 33.27 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18392
Hanwha SolarOne (Qidong) | HSL72P6-PB-4-315TW | 315 W Polycrystalline Module | UL 1703 | 315 | 282.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9149 | 72 | 1 | N | 8.9 | 45.8 | 8.52 | 37 | 46.8 | -0.46 | 0.06 | -0.36 | 0.01 | -0.48 | 1.6 | 36.21 | 6.73 | 33.27 | Rack | Flat Plate | 0.982 | 1.95 | 1 | 0.18392
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-315Q | 315 W Polycrystalline Module | UL 1703 | 315 | 283.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.02 | 45.7 | 8.48 | 37.2 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6982 | 36.985 | 6.7611 | 33.9319 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19939
Hanwha SolarOne (Qidong) | HSL72P6-PC-3-315QW | 315 W Polycrystalline Module, Black Frame | UL 1703 | 315 | 283.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9562 | 72 | 1 | N | 9.02 | 45.7 | 8.48 | 37.2 | 47.7 | -0.4257 | 0.0501 | -0.319 | 0.0005 | -0.4258 | 1.6982 | 36.985 | 6.7611 | 33.9319 | Rack | Flat Plate | 0.992 | 1.972 | 1 | 0.19939
Heliene | 20M-100GH | 100 W, 20 cell monocrystalline module, transparent pink greenhouse backsheet | UL 1703 | 100 | 85.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 1 | Y | 9.73 | 13.3 | 9.2 | 11.16 | 46 | -0.587 | 0.0168 | -0.3385 |  |  | 2 | 10.39 | 8.14 | 9.3 | [6 empty] | 2020-01-02
Heliene | 60P215 | 215 W Polycrystalline Module | UL 1703 | 215 | 190.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6632 | 60 | 1 | N | 8.1 | 36.5 | 7.6 | 28.6 | 47.2 | -0.47733 | 0.046803 | -0.31608 | 0.067829 | -0.39041 | 1.5938 | 28.0122 | 6.3877 | 25.4664 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.20765
Heliene | 60P220 | 220 W Polycrystalline Module | UL 1703 | 220 | 194.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6632 | 60 | 1 | N | 8.18 | 36.6 | 7.68 | 28.9 | 47.2 | -0.47733 | 0.046803 | -0.31608 | 0.067829 | -0.39041 | 1.6106 | 28.306 | 6.455 | 25.7335 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.20722
Heliene | 60P225 | 225 W Polycrystalline Module | UL 1703 | 225 | 199.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6632 | 60 | 1 | N | 8.29 | 36.7 | 7.74 | 29.2 | 47.2 | -0.47733 | 0.046803 | -0.31608 | 0.067829 | -0.39041 | 1.6232 | 28.5999 | 6.5054 | 26.0006 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.20632
Heliene | 60M230 | 230 W Monocrystalline Module | UL 1703 | 230 | 207.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6632 | 60 | 1 | N | 8.6 | 36.6 | 7.8 | 29.5 | 46 | -0.44292 | 0.015632 | -0.31522 | -0.062625 | -0.38 | 1.5417 | 28.4687 | 6.1687 | 26.8254 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.19082
Heliene | 60P230 | 230 W Polycrystalline Module | UL 1703 | 230 | 203.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6632 | 60 | 1 | N | 8.38 | 36.8 | 7.8 | 29.5 | 47.2 | -0.47733 | 0.046803 | -0.31608 | 0.067829 | -0.39041 | 1.6357 | 28.8937 | 6.5558 | 26.2677 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.20549
Heliene | 60M235 | 235 W Monocrystalline Module | UL 1703 | 235 | 211.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6632 | 60 | 1 | N | 8.69 | 36.7 | 7.9 | 29.75 | 46 | -0.44292 | 0.015632 | -0.31522 | -0.062625 | -0.38 | 1.5614 | 28.71 | 6.2478 | 27.0527 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.19076
Heliene | 60M240 | 240 W Monocrystalline Module | UL 1703 | 240 | 216.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6632 | 60 | 1 | N | 8.7 | 36.8 | 8 | 30 | 46 | -0.44292 | 0.015632 | -0.31522 | -0.062625 | -0.38 | 1.5812 | 28.9512 | 6.3268 | 27.2801 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.19074
Heliene | 60P240 | 240 W Polycrystalline Module | UL 1703 | 240 | 214.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6413 | 60 | 1 | N | 8.55 | 37.55 | 7.91 | 30.34 | 49 | -0.425 | 0.023 | -0.301 | -0.023 | -0.408 | 1.57 | 29.92 | 6.24 | 27.3 | Rack | Flat Plate | 0.977 | 1.6799 | 1 | 0.19573
Heliene | 60M245 | 245 W Monocrystalline Module | UL 1703 | 245 | 220.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6632 | 60 | 1 | N | 8.71 | 37.26 | 8.18 | 30.03 | 46 | -0.44292 | 0.015632 | -0.31522 | -0.062625 | -0.38 | 1.6168 | 28.9802 | 6.4692 | 27.3074 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.19124
Heliene | 60P245 | 245 W Polycrystalline Module | UL 1703 | 245 | 218.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6413 | 60 | 1 | N | 8.6 | 37.65 | 8.05 | 30.43 | 49 | -0.425 | 0.023 | -0.301 | -0.023 | -0.408 | 1.59 | 30 | 6.35 | 27.38 | Rack | Flat Plate | 0.977 | 1.6799 | 1 | 0.19469
Heliene | 60M250 | 250 W Monocrystalline Module | UL 1703 | 250 | 225.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6632 | 60 | 1 | N | 8.72 | 37.4 | 8.22 | 30.3 | 46 | -0.44292 | 0.015632 | -0.31522 | -0.062625 | -0.38 | 1.6247 | 29.2407 | 6.5008 | 27.5529 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.19003
Heliene | 60P250 | 250 W Polycrystalline Module | UL 1703 | 250 | 223.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6413 | 60 | 1 | N | 8.65 | 37.8 | 8.14 | 30.7 | 49 | -0.425 | 0.023 | -0.301 | -0.023 | -0.408 | 1.61 | 30.27 | 6.42 | 27.62 | Rack | Flat Plate | 0.977 | 1.6799 | 1 | 0.19494
Heliene | 60M255 | 255 W Monocrystalline Module | UL 1703 | 255 | 229.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6632 | 60 | 1 | N | 8.86 | 37.5 | 8.32 | 30.65 | 46.1 | -0.451 | 0.107 | -0.374 | 0.06 | -0.506 | 1.6734 | 28.8937 | 6.7037 | 27.1173 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.18961
Heliene | 60P255 | 255 W Polycrystalline Module | UL 1703 | 255 | 227.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6413 | 60 | 1 | N | 8.71 | 39.9 | 8.2 | 30.95 | 49 | -0.425 | 0.023 | -0.301 | -0.023 | -0.408 | 1.62 | 30.52 | 6.47 | 27.85 | Rack | Flat Plate | 0.977 | 1.6799 | 1 | 0.19389
Heliene | 60M260 | 260 W Monocrystalline Module | UL 1703 | 260 | 234.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6632 | 60 | 1 | N | 8.9 | 37.73 | 8.43 | 30.84 | 46.1 | -0.451 | 0.107 | -0.374 | 0.06 | -0.506 | 1.6955 | 29.0728 | 6.7923 | 27.2854 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.18959
Heliene | 60P260 | 260 W Polycrystalline Module | UL 1703 | 260 | 232.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6153 | 60 | 1 | N | 9 | 38 | 8.56 | 30.71 | 49 | -0.425 | 0.023 | -0.301 | -0.023 | -0.408 | 1.7 | 30.28 | 6.76 | 27.63 | Rack | Flat Plate | 0.979 | 1.65 | 1 | 0.19798
Heliene | 72P260 | 260 W Polycrystalline Module | UL 1703 | 260 | 229.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9523 | 72 | 1 | N | 8.03 | 42.62 | 7.5 | 34.65 | 47.5 | -0.48169 | 0.028588 | -0.31662 | -0.049186 | -0.41923 | 1.5672 | 33.4459 | 6.0448 | 32.261 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.2016
Heliene | 60M265 | 265 W Monocrystalline Module | UL 1703 | 265 | 235.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6632 | 60 | 1 | N | 9 | 38.4 | 8.5 | 31.17 | 47.8 | -0.471 | 0.042 | -0.356 | 0.017 | -0.485 | 1.7174 | 29.28 | 6.6968 | 26.49 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.18975
Heliene | 72P265 | 265 W Polycrystalline Module | UL 1703 | 265 | 234.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9523 | 72 | 1 | N | 8.13 | 42.85 | 7.6 | 34.8 | 47.5 | -0.48169 | 0.028588 | -0.31662 | -0.049186 | -0.41923 | 1.5881 | 33.5907 | 6.1254 | 32.4007 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.2013
Heliene | 60M270 | 270 W Monocrystalline Module | UL 1703 | 270 | 244.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5525 | 60 | 1 | N | 9.1 | 38.92 | 8.71 | 31.31 | 46.5 | -0.441 | 0.062 | -0.333 | 0 | -0.441 | 1.73 | 30.47 | 7 | 28.32 | Rack | Flat Plate | 0.977 | 1.589 | 1 | 0.19523
Heliene | 72P270 | 270 W Polycrystalline Module | UL 1703 | 270 | 238.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9523 | 72 | 1 | N | 8.24 | 43.05 | 7.7 | 35 | 47.5 | -0.48169 | 0.028588 | -0.31662 | -0.049186 | -0.41923 | 1.609 | 33.7837 | 6.206 | 32.5869 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.20132
Heliene | 60M275 | 275 W Monocrystalline Module | UL 1703 | 275 | 248.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5525 | 60 | 1 | N | 9.18 | 39.07 | 8.78 | 31.62 | 46.5 | -0.441 | 0.062 | -0.333 | 0 | -0.441 | 1.74 | 30.78 | 7.06 | 28.6 | Rack | Flat Plate | 0.977 | 1.589 | 1 | 0.19475
Heliene | 72P275 | 275 W Polycrystalline Module | UL 1703 | 275 | 243.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9523 | 72 | 1 | N | 8.27 | 43.36 | 7.8 | 35.25 | 47.5 | -0.48169 | 0.028588 | -0.31662 | -0.049186 | -0.41923 | 1.6299 | 34.025 | 6.2866 | 32.8196 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.20166
Heliene | 60M280 | 280 W Monocrystalline Module | UL 1703 | 280 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5525 | 60 | 1 | N | 9.26 | 39.23 | 8.85 | 31.94 | 46.5 | -0.441 | 0.062 | -0.333 | 0 | -0.441 | 1.76 | 31.09 | 7.12 | 28.89 | Rack | Flat Plate | 0.977 | 1.589 | 1 | 0.19542
Heliene | 72M280 | 280 W Monocrystalline Module | UL 1703 | 280 | 251 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.35 | 44.16 | 7.8 | 35.9 | 47.5 | -0.43357 | 0.026413 | -0.31151 | -0.054644 | -0.3865 | 1.5495 | 34.6132 | 6.2505 | 32.3389 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.19155
Heliene | 60M285 | 285 W Monocrystalline Module | UL 1703 | 285 | 258.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5525 | 60 | 1 | N | 9.34 | 39.38 | 8.92 | 32.24 | 46.5 | -0.441 | 0.062 | -0.333 | 0 | -0.441 | 1.77 | 31.38 | 7.17 | 29.16 | Rack | Flat Plate | 0.977 | 1.589 | 1 | 0.19489
Heliene | 72M285 | 285 W Monocrystalline Module | UL 1703 | 285 | 255.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.45 | 44.4 | 7.9 | 36.1 | 47.5 | -0.43357 | 0.026413 | -0.31151 | -0.054644 | -0.3865 | 1.5694 | 34.8061 | 6.3306 | 32.5191 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.19166
Heliene | 72P285 | 285 W Polycrystalline Module | UL 1703 | 285 | 253.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8381 | 72 | 1 | N | 8.41 | 44.79 | 7.82 | 38.61 | 48.9 | -0.448 | 0.064 | -0.336 | -0.011 | -0.44 | 1.55 | 37.36 | 6.32 | 34.63 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.20319
Heliene | 60M290 | 290 W Monocrystalline Module | UL 1703 | 290 | 262.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5525 | 60 | 1 | N | 9.42 | 39.6 | 8.99 | 32.45 | 46.5 | -0.441 | 0.062 | -0.333 | 0 | -0.441 | 1.78 | 31.58 | 7.23 | 29.35 | Rack | Flat Plate | 0.977 | 1.589 | 1 | 0.19384
Heliene | 72M290 | 290 W Monocrystalline Module | UL 1703 | 290 | 260.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.56 | 44.65 | 8 | 36.25 | 47.5 | -0.43357 | 0.026413 | -0.31151 | -0.054644 | -0.3865 | 1.5893 | 34.9507 | 6.4107 | 32.6542 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.19154
Heliene | 72P290 | 290 W Polycrystalline Module | UL 1703 | 290 | 257.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8381 | 72 | 1 | N | 8.49 | 44.92 | 7.9 | 38.73 | 48.9 | -0.448 | 0.064 | -0.336 | -0.011 | -0.44 | 1.57 | 37.47 | 6.38 | 34.73 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.20285
Heliene | 60M295 | 295 W Monocrystalline Module | UL 1703 | 295 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6026 | 60 | 1 | N | 9.507 | 39.679 | 9.058 | 32.838 | 48 | -0.429 | 0.057 | -0.307 | -0.007 | -0.423 | 1.8063 | 32.282 | 7.3132 | 29.743 | Rack | Flat Plate | 0.979 | 1.637 | 1 | 0.19766
Heliene | 72M295 | 295 W Monocrystalline Module | UL 1703 | 295 | 264.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.67 | 44.77 | 8.1 | 36.4 | 47.5 | -0.43357 | 0.026413 | -0.31151 | -0.054644 | -0.3865 | 1.6091 | 35.0953 | 6.4909 | 32.7893 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.19143
Heliene | 60M300 | 300 W Monocrystalline Module | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6026 | 60 | 1 | N | 9.59 | 39.83 | 9.127 | 33.139 | 48 | -0.429 | 0.057 | -0.307 | -0.007 | -0.423 | 1.82 | 32.5779 | 7.3689 | 30.0157 | Rack | Flat Plate | 0.979 | 1.637 | 1 | 0.19764
Heliene | 72M300 | 300 W Monocrystalline Module | UL 1703 | 300 | 269.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.77 | 44.96 | 8.2 | 36.55 | 47.5 | -0.43357 | 0.026413 | -0.31151 | -0.054644 | -0.3865 | 1.629 | 35.2399 | 6.571 | 32.9245 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.19135
Heliene | 72P300 | 300 W Polycrystalline Module | UL 1703 | 300 | 267 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8381 | 72 | 1 | N | 8.65 | 45.3 | 8.19 | 36.91 | 48.9 | -0.448 | 0.064 | -0.336 | -0.011 | -0.44 | 1.62 | 35.71 | 6.62 | 33.1 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19283
Heliene | 60M305 |  | UL 1703 | 305 | 273.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.904 |  |  | N | 9.45 | 39.49 | 9.03 | 32.51 | 48 | -0.429 | 0.057 | -0.307 | -0.007 | -0.423 | 1.763 | 30.77 | 7.138 | 28.35 | [6 empty] | 2017-08-01 | 2018-06-15
Heliene | 72M305 | 305 W Monocrystalline Module | UL 1703 | 305 | 269.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.86 | 45.1 | 8.32 | 36.65 | 50.1 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.7008 | 33.4998 | 6.6718 | 30.3016 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.18681
Heliene | 72P305 | 305 W Polycrystalline Module | UL 1703 | 305 | 271.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8381 | 72 | 1 | N | 8.73 | 45.51 | 8.29 | 37.06 | 48.9 | -0.448 | 0.064 | -0.336 | -0.011 | -0.44 | 1.64 | 35.86 | 6.7 | 33.24 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19282
Heliene | 60M-310 | 310 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 282.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6517 | 60 | 1 | N | 9.96 | 39.58 | 9.27 | 33.54 | 49.06 | -0.37555 | 0.03755 | -0.27249 | 1.873 |  | 1.873 | 32.37 | 7.436 | 30.17 | [6 empty] | 2020-01-13
Heliene | 72M310 | 310 W Monocrystalline Module | UL 1703 | 310 | 274.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.9 | 45.4 | 8.43 | 36.77 | 50.1 | -0.446 | 0.041 | -0.346 | 0.058 | -0.496 | 1.7233 | 33.6095 | 6.76 | 30.4008 | Rack | Flat Plate | 0.984 | 1.984 | 1 | 0.18684
Heliene | 72P310 | 310 W Polycrystalline Module | UL 1703 | 310 | 276.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8381 | 72 | 1 | N | 8.81 | 45.66 | 8.4 | 37.2 | 48.9 | -0.448 | 0.064 | -0.336 | -0.011 | -0.44 | 1.67 | 35.99 | 6.79 | 33.36 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19388
Heliene | 60M-315 | 315 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 315 | 287 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6517 | 60 | 1 | N | 10.22 | 40.01 | 9.33 | 33.9 | 49.06 | -0.37555 | 0.03755 | -0.27249 | 1.8851 |  | 1.8851 | 32.7174 | 7.4841 | 30.4938 | [6 empty] | 2020-01-13
Heliene | 72M315 | 315 W Monocrystalline Module | UL 1703 | 315 | 279.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8381 | 72 | 1 | N | 9.16 | 45.31 | 8.53 | 37.19 | 49 | -0.461 | 0.062 | -0.34 | -0.026 | -0.441 | 1.69 | 36.21 | 6.85 | 33.34 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19427
Heliene | 72P315 | 315 W Polycrystalline Module | UL 1703 | 315 | 280.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8381 | 72 | 1 | N | 8.89 | 45.81 | 8.5 | 37.33 | 48.9 | -0.448 | 0.064 | -0.336 | -0.011 | -0.44 | 1.69 | 36.12 | 6.87 | 33.48 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19379
Heliene | 60M-320 | 320 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 291.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6517 | 60 | 1 | N | 10.09 | 40.09 | 9.38 | 34.17 | 49.06 | -0.37555 | 0.03755 | -0.27249 | 1.8952 |  | 1.8952 | 32.978 | 7.5242 | 30.7367 | [6 empty] | 2020-01-13
Heliene | 72M320 | 320 W Monocrystalline Module | UL 1703 | 320 | 284.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8381 | 72 | 1 | N | 9.2 | 45.69 | 8.61 | 37.48 | 49 | -0.461 | 0.062 | -0.34 | -0.026 | -0.441 | 1.71 | 36.49 | 6.91 | 33.6 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19499
Heliene | 72P320 | 320 W Polycrystalline Module | UL 1703 | 320 | 285.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8381 | 72 | 1 | N | 8.97 | 45.96 | 8.65 | 37.42 | 48.9 | -0.448 | 0.064 | -0.336 | -0.011 | -0.44 | 1.72 | 36.21 | 6.99 | 33.56 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19463
Heliene | 60M-325 | 325 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 325 | 296.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6517 | 60 | 1 | N | 10.13 | 40.67 | 9.41 | 34.61 | 49.06 | -0.37555 | 0.03755 | -0.27249 | 1.9013 |  | 1.9013 | 33.4027 | 7.5483 | 31.1325 | [6 empty] | 2020-01-13
Heliene | 72M325 | 325 W Monocrystalline Module | UL 1703 | 325 | 288.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8381 | 72 | 1 | N | 9.27 | 46.02 | 8.69 | 37.72 | 49 | -0.461 | 0.062 | -0.34 | -0.026 | -0.441 | 1.72 | 36.73 | 6.97 | 33.82 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19439
Heliene | 72P-325 | 325 W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 325 | 290.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.05 | 46.11 | 8.745 | 37.42 | 50.8 | -0.405 | 0.0388 | -0.3065 | -0.0075 | -0.3995 | 1.72 | 36.03 | 6.869 | 33.41 | [6 empty] | 2018-06-15
Heliene | 72M330 | 330 W Monocrystalline Module | UL 1703 | 330 | 293.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8381 | 72 | 1 | N | 9.34 | 46.31 | 8.76 | 37.96 | 49 | -0.461 | 0.062 | -0.34 | -0.026 | -0.441 | 1.74 | 36.96 | 7.03 | 34.03 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19488
Heliene | 72M335 | 335 W Monocrystalline Module | UL 1703 | 335 | 298.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8381 | 72 | 1 | N | 9.41 | 46.64 | 8.83 | 38.21 | 49 | -0.461 | 0.062 | -0.34 | -0.026 | -0.441 | 1.75 | 37.2 | 7.09 | 34.26 | Rack | Flat Plate | 0.971 | 1.893 | 1 | 0.19433
Heliene | 72M340 | 340 W Monocrystalline Module | UL 1703 | 340 | 307.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9022 | 72 | 1 | N | 9.49 | 46.95 | 8.89 | 38.503 | 47.1 | -0.428 | 0.059 | -0.309 | -0.013 | -0.417 | 1.7719 | 37.6629 | 7.1883 | 35.0717 | Rack | Flat Plate | 0.979 | 1.943 | 1 | 0.19628
Heliene | 72M345 | 345 W Monocrystalline Module | UL 1703 | 345 | 312.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9022 | 72 | 1 | N | 9.57 | 47.26 | 8.95 | 38.843 | 47.1 | -0.428 | 0.059 | -0.309 | -0.013 | -0.417 | 1.7838 | 37.9955 | 7.2368 | 35.3814 | Rack | Flat Plate | 0.979 | 1.943 | 1 | 0.19646
Heliene | 72M350 | 350 W Monocrystalline Module | UL 1703 | 350 | 317.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9022 | 72 | 1 | N | 9.65 | 47.54 | 9.01 | 39.133 | 47.1 | -0.428 | 0.059 | -0.309 | -0.013 | -0.417 | 1.7958 | 38.2792 | 7.2853 | 35.6456 | Rack | Flat Plate | 0.979 | 1.943 | 1 | 0.1964
Heliene | 72M355 | 355 W Monocrystalline Module | UL 1703 | 355 | 321.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9022 | 72 | 1 | N | 9.68 | 47.82 | 9.07 | 39.423 | 47.1 | -0.428 | 0.059 | -0.309 | -0.013 | -0.417 | 1.8077 | 38.5628 | 7.3338 | 35.9098 | Rack | Flat Plate | 0.979 | 1.943 | 1 | 0.19637
Heliene | 72M360 | 360 W Monocrystalline Module | UL 1703 | 360 | 326.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9022 | 72 | 1 | N | 9.71 | 48.1 | 9.13 | 39.713 | 47.1 | -0.428 | 0.059 | -0.309 | -0.013 | -0.417 | 1.8197 | 38.8465 | 7.3823 | 36.1739 | Rack | Flat Plate | 0.979 | 1.943 | 1 | 0.19636
Heliene | 72M365 | 365 W Monocrystalline Module | UL 1703 | 365 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9022 | 72 | 1 | N | 9.74 | 48.38 | 9.19 | 39.953 | 47.1 | -0.428 | 0.059 | -0.309 | -0.013 | -0.417 | 1.8317 | 39.0813 | 7.4309 | 36.3925 | Rack | Flat Plate | 0.979 | 1.943 | 1 | 0.19612
Heliene | 72M370 | 370 W Monocrystalline Module | UL 1703 | 370 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9022 | 72 | 1 | N | 9.77 | 48.66 | 9.28 | 40.153 | 47.1 | -0.428 | 0.059 | -0.309 | -0.013 | -0.417 | 1.8496 | 39.2769 | 7.5036 | 36.5747 | Rack | Flat Plate | 0.979 | 1.943 | 1 | 0.19634
Heliene | 72M-370 Bifacial | 370 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 370 | 339.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.86 | 72 | 1 | N | 9.85 | 47.19 | 9.2 | 40.15 | 48.41 | -0.3675 | 0.0328 | -0.2704 |  |  | 1.838 | 39.09 | 7.275 | 36.73 | [6 empty] | 2020-02-21
Heliene | 72M-375 | 375 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 375 | 347.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.9 | 48.96 | 9.22 | 40.67 | 45.89 | -0.3567 | 0.032 | -0.2638 | 1.851 | 45.89 | 1.851 | 39.288 | 7.391 | 37.3434 | [6 empty] | 2020-10-01
Heliene | 72M-375 Bifacial | 375 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 375 | 343.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.86 | 72 | 1 | N | 9.92 | 47.19 | 9.09 | 41.34 | 48.41 | -0.3675 | 0.0328 | -0.2704 |  |  | 1.816 | 40.2486 | 7.188 | 37.8186 | [6 empty] | 2020-02-21
Heliene | 72M-380 | 380 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 380 | 352.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.98 | 49.55 | 9.23 | 41.2 | 45.89 | -0.3567 | 0.032 | -0.2638 | 1.853 | 45.89 | 1.853 | 39.8 | 7.399 | 37.83 | [6 empty] | 2020-10-01
Heliene | 72M-380 Bifacial | 380 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 380 | 348.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.86 | 72 | 1 | N | 9.63 | 50.51 | 9.23 | 41.2 | 48.41 | -0.3675 | 0.0328 | -0.2704 |  |  | 1.844 | 40.1123 | 7.2987 | 37.6906 | [6 empty] | 2020-02-21
Heliene | 72M-385 | 385 W, 72 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 385 | 355.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 72 | 1 | N | 10.18 | 48.62 | 9.67 | 39.81 | 46.51 | -0.3645 | 0.0392 | -0.2657 |  |  | 1.874 | 39.63 | 7.467 | 37.2 | [6 empty] | 2020-09-21
Heliene | 72M-385 Bifacial | 385 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 385 | 353.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.86 | 72 | 1 | N | 10.06 | 47.9 | 9.24 | 41.76 | 48.41 | -0.3675 | 0.0328 | -0.2704 |  |  | 1.846 | 40.6575 | 7.3066 | 38.2029 | [6 empty] | 2020-02-21
Heliene | 72M-390 | 390 W, 72 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 390 | 360.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 72 | 1 | N | 10.24 | 48.94 | 9.72 | 40.11 | 46.51 | -0.3645 | 0.0392 | -0.2657 |  |  | 1.8837 | 39.9286 | 7.5056 | 37.4803 | [6 empty] | 2020-09-21
Heliene | 72M-390 G1 Bifacial | 390 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61731 | 390 | 360.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.24 | 48.94 | 9.72 | 40.11 | 47.18 | -0.3596 | 0.031 | -0.2641 | 1.8728 |  | 1.8728 | 39.3413 | 7.4616 | 37.2028 | [6 empty] | 2021-06-01
Heliene | 96M390 | 390 W Monocrystalline Module | UL 1703 | 390 | 347.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.574 | 96 | 1 | N | 8.62 | 59.3 | 8.14 | 47.91 | 46.9 | -0.47 | 0.088 | -0.364 | 0.014 | -0.483 | 1.6725 | 45.1372 | 6.5968 | 41.5143 | Rack | Flat Plate | 1.3 | 1.98 | 1 | 0.19357
Heliene | 72M-395 G1 | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 365.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.29 | 49.26 | 9.78 | 40.4 | 47.2 | -0.3527 | 0.0343 | -0.2604 | 1.9122 |  | 1.9122 | 39.6357 | 7.625 | 37.3229 | [6 empty] | 2021-06-01
Heliene | 72M-395 G1 Bifacial | 395 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 364.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.29 | 49.26 | 9.78 | 40.4 | 47.18 | -0.3596 | 0.031 | -0.2641 | 1.8844 |  | 1.8844 | 39.6257 | 7.5076 | 37.4717 | [6 empty] | 2021-06-01
Heliene | 96M395 | 395 W Monocrystalline Module | UL 1703 | 395 | 352.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.574 | 96 | 1 | N | 8.67 | 59.5 | 8.2 | 48.17 | 46.9 | -0.47 | 0.088 | -0.364 | 0.014 | -0.483 | 1.6848 | 45.3822 | 6.6454 | 41.7396 | Rack | Flat Plate | 1.3 | 1.98 | 1 | 0.19357
Heliene | 72M-400 G1 | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 370.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.35 | 49.58 | 9.83 | 40.7 | 47.2 | -0.3527 | 0.0343 | -0.2604 | 1.922 |  | 1.922 | 39.93 | 7.664 | 37.6 | [6 empty] | 2021-06-01
Heliene | 72M-400 G1 Bifacial | 400 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 369.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.35 | 49.58 | 9.83 | 40.7 | 47.18 | -0.3596 | 0.031 | -0.2641 | 1.894 |  | 1.894 | 39.92 | 7.546 | 37.75 | [6 empty] | 2021-06-01
Heliene | 96M400 | 400 W Monocrystalline Module | UL 1703 | 400 | 357.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.574 | 96 | 1 | N | 8.82 | 59.8 | 8.26 | 48.43 | 46.9 | -0.47 | 0.088 | -0.364 | 0.014 | -0.483 | 1.6971 | 45.6271 | 6.6941 | 41.9649 | Rack | Flat Plate | 1.3 | 1.98 | 1 | 0.19359
Heliene | 72M-405 G1 | 405 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 375 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.41 | 49.9 | 9.88 | 41 | 47.2 | -0.3527 | 0.0343 | -0.2604 | 1.9318 |  | 1.9318 | 40.2243 | 7.703 | 37.8771 | [6 empty] | 2021-06-01
Heliene | 72M-405 G1 Bifacial | 405 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 374.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.41 | 49.9 | 9.88 | 41 | 47.18 | -0.3596 | 0.031 | -0.2641 | 1.9036 |  | 1.9036 | 40.2143 | 7.5844 | 38.0283 | [6 empty] | 2021-06-01
Heliene | 96M405 | 405 W Monocrystalline Module | UL 1703 | 405 | 361.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.574 | 96 | 1 | N | 8.86 | 60 | 8.32 | 48.68 | 46.9 | -0.47 | 0.088 | -0.364 | 0.014 | -0.483 | 1.7095 | 45.8627 | 6.7427 | 42.1815 | Rack | Flat Plate | 1.3 | 1.98 | 1 | 0.19358
Heliene | 72M-410 G1 | 410 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61732 | 410 | 379.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.47 | 50.2 | 9.93 | 41.32 | 47.2 | -0.3527 | 0.0343 | -0.2604 | 1.9416 |  | 1.9416 | 40.5383 | 7.742 | 38.1728 | [6 empty] | 2021-06-01
Heliene | 96M410 | 410 W Monocrystalline Module | UL 1703 | 410 | 366.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.574 | 96 | 1 | N | 8.9 | 60.25 | 8.37 | 48.98 | 46.9 | -0.47 | 0.088 | -0.364 | 0.014 | -0.483 | 1.7197 | 46.1453 | 6.7832 | 42.4414 | Rack | Flat Plate | 1.3 | 1.98 | 1 | 0.19356
Heliene | 96M415 | 415 W Monocrystalline Module | UL 1703 | 415 | 370.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.574 | 96 | 1 | N | 8.95 | 60.4 | 8.43 | 49.23 | 46.9 | -0.47 | 0.088 | -0.364 | 0.014 | -0.483 | 1.7321 | 46.3808 | 6.8318 | 42.6581 | Rack | Flat Plate | 1.3 | 1.98 | 1 | 0.19358
Heliene | 96P415 | 415 W Polycrystalline Module | UL 1703 | 415 | 371.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.5201 | 96 | 1 | N | 8.855 | 61.44 | 8.389 | 49.8 | 47.7 | -0.449 | 0.055 | -0.328 | -0.013 | -0.438 | 1.6512 | 48.246 | 6.7828 | 45.1174 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19196
Heliene | 96M420 | 420 W Monocrystalline Module | UL 1703 | 420 | 375.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.574 | 96 | 1 | N | 9 | 60.55 | 8.48 | 49.53 | 46.9 | -0.47 | 0.088 | -0.364 | 0.014 | -0.483 | 1.7423 | 46.6635 | 6.8724 | 42.918 | Rack | Flat Plate | 1.3 | 1.98 | 1 | 0.19358
Heliene | 96P420 | 420 W Polycrystalline Module | UL 1703 | 420 | 376.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.5201 | 96 | 1 | N | 8.925 | 61.515 | 8.464 | 49.96 | 47.7 | -0.449 | 0.055 | -0.328 | -0.013 | -0.438 | 1.666 | 48.401 | 6.8434 | 45.2624 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19199
Heliene | 96P425 | 425 W Polycrystalline Module | UL 1703 | 425 | 380.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.5201 | 96 | 1 | N | 8.995 | 61.585 | 8.529 | 50.14 | 47.7 | -0.449 | 0.055 | -0.328 | -0.013 | -0.438 | 1.6788 | 48.5754 | 6.896 | 45.4255 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19187
Heliene | 96P430 | 430 W Polycrystalline Module | UL 1703 | 430 | 385.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.5201 | 96 | 1 | N | 9.065 | 61.655 | 8.594 | 50.32 | 47.7 | -0.449 | 0.055 | -0.328 | -0.013 | -0.438 | 1.6916 | 48.7498 | 6.9485 | 45.5885 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19178
Heliene | 96P435 | 435 W Polycrystalline Module | UL 1703 | 435 | 390.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.5201 | 96 | 1 | N | 9.135 | 61.725 | 8.659 | 50.525 | 47.7 | -0.449 | 0.055 | -0.328 | -0.013 | -0.438 | 1.7044 | 48.9484 | 7.0011 | 45.7743 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19178
Heliene | 144HC-440 Bifacial | 440 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 410.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.17 | 50.43 | 10.51 | 41.93 | 45.42 | -0.3377 | 0.03025 | -0.26205 |  |  | 2.0489 | 39.0664 | 8.2192 | 38.1019 | [6 empty] | 2021-08-11
Heliene | 96M440 | 440 W Monocrystalline Module | UL 1703 | 440 | 397.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5201 | 96 | 1 | N | 9.331 | 60.992 | 8.736 | 50.657 | 47.3 | -0.433 | 0.055 | -0.31 | -0.02 | -0.417 | 1.7324 | 49.9735 | 7.0462 | 46.1687 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19675
Heliene | 96P440 | 440 W Polycrystalline Module | UL 1703 | 440 | 394.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.5201 | 96 | 1 | N | 9.205 | 61.795 | 8.724 | 50.73 | 47.7 | -0.449 | 0.055 | -0.328 | -0.013 | -0.438 | 1.7172 | 49.147 | 7.0536 | 45.96 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.1918
Heliene | 96M445 | 445 W Monocrystalline Module | UL 1703 | 445 | 401.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5201 | 96 | 1 | N | 9.399 | 61.194 | 8.801 | 50.855 | 47.3 | -0.433 | 0.055 | -0.31 | -0.02 | -0.417 | 1.7452 | 50.1689 | 7.0986 | 46.3491 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19676
Heliene | 144HC-450 | 450 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 415.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.51 | 50.74 | 10.69 | 42.17 | 48.05 | -0.3447 | 0.0324 | -0.265 |  |  | 2.0997 | 39.5387 | 8.4017 | 37.9341 | [6 empty] | 2021-09-13
Heliene | 144HC-450 Bifacial | 450 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 420.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.51 | 50.74 | 10.69 | 42.17 | 45.42 | -0.3377 | 0.03025 | -0.26205 |  |  | 2.084 | 39.29 | 8.36 | 38.32 | [6 empty] | 2021-08-11
Heliene | 96M450 | 450 W Monocrystalline Module | UL 1703 | 450 | 406.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5201 | 96 | 1 | N | 9.472 | 61.393 | 8.863 | 51.056 | 47.3 | -0.433 | 0.055 | -0.31 | -0.02 | -0.417 | 1.7575 | 50.3672 | 7.1486 | 46.5323 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19672
Heliene | 96M455 | 455 W Monocrystalline Module | UL 1703 | 455 | 411.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5201 | 96 | 1 | N | 9.545 | 61.592 | 8.925 | 51.257 | 47.3 | -0.433 | 0.055 | -0.31 | -0.02 | -0.417 | 1.7698 | 50.5655 | 7.1986 | 46.7155 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19669
Heliene | 144HC-460 | 460 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 425.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.93 | 51.26 | 10.88 | 42.31 | 48.05 | -0.3447 | 0.0324 | -0.265 |  |  | 2.137 | 39.67 | 8.551 | 38.06 | [6 empty] | 2021-09-13
Heliene | 144HC-460 Bifacial | 460 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 429.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.93 | 51.26 | 10.88 | 42.31 | 45.42 | -0.3377 | 0.03025 | -0.26205 |  |  | 2.121 | 39.4204 | 8.5086 | 38.4472 | [6 empty] | 2021-08-11
Heliene | 96M460 | 460 W Monocrystalline Module | UL 1703 | 460 | 415.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5201 | 96 | 1 | N | 9.618 | 61.791 | 8.987 | 51.458 | 47.3 | -0.433 | 0.055 | -0.31 | -0.02 | -0.417 | 1.7821 | 50.7637 | 7.2486 | 46.8987 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19667
Heliene | 96M465 | 465 W Monocrystalline Module | UL 1703 | 465 | 420.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5201 | 96 | 1 | N | 9.691 | 61.99 | 9.049 | 51.659 | 47.3 | -0.433 | 0.055 | -0.31 | -0.02 | -0.417 | 1.7944 | 50.962 | 7.2986 | 47.0819 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19666
Heliene | 144HC-470 | 470 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 470 | 434.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 12.27 | 51.54 | 11.07 | 42.45 | 48.05 | -0.3447 | 0.0324 | -0.265 |  |  | 2.1743 | 39.8013 | 8.7003 | 38.1859 | [6 empty] | 2021-09-13
Heliene | 96M470 | 470 W Monocrystalline Module | UL 1703 | 470 | 425.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5201 | 96 | 1 | N | 9.764 | 62.189 | 9.111 | 51.86 | 47.3 | -0.433 | 0.055 | -0.31 | -0.02 | -0.417 | 1.8067 | 51.1603 | 7.3486 | 47.2651 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19666
Heliene | 96M475 | 475 W Monocrystalline Module | UL 1703 | 475 | 429.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5201 | 96 | 1 | N | 9.837 | 62.388 | 9.173 | 52.061 | 47.3 | -0.433 | 0.055 | -0.31 | -0.02 | -0.417 | 1.819 | 51.3586 | 7.3987 | 47.4483 | Rack | Flat Plate | 1.297 | 1.943 | 1 | 0.19668
Helios USA | 6TA | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 229.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6632 | 60 | 1 | N | 8.86 | 37.5 | 8.32 | 30.65 | 46.1 | -0.451 | 0.107 | -0.374 | 0.06 | -0.506 | 1.6734 | 28.8937 | 6.7037 | 27.1173 | Rack | Flat Plate | 0.99 | 1.68 | 1 | 0.18961
Hengdian Group DMEGC Magnetics | DM175-M125-72 | 175 W Monocrystalline Module | UL 1703 | 175 | 154.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2293 | 72 | 1 | N | 5.23 | 44.7 | 4.9 | 35.8 | 46.9 | -0.51 | 0.05 | -0.37 | 0.01 | -0.52 | 0.94231 | 35.5595 | 3.9294 | 31.8913 | Rack | Flat Plate | 0.788 | 1.56 | 1 | 0.19147
Hengdian Group DMEGC Magnetics | DM180-M125-72 | 180 W Monocrystalline Module | UL 1703 | 180 | 158.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2293 | 72 | 1 | N | 5.29 | 44.8 | 5 | 36 | 46.9 | -0.51 | 0.05 | -0.37 | 0.01 | -0.52 | 0.96154 | 35.7581 | 4.0096 | 32.0694 | Rack | Flat Plate | 0.788 | 1.56 | 1 | 0.19102
Hengdian Group DMEGC Magnetics | DM185-M125-72 | 185 W Monocrystalline Module | UL 1703 | 185 | 163.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2293 | 72 | 1 | N | 5.43 | 45 | 5.09 | 36.4 | 46.9 | -0.51 | 0.05 | -0.37 | 0.01 | -0.52 | 0.97885 | 36.1554 | 4.0818 | 32.4258 | Rack | Flat Plate | 0.788 | 1.56 | 1 | 0.1913
Hengdian Group DMEGC Magnetics | DM190-M125-72 | 190 W Monocrystalline Module | UL 1703 | 190 | 167.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2293 | 72 | 1 | N | 5.56 | 45.2 | 5.19 | 36.6 | 46.9 | -0.51 | 0.05 | -0.37 | 0.01 | -0.52 | 1.0163 | 36.7434 | 4.1836 | 32.6983 | Rack | Flat Plate | 0.788 | 1.56 | 1 | 0.19654
Hengdian Group DMEGC Magnetics | DM195-M125-72 | 195 W Monocrystalline Module | UL 1703 | 195 | 172.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2293 | 72 | 1 | N | 6.05 | 45.8 | 5.3 | 36.8 | 46.9 | -0.51 | 0.05 | -0.37 | 0.01 | -0.52 | 1.0378 | 36.9442 | 4.2722 | 32.877 | Rack | Flat Plate | 0.788 | 1.56 | 1 | 0.19662
Hengdian Group DMEGC Magnetics | DM210-P156-60 | 210 W Polycrystalline Module | UL 1703 | 210 | 185.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5844 | 60 | 1 | N | 7.88 | 36.4 | 7.24 | 29 | 47.1 | -0.49 | 0.06 | -0.36 | 0.01 | -0.5 | 1.4073 | 28.3153 | 5.8142 | 26.1302 | Rack | Flat Plate | 0.972 | 1.63 | 1 | 0.18975
Hengdian Group DMEGC Magnetics | DM215-P156-60 | 215 W Polycrystalline Module | UL 1703 | 215 | 190 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5844 | 60 | 1 | N | 7.99 | 36.5 | 7.39 | 29.1 | 47.1 | -0.49 | 0.06 | -0.36 | 0.01 | -0.5 | 1.4364 | 28.4129 | 5.9347 | 26.2203 | Rack | Flat Plate | 0.972 | 1.63 | 1 | 0.18983
Hengdian Group DMEGC Magnetics | DM220-P156-60 | 220 W Polycrystalline Module | UL 1703 | 220 | 194.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5844 | 60 | 1 | N | 8.1 | 36.6 | 7.53 | 29.2 | 47.1 | -0.49 | 0.06 | -0.36 | 0.01 | -0.5 | 1.4636 | 28.5106 | 6.0471 | 26.3104 | Rack | Flat Plate | 0.972 | 1.63 | 1 | 0.18968
Hengdian Group DMEGC Magnetics | DM225-P156-60 | 225 W Polycrystalline Module | UL 1703 | 225 | 204.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.25 | 36.7 | 7.65 | 29.4 | 44.3 | -0.4301 | 0.0801 | -0.4092 | 0.0037 | -0.4336 | 1.5146 | 29.0329 | 6.2412 | 27.5346 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19543
Hengdian Group DMEGC Magnetics | DM230-M156-60 | 230 W Monocrystalline Module | UL 1703 | 230 | 203.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5844 | 60 | 1 | N | 8.35 | 36.8 | 7.78 | 29.6 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.509 | 29.4783 | 6.2808 | 26.1714 | Rack | Flat Plate | 0.972 | 1.63 | 1 | 0.1934
Hengdian Group DMEGC Magnetics | DM230-P156-60 | 230 W Polycrystalline Module | UL 1703 | 230 | 209.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.35 | 36.8 | 7.78 | 29.6 | 44.3 | -0.4301 | 0.0801 | -0.4092 | 0.0037 | -0.4336 | 1.5403 | 29.2304 | 6.3472 | 27.7219 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19576
Hengdian Group DMEGC Magnetics | DM235-M156-60 | 235 W Monocrystalline Module | UL 1703 | 235 | 207.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5844 | 60 | 1 | N | 8.47 | 36.9 | 7.88 | 29.8 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.5284 | 29.6775 | 6.3616 | 26.3482 | Rack | Flat Plate | 0.972 | 1.63 | 1 | 0.19301
Hengdian Group DMEGC Magnetics | DM235-P156-60 | 235 W Polycrystalline Module | UL 1703 | 235 | 214.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.47 | 36.9 | 7.89 | 29.8 | 44.3 | -0.4301 | 0.0801 | -0.4092 | 0.0037 | -0.4336 | 1.5621 | 29.4279 | 6.437 | 27.9092 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19561
Hengdian Group DMEGC Magnetics | DM240-M156-60 | 240 W Monocrystalline Module | UL 1703 | 240 | 212.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5844 | 60 | 1 | N | 8.96 | 37 | 8 | 30 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.5516 | 29.8766 | 6.4584 | 26.525 | Rack | Flat Plate | 0.972 | 1.63 | 1 | 0.19316
Hengdian Group DMEGC Magnetics | DM240-P156-60 | 240 W Polycrystalline Module | UL 1703 | 240 | 218.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.96 | 37.5 | 8 | 30 | 44.3 | -0.4301 | 0.0801 | -0.4092 | 0.0037 | -0.4336 | 1.5839 | 29.6254 | 6.5267 | 28.0965 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19551
Hengdian Group DMEGC Magnetics | DM245-M156-60 | 245 W Monocrystalline Module | UL 1703 | 245 | 216.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5844 | 60 | 1 | N | 9.08 | 37.1 | 8.11 | 30.2 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.573 | 30.0758 | 6.5472 | 26.7019 | Rack | Flat Plate | 0.972 | 1.63 | 1 | 0.1931
Hengdian Group DMEGC Magnetics | DM245-P156-60 | 245 W Polycrystalline Module | UL 1703 | 245 | 223.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 9.08 | 37.6 | 8.01 | 30.6 | 44.3 | -0.4301 | 0.0801 | -0.4092 | 0.0037 | -0.4336 | 1.591 | 30.2246 | 6.4915 | 28.5911 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19628
Hengdian Group DMEGC Magnetics | DM250-M156-60 | 250 W Monocrystalline Module | UL 1703 | 250 | 221.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5844 | 60 | 1 | N | 9.2 | 37.2 | 8.22 | 30.4 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.5943 | 30.275 | 6.636 | 26.8787 | Rack | Flat Plate | 0.972 | 1.63 | 1 | 0.19307
Hengdian Group DMEGC Magnetics | DM250-P156-60 | 250 W Polycrystalline Module | UL 1703 | 250 | 228.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 9.19 | 37.7 | 8.12 | 30.8 | 44.3 | -0.4301 | 0.0801 | -0.4092 | 0.0037 | -0.4336 | 1.6129 | 30.4221 | 6.5807 | 28.778 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19627
Hengdian Group DMEGC Magnetics | DM250-P156-72 | 250 W Polycrystalline Module | UL 1703 | 250 | 220.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8818 | 72 | 1 | N | 7.87 | 43.8 | 7.22 | 34.6 | 47.1 | -0.49 | 0.06 | -0.36 | 0.01 | -0.5 | 1.3774 | 33.9705 | 5.7594 | 31.7025 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.18717
Hengdian Group DMEGC Magnetics | DM255-P156-60 | 255 W Polycrystalline Module | UL 1703 | 255 | 232.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 9.22 | 37.8 | 8.23 | 31 | 44.3 | -0.4301 | 0.0801 | -0.4092 | 0.0037 | -0.4336 | 1.6347 | 30.6197 | 6.6698 | 28.9649 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19629
Hengdian Group DMEGC Magnetics | DM255-P156-72 | 255 W Polycrystalline Module | UL 1703 | 255 | 225.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8818 | 72 | 1 | N | 7.98 | 43.9 | 7.34 | 34.7 | 47.1 | -0.49 | 0.06 | -0.36 | 0.01 | -0.5 | 1.4003 | 34.0687 | 5.8551 | 31.7941 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.18709
Hengdian Group DMEGC Magnetics | DM260-P156-60 | 260 W Polycrystalline Module | UL 1703 | 260 | 237.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 9.37 | 37.9 | 8.34 | 31.2 | 44.3 | -0.4301 | 0.0801 | -0.4092 | 0.0037 | -0.4336 | 1.6566 | 30.8172 | 6.759 | 29.1517 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19635
Hengdian Group DMEGC Magnetics | DM260-P156-72 | 260 W Polycrystalline Module | UL 1703 | 260 | 229.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8818 | 72 | 1 | N | 8.08 | 44 | 7.47 | 34.8 | 47.1 | -0.49 | 0.06 | -0.36 | 0.01 | -0.5 | 1.4251 | 34.1669 | 5.9588 | 31.8858 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.18728
Hengdian Group DMEGC Magnetics | DM265-M156-72 | 265 W Monocrystalline Module | UL 1703 | 265 | 233.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8818 | 72 | 1 | N | 8.19 | 44.1 | 7.59 | 34.9 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.4864 | 35.0809 | 6.0293 | 31.0714 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.19677
Hengdian Group DMEGC Magnetics | DM265-P156-72 | 265 W Polycrystalline Module | UL 1703 | 265 | 234.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8818 | 72 | 1 | N | 8.19 | 44.1 | 7.59 | 34.9 | 47.1 | -0.49 | 0.06 | -0.36 | 0.01 | -0.5 | 1.448 | 34.2651 | 6.0545 | 31.9774 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.18723
Hengdian Group DMEGC Magnetics | DM270-M156-72 | 270 W Monocrystalline Module | UL 1703 | 270 | 238.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8818 | 72 | 1 | N | 8.14 | 44.8 | 7.71 | 35 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.5099 | 35.1814 | 6.1246 | 31.1604 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.19674
Hengdian Group DMEGC Magnetics | DM270-P156-72 | 270 W Polycrystalline Module | UL 1703 | 270 | 238.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8818 | 72 | 1 | N | 8.2 | 44.2 | 7.71 | 35 | 47.1 | -0.49 | 0.06 | -0.36 | 0.01 | -0.5 | 1.4916 | 34.3061 | 6.1893 | 31.4326 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.18953
Hengdian Group DMEGC Magnetics | DM275-M156-72 | 275 W Monocrystalline Module | UL 1703 | 275 | 242.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8818 | 72 | 1 | N | 8.3 | 44.3 | 7.83 | 35.1 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.5334 | 35.2819 | 6.2199 | 31.2494 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.19673
Hengdian Group DMEGC Magnetics | DM275-P156-72 | 275 W Polycrystalline Module | UL 1703 | 275 | 249.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.3 | 44.3 | 7.83 | 35.1 | 45.3 | -0.4308 | 0.0803 | -0.4106 | 0.0245 | -0.4512 | 1.6107 | 33.0742 | 6.3673 | 32.758 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19372
Hengdian Group DMEGC Magnetics | DM280-M156-72 | 280 W Monocrystalline Module | UL 1703 | 280 | 247.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8818 | 72 | 1 | N | 8.33 | 44.8 | 7.95 | 35.2 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.5569 | 35.3824 | 6.3152 | 31.3384 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.19674
Hengdian Group DMEGC Magnetics | DM280-P156-72 | 280 W Polycrystalline Module | UL 1703 | 280 | 254 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.41 | 44.4 | 7.88 | 35.5 | 45.3 | -0.4308 | 0.0803 | -0.4106 | 0.0245 | -0.4512 | 1.621 | 33.4512 | 6.4079 | 33.1313 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19365
Hengdian Group DMEGC Magnetics | DM285-M156-72 | 285 W Monocrystalline Module | UL 1703 | 285 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8818 | 72 | 1 | N | 8.51 | 44.5 | 8 | 35.6 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.5723 | 35.3586 | 6.398 | 32.3015 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.19507
Hengdian Group DMEGC Magnetics | DM285-P156-72 | 285 W Polycrystalline Module | UL 1703 | 285 | 258.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.51 | 44.5 | 8 | 35.6 | 45.3 | -0.4308 | 0.0803 | -0.4106 | 0.0245 | -0.4512 | 1.6456 | 33.5454 | 6.5055 | 33.2247 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1937
Hengdian Group DMEGC Magnetics | DM290-M156-72 | 290 W Monocrystalline Module | UL 1703 | 290 | 256.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8818 | 72 | 1 | N | 8.61 | 44.6 | 8.12 | 35.7 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.5959 | 35.458 | 6.494 | 32.3922 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.19513
Hengdian Group DMEGC Magnetics | DM290-P156-72 | 290 W Polycrystalline Module | UL 1703 | 290 | 263.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.61 | 44.6 | 8.12 | 35.7 | 45.3 | -0.4308 | 0.0803 | -0.4106 | 0.0245 | -0.4512 | 1.6011 | 35.1803 | 6.5966 | 33.1213 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19423
Hengdian Group DMEGC Magnetics | DM295-M156-72 | 295 W Monocrystalline Module | UL 1703 | 295 | 261.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8818 | 72 | 1 | N | 8.71 | 44.7 | 8.24 | 35.8 | 47.1 | -0.5 | 0.05 | -0.35 | 0.01 | -0.52 | 1.6195 | 35.5573 | 6.59 | 32.4829 | Rack | Flat Plate | 0.972 | 1.936 | 1 | 0.1952
Hengdian Group DMEGC Magnetics | DM295-P156-72 | 295 W Polycrystalline Module | UL 1703 | 295 | 268 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.71 | 44.7 | 8.24 | 35.8 | 45.3 | -0.4308 | 0.0803 | -0.4106 | 0.0245 | -0.4512 | 1.6247 | 35.2789 | 6.6941 | 33.2141 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1943
Hengdian Group DMEGC Magnetics | DM300-P156-72 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.81 | 44.8 | 8.36 | 35.9 | 45.3 | -0.4308 | 0.0803 | -0.4106 | 0.0245 | -0.4512 | 1.6484 | 35.3774 | 6.7916 | 33.3068 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19439
Hengdian Group DMEGC Magnetics | DM305-P156-72 | 305 W Polycrystalline Module | UL 1703 | 305 | 277.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.91 | 44.9 | 8.48 | 36 | 45.3 | -0.4308 | 0.0803 | -0.4106 | 0.0245 | -0.4512 | 1.6721 | 35.476 | 6.8891 | 33.3996 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19449
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M191SF | 191W Polycrystalline Module | UL 1703 | 191 | 172.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4509 | 54 | 1 | N | 8 | 33 | 7.3 | 26.3 | 43.6 | -0.477 | 0.039 | -0.332 | -0.025 | -0.454 | 1.4389 | 26.3907 | 5.7652 | 24.587 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19881 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M194SF | 194W Polycrystalline Module | UL 1703 | 194 | 175.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4509 | 54 | 1 | N | 8 | 33.1 | 7.3 | 26.4 | 43.6 | -0.477 | 0.039 | -0.332 | -0.025 | -0.454 | 1.4389 | 26.491 | 5.7652 | 24.6805 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19648 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M197SF | 197W Polycrystalline Module | UL 1703 | 197 | 178.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4509 | 54 | 1 | N | 8.1 | 33.3 | 7.4 | 26.6 | 43.6 | -0.477 | 0.039 | -0.332 | -0.025 | -0.454 | 1.4586 | 26.6917 | 5.8442 | 24.8674 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19763 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M200SF | 200 W Polycrystalline Module | UL 1703 | 200 | 180.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4509 | 54 | 1 | N | 8.2 | 33.6 | 7.5 | 26.7 | 43.6 | -0.477 | 0.039 | -0.332 | -0.025 | -0.454 | 1.4783 | 26.7921 | 5.9231 | 24.9609 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19804 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M203SF | 203W Polycrystalline Module | UL 1703 | 203 | 183.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4509 | 54 | 1 | N | 8.3 | 33.7 | 7.5 | 26.9 | 43.6 | -0.477 | 0.039 | -0.332 | -0.025 | -0.454 | 1.4783 | 26.9928 | 5.9231 | 25.1479 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19657 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M206SF | 206W Polycrystalline Module | UL 1703 | 206 | 186.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4509 | 54 | 1 | N | 8.3 | 33.8 | 7.6 | 26.9 | 43.6 | -0.477 | 0.039 | -0.332 | -0.025 | -0.454 | 1.498 | 26.9928 | 6.0021 | 25.1479 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19629 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S206SF | 206W Monocrystalline Module | UL 1703 | 206 | 186.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4509 | 54 | 1 | N | 8.2 | 33.5 | 7.7 | 26.8 | 44.2 | -0.4682 | 0.1206 | -0.3757 | 0.0581 | -0.5257 | 1.5206 | 26.307 | 7.4579 | 23.4278 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19419 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M209SF | 209W Polycrystalline Module | UL 1703 | 209 | 189.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4509 | 54 | 1 | N | 8.4 | 33.8 | 7.7 | 27.2 | 43.6 | -0.477 | 0.039 | -0.332 | -0.025 | -0.454 | 1.5441 | 27.1254 | 6.2176 | 25.373 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.20041 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S209SF | 209W Monocrystalline Module | UL 1703 | 209 | 189 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4509 | 54 | 1 | N | 8.2 | 33.5 | 7.8 | 26.9 | 44.2 | -0.4682 | 0.1206 | -0.3757 | 0.0581 | -0.5257 | 1.5404 | 26.4052 | 7.5547 | 23.5152 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19461 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M212SF | 212W Polycrystalline Module | UL 1703 | 212 | 188.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4509 | 54 | 1 | N | 8.5 | 33.9 | 7.8 | 27.3 | 44.2 | -0.5445 | 0.1207 | -0.4827 | 0.0549 | -0.5989 | 1.5522 | 26.8548 | 7.5852 | 24.7198 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19662 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M212SG | 212W Polycrystalline Module | UL 1703 | 212 | 191 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8 | 36.4 | 7.2 | 29.6 | 44.2 | -0.476 | 0.038 | -0.337 | -0.017 | -0.461 | 1.4439 | 29.5188 | 5.8139 | 27.6118 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.20104 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S212SF | 212W Monocrystalline Module | UL 1703 | 212 | 191.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4509 | 54 | 1 | N | 8.3 | 33.5 | 7.9 | 27 | 44.2 | -0.4682 | 0.1206 | -0.3757 | 0.0581 | -0.5257 | 1.5601 | 26.5033 | 7.6516 | 23.6026 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19504 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M215SF | 215 W Polycrystalline Module | UL 1703 | 215 | 191.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4509 | 54 | 1 | N | 8.6 | 34.1 | 7.8 | 27.4 | 44.2 | -0.5445 | 0.1207 | -0.4827 | 0.0549 | -0.5989 | 1.5522 | 26.9532 | 7.5852 | 24.8103 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19459 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M215SG | 215 W Polycrystalline Module | UL 1703 | 215 | 193.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8 | 36.5 | 7.2 | 29.8 | 44.2 | -0.476 | 0.038 | -0.337 | -0.017 | -0.461 | 1.4439 | 29.7183 | 5.8139 | 27.7984 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19958 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S215SF | 215 W Monocrystalline Module | UL 1703 | 215 | 194.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4509 | 54 | 1 | N | 8.3 | 33.6 | 8 | 27.1 | 44.2 | -0.4682 | 0.1206 | -0.3757 | 0.0581 | -0.5257 | 1.5799 | 26.6015 | 7.7484 | 23.6901 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19547 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M218SG | 218W Polycrystalline Module | UL 1703 | 218 | 196.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8 | 36.7 | 7.3 | 30 | 44.2 | -0.476 | 0.038 | -0.337 | -0.017 | -0.461 | 1.4639 | 29.9178 | 5.8947 | 27.9849 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.2009 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S218SF | 218W Monocrystalline Module | UL 1703 | 218 | 197.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4509 | 54 | 1 | N | 8.4 | 33.7 | 8.1 | 27.2 | 44.2 | -0.4682 | 0.1206 | -0.3757 | 0.0581 | -0.5257 | 1.5996 | 26.6996 | 7.8453 | 23.7775 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19591 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M221SG | 221W Polycrystalline Module | UL 1703 | 221 | 199.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.1 | 37 | 7.3 | 30.2 | 44.2 | -0.476 | 0.038 | -0.337 | -0.017 | -0.461 | 1.4639 | 30.1172 | 5.8947 | 28.1715 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.1995 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S221SF | 221W Monocrystalline Module | UL 1703 | 221 | 200.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4509 | 54 | 1 | N | 8.5 | 33.9 | 8.1 | 27.3 | 44.2 | -0.4682 | 0.1206 | -0.3757 | 0.0581 | -0.5257 | 1.5996 | 26.7978 | 7.8453 | 23.8649 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19397 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M223MG | 223W Polycrystalline Module | UL 1703 | 223 | 200.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8 | 36.5 | 7.5 | 29.9 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.5238 | 29.0847 | 5.9676 | 26.7457 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19874 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M223MG(BK) | 223W Polycrystalline Module | UL 1703 | 223 | 200.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8 | 36.5 | 7.5 | 29.9 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.5238 | 29.0847 | 5.9676 | 26.7457 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19874 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M224SG | 224W Polycrystalline Module | UL 1703 | 224 | 202 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.1 | 37.14 | 7.4 | 30.2 | 44.2 | -0.476 | 0.038 | -0.337 | -0.017 | -0.461 | 1.484 | 30.1172 | 5.9754 | 28.1715 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19952 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S224SF | 224W Monocrystalline Module | UL 1703 | 224 | 203 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4509 | 54 | 1 | N | 8.5 | 33.9 | 8.2 | 27.4 | 44.2 | -0.4682 | 0.1206 | -0.3757 | 0.0581 | -0.5257 | 1.6194 | 26.896 | 7.9421 | 23.9523 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19444 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S224SG | 224W Monocrystalline Module | UL 1703 | 224 | 196.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4509 | 60 | 1 | N | 8.2 | 37.1 | 7.4 | 30.2 | 44.1 | -0.6071 | 0.078 | -0.4459 | -0.0042 | -0.6025 | 1.48 | 29.5598 | 7.3628 | 26.613 | Rack | Flat Plate | 0.983 | 1.476 | 1 | 0.19531 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M225MG | 225 W Polycrystalline Module | UL 1703 | 225 | 202.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.1 | 36.7 | 7.6 | 30.1 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.5441 | 29.2792 | 6.0472 | 26.9247 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.20094 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M225MG(BK) | 225 W Polycrystalline Module | UL 1703 | 225 | 202.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.1 | 36.7 | 7.6 | 30.1 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.5441 | 29.2792 | 6.0472 | 26.9247 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.20094 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M227SG | 227W Polycrystalline Module | UL 1703 | 227 | 204.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.2 | 37.2 | 7.5 | 30.3 | 44.2 | -0.476 | 0.038 | -0.337 | -0.017 | -0.461 | 1.504 | 30.2169 | 6.0561 | 28.2648 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.20021 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S227SG | 227W Monocrystalline Module | UL 1703 | 227 | 198.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.2 | 37.2 | 7.5 | 30.4 | 44.1 | -0.6071 | 0.078 | -0.4459 | -0.0042 | -0.6025 | 1.5 | 29.7556 | 7.4623 | 26.7892 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19662 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M228MG | 228W Polycrystalline Module | UL 1703 | 228 | 205.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.1 | 36.8 | 7.6 | 30.1 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.5121 | 28.3699 | 7.7473 | 26.9347 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18816 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M228MG(BK) | 228W Polycrystalline Module | UL 1703 | 228 | 205.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.1 | 36.8 | 7.6 | 30.1 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.5441 | 29.2792 | 6.0472 | 26.9247 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.1983 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M230MG | 230 W Polycrystalline Module | UL 1703 | 230 | 207.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.1 | 36.9 | 7.7 | 30.1 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.532 | 28.3699 | 7.8492 | 26.9347 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18897 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M230MG(BK) | 230 W Polycrystalline Module | UL 1703 | 230 | 207 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.1 | 36.9 | 7.7 | 30.1 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.5645 | 29.2792 | 6.1267 | 26.9247 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19916 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M230SG | 230 W Polycrystalline Module | UL 1703 | 230 | 207.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.2 | 37.2 | 7.5 | 30.5 | 44.2 | -0.476 | 0.038 | -0.337 | -0.017 | -0.461 | 1.504 | 30.4164 | 6.0561 | 28.4513 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.1989 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S230SG | 230 W Monocrystalline Module | UL 1703 | 230 | 201.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.3 | 7.5 | 30.6 | 44.1 | -0.6071 | 0.078 | -0.4459 | -0.0042 | -0.6025 | 1.5 | 29.9513 | 7.4623 | 26.9655 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19533 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M233MG | 233W Polycrystalline Module | UL 1703 | 233 | 210.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.2 | 37 | 7.8 | 30.2 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.5519 | 28.4641 | 7.9512 | 27.0242 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18959 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M233MG(BK) | 233W Polycrystalline Module | UL 1703 | 233 | 209.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.2 | 37 | 7.8 | 30.2 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.5848 | 29.3765 | 6.2063 | 27.0141 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19981 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M233SG | 233W Polycrystalline Module | UL 1703 | 233 | 202.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.5 | 7.6 | 29.7 | 46.2 | -0.5822 | 0.117 | -0.4449 | 0.0212 | -0.6102 | 1.5046 | 29.1428 | 7.6 | 26.0186 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18819 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S233MG | 233W Monocrystalline Module | UL 1703 | 233 | 205.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.2 | 37.1 | 7.7 | 30.5 | 47 | -0.4974 | 0.0354 | -0.3696 | -0.0389 | -0.471 | 1.5419 | 30.0899 | 6.0223 | 27.1989 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19913 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S233SG | 233W Monocrystalline Module | UL 1703 | 233 | 204.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.4 | 7.6 | 30.8 | 44.1 | -0.6071 | 0.078 | -0.4459 | -0.0042 | -0.6025 | 1.52 | 30.1471 | 7.5618 | 27.1417 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19667 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M235MG | 235 W Polycrystalline Module | UL 1703 | 235 | 212.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.1 | 7.8 | 30.3 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.5519 | 28.5584 | 7.9512 | 27.1137 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.1886 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M235MG(BK) | 235 W Polycrystalline Module | UL 1703 | 235 | 211.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.1 | 7.8 | 30.3 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.5848 | 29.4738 | 6.2063 | 27.1036 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19876 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M235RG(BK) | 235 W Polycrystalline Module | UL 1703 | 235 | 211.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.3 | 37.1 | 7.8 | 30.5 | 46.8 | -0.43327 | 0.046591 | -0.31459 | -0.026442 | -0.41706 | 1.43 | 30.6 | 6.28 | 27.75 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1862 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S235MG | 235 W Monocrystalline Module | UL 1703 | 235 | 207.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.1 | 7.7 | 30.5 | 47 | -0.4974 | 0.0354 | -0.3696 | -0.0389 | -0.471 | 1.5419 | 30.0899 | 6.0223 | 27.1989 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19743 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S235MG(BK) | 235 W Monocrystalline Module | UL 1703 | 235 | 207.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.1 | 7.7 | 30.5 | 47 | -0.4974 | 0.0354 | -0.3696 | -0.0389 | -0.471 | 1.5419 | 30.0899 | 6.0223 | 27.1989 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19743 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M236SG | 236W Polycrystalline Module | UL 1703 | 236 | 205.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.6 | 7.6 | 29.9 | 46.2 | -0.5822 | 0.117 | -0.4449 | 0.0212 | -0.6102 | 1.5046 | 29.3391 | 7.6 | 26.1938 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18705 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S236SG | 236W Monocrystalline Module | UL 1703 | 236 | 207 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.5 | 7.6 | 31.1 | 44.1 | -0.6071 | 0.078 | -0.4459 | -0.0042 | -0.6025 | 1.52 | 30.4407 | 7.5618 | 27.4061 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19606 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M238MG | 238W Polycrystalline Module | UL 1703 | 238 | 215 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.2 | 7.9 | 30.3 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.5718 | 28.5584 | 8.0531 | 27.1137 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18861 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M238MG(BK) | 238W Polycrystalline Module | UL 1703 | 238 | 214.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.2 | 7.9 | 30.3 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.6051 | 29.4738 | 6.2859 | 27.1036 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19877 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S238MG | 238W Monocrystalline Module | UL 1703 | 238 | 214.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.2 | 7.8 | 30.6 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.5423 | 29.3162 | 7.7509 | 27.8402 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18998 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S238MG(BK) | 238W Monocrystalline Module | UL 1703 | 238 | 210.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.2 | 7.8 | 30.6 | 47 | -0.4974 | 0.0354 | -0.3696 | -0.0389 | -0.471 | 1.562 | 30.1885 | 6.1005 | 27.2881 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19812 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M239SG | 239W Polycrystalline Module | UL 1703 | 239 | 207.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.7 | 7.7 | 30 | 46.2 | -0.5822 | 0.117 | -0.4449 | 0.0212 | -0.6102 | 1.5244 | 29.4372 | 7.7 | 26.2814 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18775 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S239SG | 239W Monocrystalline Module | UL 1703 | 239 | 209.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.6 | 7.6 | 31.3 | 44.1 | -0.6071 | 0.078 | -0.4459 | -0.0042 | -0.6025 | 1.52 | 30.6365 | 7.5618 | 27.5823 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19484 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M240MG | 240 W Polycrystalline Module | UL 1703 | 240 | 216.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.3 | 8 | 30.5 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.5917 | 28.7469 | 8.155 | 27.2926 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19066 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M240MG(BK) | 240 W Polycrystalline Module | UL 1703 | 240 | 216.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.3 | 37.3 | 8 | 30.5 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.6254 | 29.6683 | 6.3654 | 27.2825 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.20093 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M240RG | 240 W Polycrystalline Module | UL 1703 | 240 | 215.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.4 | 37.1 | 7.9 | 30.6 | 46.4 | -0.44776 | 0.022099 | -0.3219 | -0.017815 | -0.43465 | 1.52 | 29.69 | 6.32 | 37.97 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18804 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M240RG(BK) | 240 W Polycrystalline Module | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.4 | 37.1 | 7.9 | 30.6 | 46.8 | -0.43327 | 0.046591 | -0.31459 | -0.026442 | -0.41706 | 1.44 | 30.7 | 6.36 | 27.84 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1842 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M240RW | 240 W Polycrystalline Module | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.3 | 37.7 | 7.9 | 30.5 | 44.2 | -0.49298 | 0.034292 | -0.35 | -0.038961 | -0.46254 | 1.87 | 30.09 | 6.45 | 27.85 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23445 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M240TG | 240 W Polycrystalline Module | UL 1703 | 240 | 215.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.4 | 37.1 | 7.9 | 30.6 | 46.4 | -0.45206 | 0.042035 | -0.34603 | -0.011862 | -0.44515 | 1.52 | 30.29 | 6.28 | 28.35 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19184 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S240MG | 240 W Monocrystalline Module | UL 1703 | 240 | 216.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.3 | 7.9 | 30.7 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.5621 | 29.412 | 7.8503 | 27.9312 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19143 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S240MG(BK) | 240 W Monocrystalline Module | UL 1703 | 240 | 212.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.3 | 7.9 | 30.7 | 47 | -0.4974 | 0.0354 | -0.3696 | -0.0389 | -0.471 | 1.582 | 30.2872 | 6.1787 | 27.3773 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19964 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M242SG | 242W Polycrystalline Module | UL 1703 | 242 | 210.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.8 | 7.7 | 30.2 | 46.2 | -0.5822 | 0.117 | -0.4449 | 0.0212 | -0.6102 | 1.5244 | 29.6334 | 7.7 | 26.4566 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18666 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S242SG | 242W Monocrystalline Module | UL 1703 | 242 | 212.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.7 | 7.7 | 31.5 | 44.1 | -0.6071 | 0.078 | -0.4459 | -0.0042 | -0.6025 | 1.54 | 30.8323 | 7.6613 | 27.7586 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19621 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M243MG | 243W Polycrystalline Module | UL 1703 | 243 | 219.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.5 | 8 | 30.6 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.5917 | 28.8411 | 8.155 | 27.3821 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18892 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M243MG(BK) | 243W Polycrystalline Module | UL 1703 | 243 | 219 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.5 | 8 | 30.6 | 43 | -0.5201 | 0.0437 | -0.3856 | -0.0197 | -0.499 | 1.6254 | 29.7656 | 6.3654 | 27.3719 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.1991 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S243MG | 243W Monocrystalline Module | UL 1703 | 243 | 219.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.3 | 7.9 | 30.8 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.5621 | 29.5078 | 7.8503 | 28.0222 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18969 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S243MG(BK) | 243W Monocrystalline Module | UL 1703 | 243 | 215.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.3 | 7.9 | 30.8 | 47 | -0.4974 | 0.0354 | -0.3696 | -0.0389 | -0.471 | 1.582 | 30.3858 | 6.1787 | 27.4664 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19782 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M245MG | 245 W Polycrystalline Module | UL 1703 | 245 | 221.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.4 | 37.5 | 8.1 | 30.7 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.6116 | 28.9354 | 8.257 | 27.4716 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19034 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M245MG(BK) | 245 W Polycrystalline Module | UL 1703 | 245 | 217.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.4 | 38 | 8 | 30.7 | 46.3 | -0.4988 | 0.043182 | -0.35547 | 0.043 | -0.3555 | 1.8892 | 30.1883 | 6.5542 | 27.8347 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23278 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M245RG | 245 W Polycrystalline Module | UL 1703 | 245 | 220.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.5 | 37.3 | 8 | 30.7 | 46.4 | -0.44776 | 0.022099 | -0.3219 | -0.017815 | -0.43465 | 1.54 | 29.79 | 6.4 | 38.1 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18725 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M245RG(BK) | 245 W Polycrystalline Module | UL 1703 | 245 | 220.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.5 | 37.3 | 8 | 30.7 | 46.8 | -0.43327 | 0.046591 | -0.31459 | -0.026442 | -0.41706 | 1.46 | 30.8 | 6.44 | 27.93 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18354 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M245RW | 245 W Polycrystalline Module | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.4 | 38 | 8 | 30.7 | 44.2 | -0.49298 | 0.034292 | -0.35 | -0.038961 | -0.46254 | 1.9 | 30.29 | 6.54 | 28.03 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.2349 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M245TG | 245 W Polycrystalline Module | UL 1703 | 245 | 220.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.5 | 37.3 | 8 | 30.7 | 46.4 | -0.45206 | 0.042035 | -0.34603 | -0.011862 | -0.44515 | 1.54 | 30.39 | 6.36 | 28.44 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19102 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S245MG | 245 W Monocrystalline Module | UL 1703 | 245 | 221.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.5 | 37.4 | 8 | 30.9 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.5819 | 29.6036 | 7.9496 | 28.1132 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19114 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S245MG(BK) | 245 W Monocrystalline Module | UL 1703 | 245 | 216.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.5 | 37.4 | 8 | 30.9 | 47 | -0.4974 | 0.0354 | -0.3696 | -0.0389 | -0.471 | 1.602 | 30.4845 | 6.2569 | 27.5556 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19933 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S245RG(BK) | 245 W Monocrystalline Module | UL 1703 | 245 | 218.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.54 | 37.5 | 7.99 | 30.71 | 45.8 | -0.49566 | 0.046336 | -0.35079 | -0.017301 | -0.47888 | 1.89 | 30.41 | 6.59 | 27.77 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23459 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M248MG | 248W Polycrystalline Module | UL 1703 | 248 | 224.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.5 | 37.6 | 8.1 | 30.7 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.6116 | 28.9354 | 8.257 | 27.4716 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18804 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M248MG(BK) | 248W Polycrystalline Module | UL 1703 | 248 | 220.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.5 | 38 | 8.1 | 30.7 | 46.3 | -0.4988 | 0.043182 | -0.35547 | 0.043 | -0.3555 | 1.9128 | 30.1883 | 6.6361 | 27.8347 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23284 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S248MG | 248W Monocrystalline Module | UL 1703 | 248 | 223.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.6 | 37.5 | 8 | 31.1 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.5819 | 29.7952 | 7.9496 | 28.2951 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19005 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S248MG(BK) | 248W Monocrystalline Module | UL 1703 | 248 | 219.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.6 | 37.5 | 8 | 31.1 | 47 | -0.4974 | 0.0354 | -0.3696 | -0.0389 | -0.471 | 1.602 | 30.6818 | 6.2569 | 27.734 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.1982 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M250MG | 250 W Polycrystalline Module | UL 1703 | 250 | 226.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.6 | 37.6 | 8.1 | 30.9 | 46.2 | -0.4321 | 0.0469 | -0.3219 | -0.0025 | -0.4347 | 1.6116 | 29.1239 | 8.257 | 27.6506 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18775 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M250MG(BK) | 250 W Polycrystalline Module | UL 1703 | 250 | 222.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.6 | 38.2 | 8.1 | 30.9 | 46.3 | -0.4988 | 0.043182 | -0.35547 | 0.043 | -0.3555 | 1.9128 | 30.385 | 6.6361 | 28.016 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23248 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M250RG | 250 W Polycrystalline Module | UL 1703 | 250 | 224.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.7 | 37.4 | 8.1 | 30.9 | 46.4 | -0.44776 | 0.022099 | -0.3219 | -0.017815 | -0.43465 | 1.56 | 29.98 | 6.48 | 38.34 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18708 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M250RG(BK) | 250 W Polycrystalline Module | UL 1703 | 250 | 225.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.7 | 37.4 | 8.1 | 30.9 | 46.8 | -0.43327 | 0.046591 | -0.31459 | -0.026442 | -0.41706 | 1.48 | 31 | 6.52 | 28.11 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18352 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M250RW | 250 W Polycrystalline Module | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.6 | 38.2 | 8.1 | 30.9 | 44.2 | -0.49298 | 0.034292 | -0.35 | -0.038961 | -0.46254 | 1.92 | 30.49 | 6.62 | 28.21 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23416 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M250TG | 250 W Polycrystalline Module | UL 1703 | 250 | 224.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.7 | 37.4 | 8.1 | 30.9 | 46.4 | -0.45206 | 0.042035 | -0.34603 | -0.011862 | -0.44515 | 1.56 | 30.59 | 6.44 | 28.63 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19088 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S250MG | 250 W Monocrystalline Module | UL 1703 | 250 | 225.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.6 | 37.5 | 8.1 | 31.1 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.6016 | 29.7952 | 8.049 | 28.2951 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19088 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S250MG(BK) | 250 W Monocrystalline Module | UL 1703 | 250 | 226.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.7 | 37.5 | 8.2 | 30.5 | 45.5 | -0.4421 | 0.042857 | -0.31549 | 0.042 | -0.3141 | 1.93 | 29.61 | 6.74 | 26.95 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.22859 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S250RG(BK) | 250 W Monocrystalline Module | UL 1703 | 250 | 223 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.67 | 37.65 | 8.11 | 30.85 | 45.8 | -0.49566 | 0.046336 | -0.35079 | -0.017301 | -0.47888 | 1.92 | 30.54 | 6.69 | 27.9 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23455 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S250RW | 250 W Monocrystalline Module | UL 1703 | 250 | 222.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.7 | 37.5 | 8.2 | 30.5 | 46.6 | -0.49112 | 0.043189 | -0.35646 | -0.022432 | -0.47318 | 1.9169 | 29.995 | 6.7478 | 27.5712 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.22999 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M253MG(BK) | 253W Polycrystalline Module | UL 1703 | 253 | 225 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.7 | 38.2 | 8.2 | 30.9 | 46.3 | -0.4988 | 0.043182 | -0.35547 | 0.043 | -0.3555 | 1.9364 | 30.385 | 6.7181 | 28.016 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23256 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S253MG | 253W Monocrystalline Module | UL 1703 | 253 | 228.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.7 | 37.6 | 8.1 | 31.3 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.6016 | 29.9868 | 8.049 | 28.4771 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18983 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S253MG(BK) | 253W Monocrystalline Module | UL 1703 | 253 | 229.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.8 | 37.6 | 8.3 | 30.5 | 45.5 | -0.4421 | 0.042857 | -0.31549 | 0.042 | -0.3141 | 1.95 | 29.61 | 6.83 | 26.95 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.22822 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M255MG(BK) | 255 W Polycrystalline Module | UL 1703 | 255 | 226.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.7 | 38.3 | 8.2 | 31.1 | 46.3 | -0.4988 | 0.043182 | -0.35547 | 0.043 | -0.3555 | 1.9364 | 30.5817 | 6.7181 | 28.1973 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23223 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M255RG | 255 W Polycrystalline Module | UL 1703 | 255 | 230.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.8 | 37.6 | 8.2 | 31 | 45.72 | -0.44687 | 0.055437 | -0.33351 | -0.0057471 | -0.43443 | 1.5457 | 38.1148 | 6.5411 | 30.0852 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23104 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M255RG(BK) | 255 W Polycrystalline Module | UL 1703 | 255 | 230.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.8 | 37.6 | 8.2 | 31 | 46.42 | -0.43265 | 0.040254 | -0.31766 | -0.012346 | -0.42226 | 1.5737 | 30.1 | 6.5434 | 28.2 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18576 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M255RW | 255 W Polycrystalline Module | UL 1703 | 255 | 229.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.7 | 38.3 | 8.2 | 31.1 | 44.2 | -0.49298 | 0.034292 | -0.35 | -0.038961 | -0.46254 | 1.95 | 30.68 | 6.7 | 28.4 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23461 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M255TG | 255 W Polycrystalline Module | UL 1703 | 255 | 229.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.8 | 37.6 | 8.2 | 31 | 46.4 | -0.45206 | 0.042035 | -0.34603 | -0.011862 | -0.44515 | 1.58 | 30.69 | 6.52 | 28.72 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19016 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S255MG | 255 W Monocrystalline Module | UL 1703 | 255 | 230.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.7 | 37.7 | 8.2 | 31.3 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.6214 | 29.9868 | 8.1484 | 28.4771 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.19067 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S255MG(BK) | 255 W Monocrystalline Module | UL 1703 | 255 | 231 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.8 | 37.7 | 8.3 | 30.8 | 45.5 | -0.4421 | 0.042857 | -0.31549 | 0.042 | -0.3141 | 1.95 | 29.9 | 6.83 | 27.21 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.22865 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S255RG | 255 W Monocrystalline Module | UL 1703 | 255 | 228 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.8 | 37.8 | 8.2 | 31 | 44.6 | -0.51907 | 0.042117 | -0.35957 | -0.012717 | -0.50374 | 1.9283 | 31 | 6.7216 | 28.1913 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23442 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S255RG(BK) | 255 W Monocrystalline Module | UL 1703 | 255 | 227.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.79 | 37.79 | 8.23 | 30.99 | 45.8 | -0.49566 | 0.046336 | -0.35079 | -0.017301 | -0.47888 | 1.95 | 30.68 | 6.79 | 28.02 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23461 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S255RW | 255 W Monocrystalline Module | UL 1703 | 255 | 226.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.8 | 37.7 | 8.3 | 30.8 | 46.6 | -0.49112 | 0.043189 | -0.35646 | -0.022432 | -0.47318 | 1.9403 | 30.2901 | 6.8301 | 27.8424 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23047 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S255TG | 255 W Monocrystalline Module | UL 1703 | 255 | 226.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.79 | 37.79 | 8.23 | 30.99 | 45.6 | -0.51796 | 0.045455 | -0.35328 | -0.034676 | -0.48467 | 1.93 | 30.99 | 6.75 | 28.1 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23455 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S258MG | 258W Monocrystalline Module | UL 1703 | 258 | 233.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.8 | 37.7 | 8.2 | 31.4 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.6214 | 30.0826 | 8.1484 | 28.5681 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18906 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S258MG(BK) | 258W Monocrystalline Module | UL 1703 | 258 | 233.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.9 | 37.7 | 8.4 | 30.8 | 45.5 | -0.4421 | 0.042857 | -0.31549 | 0.042 | -0.3141 | 1.98 | 29.9 | 6.91 | 27.21 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.22947 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M260RG | 260 W Polycrystalline Module | UL 1703 | 260 | 235 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.9 | 37.7 | 8.4 | 31.1 | 45.72 | -0.44687 | 0.055437 | -0.33351 | -0.0057471 | -0.43443 | 1.5834 | 38.2377 | 6.7007 | 30.1823 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23287 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M260RG(BK) | 260 W Polycrystalline Module | UL 1703 | 260 | 235 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.9 | 37.7 | 8.4 | 31.1 | 46.42 | -0.43265 | 0.040254 | -0.31766 | -0.012346 | -0.42226 | 1.6121 | 30.1971 | 6.703 | 28.291 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18724 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M260TG | 260 W Polycrystalline Module | UL 1703 | 260 | 235.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.9 | 37.7 | 8.4 | 31.1 | 46.2 | -0.4212 | 0.03125 | -0.30181 | -0.019802 | -0.40787 | 1.5802 | 31.3039 | 6.7551 | 27.6331 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19026 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S260MG | 260 W Monocrystalline Module | UL 1703 | 260 | 235 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.8 | 37.8 | 8.3 | 31.4 | 45.9 | -0.4451 | 0.0402 | -0.3273 | -0.0455 | -0.403 | 1.6412 | 30.0826 | 8.2477 | 28.5681 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18989 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S260MG(BK) | 260 W Monocrystalline Module | UL 1703 | 260 | 235.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 8.9 | 37.8 | 8.4 | 31 | 45.5 | -0.4421 | 0.042857 | -0.31549 | 0.042 | -0.3141 | 1.98 | 30.1 | 6.91 | 27.39 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.22922 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S260RG | 260 W Monocrystalline Module | UL 1703 | 260 | 233.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.9 | 37.9 | 8.4 | 31.1 | 44.3 | -0.50972 | 0.051525 | -0.35132 | -0.016797 | -0.49295 | 1.9754 | 31.1 | 6.8856 | 28.2822 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23628 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S260RG(BK) | 260 W Monocrystalline Module | UL 1703 | 260 | 232.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.92 | 37.94 | 8.35 | 31.13 | 45.8 | -0.48546 | 0.052576 | -0.32199 | -0.033259 | -0.45791 | 1.54 | 32.28 | 6.92 | 27.99 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1912 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S260RW | 260 W Monocrystalline Module | UL 1703 | 260 | 231.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.9 | 37.8 | 8.4 | 31 | 46.6 | -0.49112 | 0.043189 | -0.35646 | -0.022432 | -0.47318 | 1.9636 | 30.4868 | 6.9124 | 28.0232 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23025 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S260TG | 260 W Monocrystalline Module | UL 1703 | 260 | 231.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 8.92 | 37.94 | 8.35 | 31.13 | 45.6 | -0.51796 | 0.045455 | -0.35328 | -0.034676 | -0.48467 | 1.96 | 31.13 | 6.85 | 28.22 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23467 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S263MG | 263W Monocrystalline Module | UL 1703 | 263 | 235.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9 | 37.8 | 8.5 | 31 | 46.2 | -0.4767 | 0.055614 | -0.3613 | 0.0556 | -0.3614 | 1.9878 | 30.5 | 6.9098 | 27.4 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23052 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S263MG(BK) | 263W Monocrystalline Module | UL 1703 | 263 | 238.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9 | 37.8 | 8.5 | 31 | 45.5 | -0.4421 | 0.042857 | -0.31549 | 0.042 | -0.3141 | 2 | 30.1 | 6.99 | 27.39 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.2289 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M265RG | 265 W Polycrystalline Module | UL 1703 | 265 | 239.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.1 | 37.9 | 8.5 | 31.3 | 45.72 | -0.44687 | 0.055437 | -0.33351 | -0.0057471 | -0.43443 | 1.6023 | 38.4836 | 6.7805 | 30.3764 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23269 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M265RG(BK) | 265 W Polycrystalline Module | UL 1703 | 265 | 239.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.1 | 37.9 | 8.5 | 31.3 | 46.42 | -0.43265 | 0.040254 | -0.31766 | -0.012346 | -0.42226 | 1.6313 | 30.3913 | 6.7828 | 28.4729 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18709 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M265TG | 265 W Polycrystalline Module | UL 1703 | 265 | 240.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.1 | 37.9 | 8.5 | 31.3 | 46.2 | -0.4212 | 0.03125 | -0.30181 | -0.019802 | -0.40787 | 1.599 | 31.5052 | 6.8355 | 27.8108 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1901 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S265MG | 265 W Monocrystalline Module | UL 1703 | 265 | 237.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9 | 37.9 | 8.5 | 31.2 | 46.2 | -0.4767 | 0.055614 | -0.3613 | 0.0556 | -0.3614 | 1.9878 | 30.6968 | 6.9098 | 27.5768 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23025 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S265MG(BK) | 265 W Monocrystalline Module | UL 1703 | 265 | 240.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9 | 37.9 | 8.5 | 31.2 | 45.5 | -0.4421 | 0.042857 | -0.31549 | 0.042 | -0.3141 | 2 | 30.29 | 6.99 | 27.57 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.2286 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S265RG | 265 W Monocrystalline Module | UL 1703 | 265 | 238.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9 | 38.1 | 8.5 | 31.3 | 44.3 | -0.50972 | 0.051525 | -0.35132 | -0.016797 | -0.49295 | 1.9989 | 31.3 | 6.9675 | 28.4641 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23609 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S265RG(BK) | 265 W Monocrystalline Module | UL 1703 | 265 | 237.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.05 | 38.09 | 8.47 | 31.27 | 45.8 | -0.48546 | 0.052576 | -0.32199 | -0.033259 | -0.45791 | 1.56 | 32.43 | 7.01 | 28.11 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19091 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S265RW | 265 W Monocrystalline Module | UL 1703 | 265 | 236 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9 | 37.9 | 8.5 | 31.2 | 46.6 | -0.49112 | 0.043189 | -0.35646 | -0.022432 | -0.47318 | 1.987 | 30.6834 | 6.9947 | 28.204 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23007 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S265TG | 265 W Monocrystalline Module | UL 1703 | 265 | 235.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.05 | 38.09 | 8.47 | 31.27 | 45.6 | -0.51796 | 0.045455 | -0.35328 | -0.034676 | -0.48467 | 1.99 | 31.27 | 6.94 | 28.35 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23482 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S268MG | 268W Monocrystalline Module | UL 1703 | 268 | 240.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9.1 | 38 | 8.6 | 31.2 | 46.2 | -0.4767 | 0.055614 | -0.3613 | 0.0556 | -0.3614 | 2.0111 | 30.6968 | 6.9911 | 27.5768 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23036 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S268MG(BK) | 268W Monocrystalline Module | UL 1703 | 268 | 243.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9.1 | 38 | 8.6 | 31.2 | 45.5 | -0.4421 | 0.042857 | -0.31549 | 0.042 | -0.3141 | 2.02 | 30.29 | 7.07 | 27.57 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.22831 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M270RG | 270 W Polycrystalline Module | UL 1703 | 270 | 244.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.2 | 38 | 8.6 | 31.4 | 45.72 | -0.44687 | 0.055437 | -0.33351 | -0.0057471 | -0.43443 | 1.6211 | 38.6066 | 6.8602 | 30.4734 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.2318 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M270RG(BK) | 270 W Polycrystalline Module | UL 1703 | 270 | 244.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.2 | 38 | 8.6 | 31.4 | 46.42 | -0.43265 | 0.040254 | -0.31766 | -0.012346 | -0.42226 | 1.6505 | 30.4884 | 6.8626 | 28.5639 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18637 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M270TG | 270 W Polycrystalline Module | UL 1703 | 270 | 245.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.2 | 38 | 8.6 | 31.4 | 46.2 | -0.4212 | 0.03125 | -0.30181 | -0.019802 | -0.40787 | 1.6178 | 31.6059 | 6.916 | 27.8997 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18938 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S270MG | 270 W Monocrystalline Module | UL 1703 | 270 | 242.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9.1 | 38.1 | 8.7 | 31.4 | 46.2 | -0.4767 | 0.055614 | -0.3613 | 0.0556 | -0.3614 | 2.0345 | 30.8935 | 7.0724 | 27.7535 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23279 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S270MG(BK) | 270 W Monocrystalline Module | UL 1703 | 270 | 245 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9.1 | 38.1 | 8.7 | 31.4 | 45.5 | -0.4421 | 0.042857 | -0.31549 | 0.042 | -0.3141 | 2.05 | 30.49 | 7.15 | 27.74 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.2315 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S270RG | 270 W Monocrystalline Module | UL 1703 | 270 | 242.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.2 | 38.2 | 8.6 | 31.4 | 44.3 | -0.50972 | 0.051525 | -0.35132 | -0.016797 | -0.49295 | 2.0224 | 31.4 | 7.0495 | 28.555 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.2352 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S270RG(BK) | 270 W Monocrystalline Module | UL 1703 | 270 | 242 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.17 | 38.23 | 8.59 | 31.41 | 45.8 | -0.48546 | 0.052576 | -0.32199 | -0.033259 | -0.45791 | 1.58 | 32.57 | 7.11 | 28.24 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19059 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S270TG | 270 W Monocrystalline Module | UL 1703 | 270 | 240.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.17 | 38.23 | 8.59 | 31.41 | 45.6 | -0.51796 | 0.045455 | -0.35328 | -0.034676 | -0.48467 | 2.02 | 31.41 | 7.04 | 28.48 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23499 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M273MI | 273W Polycrystalline Module | UL 1703 | 273 | 245.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.2 | 43.9 | 7.6 | 36.2 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.5443 | 35.476 | 6.2335 | 33.0971 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20068 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S273MG | 273W Monocrystalline Module | UL 1703 | 273 | 244.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9.2 | 38.1 | 8.7 | 31.6 | 46.2 | -0.4767 | 0.055614 | -0.3613 | 0.0556 | -0.3614 | 2.0345 | 31.0903 | 7.0724 | 27.9303 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.2317 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M275MI | 275 W Polycrystalline Module | UL 1703 | 275 | 247.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.2 | 44 | 7.6 | 36.3 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.5443 | 35.574 | 6.2335 | 33.1886 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.19978 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M275RG | 275 W Polycrystalline Module | UL 1703 | 275 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.3 | 38.2 | 8.7 | 31.5 | 45.72 | -0.44687 | 0.055437 | -0.33351 | -0.0057471 | -0.43443 | 1.64 | 38.7295 | 6.94 | 30.5705 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23097 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M275RG(BK) | 275 W Polycrystalline Module | UL 1703 | 275 | 249 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.3 | 38.2 | 8.7 | 31.5 | 46.42 | -0.43265 | 0.040254 | -0.31766 | -0.012346 | -0.42226 | 1.6697 | 30.5855 | 6.9424 | 28.6548 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1857 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M275TG | 275 W Polycrystalline Module | UL 1703 | 275 | 249.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 9.3 | 38.2 | 8.7 | 31.5 | 46.2 | -0.4212 | 0.03125 | -0.30181 | -0.019802 | -0.40787 | 1.6366 | 31.7066 | 6.9964 | 27.9885 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1887 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S275MG | 275 W Monocrystalline Module | UL 1703 | 275 | 246.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 1 | N | 9.2 | 38.1 | 8.7 | 31.7 | 46.2 | -0.4767 | 0.055614 | -0.3613 | 0.0556 | -0.3614 | 2.0345 | 31.1887 | 7.0724 | 28.0187 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.23074 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S275RG | 275 W Monocrystalline Module | UL 1703 | 275 | 247.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.3 | 38.4 | 8.7 | 31.6 | 44.3 | -0.50972 | 0.051525 | -0.35132 | -0.016797 | -0.49295 | 2.0459 | 31.6 | 7.1315 | 28.7369 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23509 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S275RG(BK) | 275 W Monocrystalline Module | UL 1703 | 275 | 248.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.3 | 38.4 | 8.7 | 31.6 | 46.48 | -0.43723 | 0.048604 | -0.30206 | -0.029573 | -0.40958 | 1.6485 | 31.2971 | 7.0038 | 28.4703 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18761 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S275TG | 275 W Monocrystalline Module | UL 1703 | 275 | 245 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.3 | 38.38 | 8.71 | 31.55 | 45.6 | -0.51796 | 0.045455 | -0.35328 | -0.034676 | -0.48467 | 2.05 | 31.55 | 7.14 | 28.61 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23519 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M278MI | 278W Polycrystalline Module | UL 1703 | 278 | 250 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 44.2 | 7.7 | 36.4 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.5647 | 35.672 | 6.3155 | 33.28 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20077 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M280MI | 280 W Polycrystalline Module | UL 1703 | 280 | 251.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 44.4 | 7.7 | 36.5 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.5647 | 35.77 | 6.3155 | 33.3714 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.19988 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S280MI | 280 W Monocrystalline Module | UL 1703 | 280 | 249.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 44.5 | 7.7 | 36.5 | 46.5 | -0.477 | 0.048 | -0.351 | -0.002 | -0.473 | 1.5658 | 34.7625 | 6.2317 | 32.4583 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.1944 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S280RG | 280 W Monocrystalline Module | UL 1703 | 280 | 254.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.4 | 38.5 | 8.8 | 31.7 | 46.04 | -0.4316 | 0.034895 | -0.2928 | -0.02734 | -0.40682 | 1.6841 | 31.9058 | 7.0511 | 29.4357 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1919 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S280RG(BK) | 280 W Monocrystalline Module | UL 1703 | 280 | 253.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.4 | 38.5 | 8.8 | 31.7 | 46.48 | -0.43723 | 0.048604 | -0.30206 | -0.029573 | -0.40958 | 1.6675 | 31.3962 | 7.0843 | 28.5604 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18697 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S280TG | 280 W Monocrystalline Module | UL 1703 | 280 | 251.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.4 | 38.5 | 8.8 | 31.7 | 46.16 | -0.46799 | 0.053481 | -0.31745 | -0.029724 | -0.44007 | 1.6255 | 32.5397 | 7.0251 | 28.8659 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1889 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M283MI | 283W Polycrystalline Module | UL 1703 | 283 | 254.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 44.5 | 7.8 | 36.6 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.585 | 35.868 | 6.3975 | 33.4629 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20088 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S283MI | 283W Monocrystalline Module | UL 1703 | 283 | 253.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 44.6 | 7.8 | 36.6 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6026 | 35.9814 | 6.3919 | 32.9915 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20376 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M285MI | 285 W Polycrystalline Module | UL 1703 | 285 | 256.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 44.7 | 7.8 | 36.7 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.585 | 35.966 | 6.3975 | 33.5543 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20002 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S285MI | 285 W Monocrystalline Module | UL 1703 | 285 | 255.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 44.7 | 7.8 | 36.7 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6026 | 36.0797 | 6.3919 | 33.0817 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20288 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S285RG | 285 W Monocrystalline Module | UL 1703 | 285 | 258.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.5 | 38.7 | 8.9 | 31.8 | 46.04 | -0.4316 | 0.034895 | -0.2928 | -0.02734 | -0.40682 | 1.7033 | 32.0065 | 7.1312 | 29.5286 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19128 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S285RG(BK) | 285 W Monocrystalline Module | UL 1703 | 285 | 258 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.5 | 38.7 | 8.9 | 31.8 | 46.48 | -0.43723 | 0.048604 | -0.30206 | -0.029573 | -0.40958 | 1.6864 | 31.4952 | 7.1648 | 28.6505 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18637 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S285TG | 285 W Monocrystalline Module | UL 1703 | 285 | 256.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.5 | 38.7 | 8.9 | 31.8 | 46.16 | -0.46799 | 0.053481 | -0.31745 | -0.029724 | -0.44007 | 1.6439 | 32.6424 | 7.1049 | 28.957 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18829 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M288MI | 288W Polycrystalline Module | UL 1703 | 288 | 259.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 44.9 | 7.8 | 36.8 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.585 | 36.064 | 6.3975 | 33.6457 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.19847 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S288MI | 288W Monocrystalline Module | UL 1703 | 288 | 258.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 44.8 | 7.8 | 36.9 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6026 | 36.2763 | 6.3919 | 33.262 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20186 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S290FG | 290 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 290 | 269 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 9.59 | 38.87 | 9.15 | 31.7 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.7728 | 30.5447 | 7.1418 | 29.4417 | [6 empty] | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S290HG | 290 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc, wildcard "X" = 1 | UL 1703 | 290 | 269 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.59 | 38.87 | 9.15 | 31.7 | 44.64 | -0.365 | 0.042 | -0.284 | 1.8251 | 31.1903 | 1.7728 | 30.5447 | 7.1418 | 29.4417 | [6 empty] | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiD-S290RG(BK) | 290 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 290 | 262 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.75 | 39.6 | 9.2 | 31.9 | 48.9 | -0.403 | 0.032 | -0.288 | 1.7919 | 30.3542 | 1.7919 | 30.3542 | 7.0977 | 28.5525 | [6 empty] | 2019-09-03 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M290MI | 290 W Polycrystalline Module | UL 1703 | 290 | 261 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 45.1 | 7.9 | 37 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.6053 | 36.26 | 6.4796 | 33.8286 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20072 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M290RI | 290 W Polycrystalline Module | UL 1703 | 290 | 258.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 60 | 1 | N | 8.5 | 44.5 | 8.2 | 35.4 | 46.1 | -0.48521 | 0.053377 | -0.36623 | -0.025404 | -0.46341 | 1.9316 | 35.2022 | 6.7039 | 32.3346 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23448 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M290TI | 290 W Polycrystalline Module | UL 1703 | 290 | 259.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.5 | 44.5 | 8.2 | 35.4 | 46.2 | -0.49611 | 0.046237 | -0.34857 | -0.036824 | -0.46331 | 1.925 | 35.2017 | 6.7119 | 32.3261 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23366 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S290MI | 290 W Monocrystalline Module | UL 1703 | 290 | 260.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 45 | 7.9 | 37 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6232 | 36.3746 | 6.4739 | 33.3521 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20359 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S290RG | 290 W Monocrystalline Module | UL 1703 | 290 | 263.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.7 | 38.8 | 9.1 | 32 | 46.04 | -0.4316 | 0.034895 | -0.2928 | -0.02734 | -0.40682 | 1.7415 | 32.2078 | 7.2915 | 29.7143 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19342 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S290RG(BK) | 290 W Monocrystalline Module | UL 1703 | 290 | 262.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.7 | 38.8 | 9.1 | 32 | 46.48 | -0.43723 | 0.048604 | -0.30206 | -0.029573 | -0.40958 | 1.7243 | 31.6933 | 7.3258 | 28.8307 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18845 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S290TG | 290 W Monocrystalline Module | UL 1703 | 290 | 261.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.7 | 38.8 | 9.1 | 32 | 46.16 | -0.46799 | 0.053481 | -0.31745 | -0.029724 | -0.44007 | 1.6809 | 32.8477 | 7.2645 | 29.1391 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19039 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M293MI | 293W Polycrystalline Module | UL 1703 | 293 | 263.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 45.2 | 7.9 | 37.1 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.6053 | 36.358 | 6.4796 | 33.92 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.1992 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S293MI | 293W Monocrystalline Module | UL 1703 | 293 | 263.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 45 | 7.9 | 37.1 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6232 | 36.473 | 6.4739 | 33.4423 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20205 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S295FG | 295 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 295 | 273.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 9.68 | 39.05 | 9.24 | 31.93 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.7903 | 30.7663 | 7.212 | 29.6553 | [6 empty] | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S295HG | 295 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc, wildcard "X" = 1 | UL 1703 | 295 | 273.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.68 | 39.05 | 9.24 | 31.93 | 44.64 | -0.365 | 0.042 | -0.284 | 1.8426 | 31.3927 | 1.7903 | 30.7663 | 7.212 | 29.6553 | [6 empty] | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiD-S295RG(BK) | 295 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 295 | 266.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.78 | 39.8 | 9.25 | 32.3 | 48.9 | -0.403 | 0.032 | -0.288 | 1.79 | 30.83 | 1.79 | 30.83 | 7.09 | 29 | [6 empty] | 2019-09-03 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M295MI | 295 W Polycrystalline Module | UL 1703 | 295 | 265.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 45.4 | 7.9 | 37.3 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.6053 | 36.554 | 6.4796 | 34.1029 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.19892 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M295RI | 295 W Polycrystalline Module | UL 1703 | 295 | 263.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 60 | 1 | N | 8.6 | 44.7 | 8.3 | 35.6 | 46.1 | -0.48521 | 0.053377 | -0.36623 | -0.025404 | -0.46341 | 1.9552 | 35.4011 | 6.7857 | 32.5173 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23463 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M295TI | 295 W Polycrystalline Module | UL 1703 | 295 | 264 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.6 | 44.7 | 8.3 | 35.6 | 46.2 | -0.49611 | 0.046237 | -0.34857 | -0.036824 | -0.46331 | 1.9484 | 35.4006 | 6.7938 | 32.5087 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.23382 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S295MI | 295 W Monocrystalline Module | UL 1703 | 295 | 265 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.4 | 45.1 | 8 | 37.2 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6437 | 36.5713 | 6.5558 | 33.5324 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20377 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S295RG | 295 W Monocrystalline Module | UL 1703 | 295 | 268.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.8 | 39 | 9.2 | 32.1 | 46.04 | -0.43043 | 0.034722 | -0.2928 | -0.027282 | -0.40682 | 1.757 | 32.3084 | 7.3561 | 29.8071 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19242 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S295RG(BK) | 295 W Monocrystalline Module | UL 1703 | 295 | 267.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.8 | 39 | 9.2 | 32.1 | 46.48 | -0.43723 | 0.048604 | -0.30206 | -0.029573 | -0.40958 | 1.7433 | 31.7923 | 7.4064 | 28.9208 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18787 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S295TG | 295 W Monocrystalline Module | UL 1703 | 295 | 265.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.8 | 39 | 9.2 | 32.1 | 46.16 | -0.46799 | 0.053481 | -0.31745 | -0.029724 | -0.44007 | 1.6994 | 32.9503 | 7.3444 | 29.2301 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18981 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M298MI | 298W Polycrystalline Module | UL 1703 | 298 | 268.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 45.5 | 8 | 37.5 | 45.5 | -0.4626 | 0.0448 | -0.3384 | 0.045035 | -0.34 | 1.6256 | 36.75 | 6.5616 | 34.2857 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20047 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S298MI | 298W Monocrystalline Module | UL 1703 | 298 | 267.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.4 | 45.3 | 8 | 37.3 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6437 | 36.6696 | 6.5558 | 33.6225 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20226 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S300FG | 300 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 300 | 278.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 9.77 | 39.23 | 9.33 | 32.15 | 44.64 | -0.365 | 0.042 | -0.284 |  |  | 1.8077 | 30.9783 | 7.2823 | 29.8596 | [6 empty] | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S300HG | 300 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 300 | 278.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.77 | 39.23 | 9.33 | 32.15 | 44.64 | -0.365 | 0.042 | -0.284 | 1.86 | 31.595 | 1.8077 | 30.9783 | 7.2823 | 29.8596 | [6 empty] | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiD-S300RG(BK) | 300 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 300 | 271.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.83 | 40 | 9.31 | 32.6 | 48.9 | -0.403 | 0.032 | -0.288 | 1.8134 | 31.0203 | 1.8134 | 31.0203 | 7.1826 | 29.179 | [6 empty] | 2019-09-03 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M300MI | 300 W Polycrystalline Module | UL 1703 | 300 | 269 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9399 | 72 | 1 | N | 8.3 | 45.7 | 8 | 37.7 | 48 | -0.431 | 0.035 | -0.318 | -0.0225 | -0.413 | 1.5927 | 36.727 | 6.357 | 34.1495 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.19498 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M300RI | 300 W Polycrystalline Module | UL 1703 | 300 | 270.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 72 | 1 | N | 8.7 | 44.9 | 8.4 | 35.8 | 45.49 | -0.46119 | 0.057359 | -0.34273 | -0.012687 | -0.44793 | 1.5308 | 35.9972 | 6.7917 | 31.9537 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18368 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M300TI | 300 W Polycrystalline Module | UL 1703 | 300 | 268.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.7 | 44.9 | 8.4 | 35.8 | 46.2 | -0.49611 | 0.046237 | -0.34857 | -0.036824 | -0.46331 | 1.9719 | 35.5994 | 6.8756 | 32.6913 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.234 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S300MI | 300 W Monocrystalline Module | UL 1703 | 300 | 269.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.4 | 45.4 | 8 | 37.4 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6437 | 36.7679 | 6.5558 | 33.7127 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.20145 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S300RG | 300 W Monocrystalline Module | UL 1703 | 300 | 272.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.9 | 39.1 | 9.3 | 32.3 | 46.04 | -0.4316 | 0.034895 | -0.2928 | -0.02734 | -0.40682 | 1.7798 | 32.5097 | 7.4517 | 29.9929 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.19287 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S300RG(BK) | 300 W Monocrystalline Module | UL 1703 | 300 | 270.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.9 | 39.1 | 9.3 | 32.3 | 46.59 | -0.46109 | 0.044103 | -0.32861 | -0.025027 | -0.44381 | 1.7001 | 31.9924 | 7.4785 | 28.8137 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.1813 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S300TG | 300 W Monocrystalline Module | UL 1703 | 300 | 270.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6367 | 60 | 1 | N | 9.9 | 39.1 | 9.3 | 32.3 | 46.16 | -0.46799 | 0.053481 | -0.31745 | -0.029724 | -0.44007 | 1.7178 | 33.1556 | 7.4242 | 29.4123 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.18985 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S303MI | 303W Monocrystalline Module | UL 1703 | 303 | 272.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.4 | 45.5 | 8 | 37.5 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6437 | 36.8662 | 6.5558 | 33.8028 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.19999 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S305FG | 305 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 305 | 283.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.86 | 39.42 | 9.42 | 32.37 | 44.64 | -0.365 | 0.042 | -0.284 | 1.8426 | 31.3927 | 1.8426 | 31.3927 | 7.4228 | 30.259 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S305HG | 305 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 305 | 283.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.86 | 39.42 | 9.42 | 32.37 | 44.64 | -0.365 | 0.042 | -0.284 | 1.8251 | 31.1903 | 1.8251 | 31.1903 | 7.3525 | 30.0639 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiD-S305RG(BK) | 305 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 305 | 278 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 1 | N | 9.9 | 40.1 | 9.38 | 32.8 | 44.9 | -0.445 | 0.0302 | -0.3193 | 1.8329 | 31.2106 | 1.7545 | 30.5809 | 7.3217 | 28.2839 | [6 empty] | 2019-09-03 | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M305RI | 305 W Polycrystalline Module | UL 1703 | 305 | 275 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 72 | 1 | N | 8.8 | 45.1 | 8.5 | 36 | 45.49 | -0.46119 | 0.057359 | -0.34273 | -0.012687 | -0.44793 | 1.549 | 36.1983 | 6.8725 | 32.1322 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18384 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M305TI | 305 W Polycrystalline Module | UL 1703 | 305 | 273.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6367 | 60 | 1 | N | 8.8 | 45.1 | 8.5 | 36 | 46.2 | -0.49611 | 0.046237 | -0.34857 | -0.036824 | -0.46331 | 1.9954 | 35.7983 | 6.9575 | 32.8739 | Rack | Flat Plate | 0.998 | 1.64 | 1 | 0.2342 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S305MI | 305 W Monocrystalline Module | UL 1703 | 305 | 274.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.4 | 45.6 | 8 | 37.6 | 45.9 | -0.4649 | 0.0343 | -0.3344 | 0.034483 | -0.33632 | 1.6437 | 36.9645 | 6.5558 | 33.893 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.19921 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S305RI | 305 W Monocrystalline Module | UL 1703 | 305 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 8.8 | 45.3 | 8.2 | 37 | 46.2 | -0.5131 | 0.030753 | -0.37105 | 0.0306 | -0.3673 | 1.92 | 36.9 | 6.7 | 33.31 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23229 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S305TI | 305 W Monocrystalline Module | UL 1703 | 305 | 271.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 8.8 | 45.3 | 8.2 | 37 | 46.1 | -0.5007 | 0.049474 | -0.36776 | 0.0493 | -0.3636 | 1.92 | 36.59 | 6.7 | 33.65 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23034 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S310FG | 310 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 310 | 288 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.95 | 39.58 | 9.51 | 32.58 | 44.64 | -0.365 | 0.042 | -0.284 | 1.86 | 31.595 | 1.86 | 31.595 | 7.493 | 30.454 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S310HG | 310 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 310 | 288 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 9.95 | 39.58 | 9.51 | 32.58 | 44.64 | -0.365 | 0.042 | -0.284 | 1.8426 | 31.3927 | 1.8426 | 31.3927 | 7.4228 | 30.259 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiD-S310RG(BK) | 310 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 310 | 282.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 1 | N | 9.94 | 40.3 | 9.45 | 33.1 | 44.9 | -0.445 | 0.0302 | -0.3193 | 1.8504 | 31.4009 | 1.7676 | 30.8606 | 7.3763 | 28.5426 | [6 empty] | 2019-09-03 | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M310RI | 310 W Polycrystalline Module | UL 1703 | 310 | 279.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 72 | 1 | N | 8.9 | 45.3 | 8.6 | 36 | 45.49 | -0.46119 | 0.057359 | -0.34273 | -0.012687 | -0.44793 | 1.5672 | 36.1983 | 6.9534 | 32.1322 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18301 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M310TI | 310 W Polycrystalline Module | UL 1703 | 310 | 279.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 60 | 1 | N | 8.9 | 45.3 | 8.6 | 36 | 46.49 | -0.44023 | 0.048677 | -0.31277 | -0.019101 | -0.4192 | 1.6427 | 35.232 | 6.938 | 32.256 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.1867 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S310MI | 310 W Monocrystalline Module | UL 1703 | 310 | 274.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8518 | 72 | 1 | N | 8.5 | 45.9 | 8.2 | 37.8 | 46.4 | -0.5217 | 0.063181 | -0.38035 | 0.0632 | -0.3803 | 1.9339 | 37.0711 | 6.6832 | 33.9471 | Rack | Flat Plate | 0.959 | 1.931 | 1 | 0.23126 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S310RI | 310 W Monocrystalline Module | UL 1703 | 310 | 275 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 8.9 | 45.5 | 8.3 | 37.2 | 46.2 | -0.5131 | 0.030753 | -0.37105 | 0.0306 | -0.3673 | 1.95 | 37.1 | 6.78 | 33.49 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23337 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S310TI | 310 W Monocrystalline Module | UL 1703 | 310 | 276 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 8.9 | 45.5 | 8.3 | 37.2 | 46.1 | -0.5007 | 0.049474 | -0.36776 | 0.0493 | -0.3636 | 1.95 | 36.79 | 6.78 | 33.83 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23142 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S315FG | 315W, 120 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc, wildcard "X" =1 | UL 1703 | 315 | 292.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 10.04 | 39.74 | 9.6 | 32.79 | 44.64 | -0.365 | 0.042 | -0.284 | 1.86 | 31.595 | 1.86 | 31.595 | 7.493 | 30.454 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S315HG | 315 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 315 | 292.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6616 | 60 | 2 | N | 10.04 | 39.74 | 9.6 | 32.79 | 44.64 | -0.365 | 0.042 | -0.284 | 1.86 | 31.595 | 1.86 | 31.595 | 7.493 | 30.454 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiD-S315RG(BK) | 315 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 315 | 287.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 1 | N | 9.99 | 40.5 | 9.51 | 33.4 | 44.9 | -0.445 | 0.0302 | -0.3193 |  |  | 1.7788 | 31.1403 | 7.4232 | 28.8013 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M315RI | 315 W Polycrystalline Module | UL 1703 | 315 | 284.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 72 | 1 | N | 9 | 45.5 | 8.7 | 36.2 | 45.49 | -0.46119 | 0.057359 | -0.34273 | -0.012687 | -0.44793 | 1.5855 | 36.3994 | 7.0343 | 32.3107 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18321 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M315TI | 315 W Polycrystalline Module | UL 1703 | 315 | 284.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 60 | 1 | N | 9 | 45.5 | 8.7 | 36.2 | 46.49 | -0.44023 | 0.048677 | -0.31277 | -0.019101 | -0.4192 | 1.6618 | 35.4277 | 7.0187 | 32.4352 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.1869 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S315MI | 315 W Monocrystalline Module | UL 1703 | 315 | 278.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9399 | 72 | 1 | N | 8.53 | 46.13 | 8.33 | 38.03 | 46.4 | -0.5217 | 0.063181 | -0.38035 | 0.0632 | -0.3803 | 1.9638 | 37.2946 | 6.7867 | 34.1518 | Rack | Flat Plate | 0.987 | 1.9655 | 1 | 0.23251 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S315RI | 315 W Monocrystalline Module | UL 1703 | 315 | 279.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9 | 45.7 | 8.4 | 37.4 | 46.2 | -0.5131 | 0.030753 | -0.37105 | 0.0306 | -0.3673 | 1.97 | 37.3 | 6.86 | 33.67 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23327 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S315TI | 315 W Monocrystalline Module | UL 1703 | 315 | 280.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9 | 45.7 | 8.4 | 37.4 | 46.1 | -0.5007 | 0.049474 | -0.36776 | 0.0493 | -0.3636 | 1.97 | 36.99 | 6.86 | 34.01 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23133 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S320FG | 320 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 320 | 298.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.13 | 39.92 | 9.69 | 33.01 | 44.37 | -0.348 | 0.043 | -0.267 | 1.8774 | 31.807 | 1.8819 | 32.7312 | 7.6098 | 31.4513 | [6 empty] | 2019-08-15 | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S320HG | 320 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 320 | 298.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.13 | 39.92 | 9.69 | 33.01 | 44.37 | -0.348 | 0.043 | -0.267 | 1.8774 | 31.807 | 1.8819 | 32.7312 | 7.6098 | 31.4513 | [6 empty] | 2019-08-15 | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiD-S320RG(BK) | 320 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 320 | 292.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 1 | N | 10.04 | 40.6 | 9.57 | 33.7 | 44.9 | -0.445 | 0.0302 | -0.3193 |  |  | 1.79 | 31.42 | 7.47 | 29.06 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M320RI | 320 W Polycrystalline Module | UL 1703 | 320 | 288.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 72 | 1 | N | 9 | 45.7 | 8.8 | 36.4 | 45.49 | -0.46119 | 0.057359 | -0.34273 | -0.012687 | -0.44793 | 1.6037 | 36.6006 | 7.1151 | 32.4893 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18342 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M320TI | 320 W Polycrystalline Module | UL 1703 | 320 | 288.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 60 | 1 | N | 9 | 45.7 | 8.8 | 36.4 | 46.49 | -0.44023 | 0.048677 | -0.31277 | -0.019101 | -0.4192 | 1.6809 | 35.6235 | 7.0993 | 32.6144 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18712 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S320RI | 320 W Monocrystalline Module | UL 1703 | 320 | 284.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.1 | 45.9 | 8.5 | 37.6 | 46.2 | -0.5131 | 0.030753 | -0.37105 | 0.0306 | -0.3673 | 1.99 | 37.5 | 6.95 | 33.85 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.2332 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S320TI | 320 W Monocrystalline Module | UL 1703 | 320 | 285.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.1 | 45.9 | 8.5 | 37.6 | 46.1 | -0.5007 | 0.049474 | -0.36776 | 0.0493 | -0.3636 | 1.99 | 37.19 | 6.94 | 34.19 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23128 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S320VG(BK) | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 320 | 290.3 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.1 | 40.6 | 9.63 | 33.3 | 46.79 | -0.4328 | 0.0466 | -0.3261 |  |  | 1.97 | 31.74 | 7.96 | 29.7 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S325FG | 325 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 325 | 303.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.43 | 40.1 | 9.93 | 32.71 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9285 | 32.4337 | 7.7983 | 31.1654 | [6 empty] | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S325HG | 325 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 325 | 303.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.43 | 40.1 | 9.93 | 32.71 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9285 | 32.4337 | 7.7983 | 31.1654 | [6 empty] | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiD-S325RG(BK) | 325 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 325 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 1 | N | 10.09 | 40.8 | 9.62 | 34 | 44.9 | -0.445 | 0.0302 | -0.3193 |  |  | 1.7994 | 31.6997 | 7.509 | 29.3187 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M325RI | 325 W Polycrystalline Module | UL 1703 | 325 | 293.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 72 | 1 | N | 9.1 | 45.9 | 8.8 | 36.6 | 45.49 | -0.46119 | 0.057359 | -0.34273 | -0.012687 | -0.44793 | 1.6037 | 36.8017 | 7.1151 | 32.6678 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.1816 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M325TI | 325 W Polycrystalline Module | UL 1703 | 325 | 293.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 60 | 1 | N | 9.1 | 45.9 | 8.8 | 36.6 | 46.49 | -0.44023 | 0.048677 | -0.31277 | -0.019101 | -0.4192 | 1.6809 | 35.8192 | 7.0993 | 32.7936 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18526 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S325RI | 325 W Monocrystalline Module | UL 1703 | 325 | 288 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.2 | 46.1 | 8.6 | 37.8 | 46.2 | -0.52415 | 0.03072 | -0.37269 | -0.023596 | -0.50195 | 2.0196 | 37.9053 | 7.0346 | 34.2201 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.23554 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S325TI | 325 W Monocrystalline Module | UL 1703 | 325 | 294.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 60 | 1 | N | 9.2 | 46.1 | 8.6 | 37.8 | 46.03 | -0.44009 | 0.040445 | -0.29978 | -0.020277 | -0.41671 | 1.6154 | 38.1107 | 6.9296 | 34.5896 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18942 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S325VG(BK) | 325 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 325 | 295 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.15 | 41 | 9.69 | 33.6 | 46.79 | -0.4328 | 0.0466 | -0.3261 |  |  | 1.98 | 32.1 | 7.97 | 30.27 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S330FG | 330 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 330 | 308.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.51 | 40.27 | 10.02 | 32.91 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.946 | 32.632 | 7.869 | 31.356 | [6 empty] | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S330HG | 330 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 330 | 308.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.51 | 40.27 | 10.02 | 32.91 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.946 | 32.632 | 7.869 | 31.356 | [6 empty] | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiD-S330RG(BK) | 330 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 330 | 301.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 1 | N | 10.14 | 41 | 9.68 | 34.3 | 44.9 | -0.445 | 0.0302 | -0.3193 |  |  | 1.8106 | 31.9794 | 7.5559 | 29.5774 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M330RI | 330 W Polycrystalline Module | UL 1703 | 330 | 298.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 72 | 1 | N | 9.2 | 46.1 | 8.9 | 36.8 | 45.49 | -0.46119 | 0.057359 | -0.34273 | -0.012687 | -0.44793 | 1.6219 | 37.0028 | 7.196 | 32.8463 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18186 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-M330TI | 330 W Polycrystalline Module | UL 1703 | 330 | 298.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9561 | 60 | 1 | N | 9.2 | 46.1 | 8.9 | 36.8 | 46.49 | -0.44023 | 0.048677 | -0.31277 | -0.019101 | -0.4192 | 1.7 | 36.0149 | 7.18 | 32.9728 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18553 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S330RI | 330 W Monocrystalline Module | UL 1703 | 330 | 292.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.3 | 46.3 | 8.7 | 38 | 46.2 | -0.52074 | 0.030753 | -0.37105 | -0.023569 | -0.49917 | 1.59 | 34 | 7.11 | 34.21 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.16382 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S330TI | 330 W Monocrystalline Module | UL 1703 | 330 | 298.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 60 | 1 | N | 9.3 | 46.3 | 8.7 | 38 | 46.03 | -0.44009 | 0.040445 | -0.29978 | -0.020277 | -0.41671 | 1.6342 | 38.3123 | 7.0101 | 34.7726 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18972 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S330VG(BK) | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 330 | 299.7 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.2 | 41.4 | 9.74 | 33.9 | 46.79 | -0.4328 | 0.0466 | -0.3261 |  |  | 2 | 32.24 | 7.98 | 30.78 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S335FG | 335 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 335 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.6 | 40.44 | 10.11 | 33.11 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9635 | 32.8303 | 7.9397 | 31.5466 | [6 empty] | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S335HG | 335 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 335 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.6 | 40.44 | 10.11 | 33.11 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9635 | 32.8303 | 7.9397 | 31.5466 | [6 empty] | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S335RI | 335 W Monocrystalline Module | UL 1703 | 335 | 303.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.4 | 46.5 | 8.8 | 38.2 | 45.59 | -0.44803 | 0.034553 | -0.32648 | -0.02439 | -0.43733 | 1.6611 | 37.7925 | 6.9523 | 34.7365 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18739 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S335TI | 335 W Monocrystalline Module | UL 1703 | 335 | 303.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 60 | 1 | N | 9.4 | 46.5 | 8.8 | 38.2 | 46.03 | -0.44009 | 0.040445 | -0.29978 | -0.020277 | -0.41671 | 1.6529 | 38.514 | 7.0907 | 34.9556 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.19003 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S335VG(BK) | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 335 | 304.4 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.25 | 41.8 | 9.79 | 34.3 | 46.79 | -0.4328 | 0.0466 | -0.3261 |  |  | 2.02 | 32.31 | 7.98 | 31.26 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S340FG | 340 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc | UL 1703 | 340 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.69 | 40.62 | 10.21 | 33.31 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9829 | 33.0286 | 8.0182 | 31.7371 | [6 empty] | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S340HG | 340 W, 120 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc | UL 1703 | 340 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 60 | 2 | N | 10.69 | 40.62 | 10.21 | 33.31 | 44.37 | -0.348 | 0.043 | -0.267 |  |  | 1.9829 | 33.0286 | 8.0182 | 31.7371 | [6 empty] | 2020-01-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S340RI | 340 W Monocrystalline Module | UL 1703 | 340 | 308.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.5 | 46.7 | 8.9 | 38.4 | 45.59 | -0.44803 | 0.034553 | -0.32648 | -0.02439 | -0.43733 | 1.68 | 37.9904 | 7.0313 | 34.9184 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18771 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S340TI | 340 W Monocrystalline Module | UL 1703 | 340 | 308.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 60 | 1 | N | 9.5 | 46.7 | 8.9 | 38.4 | 46.03 | -0.44009 | 0.040445 | -0.29978 | -0.020277 | -0.41671 | 1.6717 | 38.7156 | 7.1713 | 35.1386 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.19036 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S340VG(BK) | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 340 | 309.1 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.3 | 42.2 | 9.84 | 34.6 | 46.79 | -0.4328 | 0.0466 | -0.3261 |  |  | 2.04 | 32.53 | 7.96 | 31.78 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S345RI | 345 W Monocrystalline Module | UL 1703 | 345 | 313 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.6 | 46.9 | 9 | 38.6 | 45.59 | -0.44803 | 0.034553 | -0.32648 | -0.02439 | -0.43733 | 1.6988 | 38.1883 | 7.1103 | 35.1003 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18804 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S345TI | 345 W Monocrystalline Module | UL 1703 | 345 | 312.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 60 | 1 | N | 9.6 | 46.9 | 9 | 38.6 | 46.03 | -0.44009 | 0.040445 | -0.29978 | -0.020277 | -0.41671 | 1.6905 | 38.9173 | 7.2519 | 35.3216 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.19069 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S350KI(BK) | 350 W, 72cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 350 | 317.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.6 | 47.1 | 9 | 38.7 | 45.64 | -0.455 | 0.0499 | -0.3206 |  |  | 1.8196 | 38.2051 | 7.3272 | 35.3348 | [6 empty] | 2019-05-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S350RI | 350 W Monocrystalline Module | UL 1703 | 350 | 317.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.6 | 47.1 | 9 | 38.7 | 45.59 | -0.44803 | 0.034553 | -0.32648 | -0.02439 | -0.43733 | 1.6988 | 38.2872 | 7.1103 | 35.1912 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18584 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S350RI(BK) | 350 W, 72cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 350 | 317.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.6 | 47.1 | 9 | 38.7 | 45.64 | -0.4526 | 0.048 | -0.3317 |  |  | 1.8196 | 38.3041 | 7.3272 | 35.0379 | [6 empty] | 2019-05-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S350TI | 350 W Monocrystalline Module | UL 1703 | 350 | 317.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 60 | 1 | N | 9.6 | 47.1 | 9 | 38.7 | 46.03 | -0.44009 | 0.040445 | -0.29978 | -0.020277 | -0.41671 | 1.6905 | 39.0181 | 7.2519 | 35.4132 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18846 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S350XG(BK) | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 350 | 326.9 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.06 | 40.3 | 10.42 | 33.6 | 45.13 | -0.3345 | 0.0279 | -0.2505 |  |  | 2.0722 | 33.0384 | 8.3182 | 30.7031 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S350YG | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 328 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.06 | 40.3 | 10.42 | 33.6 | 43.3 | -0.3509 | 0.0448 | -0.2683 |  |  | 2.083 | 32.8452 | 8.3528 | 32.0057 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S350YG(BK) | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 350 | 325.5 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.06 | 40.3 | 10.42 | 33.6 | 45.4 | -0.3509 | 0.0478 | -0.2725 |  |  | 2.0278 | 32.662 | 8.1317 | 31.7574 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S355FI | 355 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 355 | 328.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.6 | 46.82 | 9.1 | 39.01 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8005 | 37.3048 | 1.8005 | 37.3048 | 7.2242 | 36.0063 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S355HI | 355 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc, wildcard "X" = 1 | UL 1703 | 355 | 328.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.6 | 46.82 | 9.1 | 39.01 | 45.81 | -0.352 | 0.042 | -0.275 | 1.7849 | 37.124 | 1.7849 | 37.124 | 7.1613 | 35.8318 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S355XG | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 331.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8217 | 60 | 2 | N | 11.24 | 39.95 | 10.69 | 33.21 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.1132 | 32.6049 | 8.4795 | 31.5534 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S355XG(BK) | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 355 | 330.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8217 | 60 | 2 | N | 11.24 | 39.95 | 10.69 | 33.21 | 44.6 | -0.3656 | 0.0514 | -0.283 |  |  | 2.0742 | 32.8431 | 8.3187 | 31.7414 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S355XG(BK) | 355 W, 120 half cut cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 329.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.26 | 40.3 | 10.51 | 33.8 | 45.16 | -0.3706 | 0.0563 | -0.2887 |  |  | 2.1 | 33.2 | 8.3 | 31.8 | [6 empty] | 2021-08-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S355KI(BK) | 355 W, 72cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 355 | 321.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.7 | 47.3 | 9.1 | 38.9 | 45.64 | -0.455 | 0.0499 | -0.3206 |  |  | 1.8398 | 38.4026 | 7.4086 | 35.5174 | [6 empty] | 2019-05-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S355RI | 355 W Monocrystalline Module | UL 1703 | 355 | 322.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.7 | 47.3 | 9.1 | 38.9 | 45.59 | -0.44803 | 0.034553 | -0.32648 | -0.02439 | -0.43733 | 1.7177 | 38.4851 | 7.1893 | 35.3731 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18621 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S355RI(BK) | 355 W, 72cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 355 | 321.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.7 | 47.3 | 9.1 | 38.9 | 45.64 | -0.4526 | 0.048 | -0.3317 |  |  | 1.8398 | 38.502 | 7.4086 | 35.2189 | [6 empty] | 2019-05-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S355TI | 355 W Monocrystalline Module | UL 1703 | 355 | 322.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.7 | 47.3 | 9.1 | 38.9 | 46.03 | -0.44009 | 0.040445 | -0.29978 | -0.020277 | -0.41671 | 1.7093 | 39.2197 | 7.3324 | 35.5962 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.18884 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S355XG(BK) | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 355 | 331.7 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.13 | 40.6 | 10.49 | 33.9 | 45.13 | -0.3345 | 0.0279 | -0.2505 |  |  | 2.0861 | 33.3333 | 8.3741 | 30.9772 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S355YG | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 332.8 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.13 | 40.6 | 10.49 | 33.9 | 43.3 | -0.3509 | 0.0448 | -0.2683 |  |  | 2.097 | 33.1385 | 8.4089 | 32.2915 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S355YG(BK) | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 355 | 330.2 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.13 | 40.6 | 10.49 | 33.9 | 45.4 | -0.3509 | 0.0478 | -0.2725 |  |  | 2.0414 | 32.9536 | 8.1864 | 32.041 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S360FI | 360 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 360 | 333.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.69 | 47.01 | 9.18 | 39.2 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8182 | 37.4856 | 1.8182 | 37.4856 | 7.295 | 36.1808 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S360HI | 360 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc, wildcard "X" = 1 | UL 1703 | 360 | 333.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.69 | 47.01 | 9.18 | 39.2 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8005 | 37.3048 | 1.8005 | 37.3048 | 7.2242 | 36.0063 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S360XG | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 336.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8217 | 60 | 2 | N | 11.26 | 40.26 | 10.72 | 33.58 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.1191 | 32.9682 | 8.5033 | 31.905 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S360XG(BK) | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 360 | 335 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8217 | 60 | 2 | N | 11.26 | 40.26 | 10.72 | 33.58 | 44.6 | -0.3656 | 0.0514 | -0.283 |  |  | 2.08 | 33.209 | 8.342 | 32.095 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S360XG(BK) | 360 W, 120 half cut cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 360 | 333.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.35 | 40.5 | 10.59 | 34 | 45.16 | -0.3706 | 0.0563 | -0.2887 |  |  | 2.116 | 33.3964 | 8.3632 | 31.9882 | [6 empty] | 2021-08-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S360KI(BK) | 360 W, 72cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 360 | 326.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.8 | 47.4 | 9.2 | 39.1 | 45.64 | -0.455 | 0.0499 | -0.3206 |  |  | 1.86 | 38.6 | 7.49 | 35.7 | [6 empty] | 2019-05-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S360RI | 360 W Monocrystalline Module | UL 1703 | 360 | 327 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9561 | 72 | 1 | N | 9.7 | 47.4 | 9.2 | 39.1 | 45.59 | -0.44803 | 0.034553 | -0.32648 | -0.02439 | -0.43733 | 1.7366 | 38.6829 | 7.2683 | 35.5549 | Rack | Flat Plate | 0.998 | 1.96 | 1 | 0.1866 |  | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S360RI(BK) | 360 W, 72cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 360 | 326.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 | 1 | N | 9.8 | 47.4 | 9.2 | 39.1 | 45.64 | -0.4526 | 0.048 | -0.3317 |  |  | 1.86 | 38.7 | 7.49 | 35.4 | [6 empty] | 2019-05-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S360XG(BK) | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 360 | 336.5 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.2 | 41 | 10.56 | 34.1 | 45.13 | -0.3345 | 0.0279 | -0.2505 |  |  | 2.1 | 33.53 | 8.43 | 31.16 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S360YG | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 337.6 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.2 | 41 | 10.56 | 34.1 | 43.3 | -0.3509 | 0.0448 | -0.2683 |  |  | 2.111 | 33.334 | 8.465 | 32.482 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S360YG(BK) | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 360 | 335 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.2 | 41 | 10.56 | 34.1 | 45.4 | -0.3509 | 0.0478 | -0.2725 |  |  | 2.055 | 33.148 | 8.241 | 32.23 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S365FI | 365 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 365 | 338.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.77 | 47.21 | 9.27 | 39.39 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8339 | 37.6855 | 1.8339 | 37.6855 | 7.358 | 36.3737 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S365HI | 365 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc, wildcard "X" = 1 | UL 1703 | 365 | 338.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.77 | 47.21 | 9.27 | 39.39 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8182 | 37.4856 | 1.8182 | 37.4856 | 7.295 | 36.1808 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S365XG | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 341.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8217 | 60 | 2 | N | 11.28 | 40.59 | 10.76 | 33.92 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.127 | 33.302 | 8.535 | 32.228 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S365XG(BK) | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 365 | 339.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8217 | 60 | 2 | N | 11.28 | 40.59 | 10.76 | 33.92 | 44.6 | -0.3656 | 0.0514 | -0.283 |  |  | 2.0878 | 33.5452 | 8.3731 | 32.42 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S365XG(BK) | 365 W, 120 half cut cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 365 | 338.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.43 | 40.7 | 10.68 | 34.2 | 45.16 | -0.3706 | 0.0563 | -0.2887 |  |  | 2.134 | 33.5929 | 8.4343 | 32.1763 | [6 empty] | 2021-08-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S365RI | 365 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 365 | 332 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 |  | N | 9.9 | 47.6 | 9.3 | 39.3 | 45.46 | -0.4472 | 0.0365 | -0.3231 | -0.0155 | -0.435 | 1.9095 | 38.5 | 7.72 | 35.8 | [6 empty] | 2018-12-17 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S365XG(BK) | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 365 | 341.3 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.28 | 41.3 | 10.64 | 34.3 | 45.13 | -0.3345 | 0.0279 | -0.2505 |  |  | 2.1159 | 33.7267 | 8.4939 | 31.3428 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S365YG | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 342.4 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.28 | 41.3 | 10.64 | 34.3 | 43.3 | -0.3509 | 0.0448 | -0.2683 |  |  | 2.127 | 33.5295 | 8.5291 | 32.6725 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S365YG(BK) | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 365 | 339.8 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.28 | 41.3 | 10.64 | 34.3 | 45.4 | -0.3509 | 0.0478 | -0.2725 |  |  | 2.0706 | 33.3424 | 8.3034 | 32.419 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S370FI | 370 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 370 | 343.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.85 | 47.4 | 9.35 | 39.6 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8496 | 37.8853 | 1.8496 | 37.8853 | 7.421 | 36.5666 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S370HI | 370 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc, wildcard "X" = 1 | UL 1703 | 370 | 343.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.85 | 47.4 | 9.35 | 39.6 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8339 | 37.6855 | 1.8339 | 37.6855 | 7.358 | 36.3737 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S370XG | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 346.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8217 | 60 | 2 | N | 11.3 | 40.91 | 10.8 | 34.26 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.1349 | 33.6358 | 8.5667 | 32.551 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S370XG(BK) | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 370 | 344.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8217 | 60 | 2 | N | 11.3 | 40.91 | 10.8 | 34.26 | 44.6 | -0.3656 | 0.0514 | -0.283 |  |  | 2.0955 | 33.8815 | 8.4043 | 32.7449 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S370XG(BK) | 370 W, 120 half cut cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 370 | 343.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.52 | 40.9 | 10.76 | 34.4 | 45.16 | -0.3706 | 0.0563 | -0.2887 |  |  | 2.15 | 33.7893 | 8.4974 | 32.3645 | [6 empty] | 2021-08-02
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S370BI | 370 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 370 | 335.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 9.98 | 47.3 | 9.51 | 39 | 45.62 | -0.4568 | 0.0486 | -0.3444 |  |  | 1.96 | 37.8 | 8.02 | 35.2 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S370GI | 370 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 370 | 335.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 9.98 | 47.3 | 9.51 | 39 | 45.55 | -0.4551 | 0.0532 | -0.3366 |  |  | 1.96 | 37.7 | 8 | 35.1 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S370RI | 370 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 370 | 336.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 72 |  | N | 9.9 | 47.8 | 9.4 | 39.5 | 45.46 | -0.4472 | 0.0365 | -0.3231 | -0.0155 | -0.435 | 1.93 | 38.5 | 7.72 | 35.8 | [6 empty] | 2018-12-17 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S370XG(BK) | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 370 | 346.1 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.35 | 41.5 | 10.71 | 34.6 | 45.13 | -0.3345 | 0.0279 | -0.2505 |  |  | 2.1298 | 34.0216 | 8.5497 | 31.6169 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S370YG | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 347.2 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.35 | 41.5 | 10.71 | 34.6 | 43.3 | -0.3509 | 0.0448 | -0.2683 |  |  | 2.141 | 33.8228 | 8.5852 | 32.9583 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S370YG(BK) | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 370 | 344.6 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.35 | 41.5 | 10.71 | 34.6 | 45.4 | -0.3509 | 0.0478 | -0.2725 |  |  | 2.0842 | 33.634 | 8.3581 | 32.7026 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S375FI | 375 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 375 | 348 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.93 | 47.61 | 9.43 | 39.81 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8633 | 38.0852 | 1.8633 | 38.0852 | 7.476 | 36.7595 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S375HI | 375 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc, wildcard "X" = 1 | UL 1703 | 375 | 348 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 9.93 | 47.61 | 9.43 | 39.81 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8496 | 37.8853 | 1.8496 | 37.8853 | 7.421 | 36.5666 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S375XG | 375 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 350.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8217 | 60 | 2 | N | 11.32 | 41.24 | 10.84 | 34.59 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.1428 | 33.9598 | 8.5985 | 32.8646 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S375XG(BK) | 375 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 375 | 349.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.32 | 41.24 | 10.84 | 34.59 | 44.6 | -0.3656 | 0.0514 | -0.283 |  |  | 2.1033 | 34.2078 | 8.4354 | 33.0603 | [6 empty] | 2021-07-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S375BI | 375 W, 144 half-cut cell bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 375 | 339.9 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.03 | 47.6 | 9.56 | 39.3 | 45.62 | -0.4568 | 0.0486 | -0.3444 |  |  | 1.96 | 37.9 | 8.02 | 35.6 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S375GI | 375 W, 144 half-cut cell double glass bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 375 | 340.2 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.03 | 47.6 | 9.56 | 39.3 | 45.55 | -0.4551 | 0.0532 | -0.3366 |  |  | 1.95 | 38 | 8 | 35.5 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S375XG(BK) | 375 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 375 | 350.9 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.42 | 41.8 | 10.78 | 34.8 | 45.13 | -0.3345 | 0.0279 | -0.2505 |  |  | 2.1437 | 34.2183 | 8.6056 | 31.7996 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S375YG | 375 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 352 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.42 | 41.8 | 10.78 | 34.8 | 43.3 | -0.3509 | 0.0448 | -0.2683 |  |  | 2.155 | 34.0183 | 8.6414 | 33.1488 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S375YG(BK) | 375 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 375 | 349.4 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.42 | 41.8 | 10.78 | 34.8 | 45.4 | -0.3509 | 0.0478 | -0.2725 |  |  | 2.0978 | 33.8285 | 8.4127 | 32.8916 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S380FI | 380 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 380 | 352.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 10.01 | 47.8 | 9.5 | 40.02 | 45.81 | -0.352 | 0.042 | -0.275 | 1.879 | 38.266 | 1.879 | 38.266 | 7.539 | 36.934 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S380HI | 380 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc, wildcard "X" = 1 | UL 1703 | 380 | 352.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 10.01 | 47.8 | 9.5 | 40.02 | 45.81 | -0.352 | 0.042 | -0.275 | 1.8633 | 38.0852 | 1.8633 | 38.0852 | 7.476 | 36.7595 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S380BI | 380 W, 144 half-cut cell bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 380 | 344.6 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.08 | 47.9 | 9.61 | 39.6 | 45.62 | -0.4568 | 0.0486 | -0.3444 |  |  | 1.97 | 38 | 8.02 | 36 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S380GI | 380 W, 144 half-cut cell double glass bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 380 | 344.8 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.08 | 47.9 | 9.61 | 39.6 | 45.55 | -0.4551 | 0.0532 | -0.3366 |  |  | 1.96 | 38 | 8.01 | 35.8 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S380NI | 380 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 380 | 344.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.08 | 47.9 | 9.61 | 39.6 | 45.48 | -0.4589 | 0.046 | -0.3391 |  |  | 1.97 | 38 | 8.08 | 35.7 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S380PI | 380 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 380 | 344.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.08 | 47.9 | 9.61 | 39.6 | 45.58 | -0.4569 | 0.05 | -0.3442 |  |  | 1.97 | 38 | 8.09 | 35.7 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S380QI | 380 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 380 | 346.3 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.08 | 47.9 | 9.61 | 39.6 | 45.43 | -0.4403 | 0.0406 | -0.3235 |  |  | 1.98 | 38 | 8.04 | 35.7 | [6 empty] | 2020-02-03 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S380VI | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 345.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.08 | 47.9 | 9.61 | 39.6 | 45.39 | -0.4552 | 0.0414 | -0.3351 |  |  | 1.98 | 38 | 8.09 | 35.9 | [6 empty] | 2020-02-03
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S385FI | 385 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1000V max system Vdc, wildcard "X" = 1 | UL 1703 | 385 | 357.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 10.08 | 48 | 9.58 | 40.21 | 45.81 | -0.352 | 0.042 | -0.275 | 1.879 | 38.266 | 1.879 | 38.266 | 7.539 | 36.934 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S385HI | 385 W, 144 half-cell monocrystalline module, 5 busbars, white backsheet and frame, 1500V max system Vdc, wildcard "X" = 1 | UL 1703 | 385 | 357.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.984 | 72 | 2 | N | 10.08 | 48 | 9.58 | 40.21 | 45.81 | -0.352 | 0.042 | -0.275 | 1.879 | 38.266 | 1.879 | 38.266 | 7.539 | 36.934 | [6 empty] | 2019-08-15 | 2019-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S385BI | 385 W, 144 half-cut cell bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 385 | 349.3 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.13 | 48.2 | 9.67 | 39.9 | 45.62 | -0.4568 | 0.0486 | -0.3444 |  |  | 1.97 | 38.3 | 8.03 | 36.3 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S385GI | 385 W, 144 half-cut cell double glass bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 385 | 349.5 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.13 | 48.2 | 9.67 | 39.9 | 45.55 | -0.4551 | 0.0532 | -0.3366 |  |  | 1.97 | 38.4 | 8.03 | 36.2 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S385NI | 385 W, 144 half-cut cell double glass bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 385 | 349.4 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.13 | 48.2 | 9.67 | 39.9 | 45.48 | -0.4589 | 0.046 | -0.3391 |  |  | 1.97 | 38.03 | 8.08 | 36 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S385PI | 385 W, 144 half-cut cell bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 385 | 349.3 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.13 | 48.2 | 9.67 | 39.9 | 45.58 | -0.4569 | 0.05 | -0.3442 |  |  | 1.97 | 38.3 | 8.08 | 36.2 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S385QI | 385 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 385 | 351 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.13 | 48.2 | 9.67 | 39.9 | 45.43 | -0.4403 | 0.0406 | -0.3235 |  |  | 1.98 | 38.2 | 8.02 | 36.1 | [6 empty] | 2020-02-03 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S385VI | 385 W, 144 half-cut cell monocrystalline module, 9 busbars, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 385 | 349.9 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.13 | 48.2 | 9.67 | 39.9 | 45.39 | -0.4552 | 0.0414 | -0.3351 |  |  | 1.98 | 38.2 | 8.11 | 36.1 | [6 empty] | 2020-02-03 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S385XH(BK) | 385 W, 132 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 385 | 359.6 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9971 | 66 | 2 | N | 11.04 | 44.5 | 10.4 | 37.1 | 46.2 | -0.3183 | 0.0266 | -0.2371 | 2.078 | 36.0273 | 2.078 | 36.0273 | 8.1553 | 38.0939 | [6 empty] | 2021-09-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S390FI | 390 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 390 | 364.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.48 | 48.18 | 9.66 | 40.37 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.9379 | 38.7253 | 7.8452 | 37.3321 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S390HI | 390 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 390 | 364.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.48 | 48.18 | 9.66 | 40.37 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.9379 | 38.7253 | 7.8452 | 37.3321 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S390BI | 390 W, 144 half-cut cell bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 354 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.18 | 48.5 | 9.72 | 40.2 | 45.62 | -0.4568 | 0.0486 | -0.3444 |  |  | 1.96 | 38.6 | 8.02 | 36.7 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S390GI | 390 W, 144 half-cut cell double glass bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 354.2 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.18 | 48.5 | 9.72 | 40.2 | 45.55 | -0.4551 | 0.0532 | -0.3366 |  |  | 1.96 | 38.6 | 8.01 | 36.5 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S390NI | 390 W, 144 half-cut cell double glass bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 354.1 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.18 | 48.5 | 9.72 | 40.2 | 45.48 | -0.4589 | 0.046 | -0.3391 |  |  | 1.96 | 38.6 | 8.08 | 36.3 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S390PI | 390 W, 144 half-cut cell bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 354 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.18 | 48.5 | 9.72 | 40.2 | 45.58 | -0.4569 | 0.05 | -0.3442 |  |  | 1.96 | 38.5 | 8.1 | 36.4 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S390QI | 390 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 355.7 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.18 | 48.5 | 9.72 | 40.2 | 45.43 | -0.4403 | 0.0406 | -0.3235 |  |  | 1.97 | 38.4 | 8.06 | 36.3 | [6 empty] | 2020-02-03 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S390VI | 390 W, 144 half-cut cell monocrystalline module, 9 busbars, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 354.6 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.18 | 48.5 | 9.72 | 40.2 | 45.39 | -0.4552 | 0.0414 | -0.3351 |  |  | 1.98 | 38.6 | 8.1 | 36.5 | [6 empty] | 2020-02-03 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S390XH(BK) | 390 W, 132 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 390 | 364.4 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9971 | 66 | 2 | N | 11.11 | 44.8 | 10.47 | 37.3 | 46.2 | -0.3183 | 0.0266 | -0.2371 | 2.092 | 36.2216 | 2.092 | 36.2216 | 8.2102 | 38.2993 | [6 empty] | 2021-09-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S395FI | 395 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 395 | 369 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.56 | 48.37 | 9.74 | 40.55 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.954 | 38.898 | 7.9102 | 37.4986 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S395HI | 395 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 395 | 369 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.56 | 48.37 | 9.74 | 40.55 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.954 | 38.898 | 7.9102 | 37.4986 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S395BI | 395 W, 144 half-cut cell bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 358.7 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.23 | 48.8 | 9.77 | 40.5 | 45.62 | -0.4568 | 0.0486 | -0.3444 |  |  | 1.99 | 38.3 | 8.02 | 37 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S395GI | 395 W, 144 half-cut cell double glass bifacial monocrystalline module, 5 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 358.9 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.23 | 48.8 | 9.77 | 40.5 | 45.55 | -0.4551 | 0.0532 | -0.3366 |  |  | 1.98 | 38.5 | 8.02 | 36.8 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S395NI | 395 W, 144 half-cut cell double glass bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 358.7 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.23 | 48.8 | 9.77 | 40.5 | 45.48 | -0.4589 | 0.046 | -0.3391 |  |  | 1.98 | 38.3 | 8.09 | 36.7 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S395PI | 395 W, 144 half-cut cell bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 358.7 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.23 | 48.8 | 9.77 | 40.5 | 45.58 | -0.4569 | 0.05 | -0.3442 |  |  | 1.98 | 38.5 | 8.1 | 36.8 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S395QI | 395 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 360.4 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.23 | 48.8 | 9.77 | 40.5 | 45.43 | -0.4403 | 0.0406 | -0.3235 |  |  | 1.97 | 38.9 | 8.05 | 36.7 | [6 empty] | 2020-02-03 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S395VI | 395 W, 144 half-cut cell monocrystalline module, 9 busbars, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 359.3 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.23 | 48.8 | 9.77 | 40.5 | 45.39 | -0.4552 | 0.0414 | -0.3351 |  |  | 1.99 | 38.9 | 8.11 | 36.8 | [6 empty] | 2020-02-03 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S395XH(BK) | 395 W, 132 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 395 | 369.2 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9971 | 66 | 2 | N | 11.18 | 45 | 10.54 | 37.5 | 46.2 | -0.3183 | 0.0266 | -0.2371 | 2.106 | 36.4158 | 2.106 | 36.4158 | 8.2651 | 38.5046 | [6 empty] | 2021-09-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S400FI | 400 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 400 | 373.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.64 | 48.55 | 9.81 | 40.77 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.968 | 39.109 | 7.967 | 37.702 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S400HI | 400 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 400 | 373.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.64 | 48.55 | 9.81 | 40.77 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.968 | 39.109 | 7.967 | 37.702 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S400NI | 400 W, 144 half-cut cell double glass bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 400 | 363.4 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.28 | 49.1 | 9.82 | 40.8 | 45.48 | -0.4589 | 0.046 | -0.3391 |  |  | 2 | 38.4 | 8.1 | 36.9 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S400PI | 400 W, 144 half-cut cell bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 400 | 363.4 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.28 | 49.1 | 9.82 | 40.8 | 45.58 | -0.4569 | 0.05 | -0.3442 |  |  | 2 | 38.4 | 8.1 | 37 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S400QI | 400 W, 144 half-cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 365.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.28 | 49.1 | 9.82 | 40.8 | 45.43 | -0.4403 | 0.0406 | -0.3235 |  |  | 1.97 | 39.2 | 8.04 | 37.1 | [6 empty] | 2020-02-03
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S400VI | 400 W, 144 half-cut cell monocrystalline module, 9 busbars, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 400 | 364 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.28 | 49.1 | 9.82 | 40.8 | 45.39 | -0.4552 | 0.0414 | -0.3351 |  |  | 1.98 | 39 | 8.11 | 37.1 | [6 empty] | 2020-02-03 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S400XH(BK) | 400 W, 132 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 400 | 373.9 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9971 | 66 | 2 | N | 11.25 | 45.3 | 10.61 | 37.7 | 46.2 | -0.3183 | 0.0266 | -0.2371 | 2.12 | 36.61 | 2.12 | 36.61 | 8.32 | 38.71 | [6 empty] | 2021-09-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S405FI | 405 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 405 | 378.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.71 | 48.73 | 9.89 | 40.95 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.984 | 39.2817 | 8.032 | 37.8685 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S405HI | 405 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 405 | 378.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.71 | 48.73 | 9.89 | 40.95 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 1.984 | 39.2817 | 8.032 | 37.8685 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S405NI | 405 W, 144 half-cut cell double glass bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 405 | 368.2 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.33 | 49.4 | 9.87 | 41.1 | 45.48 | -0.4589 | 0.046 | -0.3391 |  |  | 2.01 | 38.8 | 8.08 | 37.3 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S405PI | 405 W, 144 half-cut cell bifacial monocrystalline module, 9 busbars, 1500V max system Vdc | UL 61730, UL 1703 | 405 | 368.1 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 2 | N | 10.33 | 49.4 | 9.87 | 41.1 | 45.58 | -0.4569 | 0.05 | -0.3442 |  |  | 2.01 | 38.9 | 8.11 | 37.4 | [6 empty] | 2019-12-23 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S405QI | 405 W, 144 half-cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 405 | 369.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.33 | 49.4 | 9.87 | 41.1 | 45.43 | -0.4403 | 0.0406 | -0.3235 |  |  | 1.98 | 39.4 | 8.04 | 37.4 | [6 empty] | 2020-02-03
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S405VI | 405 W, 144 half-cut cell monocrystalline module, 9 busbars, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 405 | 368.7 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.02 | 72 | 2 | N | 10.33 | 49.4 | 9.87 | 41.1 | 45.39 | -0.4552 | 0.0414 | -0.3351 |  |  | 1.98 | 39.3 | 8.11 | 37.5 | [6 empty] | 2020-02-03 | 2020-10-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S405XH(BK) | 405 W, 132 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 405 | 378.7 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9971 | 66 | 2 | N | 11.33 | 45.6 | 10.69 | 37.9 | 46.2 | -0.3183 | 0.0266 | -0.2371 | 2.136 | 36.8042 | 2.136 | 36.8042 | 8.3827 | 38.9154 | [6 empty] | 2021-09-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S410FI | 410 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1000V max system Vdc | UL 1703 | 410 | 383.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.79 | 48.91 | 9.97 | 41.12 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 2.0001 | 39.4447 | 8.0969 | 38.0257 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S410HI | 410 W, 144 half-cut cell monocrystalline module, 5 busbars, white backsheet and white aluminum frame, 1500V max system Vdc | UL 1703 | 410 | 383.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 72 | 2 | N | 10.79 | 48.91 | 9.97 | 41.12 | 44.52 | -0.349 | 0.043 | -0.267 |  |  | 2.0001 | 39.4447 | 8.0969 | 38.0257 | [6 empty] | 2019-12-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S410XH(BK) | 410 W, 132 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 410 | 383.5 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9971 | 66 | 2 | N | 11.4 | 45.9 | 10.76 | 38.1 | 46.2 | -0.3183 | 0.0266 | -0.2371 | 2.15 | 36.9984 | 2.15 | 36.9984 | 8.4376 | 39.1207 | [6 empty] | 2021-09-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S420PJ | 420 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 420 | 393.2 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 78 | 2 | N | 10.22 | 52 | 9.73 | 43.2 | 43.46 | -0.3523 | 0.0478 | -0.2677 |  |  | 1.9489 | 42.0392 | 7.7918 | 40.8152 | [6 empty] | 2020-11-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S420VJ | 420 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 381 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 78 | 2 | N | 10.22 | 52 | 9.73 | 43.2 | 46.86 | -0.434 | 0.041 | -0.3268 |  |  | 1.96 | 41.49 | 8.16 | 38.74 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S420XI | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 393.8 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.04 | 48.6 | 10.4 | 40.4 | 45.6 | -0.3098 | 0.0257 | -0.2262 |  |  | 2.0722 | 39.4194 | 8.2889 | 38.0662 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S420YI | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 393.4 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.04 | 48.6 | 10.4 | 40.4 | 44 | -0.3412 | 0.0447 | -0.2641 |  |  | 2.0557 | 39.189 | 8.2529 | 38.1584 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S425PJ | 425 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 398 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 78 | 2 | N | 10.27 | 52.3 | 9.78 | 43.5 | 43.46 | -0.3523 | 0.0478 | -0.2677 |  |  | 1.959 | 42.3312 | 7.8319 | 41.0987 | [6 empty] | 2020-11-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S425VJ | 425 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 385.7 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 78 | 2 | N | 10.27 | 52.3 | 9.78 | 43.5 | 46.86 | -0.434 | 0.041 | -0.3268 |  |  | 1.98 | 41.51 | 8.18 | 38.912 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S425XI | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 398.6 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.11 | 48.8 | 10.47 | 40.6 | 45.6 | -0.3098 | 0.0257 | -0.2262 |  |  | 2.0862 | 39.6146 | 8.3447 | 38.2547 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S425YI | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 398.2 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.11 | 48.8 | 10.47 | 40.6 | 44 | -0.3412 | 0.0447 | -0.2641 |  |  | 2.0695 | 39.383 | 8.3084 | 38.3473 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S430XI | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 402 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1736 | 72 | 2 | N | 10.85 | 49.17 | 10.36 | 41.51 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.0969 | 39.2908 | 8.4053 | 38.0649 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S430NI | 430 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 400.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2049 | 72 | 2 | N | 11.2 | 48.6 | 10.65 | 40.4 | 46.18 | -0.3307 | 0.0522 | -0.2647 |  |  | 2.1918 | 39.9714 | 8.571 | 38.179 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S430XI | 430 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 430 | 398.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.19 | 49.2 | 10.6 | 40.6 | 44.98 | -0.3729 | 0.0471 | -0.2983 | 2.1454 | 39.5213 | 2.1454 | 39.5213 | 8.4839 | 37.9522 | [6 empty] | 2021-09-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S430YI | 430 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 399.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.2 | 48.6 | 10.65 | 40.4 | 45.73 | -0.3515 | 0.0506 | -0.2802 |  |  | 2.1575 | 39.8088 | 8.4337 | 38.4293 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S430PJ | 430 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 402.8 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 78 | 2 | N | 10.32 | 52.6 | 9.83 | 43.8 | 43.46 | -0.3523 | 0.0478 | -0.2677 |  |  | 1.969 | 42.6231 | 7.8719 | 41.3821 | [6 empty] | 2020-11-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S430VJ | 430 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 390.4 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 78 | 2 | N | 10.32 | 52.6 | 9.83 | 43.8 | 46.86 | -0.434 | 0.041 | -0.3268 |  |  | 2.01 | 41.54 | 8.18 | 39.29 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S430XI | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 403.4 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.18 | 49 | 10.54 | 40.8 | 45.6 | -0.3098 | 0.0257 | -0.2262 |  |  | 2.1001 | 39.8097 | 8.4004 | 38.4431 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S430YI | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 403 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.18 | 49 | 10.54 | 40.8 | 44 | -0.3412 | 0.0447 | -0.2641 |  |  | 2.0834 | 39.577 | 8.364 | 38.5362 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S435XI | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 406.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1736 | 72 | 2 | N | 10.92 | 49.38 | 10.42 | 41.75 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.109 | 39.518 | 8.454 | 38.285 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S435NI | 435 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 405.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2049 | 72 | 2 | N | 11.28 | 48.8 | 10.72 | 40.6 | 46.18 | -0.3307 | 0.0522 | -0.2647 |  |  | 2.2062 | 40.1692 | 8.6273 | 38.368 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S435XI | 435 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 435 | 403.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.26 | 49.4 | 10.67 | 40.8 | 44.98 | -0.3729 | 0.0471 | -0.2983 | 2.1595 | 39.7159 | 2.1595 | 39.7159 | 8.5399 | 38.1391 | [6 empty] | 2021-09-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S435YI | 435 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 404.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.28 | 48.8 | 10.72 | 40.6 | 45.73 | -0.3515 | 0.0506 | -0.2802 |  |  | 2.1716 | 40.0059 | 8.4891 | 38.6195 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S435PJ | 435 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 407.6 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 78 | 2 | N | 10.36 | 52.9 | 9.87 | 44.1 | 43.46 | -0.3523 | 0.0478 | -0.2677 |  |  | 1.977 | 42.9151 | 7.904 | 41.6656 | [6 empty] | 2020-11-12
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S435VJ | 435 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 395.1 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 78 | 2 | N | 10.36 | 52.9 | 9.87 | 44.1 | 46.86 | -0.434 | 0.041 | -0.3268 |  |  | 2.04 | 41.45 | 8.2 | 39.85 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S435XI | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 408.2 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.25 | 49.2 | 10.61 | 41 | 45.6 | -0.3098 | 0.0257 | -0.2262 |  |  | 2.1141 | 40.0049 | 8.4562 | 38.6316 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S435YI | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 407.8 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.25 | 49.2 | 10.61 | 41 | 44 | -0.3412 | 0.0447 | -0.2641 |  |  | 2.0972 | 39.771 | 8.4195 | 38.7251 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S440XI | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 411.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1736 | 72 | 2 | N | 11 | 49.57 | 10.48 | 41.99 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.1211 | 39.7452 | 8.5027 | 38.5051 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S440NI | 440 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 410.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2049 | 72 | 2 | N | 11.36 | 49 | 10.79 | 40.8 | 46.18 | -0.3307 | 0.0522 | -0.2647 |  |  | 2.2206 | 40.3671 | 8.6837 | 38.557 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S440XI | 440 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 440 | 408.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.34 | 49.6 | 10.74 | 41 | 44.98 | -0.3729 | 0.0471 | -0.2983 | 2.1737 | 39.9106 | 2.1737 | 39.9106 | 8.596 | 38.3261 | [6 empty] | 2021-09-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S440YI | 440 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 409.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.36 | 49 | 10.79 | 40.8 | 45.73 | -0.3515 | 0.0506 | -0.2802 |  |  | 2.1858 | 40.2029 | 8.5446 | 38.8098 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S440PJ | 440 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 412.4 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 78 | 2 | N | 10.41 | 53.2 | 9.92 | 44.4 | 43.46 | -0.3523 | 0.0478 | -0.2677 |  |  | 1.987 | 43.207 | 7.944 | 41.949 | [6 empty] | 2020-11-12 | 2020-12-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S440VJ | 440 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 399.8 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 78 | 2 | N | 10.41 | 53.2 | 9.92 | 44.4 | 46.86 | -0.434 | 0.041 | -0.3268 |  |  | 2.03 | 41.97 | 8.19 | 40.19 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S440XI | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 413 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.33 | 49.4 | 10.69 | 41.2 | 45.6 | -0.3098 | 0.0257 | -0.2262 |  |  | 2.13 | 40.2 | 8.52 | 38.82 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S440YI | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 412.6 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.33 | 49.4 | 10.69 | 41.2 | 44 | -0.3412 | 0.0447 | -0.2641 |  |  | 2.113 | 39.965 | 8.483 | 38.914 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S445XI | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 416.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1736 | 72 | 2 | N | 11.07 | 49.75 | 10.54 | 42.22 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.1333 | 39.9629 | 8.5514 | 38.716 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S445NI | 445 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 415 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2049 | 72 | 2 | N | 11.44 | 49.2 | 10.86 | 41 | 46.18 | -0.3307 | 0.0522 | -0.2647 |  |  | 2.235 | 40.565 | 8.74 | 38.746 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S445XI | 445 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 445 | 413.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.42 | 49.8 | 10.81 | 41.2 | 44.98 | -0.3729 | 0.0471 | -0.2983 | 2.1879 | 40.1053 | 2.1879 | 40.1053 | 8.652 | 38.513 | [6 empty] | 2021-09-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S445YI | 445 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 413.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.44 | 49.2 | 10.86 | 41 | 45.73 | -0.3515 | 0.0506 | -0.2802 |  |  | 2.2 | 40.4 | 8.6 | 39 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S445PJ | 445 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 417.2 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 78 | 2 | N | 10.46 | 53.5 | 9.97 | 44.7 | 43.46 | -0.3523 | 0.0478 | -0.2677 |  |  | 1.997 | 43.4989 | 7.984 | 42.2324 | [6 empty] | 2020-12-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S445VJ | 445 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 404.5 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 78 | 2 | N | 10.46 | 53.5 | 9.97 | 44.7 | 46.86 | -0.434 | 0.041 | -0.3268 |  |  | 2.04 | 42.34 | 8.19 | 40.63 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S445XI | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 417.8 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.4 | 49.6 | 10.76 | 41.4 | 45.6 | -0.3098 | 0.0257 | -0.2262 |  |  | 2.1439 | 40.3951 | 8.5758 | 39.0084 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S445YI | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 417.4 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.4 | 49.6 | 10.76 | 41.4 | 44 | -0.3412 | 0.0447 | -0.2641 |  |  | 2.1268 | 40.159 | 8.5385 | 39.1029 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiA-S450XI | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 421.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.1736 | 72 | 2 | N | 11.14 | 49.93 | 10.6 | 42.45 | 43.8 | -0.3581 | 0.0485 | -0.275 |  |  | 2.1454 | 40.1806 | 8.6 | 38.9269 | [6 empty] | 2021-07-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S450NI | 450 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 419.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2049 | 72 | 2 | N | 11.52 | 49.4 | 10.93 | 41.2 | 46.18 | -0.3307 | 0.0522 | -0.2647 |  |  | 2.2494 | 40.7629 | 8.7963 | 38.935 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S450XI | 450 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 450 | 418 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.5 | 50 | 10.87 | 41.4 | 44.98 | -0.3729 | 0.0471 | -0.2983 | 2.2 | 40.3 | 2.2 | 40.3 | 8.7 | 38.7 | [6 empty] | 2021-09-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S450YI | 450 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 418.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.52 | 49.4 | 10.93 | 41.2 | 45.73 | -0.3515 | 0.0506 | -0.2802 |  |  | 2.2142 | 40.5971 | 8.6554 | 39.1902 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S450PJ | 450 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 422 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 78 | 2 | N | 10.51 | 53.8 | 10.02 | 45 | 43.46 | -0.3523 | 0.0478 | -0.2677 |  |  | 2.007 | 43.7909 | 8.0241 | 42.5159 | [6 empty] | 2020-12-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S450VJ | 450 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 409.2 |  | 2020-07-29 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 78 | 2 | N | 10.51 | 53.8 | 10.02 | 45 | 46.86 | -0.434 | 0.041 | -0.3268 |  |  | 2.06 | 42.25 | 8.2 | 41.08 | [6 empty] | 2020-11-23
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S450XI | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 422.6 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.47 | 49.8 | 10.83 | 41.6 | 45.6 | -0.3098 | 0.0257 | -0.2262 |  |  | 2.1579 | 40.5903 | 8.6316 | 39.1969 | [6 empty] | 2021-03-11
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiS-S450YI | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 422.2 |  | 2021-01-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.47 | 49.8 | 10.83 | 41.6 | 44 | -0.3412 | 0.0447 | -0.2641 |  |  | 2.1407 | 40.353 | 8.5941 | 39.2918 | [6 empty] | 2021-02-22
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S455NI | 455 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 424.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2049 | 72 | 2 | N | 11.6 | 49.6 | 11 | 41.4 | 46.18 | -0.3307 | 0.0522 | -0.2647 |  |  | 2.2638 | 40.9608 | 8.8527 | 39.124 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S455XI | 455 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 455 | 422.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.59 | 50.2 | 10.94 | 41.6 | 44.98 | -0.3729 | 0.0471 | -0.2983 | 2.2142 | 40.4947 | 2.2142 | 40.4947 | 8.756 | 38.887 | [6 empty] | 2021-09-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S455YI | 455 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 423.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.6 | 49.6 | 11 | 41.4 | 45.73 | -0.3515 | 0.0506 | -0.2802 |  |  | 2.2284 | 40.7941 | 8.7109 | 39.3805 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S460NI | 460 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 429.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2049 | 72 | 2 | N | 11.67 | 49.8 | 11.06 | 41.6 | 46.18 | -0.3307 | 0.0522 | -0.2647 |  |  | 2.2762 | 41.1586 | 8.901 | 39.313 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S460XI | 460 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 460 | 427.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.67 | 50.4 | 11.01 | 41.8 | 44.98 | -0.3729 | 0.0471 | -0.2983 | 2.2283 | 40.6894 | 2.2283 | 40.6894 | 8.8121 | 39.0739 | [6 empty] | 2021-09-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S460YI | 460 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 428.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.67 | 49.8 | 11.06 | 41.6 | 45.73 | -0.3515 | 0.0506 | -0.2802 |  |  | 2.2405 | 40.9912 | 8.7584 | 39.5707 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S465XI | 465 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 465 | 432.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.74 | 50.6 | 11.08 | 42 | 44.98 | -0.3729 | 0.0471 | -0.2983 | 2.2425 | 40.8841 | 2.2425 | 40.8841 | 8.8681 | 39.2609 | [6 empty] | 2021-09-21
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S465YI | 465 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 465 | 433 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.75 | 50 | 11.13 | 41.8 | 45.73 | -0.3515 | 0.0506 | -0.2802 |  |  | 2.2547 | 41.1883 | 8.8138 | 39.761 | [6 empty] | 2021-10-01
HYUNDAI ENERGY SOLUTIONS CO., LTD. | HiG-S470XI | 470 W, 144 half-cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 470 | 437.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.19 | 72 | 2 | N | 11.81 | 50.8 | 11.14 | 42.2 | 44.98 | -0.3729 | 0.0471 | -0.2983 | 2.2546 | 41.0787 | 2.2546 | 41.0787 | 8.9161 | 39.4478 | [6 empty] | 2021-09-21
JA Solar | JAM5-72-165 | 165 W Monocrystalline Module | UL 1703 | 165 | 148 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.03 | 44.79 | 4.56 | 36.2 | 46.1 | -0.45 | 0.05 | -0.32 | -0.01 | -0.44 | 0.89876 | 35.0199 | 3.718 | 31.9133 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19075 |  | 2018-09-17
JA Solar | JAM5-72-170 | 170 W Monocrystalline Module | UL 1703 | 170 | 152.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.11 | 44.96 | 4.67 | 36.4 | 46.1 | -0.45 | 0.05 | -0.32 | -0.01 | -0.44 | 0.92044 | 35.2134 | 3.8077 | 32.0896 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19066 |  | 2018-09-17
JA Solar | JAM5-72-175 | 175 W Monocrystalline Module | UL 1703 | 175 | 157.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 45.13 | 4.78 | 36.6 | 46.1 | -0.45 | 0.05 | -0.32 | -0.01 | -0.44 | 0.94212 | 35.4069 | 3.8974 | 32.2659 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19061 |  | 2018-09-17
JA Solar | JAM5(L)(BK)-72-180/SI | 180 W Monocrystalline Module | UL 1703 | 180 | 160.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.44 | 44.88 | 4.94 | 36.42 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 0.97895 | 35.4578 | 3.9784 | 32.6201 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19284 |  | 2018-09-17
JA Solar | JAM5(L)-72-180/SI | 180 W Monocrystalline Module | UL 1703 | 180 | 160.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.44 | 44.88 | 4.94 | 36.42 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 0.97895 | 35.4578 | 3.9784 | 32.6201 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19284 |  | 2018-09-17
JA Solar | JAM5-72-180 | 180 W Monocrystalline Module | UL 1703 | 180 | 161.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.28 | 45.3 | 4.89 | 36.8 | 46.1 | -0.45 | 0.05 | -0.32 | -0.01 | -0.44 | 0.95322 | 35.9123 | 3.9082 | 34.036 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19018 |  | 2018-09-17
JA Solar | JAM5(L)(BK)-72-185/SI | 185 W Monocrystalline Module | UL 1703 | 185 | 164.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.52 | 45.18 | 5.06 | 36.54 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0027 | 35.5747 | 4.075 | 32.7276 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19282 |  | 2018-09-17
JA Solar | JAM5(L)-72-185/SI | 185 W Monocrystalline Module | UL 1703 | 185 | 164.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.52 | 45.18 | 5.06 | 36.54 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0027 | 35.5747 | 4.075 | 32.7276 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19282 |  | 2018-09-17
JA Solar | JAM5-72-185 | 185 W Monocrystalline Module | UL 1703 | 185 | 166.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.37 | 45.47 | 5 | 37 | 46.1 | -0.45 | 0.05 | -0.32 | -0.01 | -0.44 | 0.97466 | 36.1075 | 3.9961 | 34.2209 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19023 |  | 2018-09-17
JA Solar | JAM5(L)(BK)-72-190/SI | 190 W Monocrystalline Module | UL 1703 | 190 | 169.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.58 | 45.38 | 5.18 | 36.66 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0265 | 35.6915 | 4.1717 | 32.8351 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19283 |  | 2018-09-17
JA Solar | JAM5(L)-72-190/SI | 190 W Monocrystalline Module | UL 1703 | 190 | 169.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.58 | 45.38 | 5.18 | 36.66 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0265 | 35.6915 | 4.1717 | 32.8351 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19283 |  | 2018-09-17
JA Solar | JAM5-72-190 | 190 W Monocrystalline Module | UL 1703 | 190 | 171 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.45 | 45.64 | 5.11 | 37.2 | 46.1 | -0.45 | 0.05 | -0.32 | -0.01 | -0.44 | 0.9961 | 36.3026 | 4.084 | 34.4059 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19032 |  | 2018-09-17
JA Solar | JAM5(L)(BK)-72-195/SI | 195 W Monocrystalline Module | UL 1703 | 195 | 173.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.63 | 45.5 | 5.28 | 36.96 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0396 | 36.2144 | 4.2394 | 32.9538 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19307 |  | 2018-09-17
JA Solar | JAM5(L)-72-195/SI | 195 W Monocrystalline Module | UL 1703 | 195 | 173.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.63 | 45.5 | 5.28 | 36.96 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0396 | 36.2144 | 4.2394 | 32.9538 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19307 |  | 2018-09-17
JA Solar | JAM5-72-195 | 195 W Monocrystalline Module | UL 1703 | 195 | 175.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.54 | 45.81 | 5.21 | 37.4 | 46.1 | -0.45 | 0.05 | -0.32 | -0.01 | -0.44 | 1.0156 | 36.4978 | 4.1639 | 34.5909 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19009 |  | 2018-09-17
JA Solar | JAM5(L)(BK)-72-200/SI | 200 W Monocrystalline Module | UL 1703 | 200 | 178.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.66 | 45.62 | 5.37 | 37.26 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0573 | 36.5084 | 4.3116 | 33.2213 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19301 |  | 2018-09-17
JA Solar | JAM5(L)-72-200/SI | 200 W Monocrystalline Module | UL 1703 | 200 | 178.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.66 | 45.62 | 5.37 | 37.26 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0573 | 36.5084 | 4.3116 | 33.2213 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19301 |  | 2018-09-17
JA Solar | JAM6-60-200 | 200 W Monocrystalline Module | UL 1703 | 200 | 178.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 7.83 | 36.12 | 7.17 | 27.88 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.4728 | 27.5984 | 5.862 | 25.0833 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20323 |  | 2018-09-17
JA Solar | JAP6-60-200 | 200 W Polycrystalline Module | UL 1703 | 200 | 178.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 7.8 | 36.15 | 7.11 | 28.12 | 46.7 | -0.46 | 0.06 | -0.33 | -0.02 | -0.46 | 1.4201 | 28.3196 | 5.8043 | 25.5446 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20108 |  | 2018-09-17
JA Solar | JAM5(L)(BK)-72-205/SI | 205 W Monocrystalline Module | UL 1703 | 205 | 183.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.69 | 45.74 | 5.46 | 37.56 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0751 | 36.8023 | 4.3839 | 33.4888 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.193 |  | 2018-09-17
JA Solar | JAM5(L)-72-205/SI | 205 W Monocrystalline Module | UL 1703 | 205 | 183.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.69 | 45.74 | 5.46 | 37.56 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0751 | 36.8023 | 4.3839 | 33.4888 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.193 |  | 2018-09-17
JA Solar | JAM6-60-205 | 205 W Monocrystalline Module | UL 1703 | 205 | 183.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 7.92 | 36.29 | 7.3 | 28.08 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.4995 | 27.7964 | 5.9682 | 25.2632 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20331 |  | 2018-09-17
JA Solar | JAP6-60-205 | 205 W Polycrystalline Module | UL 1703 | 205 | 182.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 7.89 | 36.32 | 7.24 | 28.32 | 46.7 | -0.46 | 0.06 | -0.33 | -0.02 | -0.46 | 1.4461 | 28.5211 | 5.9104 | 25.7263 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20119 |  | 2018-09-17
JA Solar | JAM5(L)(BK)-72-210/SI | 210 W Monocrystalline Module | UL 1703 | 210 | 187.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.73 | 45.9 | 5.55 | 37.86 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0928 | 37.0963 | 4.4562 | 33.7563 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19304 |  | 2018-09-17
JA Solar | JAM5(L)-72-210/SI | 210 W Monocrystalline Module | UL 1703 | 210 | 187.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.73 | 45.9 | 5.55 | 37.86 | 47.6 | -0.4567 | 0.0615 | -0.3526 | 0.0128 | -0.464 | 1.0928 | 37.0963 | 4.4562 | 33.7563 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19304 |  | 2018-09-17
JA Solar | JAM6-60-210 | 210 W Monocrystalline Module | UL 1703 | 210 | 187.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8 | 36.46 | 7.43 | 28.28 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5262 | 27.9943 | 6.0745 | 25.4431 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20345 |  | 2018-09-17
JA Solar | JAP6-60-210 | 210 W Polycrystalline Module | UL 1703 | 210 | 187.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 7.97 | 36.49 | 7.36 | 28.52 | 46.7 | -0.46 | 0.06 | -0.33 | -0.02 | -0.46 | 1.47 | 28.7225 | 6.0084 | 25.9079 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20106 |  | 2018-09-17
JA Solar | JAM6-60-215 | 215 W Monocrystalline Module | UL 1703 | 215 | 192.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.09 | 36.63 | 7.55 | 28.48 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5508 | 28.1923 | 6.1726 | 25.6231 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20335 |  | 2018-09-17
JA Solar | JAP6(BK)-60-215 | 215 W Polycrystalline Module | UL 1703 | 215 | 190.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.06 | 36.66 | 7.49 | 28.72 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.4742 | 28.8798 | 6.0273 | 25.5573 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19802 |  | 2018-09-17
JA Solar | JAM6-60-220 | 220 W Monocrystalline Module | UL 1703 | 220 | 197 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.17 | 36.8 | 7.67 | 28.68 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5755 | 28.3903 | 6.2707 | 25.803 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20331 |  | 2018-09-17
JA Solar | JAP6(BK)-60-220 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.14 | 36.83 | 7.61 | 28.92 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.4978 | 29.0809 | 6.1238 | 25.7353 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19799 |  | 2018-09-17
JA Solar | JAM6-60-225 | 225 W Monocrystalline Module | UL 1703 | 225 | 201.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.26 | 36.97 | 7.79 | 28.88 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.546 | 29.2671 | 6.3238 | 26.1706 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.2011 |  | 2018-09-17
JA Solar | JAP6(BK)-60-225 | 225 W Polycrystalline Module | UL 1703 | 225 | 200 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.23 | 37 | 7.73 | 29.12 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.5214 | 29.282 | 6.2204 | 25.9133 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.198 |  | 2018-09-17
JA Solar | JAP6-60-225/MP | 225 W Polycrystalline Module | UL 1703 | 225 | 198.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.57 | 37.32 | 7.77 | 28.94 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5196 | 27.8832 | 6.29 | 25.7233 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18831 |  | 2018-09-17
JA Solar | JAM6-60-230 | 230 W Monocrystalline Module | UL 1703 | 230 | 206.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.34 | 37.14 | 7.91 | 29.08 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5698 | 29.4697 | 6.4212 | 26.3519 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20114 |  | 2018-09-17
JA Solar | JAP6(BK)-60-230 | 230 W Polycrystalline Module | UL 1703 | 230 | 204.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.31 | 37.17 | 7.84 | 29.32 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.543 | 29.4831 | 6.3089 | 26.0912 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.1978 |  | 2018-09-17
JA Solar | JAP6-60-230/MP | 230 W Polycrystalline Module | UL 1703 | 230 | 202.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.66 | 37.37 | 7.88 | 29.18 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5411 | 28.1145 | 6.379 | 25.9366 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18838 |  | 2018-09-17
JA Solar | JAM6-60-235 | 235 W Monocrystalline Module | UL 1703 | 235 | 210.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.43 | 37.31 | 8.03 | 29.28 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5937 | 29.6724 | 6.5186 | 26.5331 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.20122 |  | 2018-09-17
JA Solar | JAM6-60-235/SI | 235 W Monocrystalline Module | UL 1703 | 235 | 208.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.49 | 37.19 | 7.74 | 30.36 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.4966 | 29.7447 | 6.1784 | 27.25 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18942 |  | 2018-09-17
JA Solar | JAP6(BK)-60-235 | 235 W Polycrystalline Module | UL 1703 | 235 | 209.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.39 | 37.34 | 7.96 | 29.52 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 0.57567 | 29.3006 | 6.4286 | 30.0029 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.071776 |  | 2018-09-17
JA Solar | JAP6-60-235/MP | 235 W Polycrystalline Module | UL 1703 | 235 | 207.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.71 | 37.51 | 7.99 | 29.42 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5626 | 28.3457 | 6.4681 | 26.1499 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18848 |  | 2018-09-17
JA Solar | JAM6-60-240 | 240 W Monocrystalline Module | UL 1703 | 240 | 215.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.51 | 37.48 | 8.14 | 29.48 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.6155 | 29.8751 | 6.6079 | 26.7144 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.2011 |  | 2018-09-17
JA Solar | JAM6-60-240/SI | 240 W Monocrystalline Module | UL 1703 | 240 | 212.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.54 | 37.49 | 7.85 | 30.56 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5178 | 29.9407 | 6.2662 | 27.4295 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18935 |  | 2018-09-17
JA Solar | JAP6(BK)-60-240 | 240 W Polycrystalline Module | UL 1703 | 240 | 213.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.48 | 37.51 | 8.08 | 29.72 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 0.58434 | 29.4991 | 6.5255 | 30.2061 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.071824 |  | 2018-09-17
JA Solar | JAP6-60-240/MP | 240 W Polycrystalline Module | UL 1703 | 240 | 211.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.76 | 37.58 | 8.09 | 29.66 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5822 | 28.5769 | 6.549 | 26.3633 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18839 |  | 2018-09-17
JA Solar | JAM6-60-245/SI | 245 W Monocrystalline Module | UL 1703 | 245 | 217.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.58 | 37.74 | 7.96 | 30.76 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5391 | 30.1366 | 6.354 | 27.609 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18932 |  | 2018-09-17
JA Solar | JAP6(BK)-60-245 | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.56 | 37.68 | 8.19 | 29.92 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 0.5923 | 29.6976 | 6.6144 | 30.4094 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.071795 |  | 2018-09-17
JA Solar | JAP6-60-245 | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.56 | 37.68 | 8.19 | 29.92 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 0.5923 | 29.6976 | 6.6144 | 30.4094 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.071795 |  | 2018-09-17
JA Solar | JAP6-60-245/3BB | 245 W Polycrystalline Module | UL 1703 | 245 | 218.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.78 | 37.45 | 8.27 | 29.63 | 46.3 | -0.487 | 0.06 | -0.36 | 0.021 | -0.503 | 1.592 | 28.9751 | 6.6741 | 26.3887 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18827 |  | 2018-09-17
JA Solar | JAP6-60-245/MP | 245 W Polycrystalline Module | UL 1703 | 245 | 216.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.81 | 37.64 | 8.19 | 29.9 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5847 | 29.0912 | 6.6338 | 26.1574 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18817 |  | 2018-09-17
JA Solar | JAM6-60-250/SI | 250 W Monocrystalline Module | UL 1703 | 250 | 222.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.62 | 37.92 | 8.07 | 30.96 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5813 | 30.074 | 6.4877 | 27.2844 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19023 |  | 2018-09-17
JA Solar | JAP6(BK)-60-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.65 | 37.85 | 8.3 | 30.12 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 0.60025 | 29.8962 | 6.7032 | 30.6127 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.071781 |  | 2018-09-17
JA Solar | JAP6-60-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.65 | 37.85 | 8.3 | 30.12 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 0.60025 | 29.8962 | 6.7032 | 30.6127 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.071781 |  | 2018-09-17
JA Solar | JAP6-60-250/3BB | 250 W Polycrystalline Module | UL 1703 | 250 | 222.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.84 | 37.54 | 8.34 | 29.98 | 46.3 | -0.487 | 0.06 | -0.36 | 0.021 | -0.503 | 1.6054 | 29.3174 | 6.7306 | 26.7005 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18827 |  | 2018-09-17
JA Solar | JAP6-60-250/MP | 250 W Polycrystalline Module | UL 1703 | 250 | 221 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.86 | 37.71 | 8.29 | 30.14 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.6041 | 29.3247 | 6.7148 | 26.3673 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18815 |  | 2018-09-17
JA Solar | JAP6-72-250 | 250 W Polycrystalline Module | UL 1703 | 250 | 222.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9523 | 72 | 1 | N | 7.8 | 43.6 | 7.09 | 35.26 | 46.7 | -0.46 | 0.06 | -0.33 | -0.02 | -0.46 | 1.4217 | 34.471 | 5.7514 | 31.9019 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.19603 |  | 2018-09-17
JA Solar | JAM6-60-255/SI | 255 W Monocrystalline Module | UL 1703 | 255 | 226.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.64 | 38.1 | 8.18 | 31.16 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.6029 | 30.2682 | 6.5761 | 27.4606 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19026 |  | 2018-09-17
JA Solar | JAM6-72-255 | 255 W Monocrystalline Module | UL 1703 | 255 | 228.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8 | 44.5 | 7.3 | 34.93 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5018 | 34.4425 | 5.9693 | 31.2888 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.20285 |  | 2018-09-17
JA Solar | JAP6-60-255/3BB | 255 W Polycrystalline Module | UL 1703 | 255 | 230.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.98 | 37.82 | 8.42 | 30.29 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.67 | 29.39 | 6.73 | 27.36 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19248 |  | 2018-09-17
JA Solar | JAP6-60-255/4BB | 255 W Polycrystalline Module | UL 1703 | 255 | 236 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.9 | 37.61 | 8.34 | 30.59 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.6379 | 29.2597 | 6.6082 | 28.3939 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18794 |  | 2018-09-17
JA Solar | JAP6-60-255/MP | 255 W Polycrystalline Module | UL 1703 | 255 | 225.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.91 | 37.78 | 8.4 | 30.36 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.6253 | 29.5387 | 6.8039 | 26.5598 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18828 |  | 2018-09-17
JA Solar | JAP6-72-255 | 255 W Polycrystalline Module | UL 1703 | 255 | 227.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9523 | 72 | 1 | N | 7.9 | 43.8 | 7.16 | 35.61 | 46.7 | -0.46 | 0.06 | -0.33 | -0.02 | -0.46 | 1.4357 | 34.8132 | 5.8082 | 32.2186 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.19601 |  | 2018-09-17
JA Solar | JAM6-60-260/SI | 260 W Monocrystalline Module | UL 1703 | 260 | 234.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 8.92 | 38.08 | 8.44 | 30.81 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.68 | 29.29 | 7.23 | 34.83 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18926 |  | 2018-09-17
JA Solar | JAM6-72-260 | 260 W Monocrystalline Module | UL 1703 | 260 | 232.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.1 | 44.6 | 7.4 | 35.14 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5224 | 34.6496 | 6.051 | 31.4769 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.20289 |  | 2018-09-17
JA Solar | JAP6-60-260/3BB | 260 W Polycrystalline Module | UL 1703 | 260 | 234.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.04 | 37.98 | 8.49 | 30.63 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.68 | 29.72 | 6.79 | 27.67 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19204 |  | 2018-09-17
JA Solar | JAP6-60-260/4BB | 260 W Polycrystalline Module | UL 1703 | 260 | 240.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.04 | 37.84 | 8.44 | 30.81 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.6575 | 29.4702 | 6.6875 | 28.5981 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18787 |  | 2018-09-17
JA Solar | JAP6-60-260/4BB/RE | 260 W Multi Riecium Module | UL 1703 | 260 | 238 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.04 | 37.98 | 8.51 | 30.55 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.6959 | 29.2042 | 6.7528 | 27.9031 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19049 |  | 2018-09-17
JA Solar | JAP6-60-260/MP | 260 W Polycrystalline Module | UL 1703 | 260 | 230.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 8.96 | 37.84 | 8.51 | 30.57 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.6466 | 29.743 | 6.893 | 26.7435 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18837 |  | 2018-09-17
JA Solar | JAP6-72-260 | 260 W Polycrystalline Module | UL 1703 | 260 | 232 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9523 | 72 | 1 | N | 8 | 43.8 | 7.27 | 35.76 | 46.7 | -0.46 | 0.06 | -0.33 | -0.02 | -0.46 | 1.4578 | 34.9599 | 5.8974 | 32.3543 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.19602 |  | 2018-09-17
JA Solar | JAM6-60-265/SI | 265 W Monocrystalline Module | UL 1703 | 265 | 239.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 9 | 38.26 | 8.52 | 31.11 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.69 | 29.58 | 7.3 | 35.17 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18864 |  | 2018-09-17
JA Solar | JAM6-72-265 | 265 W Monocrystalline Module | UL 1703 | 265 | 237.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.2 | 44.6 | 7.5 | 35.33 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.543 | 34.8369 | 6.1328 | 31.6471 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.20284 |  | 2018-09-17
JA Solar | JAP6(BK)-72-265 | 265 W Monocrystalline Module | UL 1703 | 265 | 235.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.1 | 44 | 7.37 | 35.96 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.4587 | 35.6321 | 5.917 | 32.236 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19614 |  | 2018-09-17
JA Solar | JAP6-60-265/3BB | 265 W Polycrystalline Module | UL 1703 | 265 | 239.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.1 | 38.14 | 8.56 | 30.96 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.7 | 30.04 | 6.84 | 27.97 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19271 |  | 2018-09-17
JA Solar | JAP6-60-265/4BB | 265 W Polycrystalline Module | UL 1703 | 265 | 245.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.08 | 38.05 | 8.54 | 31.02 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.6772 | 29.671 | 6.7667 | 28.793 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18779 |  | 2018-09-17
JA Solar | JAP6-60-265/4BB/RE | 265 W Multi Riecium Module | UL 1703 | 265 | 242.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.1 | 38.14 | 8.58 | 30.89 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.7098 | 29.5292 | 6.8083 | 28.2136 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19053 |  | 2018-09-17
JA Solar | JAM6-60-270/SI | 270 W Monocrystalline Module | UL 1703 | 270 | 243.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 9.09 | 38.46 | 8.62 | 31.33 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.71 | 29.79 | 7.39 | 35.42 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18867 |  | 2018-09-17
JA Solar | JAM6-72-270 | 270 W Monocrystalline Module | UL 1703 | 270 | 241.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.3 | 44.7 | 7.6 | 35.33 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5635 | 34.8369 | 6.2146 | 31.6471 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.20174 |  | 2018-09-17
JA Solar | JAP6(BK)-72-270 | 270 W Monocrystalline Module | UL 1703 | 270 | 240.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.2 | 44 | 7.5 | 36 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.4844 | 35.6718 | 6.0214 | 32.2719 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19612 |  | 2018-09-17
JA Solar | JAP6-60-270/3BB | 270 W Polycrystalline Module | UL 1703 | 270 | 244 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.16 | 38.3 | 8.63 | 31.29 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.71 | 30.36 | 6.9 | 28.27 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19228 |  | 2018-09-17
JA Solar | JAP6-60-270/4BB | 270 W Polycrystalline Module | UL 1703 | 270 | 250.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.15 | 38.27 | 8.65 | 31.23 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.6988 | 29.8719 | 6.8539 | 28.9879 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18795 |  | 2018-09-17
JA Solar | JAP6-60-270/4BB/RE | 270 W Multi Riecium Module | UL 1703 | 270 | 247.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.16 | 38.3 | 8.65 | 31.21 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.7238 | 29.8351 | 6.8638 | 28.5059 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19048 |  | 2018-09-17
JA Solar | JAM6-60-275/SI | 275 W Monocrystalline Module | UL 1703 | 275 | 248.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 9.18 | 38.66 | 8.71 | 31.58 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.73 | 30.02 | 7.47 | 35.7 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18885 |  | 2018-09-17
JA Solar | JAM6-72-275 | 275 W Monocrystalline Module | UL 1703 | 275 | 246.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.4 | 44.8 | 7.7 | 35.71 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5841 | 35.2116 | 6.2964 | 31.9875 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.20283 |  | 2018-09-17
JA Solar | JAP6(BK)-72-275 | 275 W Monocrystalline Module | UL 1703 | 275 | 244.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.25 | 44.2 | 7.53 | 36.52 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.4904 | 36.187 | 6.0455 | 32.738 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19612 |  | 2018-09-17
JA Solar | JAP6-60-275/3BB | 275 W Polycrystalline Module | UL 1703 | 275 | 248.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.22 | 38.46 | 8.7 | 31.61 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.72 | 30.67 | 6.96 | 28.56 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19183 |  | 2018-09-17
JA Solar | JAP6-60-275/4BB | 275 W Polycrystalline Module | UL 1703 | 275 | 254.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.26 | 38.48 | 8.75 | 31.44 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.7184 | 30.0728 | 6.9331 | 29.1829 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18792 |  | 2018-09-17
JA Solar | JAP6-60-275/4BB/RE | 275 W Multi Riecium Module | UL 1703 | 275 | 252 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.22 | 38.46 | 8.72 | 31.54 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.7377 | 30.1506 | 6.9194 | 28.8073 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19052 |  | 2018-09-17
JA Solar | JAP6-72-275/3BB | 275 W Polycrystalline Module | UL 1703 | 275 | 245.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.27 | 44.53 | 7.54 | 36.45 | 47.2 | -0.45 | 0.04 | -0.3 | 0.01 | -0.46 | 1.3935 | 35.8294 | 5.9915 | 32.9444 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18156 |  | 2018-09-17
JA Solar | JAM60S01-280/PR | 280 W, 60 Cell Mono PERC PV Module | UL 1703 | 280 | 258.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 |  | N | 9.38 | 39.05 | 8.86 | 31.6 | 45.1 | -0.377 | 0.036 | -0.281 | -0.003 | -0.374 | 1.825 | 31.497 | 7.338 | 30.16 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM60S02-280/PR | 280 W, 60 Cell Mono PERC Module | UL 1703 | 280 | 256.6 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 9.38 | 39.05 | 8.86 | 31.6 | 46.46 | -0.387 | 0.037 | -0.283 | -0.003 | -0.385 | 1.788 | 31.331 | 7.189 | 29.753 | [6 empty] | 2018-02-01 | 2018-09-17
JA Solar | JAM6-60-280/SI | 280 W Monocrystalline Module | UL 1703 | 280 | 253.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6351 | 60 | 1 | N | 9.27 | 38.86 | 8.8 | 31.82 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.75 | 30.25 | 7.54 | 35.97 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.18906 |  | 2018-09-17
JA Solar | JAM6-72-280 | 280 W Monocrystalline Module | UL 1703 | 280 | 251.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.5 | 44.8 | 7.8 | 35.9 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.5659 | 35.4052 | 6.1947 | 32.8402 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.198 |  | 2018-09-17
JA Solar | JAP6(BK)-72-280 | 280 W Monocrystalline Module | UL 1703 | 280 | 249.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.32 | 44.2 | 7.62 | 36.75 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.5082 | 36.4149 | 6.1178 | 32.9442 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19614 |  | 2018-09-17
JA Solar | JAP6(BK)-72-280/MP | 280 W Monocrystalline Module | UL 1703 | 280 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.56 | 45.33 | 7.82 | 35.81 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5296 | 34.8446 | 6.2737 | 31.1258 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19036 |  | 2018-09-17
JA Solar | JAP6-60-280/4BB/RE | 280 W Multi Riecium Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6351 | 60 | 1 | N | 9.33 | 38.85 | 8.78 | 31.88 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.7497 | 30.4756 | 6.967 | 29.1179 | Rack | Flat Plate | 0.991 | 1.65 | 1 | 0.19044 |  | 2018-09-17
JA Solar | JAP6-72-280/3BB | 280 W Polycrystalline Module | UL 1703 | 280 | 250.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.29 | 45.38 | 7.78 | 35.99 | 47.2 | -0.45 | 0.04 | -0.3 | 0.01 | -0.46 | 1.4379 | 35.3772 | 6.1823 | 32.5286 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18167 |  | 2018-09-17
JA Solar | JAP6-72-280/MP | 280 W Polycrystalline Module | UL 1703 | 280 | 247.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.56 | 45.33 | 7.82 | 35.81 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5296 | 34.8446 | 6.2737 | 31.1258 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19036 |  | 2018-09-17
JA Solar | JAM6(BK)-72-285/SI | 285 W Monocrystalline Module | UL 1703 | 285 | 252.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.56 | 45.42 | 7.78 | 36.63 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5 | 35.3671 | 6.1867 | 32.6357 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18615 |  | 2018-09-17
JA Solar | JAM60S01-285/PR | 285 W, 60 Cell Mono PERC PV Module | UL 1703 | 285 | 263.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 |  | N | 9.46 | 39.25 | 8.99 | 31.7 | 45.1 | -0.377 | 0.036 | -0.281 | -0.003 | -0.374 | 1.825 | 31.497 | 7.338 | 30.16 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM60S02-285/PR | 285 W, 60 Cell Mono PERC Module | UL 1703 | 285 | 261.3 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 9.46 | 39.25 | 8.99 | 31.7 | 46.46 | -0.387 | 0.037 | -0.283 | -0.003 | -0.385 | 1.788 | 31.331 | 7.189 | 29.753 | [6 empty] | 2018-02-01 | 2018-09-17
JA Solar | JAM6-72-285 | 285 W Monocrystalline Module | UL 1703 | 285 | 255.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.6 | 44.8 | 7.87 | 36.21 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.58 | 35.7109 | 6.2503 | 33.1237 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.19797 |  | 2018-09-17
JA Solar | JAM6-72-285/SI | 285 W Monocrystalline Module | UL 1703 | 285 | 252.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.56 | 45.42 | 7.78 | 36.63 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5 | 35.3671 | 6.1867 | 32.6357 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18615 |  | 2018-09-17
JA Solar | JAP6(BK)-72-285 | 285 W Monocrystalline Module | UL 1703 | 285 | 253.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.38 | 44.4 | 7.7 | 37.01 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.4714 | 37.074 | 6.1569 | 33.2989 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.1914 |  | 2018-09-17
JA Solar | JAP6(BK)-72-285/MP | 285 W Monocrystalline Module | UL 1703 | 285 | 251.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.6 | 45.42 | 7.9 | 36.08 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5453 | 35.1074 | 6.3379 | 31.3605 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19035 |  | 2018-09-17
JA Solar | JAP6-72-285/3BB | 285 W Polycrystalline Module | UL 1703 | 285 | 254.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.38 | 45.41 | 7.9 | 36.08 | 47.2 | -0.45 | 0.04 | -0.3 | 0.01 | -0.46 | 1.46 | 35.4657 | 6.2776 | 32.6099 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18169 |  | 2018-09-17
JA Solar | JAP6-72-285/MP | 285 W Polycrystalline Module | UL 1703 | 285 | 251.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.6 | 45.42 | 7.9 | 36.08 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5453 | 35.1074 | 6.3379 | 31.3605 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19035 |  | 2018-09-17
JA Solar | JAM6(BK)-72-290/SI | 290 W Monocrystalline Module | UL 1703 | 290 | 257.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.6 | 45.72 | 7.89 | 36.76 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5213 | 35.4927 | 6.2742 | 32.7515 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18618 |  | 2018-09-17
JA Solar | JAM60S01-290/PR | 290 W, 60 Cell Mono PERC PV Module | UL 1703 | 290 | 268.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 |  | N | 9.57 | 39.46 | 9.12 | 31.8 | 45.1 | -0.377 | 0.036 | -0.281 | -0.003 | -0.374 | 1.825 | 31.497 | 7.338 | 30.16 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM60S02-290/PR | 290 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 290 | 266 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.588 | 60 | 1 | N | 9.57 | 39.46 | 9.12 | 31.8 | 46.46 | -0.387 | 0.037 | -0.283 | 1.788 | 31.331 | 1.788 | 31.331 | 7.189 | 29.753 | [6 empty] | 2018-02-01 | 2019-03-15
JA Solar | JAM6-72-290 | 290 W Monocrystalline Module | UL 1703 | 290 | 260.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.6 | 44.85 | 7.87 | 36.85 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.58 | 36.3421 | 6.2503 | 33.7092 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.198 |  | 2018-09-17
JA Solar | JAM6-72-290/SI | 290 W Monocrystalline Module | UL 1703 | 290 | 257.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.6 | 45.72 | 7.89 | 36.76 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5213 | 35.4927 | 6.2742 | 32.7515 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18618 |  | 2018-09-17
JA Solar | JAP6(BK)-72-290 | 290 W Monocrystalline Module | UL 1703 | 290 | 258.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.42 | 44.4 | 7.74 | 37.47 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.479 | 37.5348 | 6.1889 | 33.7128 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19143 |  | 2018-09-17
JA Solar | JAP6(BK)-72-290/MP | 290 W Monocrystalline Module | UL 1703 | 290 | 256.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.64 | 45.5 | 7.98 | 36.34 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5609 | 35.3604 | 6.402 | 31.5864 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19033 |  | 2018-09-17
JA Solar | JAP6-72-290/3BB | 290 W Polycrystalline Module | UL 1703 | 290 | 259.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.42 | 45.72 | 7.97 | 36.39 | 47.2 | -0.45 | 0.04 | -0.3 | 0.01 | -0.46 | 1.6057 | 36.0303 | 6.3184 | 33.1987 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19949 |  | 2018-09-17
JA Solar | JAP6-72-290/MP | 290 W Polycrystalline Module | UL 1703 | 290 | 256.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.64 | 45.5 | 7.98 | 36.34 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5609 | 35.3604 | 6.402 | 31.5864 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19033 |  | 2018-09-17
JA Solar | JAM6(BK)-72-295/SI | 295 W Monocrystalline Module | UL 1703 | 295 | 262 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.64 | 45.92 | 7.99 | 36.92 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5654 | 36.0047 | 6.3813 | 32.5951 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19106 |  | 2018-09-17
JA Solar | JAM60S01-295/PR | 295 W, 60 Cell Mono PERC PV Module | UL 1703 | 295 | 272.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 |  | N | 9.66 | 39.64 | 9.21 | 32.03 | 45.1 | -0.377 | 0.036 | -0.281 | -0.003 | -0.374 | 1.825 | 31.497 | 7.338 | 30.16 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM60S02-295/PR | 295 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 295 | 270.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.588 | 60 | 1 | N | 9.66 | 39.64 | 9.21 | 32.03 | 46.46 | -0.387 | 0.037 | -0.283 | 1.8056 | 31.5576 | 1.8056 | 31.5576 | 7.2599 | 29.9682 | [6 empty] | 2019-03-15
JA Solar | JAM6-72-295 | 295 W Monocrystalline Module | UL 1703 | 295 | 264.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.7 | 44.9 | 7.98 | 36.97 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.602 | 36.4604 | 6.3377 | 33.819 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.198 |  | 2018-09-17
JA Solar | JAM6-72-295/SI | 295 W Monocrystalline Module | UL 1703 | 295 | 262 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.64 | 45.92 | 7.99 | 36.92 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5654 | 36.0047 | 6.3813 | 32.5951 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19106 |  | 2018-09-17
JA Solar | JAP6(BK)-72-295 | 295 W Monocrystalline Module | UL 1703 | 295 | 262.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.48 | 44.6 | 7.8 | 37.82 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.4905 | 37.8854 | 6.2369 | 34.0277 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19142 |  | 2018-09-17
JA Solar | JAP6(BK)-72-295/MP | 295 W Monocrystalline Module | UL 1703 | 295 | 260.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.68 | 45.59 | 8.07 | 36.56 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5568 | 35.6011 | 6.4783 | 32.6947 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18787 |  | 2018-09-17
JA Solar | JAP6-72-295 | 295 W Polycrystalline Module | UL 1703 | 295 | 264.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9523 | 72 | 1 | N | 8.48 | 44.6 | 7.8 | 37.82 | 46.7 | -0.46 | 0.06 | -0.33 | -0.02 | -0.46 | 1.5659 | 37.2987 | 6.2043 | 34.5327 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.19799 |  | 2018-09-17
JA Solar | JAP6-72-295/3BB | 295 W Polycrystalline Module | UL 1703 | 295 | 264.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.48 | 45.9 | 8.06 | 36.6 | 47.2 | -0.45 | 0.04 | -0.3 | 0.01 | -0.46 | 1.6238 | 36.2382 | 6.3897 | 33.3902 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19947 |  | 2018-09-17
JA Solar | JAP6-72-295/MP | 295 W Polycrystalline Module | UL 1703 | 295 | 260.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.68 | 45.59 | 8.07 | 36.56 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5568 | 35.6011 | 6.4783 | 32.6947 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18787 |  | 2018-09-17
JA Solar | JAM6(BK)-72-300/SI | 300 W Monocrystalline Module | UL 1703 | 300 | 266.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.68 | 46.1 | 8.08 | 37.13 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5831 | 36.2095 | 6.4532 | 32.7805 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19107 |  | 2018-09-17
JA Solar | JAM60S01-300/PR | 300 W, 60 Cell Mono PERC PV Module | UL 1703 | 300 | 277.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 |  | N | 9.75 | 39.85 | 9.3 | 32.26 | 45.1 | -0.377 | 0.036 | -0.281 | -0.003 | -0.374 | 1.825 | 31.497 | 7.338 | 30.16 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM60S02-300/PR | 300 W, 60 Cell Mono PERC Module | UL 1703 | 300 | 275.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 9.75 | 39.85 | 9.3 | 32.26 | 46.46 | -0.387 | 0.037 | -0.283 | -0.003 | -0.385 | 1.8233 | 31.7842 | 7.3309 | 30.1834 | [6 empty] | 2018-02-01 | 2018-09-17
JA Solar | JAM6-72-300 | 300 W Monocrystalline Module | UL 1703 | 300 | 269.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9523 | 72 | 1 | N | 8.75 | 44.9 | 8.03 | 37.36 | 46.6 | -0.45 | 0.05 | -0.32 | 0.02 | -0.47 | 1.6121 | 36.8451 | 6.3774 | 34.1757 | Rack | Flat Plate | 0.991 | 1.97 | 1 | 0.19799 |  | 2018-09-17
JA Solar | JAM6-72-300/SI | 300 W Monocrystalline Module | UL 1703 | 300 | 266.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.68 | 46.1 | 8.08 | 37.13 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5831 | 36.2095 | 6.4532 | 32.7805 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19107 |  | 2018-09-17
JA Solar | JAP6(BK)-72-300 | 300 W Monocrystalline Module | UL 1703 | 300 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.53 | 44.6 | 7.83 | 38.17 | 47.9 | -0.4531 | 0.0644 | -0.3642 | 0.0192 | -0.4721 | 1.4962 | 38.236 | 6.2608 | 34.3426 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.1907 |  | 2018-09-17
JA Solar | JAP6(BK)-72-300/MP | 300 W Monocrystalline Module | UL 1703 | 300 | 265.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.73 | 45.67 | 8.13 | 36.9 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5683 | 35.9321 | 6.5265 | 32.9987 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18784 |  | 2018-09-17
JA Solar | JAP6-72-300 | 300 W Polycrystalline Module | UL 1703 | 300 | 271.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.68 | 45.31 | 8.18 | 36.74 | 45.2 | -0.4479 | 0.05654 | -0.3287 | -0.01245 | -0.4382 | 1.6851 | 35.9088 | 6.5199 | 33.566 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.2017 |  | 2018-09-17
JA Solar | JAP6-72-300/3BB | 300 W Polycrystalline Module | UL 1703 | 300 | 270.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.73 | 45.2 | 8.24 | 36.41 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.64 | 35.2 | 6.59 | 33.02 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19243 |  | 2018-09-17
JA Solar | JAP6-72-300/MP | 300 W Polycrystalline Module | UL 1703 | 300 | 265.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.73 | 45.67 | 8.13 | 36.9 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5683 | 35.9321 | 6.5265 | 32.9987 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18784 |  | 2018-09-17
JA Solar | JAM6(BK)-72-305/SI | 305 W Monocrystalline Module | UL 1703 | 305 | 271.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.73 | 46.28 | 8.13 | 37.52 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.5929 | 36.5898 | 6.4932 | 33.1248 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19109 |  | 2018-09-17
JA Solar | JAM60S01-305/PR | 305 W, 60 Cell Mono PERC PV Module | UL 1703 | 305 | 282.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 |  | N | 9.86 | 40.05 | 9.37 | 32.57 | 45.1 | -0.377 | 0.036 | -0.281 | -0.003 | -0.374 | 1.825 | 31.497 | 7.338 | 30.16 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM6-72-305/SI | 305 W Monocrystalline Module | UL 1703 | 305 | 275.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.78 | 45.41 | 8.26 | 36.93 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.65 | 35.03 | 6.6 | 33.04 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18951 |  | 2018-09-17
JA Solar | JAP6(BK)-72-305/MP | 305 W Monocrystalline Module | UL 1703 | 305 | 269.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.77 | 45.74 | 8.19 | 37.24 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5799 | 36.2632 | 6.5747 | 33.3028 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18784 |  | 2018-09-17
JA Solar | JAP6-72-305 | 305 W Polycrystalline Module | UL 1703 | 305 | 276.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.72 | 45.42 | 8.37 | 36.36 | 45.2 | -0.4479 | 0.05654 | -0.3287 | -0.01245 | -0.4382 | 1.7242 | 35.5374 | 6.6713 | 33.2189 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.2009 |  | 2018-09-17
JA Solar | JAP6-72-305/3BB | 305 W Polycrystalline Module | UL 1703 | 305 | 275.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.79 | 45.35 | 8.31 | 36.71 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.65 | 35.49 | 6.65 | 33.29 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.192 |  | 2018-09-17
JA Solar | JAP6-72-305/4BB | 305 W Polycrystalline Module | UL 1703 | 305 | 282.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.81 | 45.37 | 8.27 | 36.88 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.6536 | 35.3167 | 6.6682 | 34.0237 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19148 |  | 2018-09-17
JA Solar | JAP6-72-305/4BB/RE | 305 W Multi Riecium Module | UL 1703 | 305 | 279.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.76 | 45.48 | 8.41 | 36.28 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.6728 | 34.7786 | 6.7774 | 33.1283 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19074 |  | 2018-09-17
JA Solar | JAP6-72-305/MP | 305 W Polycrystalline Module | UL 1703 | 305 | 269.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.77 | 45.74 | 8.19 | 37.24 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5799 | 36.2632 | 6.5747 | 33.3028 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18784 |  | 2018-09-17
JA Solar | JAP72S01-305/SC | 305 W, 72 Cell Poly c-Si PV Module | UL 1703 | 305 | 281.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.88 | 72 |  | N | 8.84 | 45.27 | 8.29 | 36.78 | 44.53 | -0.387 | 0.045 | -0.303 | 0.007 | -0.393 | 1.701 | 35.841 | 6.95 | 34.541 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM6(BK)-72-310/SI | 310 W Monocrystalline Module | UL 1703 | 310 | 275.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.78 | 46.46 | 8.18 | 37.9 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.6027 | 36.9604 | 6.5331 | 33.4603 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19108 |  | 2018-09-17
JA Solar | JAM60S01-310/PR | 310 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 310 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 | 1 | N | 9.91 | 40.3 | 9.44 | 32.84 | 44.12 | -0.375 | 0.036 | -0.271 | -0.006 | -0.371 | 1.835 | 32.147 | 7.397 | 30.675 | [6 empty] | 2019-03-01
JA Solar | JAM6-72-310/SI | 310 W Monocrystalline Module | UL 1703 | 310 | 279.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.85 | 45.57 | 8.37 | 37.04 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.67 | 35.14 | 6.69 | 33.13 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.1893 |  | 2018-09-17
JA Solar | JAP6(BK)-72-310/MP | 310 W Monocrystalline Module | UL 1703 | 310 | 274.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.8 | 45.81 | 8.25 | 37.58 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5915 | 36.5943 | 6.6228 | 33.6068 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18787 |  | 2018-09-17
JA Solar | JAP6-72-310 | 310 W Polycrystalline Module | UL 1703 | 310 | 281 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.78 | 45.61 | 8.41 | 36.49 | 45.2 | -0.4479 | 0.05654 | -0.3287 | -0.01245 | -0.4382 | 1.7325 | 35.6645 | 6.7032 | 33.3376 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19931 |  | 2018-09-17
JA Solar | JAP6-72-310/3BB | 310 W Polycrystalline Module | UL 1703 | 310 | 279.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.85 | 45.45 | 8.38 | 37 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.67 | 35.77 | 6.7 | 33.56 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.1927 |  | 2018-09-17
JA Solar | JAP6-72-310/4BB | 310 W Polycrystalline Module | UL 1703 | 310 | 287 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.89 | 45.66 | 8.38 | 36.99 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.6756 | 35.4221 | 6.7569 | 34.1252 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19146 |  | 2018-09-17
JA Solar | JAP6-72-310/4BB/RE | 310 W Multi Riecium Module | UL 1703 | 310 | 283.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.83 | 45.68 | 8.49 | 36.51 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.6887 | 34.9991 | 6.8419 | 33.3384 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19065 |  | 2018-09-17
JA Solar | JAP6-72-310/MP | 310 W Polycrystalline Module | UL 1703 | 310 | 274.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.8 | 45.81 | 8.25 | 37.58 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.5915 | 36.5943 | 6.6228 | 33.6068 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18787 |  | 2018-09-17
JA Solar | JAP72S01-310/SC | 310 W, 72 Cell Poly c-Si PV Module | UL 1703 | 310 | 286 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.88 | 72 |  | N | 8.92 | 45.56 | 8.4 | 36.89 | 44.53 | -0.387 | 0.045 | -0.303 | 0.007 | -0.393 | 1.701 | 35.841 | 6.95 | 34.541 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM6(BK)-72-315/SI | 315 W Monocrystalline Module | UL 1703 | 315 | 280.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.83 | 46.61 | 8.23 | 38.27 | 48 | -0.4645 | 0.0637 | -0.3397 | 0.0199 | -0.4831 | 1.6125 | 37.3212 | 6.573 | 33.7869 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19105 |  | 2018-09-17
JA Solar | JAM60S01-315/PR | 315 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 293.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 | 1 | N | 9.98 | 40.53 | 9.5 | 33.16 | 44.12 | -0.375 | 0.036 | -0.271 | -0.006 | -0.371 | 1.8467 | 32.4602 | 7.444 | 30.9739 | [6 empty] | 2019-03-01
JA Solar | JAM6-72-315/SI | 315 W Monocrystalline Module | UL 1703 | 315 | 284.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.92 | 45.73 | 8.48 | 37.15 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.7 | 35.24 | 6.77 | 33.23 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19018 |  | 2018-09-17
JA Solar | JAP6(BK)-72-315/MP | 315 W Monocrystalline Module | UL 1703 | 315 | 279 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.84 | 45.9 | 8.31 | 37.91 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.6031 | 36.9157 | 6.671 | 33.9019 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18787 |  | 2018-09-17
JA Solar | JAP6-72-315 | 315 W Polycrystalline Module | UL 1703 | 315 | 285.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.91 | 45.91 | 8.57 | 36.72 | 45.2 | -0.4479 | 0.05654 | -0.3287 | -0.01245 | -0.4382 | 1.7654 | 35.8892 | 6.8307 | 33.5478 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.20114 |  | 2018-09-17
JA Solar | JAP6-72-315/3BB | 315 W Polycrystalline Module | UL 1703 | 315 | 284.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.91 | 45.6 | 8.45 | 37.28 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.68 | 36.04 | 6.76 | 33.81 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19221 |  | 2018-09-17
JA Solar | JAP6-72-315/4BB | 315 W Polycrystalline Module | UL 1703 | 315 | 291.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.98 | 45.95 | 8.47 | 37.19 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.6936 | 35.6136 | 6.8294 | 34.3097 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19148 |  | 2018-09-17
JA Solar | JAP6-72-315/4BB/RE | 315 W Multi Riecium Module | UL 1703 | 315 | 288.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.89 | 45.98 | 8.58 | 36.73 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.7066 | 35.21 | 6.9144 | 33.5393 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19076 |  | 2018-09-17
JA Solar | JAP6-72-315/MP | 315 W Polycrystalline Module | UL 1703 | 315 | 279 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.84 | 45.9 | 8.31 | 37.91 | 48.5 | -0.472 | 0.0848 | -0.3444 | 0.0054 | -0.4791 | 1.6031 | 36.9157 | 6.671 | 33.9019 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18787 |  | 2018-09-17
JA Solar | JAP72S01-315/SC | 315 W, 72 Cell Poly c-Si PV Module | UL 1703 | 315 | 290.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.88 | 72 |  | N | 9.01 | 45.85 | 8.49 | 37.09 | 44.53 | -0.387 | 0.045 | -0.303 | 0.007 | -0.393 | 1.701 | 35.841 | 6.95 | 34.541 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM60S01-320/PR | 320 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 320 | 297.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 | 1 | N | 10.05 | 40.8 | 9.56 | 33.48 | 44.12 | -0.375 | 0.036 | -0.271 | -0.006 | -0.371 | 1.8583 | 32.7735 | 7.491 | 31.2728 | [6 empty] | 2019-03-01
JA Solar | JAM60S10-320/PR | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 320 | 299.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.16 | 40.27 | 9.52 | 33.62 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.8832 | 32.1966 | 7.615 | 31.2893 | [6 empty] | 2020-02-03
JA Solar | JAM60S17-320/MR | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 320 | 296.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.16 | 40.6 | 9.49 | 33.73 | 47.59 | -0.336 | 0.041 | -0.261 |  |  | 1.8395 | 32.7103 | 7.479 | 31.4741 | [6 empty] | 2021-01-04
JA Solar | JAM6-72-320/SI | 320 W Monocrystalline Module | UL 1703 | 320 | 289 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 8.99 | 45.86 | 8.57 | 37.35 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.71 | 35.43 | 6.85 | 33.41 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18933 |  | 2018-09-17
JA Solar | JAP6-72-320/3BB | 320 W Polycrystalline Module | UL 1703 | 320 | 289.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 8.97 | 45.75 | 8.52 | 37.56 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.69 | 36.31 | 6.82 | 34.07 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19176 |  | 2018-09-17
JA Solar | JAP6-72-320/4BB | 320 W Polycrystalline Module | UL 1703 | 320 | 296.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.06 | 46.22 | 8.56 | 37.38 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.7116 | 35.7955 | 6.902 | 34.485 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19146 |  | 2018-09-17
JA Solar | JAP6-72-320/4BB/RE | 320 W Multi Riecium Module | UL 1703 | 320 | 293.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.05 | 46.48 | 8.74 | 37.17 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.7384 | 35.6318 | 7.0434 | 33.941 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19357 |  | 2018-09-17
JA Solar | JAP72S01-320/SC | 320 W, 72 Cell Poly c-Si PV Module | UL 1703 | 320 | 295.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.88 | 72 |  | N | 9.09 | 46.12 | 8.58 | 37.28 | 44.53 | -0.387 | 0.045 | -0.303 | 0.007 | -0.393 | 1.701 | 35.841 | 6.95 | 34.541 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM60S10-325/PR | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 325 | 304.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.23 | 40.56 | 9.6 | 33.87 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.899 | 32.436 | 7.679 | 31.522 | [6 empty] | 2020-02-03
JA Solar | JAM60S17-325/MR | 325 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 325 | 301.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.23 | 40.87 | 9.57 | 33.97 | 47.59 | -0.336 | 0.041 | -0.261 |  |  | 1.855 | 32.943 | 7.542 | 31.698 | [6 empty] | 2021-01-04
JA Solar | JAM6-72-325/SI | 325 W Monocrystalline Module | UL 1703 | 325 | 293.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 9.06 | 46.02 | 8.67 | 37.49 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.73 | 35.56 | 6.93 | 33.54 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18929 |  | 2018-09-17
JA Solar | JAP6-72-325/3BB | 325 W Polycrystalline Module | UL 1703 | 325 | 293.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.03 | 45.9 | 8.59 | 37.84 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.71 | 36.58 | 6.87 | 34.32 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19247 |  | 2018-09-17
JA Solar | JAP6-72-325/4BB | 325 W Polycrystalline Module | UL 1703 | 325 | 301.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.14 | 46.48 | 8.67 | 37.49 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.7336 | 35.9009 | 6.9907 | 34.5865 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.1915 |  | 2018-09-17
JA Solar | JAP6-72-325/4BB/RE | 325 W Multi Riecium Module | UL 1703 | 325 | 297.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.21 | 46.98 | 8.6413 | 37.61 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.7188 | 36.0536 | 6.9638 | 34.3428 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19067 |  | 2018-09-17
JA Solar | JAP72S01-325/SC | 325 W, 72 Cell Poly c-Si PV Module | UL 1703 | 325 | 300.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.88 | 72 |  | N | 9.17 | 46.38 | 8.69 | 37.39 | 44.53 | -0.387 | 0.045 | -0.303 | 0.007 | -0.393 | 1.701 | 35.841 | 6.95 | 34.541 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAP72S09-325/SC | 325 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 325 | 298.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.28 | 45.56 | 8.81 | 36.9 | 45.32 | -0.389 | 0.05 | -0.299 | 1.7285 | 35.6132 | 1.7285 | 35.6132 | 6.9732 | 33.8317 | [6 empty] | 2020-01-13
JA Solar | JAM60S10-330/MR | 330 W, 120 half-cut cell monocrystalline module,white backsheet, 1500V max system Vdc | UL 61730 | 330 | 305.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.3 | 41.08 | 9.64 | 34.24 | 47.27 | -0.341 | 0.031 | -0.259 |  |  | 1.9034 | 32.6655 | 7.714 | 31.3888 | [6 empty] | 2021-01-04
JA Solar | JAM60S10-330/PR | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 330 | 309 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.3 | 40.84 | 9.67 | 34.13 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.9128 | 32.685 | 7.735 | 31.764 | [6 empty] | 2020-02-03
JA Solar | JAM60S17-330/MR | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 330 | 305.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.3 | 41.08 | 9.64 | 34.24 | 47.59 | -0.336 | 0.041 | -0.261 |  |  | 1.8686 | 33.2048 | 7.5972 | 31.9499 | [6 empty] | 2021-01-04
JA Solar | JAM6-72-330/SI | 330 W Monocrystalline Module | UL 1703 | 330 | 298.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 9.13 | 46.47 | 8.7 | 37.93 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.74 | 35.98 | 6.95 | 33.93 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18971 |  | 2018-09-17
JA Solar | JAP6-72-330/3BB | 330 W Polycrystalline Module | UL 1703 | 330 | 298.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.09 | 46.05 | 8.66 | 38.11 | 47.9 | -0.41 | 0.05 | -0.31 | -0.01 | -0.4 | 1.72 | 36.85 | 6.93 | 34.56 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19207 |  | 2018-09-17
JA Solar | JAP6-72-330/4BB | 330 W Polycrystalline Module | UL 1703 | 330 | 306 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.22 | 46.48 | 8.7766 | 37.6 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.7549 | 36.0062 | 7.0766 | 34.6879 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19148 |  | 2018-09-17
JA Solar | JAP6-72-330/4BB/RE | 330 W Multi Riecium Module | UL 1703 | 330 | 302.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.37 | 47.48 | 8.6728 | 38.05 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.7251 | 36.4754 | 6.9892 | 34.7446 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19067 |  | 2018-09-17
JA Solar | JAP72S01-330/SC | 330 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 330 | 304.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.884 | 72 | 1 | N | 9.28 | 46.4 | 8.77 | 37.65 | 45.11 | -0.385 | 0.044 | -0.296 | 0.004 | -0.388 | 1.739 | 36.305 | 6.988 | 34.78 | [6 empty] | 2017-10-16 | 2019-03-01
JA Solar | JAP72S09-330/SC | 330 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 330 | 303.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.35 | 45.83 | 8.88 | 37.18 | 45.32 | -0.389 | 0.05 | -0.299 | 1.7423 | 35.8834 | 1.7423 | 35.8834 | 7.0286 | 34.0885 | [6 empty] | 2020-01-13
JA Solar | JAM60S10-335/MR | 335 W, 120 half-cut cell monocrystalline module,white backsheet, 1500V max system Vdc | UL 61730 | 335 | 310.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.38 | 41.32 | 9.72 | 34.48 | 47.27 | -0.341 | 0.031 | -0.259 |  |  | 1.9192 | 32.8945 | 7.778 | 31.6088 | [6 empty] | 2021-01-04
JA Solar | JAM60S10-335/PR | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 335 | 313.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.38 | 41.12 | 9.75 | 34.36 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.9287 | 32.9053 | 7.799 | 31.978 | [6 empty] | 2020-02-03
JA Solar | JAM6-72-335/SI | 335 W Monocrystalline Module | UL 1703 | 335 | 303 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9384 | 72 | 1 | N | 9.21 | 46.76 | 8.76 | 38.24 | 47.5 | -0.42 | 0.04 | -0.31 | -0.01 | -0.41 | 1.75 | 36.28 | 7 | 34.21 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.18952 |  | 2018-09-17
JA Solar | JAM72S01-335/PR | 335 W, 72 Cell Mono PERC PV Module | UL 1703 | 335 | 309.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.884 | 72 |  | N | 9.38 | 46.68 | 8.83 | 37.96 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.814 | 37.64 | 7.35 | 35.906 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAP6-72-335/4BB/RE | 335 W Multi Riecium Module | UL 1703 | 335 | 307.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9384 | 72 | 1 | N | 9.53 | 47.98 | 8.72 | 38.49 | 46.25 | -0.385 | 0.048 | -0.301 | 0.005 | -0.389 | 1.7344 | 36.8972 | 7.0272 | 35.1464 | Rack | Flat Plate | 0.991 | 1.956 | 1 | 0.19103 |  | 2018-09-17
JA Solar | JAP72S01-335/SC | 335 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 335 | 309 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.884 | 72 | 1 | N | 9.35 | 46.7 | 8.87 | 37.83 | 45.11 | -0.385 | 0.044 | -0.296 | 0.004 | -0.388 | 1.7588 | 36.4786 | 7.0677 | 34.9463 | [6 empty] | 2019-03-01
JA Solar | JAP72S09-335/SC | 335 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 335 | 308.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.42 | 46.1 | 8.95 | 37.45 | 45.32 | -0.389 | 0.05 | -0.299 | 1.756 | 36.144 | 1.756 | 36.144 | 7.084 | 34.336 | [6 empty] | 2020-01-13
JA Solar | JAM60S10-340/MR | 340 W, 120 half-cut cell monocrystalline module,white backsheet, 1500V max system Vdc | UL 61730 | 340 | 315.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.46 | 41.55 | 9.79 | 34.73 | 47.27 | -0.341 | 0.031 | -0.259 |  |  | 1.933 | 33.133 | 7.834 | 31.838 | [6 empty] | 2021-01-04
JA Solar | JAM60S10-340/PR | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 340 | 318.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.46 | 41.36 | 9.82 | 34.63 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.9425 | 33.1638 | 7.855 | 32.2293 | [6 empty] | 2020-02-03
JA Solar | JAM72S01-340/PR | 340 W, 72 Cell Mono PERC PV Module | UL 1703 | 340 | 313.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.884 | 72 |  | N | 9.46 | 46.86 | 8.91 | 38.18 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.814 | 37.64 | 7.35 | 35.906 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAP72S01-340/SC | 340 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 340 | 313.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.884 | 72 | 1 | N | 9.42 | 47 | 8.97 | 38.02 | 45.11 | -0.385 | 0.044 | -0.296 | 0.004 | -0.388 | 1.7787 | 36.6618 | 7.1474 | 35.1218 | [6 empty] | 2019-03-01
JA Solar | JAP72S09-340/SC | 340 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 340 | 312.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.48 | 46.39 | 9.01 | 37.74 | 45.32 | -0.389 | 0.05 | -0.299 | 1.7678 | 36.4239 | 1.7678 | 36.4239 | 7.1315 | 34.6019 | [6 empty] | 2020-01-13
JA Solar | JAM60S10-345/MR | 345 W, 120 half-cut cell monocrystalline module,white backsheet, 1500V max system Vdc | UL 61730 | 345 | 320.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 2 | N | 10.54 | 41.76 | 9.86 | 34.99 | 47.27 | -0.341 | 0.031 | -0.259 |  |  | 1.9468 | 33.381 | 7.89 | 32.0763 | [6 empty] | 2021-01-04
JA Solar | JAM72S01-345/PR | 345 W, 72 Cell Mono PERC PV Module | UL 1703 | 345 | 318.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.884 | 72 |  | N | 9.54 | 47.05 | 8.99 | 38.39 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.814 | 37.64 | 7.35 | 35.906 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAP72S09-345/SC | 345 W, 72 cell polycrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 1703 | 345 | 317.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.938 | 72 | 1 | N | 9.55 | 46.68 | 9.07 | 38.04 | 45.32 | -0.389 | 0.05 | -0.299 | 1.7795 | 36.7134 | 1.7795 | 36.7134 | 7.179 | 34.8769 | [6 empty] | 2020-01-13
JA Solar | JAM72S01-350/PR | 350 W, 72 Cell Mono PERC PV Module | UL 1703 | 350 | 323.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.884 | 72 |  | N | 9.61 | 47.24 | 9.07 | 38.58 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.814 | 37.64 | 7.35 | 35.906 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM72S01-355/PR | 355 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 328.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.884 | 72 |  | N | 9.69 | 47.45 | 9.16 | 38.76 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.814 | 37.64 | 7.35 | 35.906 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM72S01-360/PR | 360 W, 72 Cell Mono PERC PV Module | UL 1703 | 360 | 332.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.884 | 72 |  | N | 9.78 | 47.66 | 9.24 | 38.96 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.814 | 37.64 | 7.35 | 35.906 | [6 empty] | 2017-10-16 | 2018-09-17
JA Solar | JAM72S01-365/PR | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 337.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.884 | 72 |  | N | 9.85 | 47.93 | 9.31 | 39.21 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.8437 | 38.077 | 7.4704 | 36.3229 | [6 empty] | 2018-09-17
JA Solar | JAM72D09-370/BP | 370 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 370 | 343.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.973 | 72 | 1 | N | 9.91 | 48.2 | 9.39 | 39.41 | 45.1 | -0.362 | 0.041 | -0.27 | 1.882 | 38.3496 | 1.882 | 38.3496 | 7.5826 | 36.6742 | [6 empty] | 2019-08-15
JA Solar | JAM72S01-370/PR | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 343.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.91 | 48.18 | 9.38 | 39.45 | 44.91 | -0.369 | 0.042 | -0.27 | 0.003 | -0.372 | 1.851 | 38.696 | 7.387 | 36.808 | [6 empty] | 2019-01-02
JA Solar | JAM72D09-375/BP | 375 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 375 | 348.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.973 | 72 | 1 | N | 9.97 | 48.51 | 9.44 | 39.73 | 45.1 | -0.362 | 0.041 | -0.27 | 1.892 | 38.661 | 1.892 | 38.661 | 7.623 | 36.972 | [6 empty] | 2019-08-15
JA Solar | JAM72S01-375/PR | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 348.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.98 | 48.45 | 9.44 | 39.75 | 44.91 | -0.369 | 0.042 | -0.27 | 0.003 | -0.372 | 1.8628 | 38.9903 | 7.4343 | 37.0879 | [6 empty] | 2019-01-02
JA Solar | JAM72S09-375/PR | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 349.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 10.06 | 48.47 | 9.55 | 39.27 | 44.35 | -0.361 | 0.038 | -0.268 | 1.8734 | 38.333 | 1.8734 | 38.333 | 7.5786 | 36.5044 | [6 empty] | 2019-09-03
JA Solar | JAM72D09-380/BP | 380 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 380 | 353 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.973 | 72 | 1 | N | 10.03 | 48.81 | 9.5 | 40.02 | 45.1 | -0.362 | 0.041 | -0.27 | 1.904 | 38.9432 | 1.904 | 38.9432 | 7.6715 | 37.2419 | [6 empty] | 2019-08-15
JA Solar | JAM72S01-380/PR | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 353.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 10.05 | 48.71 | 9.5 | 40.03 | 44.91 | -0.369 | 0.042 | -0.27 | 0.003 | -0.372 | 1.8747 | 39.2649 | 7.4815 | 37.3492 | [6 empty] | 2019-01-02
JA Solar | JAM72S09-380/PR | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system dc. | UL 1703 | 380 | 354.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 10.12 | 48.75 | 9.6 | 39.59 | 44.35 | -0.361 | 0.038 | -0.268 | 1.8832 | 38.6454 | 1.8832 | 38.6454 | 7.6183 | 36.8018 | [6 empty] | 2019-09-03
JA Solar | JAM54S31-385/MR | 385 W, 108 half-cut cell monocrystalline module, black backsheet | UL 61730 | 385 | 359.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 54 | 2 | N | 13.52 | 36.71 | 12.64 | 30.46 | 46.24 | -0.329 | 0.045 | -0.259 |  |  | 2.4863 | 29.8208 | 10.0157 | 28.7084 | [6 empty] | 2021-10-11
JA Solar | JAM72D09-385/BP | 385 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 385 | 357.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.973 | 72 | 1 | N | 10.09 | 49.11 | 9.55 | 40.33 | 45.1 | -0.362 | 0.041 | -0.27 | 1.914 | 39.2449 | 1.914 | 39.2449 | 7.7118 | 37.5303 | [6 empty] | 2019-08-15
JA Solar | JAM72S01-385/PR | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 357.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 10.11 | 48.98 | 9.56 | 40.29 | 44.91 | -0.369 | 0.042 | -0.27 | 0.003 | -0.372 | 1.8865 | 39.5199 | 7.5288 | 37.5917 | [6 empty] | 2019-01-02
JA Solar | JAM72S09-385/PR | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 359 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.17 | 49.04 | 9.65 | 39.9 | 44.35 | -0.361 | 0.038 | -0.268 | 1.893 | 38.948 | 1.893 | 38.948 | 7.658 | 37.09 | [6 empty] | 2019-09-03 | 2021-10-11
JA Solar | JAM72S10-385/PR | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 360.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.11 | 48.62 | 9.57 | 40.24 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.901 | 39.231 | 7.701 | 38.034 | [6 empty] | 2020-02-03
JA Solar | JAM54S31-390/MR | 390 W, 108 half-cut cell monocrystalline module, black backsheet | UL 61730 | 390 | 363.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 54 | 2 | N | 13.61 | 36.85 | 12.73 | 30.64 | 46.24 | -0.329 | 0.045 | -0.259 |  |  | 2.504 | 29.997 | 10.087 | 28.878 | [6 empty] | 2021-10-11
JA Solar | JAM72D09-390/BP | 390 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 390 | 362.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.973 | 72 | 1 | N | 10.14 | 49.42 | 9.6 | 40.63 | 45.1 | -0.362 | 0.041 | -0.27 | 1.9241 | 39.5368 | 1.9241 | 39.5368 | 7.7522 | 37.8095 | [6 empty] | 2019-08-15
JA Solar | JAM72D10-390/MB | 390 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 366.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.987 | 72 | 2 | N | 10.02 | 49.05 | 9.4 | 41.49 | 44.06 | -0.331 | 0.039 | -0.263 |  |  | 1.879 | 39.0808 | 7.6701 | 38.0332 | [6 empty] | 2020-10-21
JA Solar | JAM72S09-390/PR | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 363.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 10.22 | 49.35 | 9.7 | 40.21 | 44.35 | -0.361 | 0.038 | -0.268 | 1.9028 | 39.2506 | 1.9028 | 39.2506 | 7.6977 | 37.3782 | [6 empty] | 2019-09-03
JA Solar | JAM72S10-390/PR | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 365 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.16 | 48.91 | 9.62 | 40.55 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.9109 | 39.5332 | 7.7412 | 38.327 | [6 empty] | 2020-02-03
JA Solar | JAM54S31-395/MR | 395 W, 108 half-cut cell monocrystalline module, black backsheet | UL 61730 | 395 | 368.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 54 | 2 | N | 13.7 | 36.98 | 12.81 | 30.84 | 46.24 | -0.329 | 0.045 | -0.259 |  |  | 2.5197 | 30.1928 | 10.1504 | 29.0665 | [6 empty] | 2021-10-11
JA Solar | JAM72D10-395/MB | 395 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 370.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.987 | 72 | 2 | N | 10.08 | 49.31 | 9.46 | 41.76 | 44.06 | -0.331 | 0.039 | -0.263 |  |  | 1.891 | 39.3351 | 7.719 | 38.2807 | [6 empty] | 2020-10-21
JA Solar | JAM72S09-395/PR | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 368.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 10.27 | 49.64 | 9.76 | 40.48 | 44.35 | -0.361 | 0.038 | -0.268 | 1.9146 | 39.5142 | 1.9146 | 39.5142 | 7.7453 | 37.6292 | [6 empty] | 2019-09-03
JA Solar | JAM72S10-395/MR | 395 W, 144 half-cut cell monocrystalline module, white backsheet | UL 61730 | 395 | 369.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.27 | 49.3 | 9.62 | 41.06 | 44.08 | -0.349 | 0.039 | -0.267 |  |  | 1.8875 | 38.4592 | 7.6604 | 37.3212 | [6 empty] | 2020-12-21
JA Solar | JAM72S10-395/PR | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 369.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.21 | 49.21 | 9.67 | 40.85 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.9209 | 39.8257 | 7.7815 | 38.6106 | [6 empty] | 2020-02-03
JA Solar | JAM54S30-400/MR | 400 W, 108 half-cut cell monocrystalline module, white backsheet | UL 61730 | 400 | 374.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 54 | 2 | N | 13.79 | 37.07 | 12.9 | 30.01 | 45.02 | -0.333 | 0.039 | -0.259 |  |  | 2.5621 | 28.7523 | 10.3389 | 27.8061 | [6 empty] | 2021-10-11
JA Solar | JAM54S31-400/MR | 400 W, 108 half-cut cell monocrystalline module, black backsheet | UL 61730 | 400 | 373.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 54 | 2 | N | 13.79 | 37.07 | 12.9 | 31.01 | 46.24 | -0.329 | 0.045 | -0.259 |  |  | 2.5374 | 30.3592 | 10.2217 | 29.2267 | [6 empty] | 2021-10-11
JA Solar | JAM72D10-400/MB | 400 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 375.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.987 | 72 | 2 | N | 10.14 | 49.57 | 9.52 | 42.02 | 44.06 | -0.331 | 0.039 | -0.263 |  |  | 1.903 | 39.58 | 7.768 | 38.519 | [6 empty] | 2020-10-21
JA Solar | JAM72S09-400/PR | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 373.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.33 | 49.92 | 9.81 | 40.78 | 44.35 | -0.361 | 0.038 | -0.268 |  |  | 1.9244 | 39.807 | 7.785 | 37.908 | [6 empty] | 2021-10-11
JA Solar | JAM72S10-400/MR | 400 W, 144 half-cut cell monocrystalline module, white backsheet | UL 61730 | 400 | 374.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.33 | 49.58 | 9.68 | 41.33 | 44.08 | -0.349 | 0.039 | -0.267 |  |  | 1.8992 | 38.7121 | 7.7082 | 37.5666 | [6 empty] | 2020-12-21
JA Solar | JAM72S10-400/PR | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 374.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.26 | 49.5 | 9.72 | 41.17 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.9308 | 40.1377 | 7.8217 | 38.913 | [6 empty] | 2020-02-03
JA Solar | JAM54S30-405/MR | 405 W, 108 half-cut cell monocrystalline module, white backsheet | UL 61730 | 405 | 379.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 54 | 2 | N | 13.87 | 37.23 | 12.98 | 31.21 | 45.02 | -0.333 | 0.039 | -0.259 |  |  | 2.578 | 29.902 | 10.403 | 28.918 | [6 empty] | 2021-10-11
JA Solar | JAM54S31-405/MR | 405 W, 108 half-cut cell monocrystalline module, black backsheet | UL 61730 | 405 | 378.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 54 | 2 | N | 13.87 | 37.23 | 12.98 | 31.21 | 46.24 | -0.329 | 0.045 | -0.259 |  |  | 2.5532 | 30.555 | 10.2851 | 29.4152 | [6 empty] | 2021-10-11
JA Solar | JAM72D10-405/MB | 405 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 380.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.987 | 72 | 2 | N | 10.2 | 49.82 | 9.58 | 42.28 | 44.06 | -0.331 | 0.039 | -0.263 |  |  | 1.915 | 39.8249 | 7.817 | 38.7573 | [6 empty] | 2020-10-21
JA Solar | JAM72S10-405/MR | 405 W, 144 half-cut cell monocrystalline module, white backsheet | UL 61730 | 405 | 379.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.39 | 49.86 | 9.74 | 41.6 | 44.08 | -0.349 | 0.039 | -0.267 |  |  | 1.911 | 38.965 | 7.756 | 37.812 | [6 empty] | 2020-12-21
JA Solar | JAM72S10-405/PR | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 405 | 379.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.32 | 49.81 | 9.77 | 41.46 | 44.62 | -0.338 | 0.042 | -0.266 |  |  | 1.9407 | 40.4204 | 7.8619 | 39.1871 | [6 empty] | 2020-02-03
JA Solar | JAM54S30-410/MR | 410 W, 108 half-cut cell monocrystalline module, white backsheet | UL 61730 | 410 | 384.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 54 | 2 | N | 13.95 | 37.32 | 13.04 | 31.45 | 45.02 | -0.333 | 0.039 | -0.259 |  |  | 2.5899 | 30.1319 | 10.4511 | 29.1404 | [6 empty] | 2021-10-11
JA Solar | JAM72D10-410/MB | 410 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 385.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.987 | 72 | 2 | N | 10.26 | 50.08 | 9.64 | 42.54 | 44.06 | -0.331 | 0.039 | -0.263 |  |  | 1.927 | 40.0698 | 7.8659 | 38.9957 | [6 empty] | 2020-10-21
JA Solar | JAM72S10-410/MR | 410 W, 144 half-cut cell monocrystalline module, white backsheet | UL 61730 | 410 | 384.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.45 | 50.12 | 9.79 | 41.88 | 44.08 | -0.349 | 0.039 | -0.267 |  |  | 1.9208 | 39.2273 | 7.7958 | 38.0665 | [6 empty] | 2020-12-21
JA Solar | JAM72S10-415/MR | 415 W, 144 half-cut cell monocrystalline module, white backsheet | UL 61730 | 415 | 389 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.51 | 50.41 | 9.84 | 42.18 | 44.08 | -0.349 | 0.039 | -0.267 |  |  | 1.9306 | 39.5083 | 7.8356 | 38.3392 | [6 empty] | 2020-12-21
JA Solar | JAM72D20-435/MB | 435 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 408.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11.29 | 49.15 | 10.8 | 40.28 | 44.22 | -0.331 | 0.039 | -0.263 |  |  | 2.0972 | 39.2204 | 8.4766 | 38.3295 | [6 empty] | 2021-05-11
JA Solar | JAM72D20-440/MB | 440 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 412.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11.33 | 49.3 | 10.84 | 40.6 | 44.22 | -0.331 | 0.039 | -0.263 |  |  | 2.105 | 39.532 | 8.508 | 38.634 | [6 empty] | 2021-05-11
JA Solar | JAM72S20-440/MR | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 412.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.28 | 49.4 | 10.76 | 40.9 | 44.61 | -0.335 | 0.035 | -0.265 |  |  | 2.096 | 39.464 | 8.492 | 38.451 | [6 empty] | 2021-06-21
JA Solar | JAM72D20-445/MB | 445 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 417.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11.38 | 49.45 | 10.88 | 40.91 | 44.22 | -0.331 | 0.039 | -0.263 |  |  | 2.1128 | 39.8338 | 8.5394 | 38.929 | [6 empty] | 2021-05-11
JA Solar | JAM72S20-445/MR | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 417 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.32 | 49.56 | 10.8 | 41.21 | 44.61 | -0.335 | 0.035 | -0.265 |  |  | 2.1038 | 39.7631 | 8.5236 | 38.7424 | [6 empty] | 2021-06-21
JA Solar | JAM72D20-450/MB | 450 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 422.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11.42 | 49.61 | 10.92 | 41.21 | 44.22 | -0.331 | 0.039 | -0.263 |  |  | 2.1205 | 40.126 | 8.5708 | 39.2145 | [6 empty] | 2021-05-11
JA Solar | JAM72S20-450/MR | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 421.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.36 | 49.7 | 10.84 | 41.52 | 44.61 | -0.335 | 0.035 | -0.265 |  |  | 2.1116 | 40.0622 | 8.5551 | 39.0339 | [6 empty] | 2021-06-21
JA Solar | JAM72D20-455/MB | 455 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 427.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11.46 | 49.75 | 10.96 | 41.52 | 44.22 | -0.331 | 0.039 | -0.263 |  |  | 2.1283 | 40.4278 | 8.6022 | 39.5095 | [6 empty] | 2021-05-11
JA Solar | JAM72S20-455/MR | 455 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 426.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.41 | 49.85 | 10.88 | 41.82 | 44.61 | -0.335 | 0.035 | -0.265 |  |  | 2.1194 | 40.3517 | 8.5867 | 39.3159 | [6 empty] | 2021-06-21
JA Solar | JAM72D20-460/MB | 460 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 432.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11.5 | 49.91 | 11.01 | 41.79 | 44.22 | -0.331 | 0.039 | -0.263 |  |  | 2.138 | 40.6907 | 8.6414 | 39.7664 | [6 empty] | 2021-05-11
JA Solar | JAM72S20-460/MR | 460 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 460 | 431.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.45 | 50.01 | 10.92 | 42.13 | 44.61 | -0.335 | 0.035 | -0.265 |  |  | 2.1272 | 40.6508 | 8.6183 | 39.6074 | [6 empty] | 2021-06-21
JA Solar | JAM72D30-530/MB | 530 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 530 | 497.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.52 | 72 | 2 | N | 13.72 | 49.3 | 12.83 | 41.31 | 44.81 | -0.33 | 0.039 | -0.261 |  |  | 2.5063 | 40.3527 | 10.1805 | 39.0288 | [6 empty] | 2021-06-21
JA Solar | JAM72D30-535/MB | 535 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 502 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.52 | 72 | 2 | N | 13.79 | 49.45 | 12.9 | 41.47 | 44.81 | -0.33 | 0.039 | -0.261 |  |  | 2.52 | 40.509 | 10.236 | 39.18 | [6 empty] | 2021-05-11 | 2021-06-21
JA Solar | JAM72D30-540/MB | 540 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 506.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.52 | 72 | 2 | N | 13.86 | 49.6 | 12.97 | 41.64 | 44.81 | -0.33 | 0.039 | -0.261 |  |  | 2.5337 | 40.6751 | 10.2915 | 39.3406 | [6 empty] | 2021-05-11 | 2021-06-21
JA Solar | JAM72D30-545/MB | 545 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 545 | 511.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.52 | 72 | 2 | N | 13.93 | 49.75 | 13.04 | 41.8 | 44.81 | -0.33 | 0.039 | -0.261 |  |  | 2.5473 | 40.8314 | 10.3471 | 39.4918 | [6 empty] | 2021-05-11 | 2021-06-21
Japan Solar (Infini Co., Ltd.) | JS-250U-PI60 | 250 W Polycrystalline | UL 1703 | 250 | 223.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.7 | 37.8 | 8.3 | 30.2 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 28.33 | 6.97 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-255U-PI60 | 255 W Polycrystalline | UL 1703 | 255 | 228.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.8 | 37.9 | 8.42 | 30.4 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 28.33 | 6.97 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-260M-PI60 | 260 W Monocrystalline | UL 1703 | 260 | 234.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.37 | 39.1 | 8.44 | 30.92 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-260U-PI60 | 260 W Polycrystalline | UL 1703 | 260 | 233 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.9 | 38 | 8.54 | 30.6 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 28.33 | 6.97 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-265M-PI60 | 265 W Monocrystalline | UL 1703 | 265 | 239.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.43 | 39.2 | 8.55 | 31.08 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-265U-PI60 | 265 W Polycrystalline | UL 1703 | 265 | 237.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9 | 38.1 | 8.59 | 30.8 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 28.33 | 6.97 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JPS-270P-60-A | 270W Polycrystalline Module, white backsheet | UL 1703 | 270 | 250.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.635 | 60 |  | N | 9.18 | 38.17 | 8.67 | 31.13 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.675 | 30.244 | 6.758 | 29.349 | [6 empty] | 2017-11-01 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-270M-PI60 | 270 W Monocrystalline | UL 1703 | 270 | 243.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.48 | 39.3 | 8.66 | 31.24 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-270U-PI60 | 270 W Polycrystalline | UL 1703 | 270 | 242.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.09 | 38.39 | 8.61 | 31.44 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 28.33 | 6.97 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JPS-275P-60-A | 275W Polycrystalline Module, white backsheet | UL 1703 | 275 | 254.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.635 | 60 |  | N | 9.29 | 38.38 | 8.77 | 31.34 | 43.46 | -0.388 | 0.042 | -0.301 | 0.005 | -0.392 | 1.675 | 30.244 | 6.758 | 29.349 | [6 empty] | 2017-11-01 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-275M-PI60 | 275 W Monocrystalline | UL 1703 | 275 | 248.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.54 | 39.4 | 8.77 | 31.4 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-275U-PI60 | 275 W Polycrystalline | UL 1703 | 275 | 246.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.17 | 38.68 | 8.66 | 31.79 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 28.33 | 6.97 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-280M-PI60 | 280 W Monocrystalline | UL 1703 | 280 | 253.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.59 | 39.5 | 8.88 | 31.56 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-280U-PI60 | 280 W Polycrystalline | UL 1703 | 280 | 251.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.25 | 39.02 | 8.73 | 32.1 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 28.33 | 6.97 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-285M-60 | 285W Monocrystalline Module | UL 1703 | 285 | 257.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.33 | 39.1 | 9.05 | 31.5 | 45.8 | -0.4578 | 0.0352 | -0.2432 | -0.0129 | -0.3017 | 1.79 | 31.02 | 7.16 | 29.37 | [7 empty] | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-285M-PI60 | 285 W Monocrystalline | UL 1703 | 285 | 257.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.65 | 39.6 | 8.99 | 31.72 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-285U-PI60 | 285 W Polycrystalline | UL 1703 | 285 | 256.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.32 | 39.35 | 8.81 | 32.42 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 28.33 | 6.97 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-290M-60 | 290W Monocrystalline Module | UL 1703 | 290 | 262.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.44 | 39.3 | 9.15 | 31.7 | 45.8 | -0.4578 | 0.0352 | -0.2432 | -0.0129 | -0.3017 | 1.79 | 31.02 | 7.16 | 29.37 | [7 empty] | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-290M-PI60 | 290 W Monocrystalline | UL 1703 | 290 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.71 | 39.7 | 9.1 | 31.87 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-295M-60 | 295W Monocrystalline Module | UL 1703 | 295 | 267 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.56 | 39.5 | 9.25 | 31.9 | 45.8 | -0.4578 | 0.0352 | -0.2432 | -0.0129 | -0.3017 | 1.79 | 31.02 | 7.16 | 29.37 | [7 empty] | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-295M-PI60 | 295 W Monocrystalline | UL 1703 | 295 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.74 | 39.8 | 9.2 | 32.07 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-295U-PI72 | 295 W Polycrystalline | UL 1703 | 295 | 262.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 8.8 | 44.12 | 8.29 | 35.62 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JPS-300M-60-A | 300W Monocrystalline Module | UL 1703 | 300 | 277.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 |  | N | 9.75 | 39.85 | 9.3 | 32.26 | 45.1 | -0.377 | 0.036 | -0.281 | -0.003 | -0.374 | 1.825 | 31.497 | 7.338 | 30.16 | [6 empty] | 2018-02-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JPS-300M-60-A-BB | 300W 72 cell PERC Monocrystalline Module, black backsheet | UL 1703 | 300 | 275.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.585 | 60 |  | N | 9.75 | 39.85 | 9.3 | 32.26 | 46.46 | -0.387 | 0.037 | -0.283 | -0.003 | -0.385 | 1.8233 | 31.7842 | 7.3309 | 30.1834 | [6 empty] | 2018-04-16 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-300M-60 | 300W Monocrystalline Module | UL 1703 | 300 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.65 | 39.7 | 9.35 | 32.1 | 45.8 | -0.4578 | 0.0352 | -0.2432 | -0.0129 | -0.3017 | 1.79 | 31.02 | 7.16 | 29.37 | [7 empty] | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-300U-PI72 | 300 W Polycrystalline | UL 1703 | 300 | 266.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 8.85 | 44.49 | 8.33 | 36.04 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-305U-PI72 | 305 W Polycrystalline | UL 1703 | 305 | 271.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 8.9 | 44.87 | 8.37 | 36.45 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-310U-PI72 | 310 W Polycrystalline | UL 1703 | 310 | 276 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 8.95 | 45.24 | 8.41 | 36.87 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-315M-PI72 | 315 W Monocrystalline | UL 1703 | 315 | 283.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.32 | 46.8 | 8.55 | 36.99 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-315U-PI72 | 315 W Polycrystalline | UL 1703 | 315 | 280.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.01 | 45.59 | 8.45 | 37.28 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-320M-PI72 | 320 W Monocrystalline | UL 1703 | 320 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.37 | 46.92 | 8.64 | 37.18 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-320U-PI72 | 320 W Polycrystalline | UL 1703 | 320 | 285.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.03 | 46.04 | 8.49 | 37.7 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-325M-PI72 | 325 W Monocrystalline | UL 1703 | 325 | 293 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.43 | 47.04 | 8.72 | 37.36 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-325U-PI72 | 325 W Polycrystalline | UL 1703 | 325 | 289.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.11 | 46.34 | 8.53 | 38.11 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-330M-PI72 | 330 W Monocrystalline | UL 1703 | 330 | 297.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.48 | 47.16 | 8.81 | 37.55 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-330U-PI72 | 330 W Polycrystalline | UL 1703 | 330 | 294.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.15 | 46.74 | 8.57 | 38.53 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-335M-PI72 | 335 W Monocrystalline | UL 1703 | 335 | 302.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.54 | 47.28 | 8.89 | 37.73 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-335U-PI72 | 335 W Polycrystalline | UL 1703 | 335 | 299 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.2 | 47.12 | 8.61 | 38.94 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-340M-PI72 | 340 W Monocrystalline | UL 1703 | 340 | 307 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.59 | 47.4 | 8.98 | 37.91 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-340U-PI72 | 340 W Polycrystalline | UL 1703 | 340 | 303.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.25 | 47.49 | 8.65 | 39.36 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-345M-PI72 | 345 W Monocrystalline | UL 1703 | 345 | 311.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.65 | 47.52 | 9.06 | 38.1 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-350M-PI72 | 350 W Monocrystalline | UL 1703 | 350 | 316.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.71 | 47.64 | 9.15 | 38.26 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JPS-355M-72-A | 355W Monocrystalline Module | UL 1703 | 355 | 328.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.884 | 72 |  | N | 9.69 | 47.45 | 9.16 | 38.76 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.814 | 37.64 | 7.35 | 35.906 | [6 empty] | 2018-02-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-355M-PI72 | 355 W Monocrystalline | UL 1703 | 355 | 321 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.74 | 47.76 | 9.22 | 38.51 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JPS-360M-72-A | 360W Monocrystalline Module | UL 1703 | 360 | 332.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.884 | 72 |  | N | 9.78 | 47.66 | 9.24 | 38.96 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.814 | 37.64 | 7.35 | 35.906 | [6 empty] | 2018-02-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JS-360M-PI72 | 330 W Monocrystalline | UL 1703 | 360 | 325.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.82 | 47.88 | 9.32 | 38.63 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-15 | 2018-10-01
Japan Solar (Infini Co., Ltd.) | JPS-365M-72-A-1500 | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 337.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.85 | 47.93 | 9.31 | 39.21 | 45.85 | -0.369 | 0.051 | -0.283 | 0.01 | -0.378 | 1.8437 | 38.077 | 7.4704 | 36.3229 | [6 empty] | 2019-01-15
Japan Solar (Infini Co., Ltd.) | JPS-370M-72-A-1500 | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 343.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.91 | 48.18 | 9.38 | 39.45 | 44.91 | -0.369 | 0.042 | -0.27 | 0.003 | -0.372 | 1.851 | 38.696 | 7.387 | 36.808 | [6 empty] | 2019-01-15
Japan Solar (Infini Co., Ltd.) | JPS-375M-72-A-1500 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 348.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.98 | 48.45 | 9.44 | 39.75 | 44.91 | -0.369 | 0.042 | -0.27 | 0.003 | -0.372 | 1.8628 | 38.9903 | 7.4343 | 37.0879 | [6 empty] | 2019-01-15
Jetion Solar (China) | JT250PPg | 250 W Polycrystalline Module | UL 1703 | 250 | 223.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 20 | N | 8.86 | 37.6 | 8.28 | 30.3 | 47.7 | -0.4467 | 0.0398 | -0.3488 | -0.003 | -0.4466 | 1.6839 | 36.8818 | 6.6061 | 33.8388 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24842
Jetion Solar (China) | JT255PPg | 255 W Polycrystalline Module | UL 1703 | 255 | 228.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 20 | N | 8.92 | 37.8 | 8.36 | 30.6 | 47.7 | -0.4467 | 0.0398 | -0.3488 | -0.003 | -0.4466 | 1.7002 | 37.078 | 6.6699 | 34.0188 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24721
Jetion Solar (China) | JT260PPg | 260 W Polycrystalline Module | UL 1703 | 260 | 232.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 20 | N | 8.98 | 38 | 8.44 | 30.9 | 47.7 | -0.4467 | 0.0398 | -0.3488 | -0.003 | -0.4466 | 1.7164 | 37.2742 | 6.7337 | 34.1988 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24607
Jetion Solar (China) | JT265PPg | 265 W Polycrystalline Module | UL 1703 | 265 | 237.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 20 | N | 9.03 | 38.2 | 8.52 | 31.2 | 47.7 | -0.4467 | 0.0398 | -0.3488 | -0.003 | -0.4466 | 1.7327 | 37.4704 | 6.7975 | 34.3788 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.245
Jetion Solar (China) | JT270PPg | 270 W Polycrystalline Module | UL 1703 | 270 | 242 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 20 | N | 9.08 | 38.4 | 8.6 | 31.5 | 47.7 | -0.4467 | 0.0398 | -0.3488 | -0.003 | -0.4466 | 1.749 | 37.6666 | 6.8614 | 34.5588 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.24399
Jetion Solar (China) | JT300PAg | 300 W Polycrystalline Module | UL 1703 | 300 | 269.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 24 | N | 8.83 | 45.1 | 8.28 | 36.4 | 46.6 | -0.4476 | 0.0289 | -0.3454 | -0.0331 | -0.4368 | 1.6925 | 44.0526 | 6.6078 | 40.6695 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.24853
Jetion Solar (China) | JT305PAg | 305 W Polycrystalline Module | UL 1703 | 305 | 274.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 24 | N | 8.88 | 45.3 | 8.35 | 36.7 | 46.6 | -0.4476 | 0.0289 | -0.3454 | -0.0331 | -0.4368 | 1.7068 | 44.2479 | 6.6636 | 40.8498 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.24761
Jetion Solar (China) | JT310PAg | 310 W Polycrystalline Module | UL 1703 | 310 | 279 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 24 | N | 8.93 | 45.5 | 8.42 | 37 | 46.6 | -0.4476 | 0.0289 | -0.3454 | -0.0331 | -0.4368 | 1.7211 | 44.4433 | 6.7195 | 41.0302 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.24675
Jetion Solar (China) | JT315PAg | 315 W Polycrystalline Module | UL 1703 | 315 | 283.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 24 | N | 8.98 | 45.8 | 8.49 | 37.3 | 46.6 | -0.4476 | 0.0289 | -0.3454 | -0.0331 | -0.4368 | 1.7354 | 44.7363 | 6.7754 | 41.3007 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.24646
Jetion Solar (China) | JT320PAg | 320 W Polycrystalline Module | UL 1703 | 320 | 288.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 24 | N | 9.03 | 46.1 | 8.56 | 37.6 | 46.6 | -0.4476 | 0.0289 | -0.3454 | -0.0331 | -0.4368 | 1.7497 | 45.0293 | 6.8312 | 41.5712 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.24621
Jetion Solar (China) Co.,Ltd. | JT350SAh(1500) | 350 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 323.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.65 | 46.85 | 9.07 | 38.6 | 46.4 | -0.3577 | 0.0475 | -0.2734 |  |  | 1.8473 | 36.8273 | 7.3658 | 35.5622 | [6 empty] | 2020-02-11
Jetion Solar (China) Co.,Ltd. | JT355SAh(1500) | 355 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 328 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.7 | 46.9 | 9.15 | 38.8 | 46.4 | -0.3577 | 0.0475 | -0.2734 |  |  | 1.8636 | 37.0181 | 7.4308 | 35.7464 | [6 empty] | 2020-02-11
Jetion Solar (China) Co.,Ltd. | JT360SAh(1500) | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 332.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.75 | 47.2 | 9.14 | 39.4 | 46.4 | -0.3577 | 0.0475 | -0.2734 |  |  | 1.8616 | 37.5906 | 7.4227 | 36.2992 | [6 empty] | 2020-02-11
Jetion Solar (China) Co.,Ltd. | JT365SAh(1500) | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 337.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.81 | 47.5 | 9.2 | 39.7 | 46.4 | -0.3577 | 0.0475 | -0.2734 |  |  | 1.8738 | 37.8768 | 7.4714 | 36.5756 | [6 empty] | 2020-02-11
Jetion Solar (China) Co.,Ltd. | JT370SAh(1500) | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 342.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.87 | 47.8 | 9.25 | 40 | 46.4 | -0.3577 | 0.0475 | -0.2734 |  |  | 1.884 | 38.163 | 7.512 | 36.852 | [6 empty] | 2020-02-11
Jetion Solar (China) Co.,Ltd. | JT375SAh(1500) | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 346.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.93 | 48.1 | 9.33 | 40.2 | 46.4 | -0.3577 | 0.0475 | -0.2734 |  |  | 1.9003 | 38.3538 | 7.577 | 37.0363 | [6 empty] | 2020-02-11
Jetion Solar (China) Co.,Ltd. | JT380SAh(1500) | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 351.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.99 | 48.4 | 9.39 | 40.5 | 46.4 | -0.3577 | 0.0475 | -0.2734 |  |  | 1.9125 | 38.64 | 7.6257 | 37.3126 | [6 empty] | 2020-02-11
Jiangyin Hareon Power | HR-165W/24V | 165 W Monocrystalline Module | UL 1741 | 165 | 148 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.07 | 43 | 4.75 | 34.8 | 45.4 | -0.463 | 0.043 | -0.33 | -0.028 | -0.439 | 0.79816 | 35.2293 | 3.9421 | 31.2162 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17041
Jiangyin Hareon Power | HR-170W/24V | 170 W Monocrystalline Module | UL 1741 | 170 | 152.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.14 | 43.8 | 4.83 | 35.2 | 45.4 | -0.463 | 0.043 | -0.33 | -0.028 | -0.439 | 0.8116 | 35.6342 | 4.0085 | 31.575 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17012
Jiangyin Hareon Power | HR-240P-AC/Bb | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 216.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.48 | 37.25 | 8.09 | 29.67 | 45.8 | -0.453 | 0.057 | -0.349 | 0.012 | -0.463 | 1.61 | 29.08 | 6.57 | 26.9 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.19508
Jiangyin Hareon Power | HR-240P-AC/BbP | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 213.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6229 | 60 | 1 | N | 8.48 | 37.25 | 8.09 | 29.67 | 47.1 | -0.48 | 0.039 | -0.34 | 0.041 | -0.46 | 1.54 | 28.89 | 6.43 | 27.09 | Rack | Flat Plate | 0.992 | 1.636 | 1 | 0.18538
Jinko Solar Co., Ltd | JKM175M-72 | 175 W Monocrystalline Module | UL 1703 | 175 | 154.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.23 | 44.7 | 4.9 | 35.8 | 47.2 | -0.4849 | 0.0306 | -0.3552 | -0.0124 | -0.4714 | 1.0023 | 34.5249 | 3.9483 | 31.9748 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19773
Jinko Solar Co., Ltd | JKM180M-72 | 180 W Monocrystalline Module | UL 1703 | 180 | 159.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.29 | 44.8 | 5 | 36 | 47.2 | -0.4849 | 0.0306 | -0.3552 | -0.0124 | -0.4714 | 1.0227 | 34.7178 | 4.0289 | 32.1534 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19726
Jinko Solar Co., Ltd | JKM185M-72 | 185 W Monocrystalline Module | UL 1703 | 185 | 166.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.43 | 45 | 5.09 | 36.4 | 46.9 | -0.4384 | 0.0775 | -0.3931 | 0.0116 | -0.4488 | 1.1345 | 34.8213 | 4.027 | 33.7253 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.21354
Jinko Solar Co., Ltd | JKM190M-72 | 190 W Monocrystalline Module | UL 1703 | 190 | 170.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.56 | 45.2 | 5.19 | 36.6 | 46.9 | -0.4384 | 0.0775 | -0.3931 | 0.0116 | -0.4488 | 1.1568 | 35.0127 | 4.1061 | 33.9106 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.21317
Jinko Solar Co., Ltd | JKM195M-72 | 195 W Monocrystalline Module | UL 1703 | 195 | 175.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.67 | 45.4 | 5.3 | 36.8 | 46.9 | -0.4384 | 0.0775 | -0.3931 | 0.0116 | -0.4488 | 1.1813 | 35.204 | 4.1931 | 34.0959 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.21326
Jinko Solar Co., Ltd | JKM200M-60B | 200 W Monocrystalline Module | UL 1703 | 200 | 178.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 7.45 | 36.6 | 6.93 | 28.9 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.3992 | 28.2511 | 5.6782 | 25.9351 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19764
Jinko Solar Co., Ltd | JKM200M-72 | 200 W Monocrystalline Module | UL 1703 | 200 | 180 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.8 | 45.6 | 5.42 | 36.9 | 46.9 | -0.4384 | 0.0775 | -0.3931 | 0.0116 | -0.4488 | 1.208 | 35.2996 | 4.2881 | 34.1886 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.21322
Jinko Solar Co., Ltd | JKM200P-60B | 200 W Polycrystalline Module | UL 1703 | 200 | 178.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 7.61 | 36.3 | 6.95 | 28.8 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.4041 | 27.1366 | 5.637 | 26.3885 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19051
Jinko Solar Co., Ltd | JKM205M-60B | 205 W Monocrystalline Module | UL 1703 | 205 | 183.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 7.56 | 36.7 | 7.05 | 29.1 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.4234 | 28.4466 | 5.7765 | 26.1146 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19751
Jinko Solar Co., Ltd | JKM205M-72 | 205 W Monocrystalline Module | UL 1703 | 205 | 184.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.9 | 45.9 | 5.52 | 37.2 | 46.9 | -0.4384 | 0.0775 | -0.3931 | 0.0116 | -0.4488 | 1.2303 | 35.5866 | 4.3672 | 34.4665 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.21358
Jinko Solar Co., Ltd | JKM205P-60B | 205 W Polycrystalline Module | UL 1703 | 205 | 183.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 7.72 | 36.4 | 7.1 | 28.9 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.4344 | 27.2308 | 5.7587 | 26.4801 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19053
Jinko Solar Co., Ltd | JKM210M-60B | 210 W Monocrystalline Module | UL 1703 | 210 | 188 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 7.66 | 36.8 | 7.17 | 29.3 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.4476 | 28.6421 | 5.8748 | 26.2941 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19744
Jinko Solar Co., Ltd | JKM210P-60B | 210 W Polycrystalline Module | UL 1703 | 210 | 187.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 7.89 | 36.5 | 7.22 | 29.1 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.4586 | 27.4192 | 5.856 | 26.6634 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19045
Jinko Solar Co., Ltd | JKM215M-60B | 215 W Monocrystalline Module | UL 1703 | 215 | 192.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 7.8 | 36.8 | 7.29 | 29.8 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.4718 | 29.1309 | 5.9731 | 26.7428 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19942
Jinko Solar Co., Ltd | JKM215P-60B | 215 W Polycrystalline Module | UL 1703 | 215 | 192.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 7.97 | 36.7 | 7.37 | 29.2 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.4889 | 27.5135 | 5.9777 | 26.755 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19054
Jinko Solar Co., Ltd | JKM220M-60 | 220 W Monocrystalline Module | UL 1703 | 220 | 184.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 7.97 | 36.9 | 7.46 | 29.5 | 47.6 | -0.6618 | 0.0067 | -0.4539 | -0.0209 | -0.6415 | 1.5274 | 29.3997 | 5.9419 | 26.0884 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20411
Jinko Solar Co., Ltd | JKM220M-60B | 220 W Monocrystalline Module | UL 1703 | 220 | 197.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 7.92 | 37 | 7.41 | 29.7 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.4961 | 29.0332 | 6.0715 | 26.6531 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19743
Jinko Solar Co., Ltd | JKM220P-60 | 220 W Polycrystalline Module | UL 1703 | 220 | 187 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.1 | 36.6 | 7.53 | 29.2 | 48 | -0.6053 | 0.0595 | -0.441 | 0.0218 | -0.629 | 1.5156 | 28.7051 | 4.9976 | 26.4285 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19775
Jinko Solar Co., Ltd | JKM220P-60B | 220 W Polycrystalline Module | UL 1703 | 220 | 197 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.07 | 36.8 | 7.49 | 29.4 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.5132 | 27.7019 | 6.075 | 26.9383 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19054
Jinko Solar Co., Ltd | JKM225M-60 | 225 W Monocrystalline Module | UL 1703 | 225 | 202.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.08 | 37 | 7.57 | 29.7 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.5155 | 29.7894 | 6.197 | 26.582 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20065
Jinko Solar Co., Ltd | JKM225M-60B | 225 W Monocrystalline Module | UL 1703 | 225 | 201.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.02 | 37.2 | 7.53 | 29.9 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.4951 | 29.3422 | 6.0695 | 26.7128 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19497
Jinko Solar Co., Ltd | JKM225P-60 | 225 W Polycrystalline Module | UL 1703 | 225 | 200.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.25 | 36.7 | 7.65 | 29.4 | 46.6 | -0.4634 | 0.0738 | -0.3525 | 0.0263 | -0.4011 | 1.5397 | 28.9017 | 5.0773 | 26.6095 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19778
Jinko Solar Co., Ltd | JKM225P-60B | 225 W Polycrystalline Module | UL 1703 | 225 | 201.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.2 | 36.9 | 7.61 | 29.6 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.5046 | 28.6791 | 6.1555 | 26.4933 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19179
Jinko Solar Co., Ltd | JKM230M-60 | 230 W Monocrystalline Module | UL 1703 | 230 | 206.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.2 | 37.1 | 7.69 | 29.9 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.5396 | 29.99 | 6.2953 | 26.761 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20074
Jinko Solar Co., Ltd | JKM230M-60B | 230 W Monocrystalline Module | UL 1703 | 230 | 206.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.16 | 37.4 | 7.67 | 30 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.5229 | 29.4404 | 6.1823 | 26.8021 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19493
Jinko Solar Co., Ltd | JKM230P-60 | 230 W Polycrystalline Module | UL 1703 | 230 | 205.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.35 | 36.8 | 7.78 | 29.6 | 46.6 | -0.4634 | 0.0738 | -0.3525 | 0.0263 | -0.4011 | 1.5659 | 29.0983 | 5.1635 | 26.7905 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19811
Jinko Solar Co., Ltd | JKM230P-60B | 230 W Polycrystalline Module | UL 1703 | 230 | 206.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.32 | 37 | 7.72 | 29.8 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.5264 | 28.8729 | 6.2444 | 26.6723 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19162
Jinko Solar Co., Ltd | JKM235M-60 | 235 W Monocrystalline Module | UL 1703 | 235 | 211.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.31 | 37.2 | 7.83 | 30 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.5676 | 30.0903 | 6.4099 | 26.8506 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20072
Jinko Solar Co., Ltd | JKM235M-60B | 235 W Monocrystalline Module | UL 1703 | 235 | 211 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.28 | 37.5 | 7.79 | 30.2 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.5467 | 29.6366 | 6.2791 | 26.9808 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19506
Jinko Solar Co., Ltd | JKM235P-60 | 235 W Polycrystalline Module | UL 1703 | 235 | 210 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.47 | 36.9 | 7.89 | 29.8 | 46.6 | -0.4634 | 0.0738 | -0.3525 | 0.0263 | -0.4011 | 1.5881 | 29.2949 | 5.2365 | 26.9715 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19797
Jinko Solar Co., Ltd | JKM235P-60B | 235 W Polycrystalline Module | UL 1703 | 235 | 210.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.43 | 37.2 | 7.84 | 30 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.5501 | 29.0667 | 6.3415 | 26.8513 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19173
Jinko Solar Co., Ltd | JKM240M-60 | 240 W Monocrystalline Module | UL 1703 | 240 | 216.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.45 | 37.3 | 7.95 | 30.2 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.5916 | 30.2909 | 6.5081 | 27.0296 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20088
Jinko Solar Co., Ltd | JKM240M-60B | 240 W Monocrystalline Module | UL 1703 | 240 | 215.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.38 | 37.7 | 7.87 | 30.5 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.5626 | 29.931 | 6.3435 | 27.2488 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19487
Jinko Solar Co., Ltd | JKM240P-60 | 240 W Polycrystalline Module | UL 1703 | 240 | 214.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.56 | 37.2 | 8.01 | 30 | 46.6 | -0.4634 | 0.0738 | -0.3525 | 0.0263 | -0.4011 | 1.6122 | 29.4915 | 5.3162 | 27.1525 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19811
Jinko Solar Co., Ltd | JKM240P-60B | 240 W Polycrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.54 | 37.4 | 7.95 | 30.2 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.5719 | 29.2604 | 6.4305 | 27.0303 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19164
Jinko Solar Co., Ltd | JKM240PP-60B | 240 W Polycrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.54 | 37.4 | 7.95 | 30.2 | 46.9 | -0.4423 | 0.07 | -0.3462 | 0.0519 | -0.419 | 1.5719 | 29.2604 | 6.4305 | 27.0303 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19164
Jinko Solar Co., Ltd | JKM245M-60 | 245 W Monocrystalline Module | UL 1703 | 245 | 220.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.58 | 37.4 | 8.06 | 30.4 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.6136 | 30.4915 | 6.5982 | 27.2086 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20082
Jinko Solar Co., Ltd | JKM245M-60B | 245 W Monocrystalline Module | UL 1703 | 245 | 220.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.47 | 37.9 | 7.96 | 30.8 | 46.8 | -0.4414 | 0.0804 | -0.3769 | 0.014 | -0.4256 | 1.5804 | 30.2254 | 6.4161 | 27.5169 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19498
Jinko Solar Co., Ltd | JKM245P-60 | 245 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 245 | 224.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.69 | 37.4 | 8.12 | 30.2 | 43 | -0.4324 | 0.05782 | -0.31781 | 0.00119 | -0.44783 | 1.6266 | 30.0974 | 6.9511 | 27.9835 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19983
Jinko Solar Co., Ltd | JKM245P-60B | 245 W Polycrystalline Module | UL 1703 | 245 | 221.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.76 | 37.5 | 8.14 | 30.1 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.61 | 28.91 | 6.51 | 27.62 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18998
Jinko Solar Co., Ltd | JKM245PP-60(Plus) | 245 W Polycrystalline Module | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.76 | 37.5 | 8.14 | 30.1 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.61 | 28.92 | 6.53 | 28.33 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19005
Jinko Solar Co., Ltd | JKM245PP-60B | 245 W Polycrystalline Module | UL 1703 | 245 | 221.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.76 | 37.5 | 8.14 | 30.1 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.61 | 28.91 | 6.51 | 27.62 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18998
Jinko Solar Co., Ltd | JKMS245P-60 | 245 W Polycrystalline Module with MX,SE or TG smart junction box | UL 1703 | 245 | 221 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.637 | 60 |  | N | 9.23 | 35.6 | 8.57 | 28.6 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.67 | 28.12 | 6.9 | 25.84 | [6 empty] | 2015-10-01 | 2018-02-01
Jinko Solar Co., Ltd | JKMS245PP-60 | 245 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 245 | 224.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.69 | 37.4 | 8.12 | 30.2 | 43 | -0.4324 | 0.05782 | -0.31781 | 0.00119 | -0.44783 | 1.6266 | 30.0974 | 6.9511 | 27.9835 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19983
Jinko Solar Co., Ltd | JKM250M-60 | 250 W Monocrystalline Module | UL 1703 | 250 | 228.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.7 | 37.6 | 8.17 | 30.6 | 43.2 | -0.44222 | 0.04816 | -0.33017 | 0.00619 | -0.438 | 1.6382 | 29.8622 | 6.3804 | 27.5052 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19568
Jinko Solar Co., Ltd | JKM250M-72B | 250 W Monocrystalline Module | UL 1703 | 250 | 223.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 7.88 | 43.9 | 7.02 | 35.6 | 47.3 | -0.4405 | 0.0732 | -0.3513 | 0.0163 | -0.3795 | 1.3791 | 35.2202 | 5.6654 | 32.4896 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19429
Jinko Solar Co., Ltd | JKM250P-60 | 250 W Polycrystalline Module | UL 1703 | 250 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6537 | 36.4761 | 6.6165 | 34.5583 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24128
Jinko Solar Co., Ltd | JKM250P-60B | 250 W Polycrystalline Module | UL 1703 | 250 | 226.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.62 | 29.3 | 6.56 | 27.99 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18986
Jinko Solar Co., Ltd | JKM250P-60-J4 | 250 W Polycrystalline Module | UL 1703 | 250 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6537 | 36.4761 | 6.6165 | 34.5583 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24128
Jinko Solar Co., Ltd | JKM250P-60-V | 250 W Polycrystalline Module | UL 1703 | 250 | 228.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.6381 | 36.7908 | 6.629 | 35.0223 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24107
Jinko Solar Co., Ltd | JKM250P-72 | 250 W Polycrystalline Module | UL 1703 | 250 | 222.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.11 | 43.5 | 7.2 | 34.7 | 47.1 | -0.4575 | 0.0564 | -0.2743 | 0.0175 | -0.2338 | 1.4298 | 33.5052 | 5.7219 | 32.4308 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19162
Jinko Solar Co., Ltd | JKM250P-72B | 250 W Polycrystalline Module | UL 1703 | 250 | 223.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.09 | 43.7 | 7.18 | 34.8 | 47.2 | -0.4422 | 0.0743 | -0.3672 | 0.0163 | -0.4179 | 1.4387 | 33.3735 | 5.9686 | 31.4205 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19206
Jinko Solar Co., Ltd | JKM250PP-60 | 250 W Polycrystalline Module | UL 1703 | 250 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6537 | 36.4761 | 6.6165 | 34.5583 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24128
Jinko Solar Co., Ltd | JKM250PP-60(Plus) | 250 W Polycrystalline Module | UL 1703 | 250 | 226 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.62 | 29.3 | 6.58 | 28.71 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18986
Jinko Solar Co., Ltd | JKM250PP-60B | 250 W Polycrystalline Module | UL 1703 | 250 | 226.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.62 | 29.3 | 6.56 | 27.99 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18986
Jinko Solar Co., Ltd | JKM250PP-60-J4 | 250 W Polycrystalline Module | UL 1703 | 250 | 228.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6537 | 36.4761 | 6.6165 | 34.5583 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24128
Jinko Solar Co., Ltd | JKM250PP-60-V | 250 W Polycrystalline Module | UL 1703 | 250 | 228.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.6381 | 36.7908 | 6.629 | 35.0223 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24107
Jinko Solar Co., Ltd | JKMS250P-60 | 250 W Polycrystalline Module with MX,SE or TG smart junction box | UL 1703 | 250 | 225.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.637 | 60 |  | N | 9.32 | 35.8 | 8.63 | 29 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.68 | 28.52 | 6.95 | 26.2 | [6 empty] | 2015-10-01 | 2018-02-01
Jinko Solar Co., Ltd | JKMS250PP-60 | 250 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 250 | 227.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5811 | 60 | 1 | N | 8.85 | 37.7 | 8.2 | 30.5 | 45.1 | -0.4249 | 0.0635 | -0.325 | 0.0161 | -0.437 | 1.52 | 30.11 | 6.56 | 27.66 | Rack | Flat Plate | 0.97 | 1.63 | 1 | 0.18307
Jinko Solar Co., Ltd | JKM255M-60 | 255 W Monocrystalline Module | UL 1703 | 255 | 230.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.621 | 60 | 1 | N | 8.96 | 37.8 | 8.28 | 30.8 | 46.5 | -0.432 | 0.0748 | -0.4095 | 0.0083 | -0.439 | 1.6243 | 31.0457 | 6.6055 | 28.2615 | Rack | Flat Plate | 0.986 | 1.644 | 1 | 0.19776
Jinko Solar Co., Ltd | JKM255M-72B | 255 W Monocrystalline Module | UL 1703 | 255 | 227.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 7.94 | 44.4 | 7.14 | 35.7 | 47.3 | -0.4405 | 0.0732 | -0.3513 | 0.0163 | -0.3795 | 1.4027 | 35.3191 | 5.7622 | 32.5809 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19428
Jinko Solar Co., Ltd | JKM255M-96 | 255 W Monocrystalline Module | UL 1703 | 255 | 229.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7042 | 96 | 1 | N | 5.66 | 60.5 | 5.1 | 50 | 46.6 | -0.4326 | 0.0853 | -0.3853 | 0.0111 | -0.4346 | 1.0293 | 49.4379 | 4.2084 | 44.8078 | Rack | Flat Plate | 1.082 | 1.575 | 1 | 0.19956
Jinko Solar Co., Ltd | JKM255P-60 | 255 W Polycrystalline Module | UL 1703 | 255 | 233.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6698 | 36.7664 | 6.6811 | 34.8333 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24075
Jinko Solar Co., Ltd | JKM255P-60B | 255 W Polycrystalline Module | UL 1703 | 255 | 230.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.64 | 29.58 | 6.62 | 28.27 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19024
Jinko Solar Co., Ltd | JKM255P-60-J4 | 255 W Polycrystalline Module | UL 1703 | 255 | 233.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6698 | 36.7664 | 6.6811 | 34.8333 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24075
Jinko Solar Co., Ltd | JKM255P-60-V | 255 W Polycrystalline Module | UL 1703 | 255 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.6541 | 37.0836 | 6.6937 | 35.301 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24054
Jinko Solar Co., Ltd | JKM255P-72 | 255 W Polycrystalline Module | UL 1703 | 255 | 227.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.2 | 43.7 | 7.31 | 34.9 | 47.1 | -0.4575 | 0.0564 | -0.2743 | 0.0175 | -0.2338 | 1.4516 | 33.6983 | 5.8093 | 32.6178 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19183
Jinko Solar Co., Ltd | JKM255P-72B | 255 W Polycrystalline Module | UL 1703 | 255 | 227.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.12 | 43.9 | 7.29 | 35 | 47.2 | -0.4422 | 0.0743 | -0.3672 | 0.0163 | -0.4179 | 1.4607 | 33.5653 | 6.0601 | 31.6011 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19227
Jinko Solar Co., Ltd | JKM255PP-60 | 255 W Polycrystalline Module | UL 1703 | 255 | 233.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6698 | 36.7664 | 6.6811 | 34.8333 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24075
Jinko Solar Co., Ltd | JKM255PP-60(Plus) | 255 W Polycrystalline Module | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.64 | 29.59 | 6.64 | 28.99 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.1903
Jinko Solar Co., Ltd | JKM255PP-60B | 255 W Polycrystalline Module | UL 1703 | 255 | 230.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.64 | 29.58 | 6.62 | 28.27 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19024
Jinko Solar Co., Ltd | JKM255PP-60-J4 | 255 W Polycrystalline Module | UL 1703 | 255 | 233.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6698 | 36.7664 | 6.6811 | 34.8333 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24075
Jinko Solar Co., Ltd | JKM255PP-60-V | 255 W Polycrystalline Module | UL 1703 | 255 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.6541 | 37.0836 | 6.6937 | 35.301 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.24054
Jinko Solar Co., Ltd | JKMS255P-60 | 255 W Polycrystalline Module with MX,SE or TG smart junction box | UL 1703 | 255 | 230.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.637 | 60 |  | N | 9.39 | 36.1 | 8.72 | 29.3 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.7 | 28.81 | 7.02 | 26.47 | [6 empty] | 2015-10-01 | 2018-02-01
Jinko Solar Co., Ltd | JKMS255PP-60 | 255 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 255 | 232.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5811 | 60 | 1 | N | 8.92 | 38 | 8.28 | 30.8 | 45.1 | -0.4249 | 0.0635 | -0.325 | 0.0161 | -0.437 | 1.53 | 30.4 | 6.62 | 27.93 | Rack | Flat Plate | 0.97 | 1.63 | 1 | 0.1824
Jinko Solar Co., Ltd | JKM260M-60B | 260 W Monocrystalline Module | UL 1703 | 260 | 234.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 9.1 | 38 | 8.42 | 30.9 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.64 | 30.31 | 6.71 | 28.43 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19119
Jinko Solar Co., Ltd | JKM260M-72B | 260 W Monocrystalline Module | UL 1703 | 260 | 232.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.01 | 44.8 | 7.24 | 35.9 | 47.3 | -0.4405 | 0.0732 | -0.3513 | 0.0163 | -0.3795 | 1.4224 | 35.517 | 5.8429 | 32.7634 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1943
Jinko Solar Co., Ltd | JKM260M-96 | 260 W Monocrystalline Module | UL 1703 | 260 | 234.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7042 | 96 | 1 | N | 5.72 | 61.1 | 5.15 | 50.5 | 46.6 | -0.4326 | 0.0853 | -0.3853 | 0.0111 | -0.4346 | 1.0394 | 49.9322 | 4.2497 | 45.2559 | Rack | Flat Plate | 1.082 | 1.575 | 1 | 0.19961
Jinko Solar Co., Ltd | JKM260P-60 | 260 W Polycrystalline Module | UL 1703 | 260 | 238.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6879 | 36.8632 | 6.7537 | 34.925 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23932
Jinko Solar Co., Ltd | JKM260P-60B | 260 W Polycrystalline Module | UL 1703 | 260 | 235.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.66 | 29.87 | 6.69 | 28.54 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19071
Jinko Solar Co., Ltd | JKM260P-60-J4 | 260 W Polycrystalline Module | UL 1703 | 260 | 238.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6879 | 36.8632 | 6.7537 | 34.925 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23932
Jinko Solar Co., Ltd | JKM260P-60-V | 260 W Polycrystalline Module | UL 1703 | 260 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.672 | 37.1812 | 6.7664 | 35.3939 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23911
Jinko Solar Co., Ltd | JKM260P-72 | 260 W Polycrystalline Module | UL 1703 | 260 | 231.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.3 | 43.9 | 7.43 | 35 | 47.1 | -0.4575 | 0.0564 | -0.2743 | 0.0175 | -0.2338 | 1.4754 | 33.7948 | 5.9046 | 32.7112 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19178
Jinko Solar Co., Ltd | JKM260P-72B | 260 W Polycrystalline Module | UL 1703 | 260 | 232.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.2 | 44 | 7.39 | 35.2 | 47.2 | -0.4422 | 0.0743 | -0.3672 | 0.0163 | -0.4179 | 1.4808 | 33.7571 | 6.1432 | 31.7817 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19226
Jinko Solar Co., Ltd | JKM260PP-60 | 260 W Polycrystalline Module | UL 1703 | 260 | 238.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6879 | 36.8632 | 6.7537 | 34.925 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23932
Jinko Solar Co., Ltd | JKM260PP-60(Plus) | 260 W Polycrystalline Module | UL 1703 | 260 | 235.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.66 | 29.88 | 6.71 | 29.27 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19077
Jinko Solar Co., Ltd | JKM260PP-60B | 260 W Polycrystalline Module | UL 1703 | 260 | 235.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.66 | 29.87 | 6.69 | 28.54 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19071
Jinko Solar Co., Ltd | JKM260PP-60-J4 | 260 W Polycrystalline Module | UL 1703 | 260 | 238.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6879 | 36.8632 | 6.7537 | 34.925 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23932
Jinko Solar Co., Ltd | JKM260PP-60-V | 260 W Polycrystalline Module | UL 1703 | 260 | 237.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.672 | 37.1812 | 6.7664 | 35.3939 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23911
Jinko Solar Co., Ltd | JKMS260M-60 | 260 W Monocrystalline Module with MX, SE or TG smart junction box | UL 1703 | 260 | 235.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 9.1 | 38 | 8.42 | 30.9 | 45.6 | -0.441 | 0.059 | -0.342 | 0.007 | -0.458 | 1.59 | 30.41 | 6.78 | 27.98 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18597
Jinko Solar Co., Ltd | JKMS260M-60B-EP | 260W Monocrystalline module，DC module' model number is JKM260M-60B，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 260 | 236.6 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.1 | 37.9 | 8.42 | 30.9 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.658 | 32.132 | 6.827 | 30.16 | [6 empty] | 2017-11-01
Jinko Solar Co., Ltd | JKMS260M-60B-MX | 260 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 260 | 236.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 8.86 | 29.4 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.5661 | 31.075 | 6.4485 | 29.1679 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS260P-60 | 260 W Polycrystalline Module with MX,SE or TG smart junction box | UL 1703 | 260 | 234.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.637 | 60 |  | N | 9.45 | 36.2 | 8.81 | 29.5 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.71 | 29.01 | 7.1 | 26.65 | [6 empty] | 2015-10-01 | 2018-02-01
Jinko Solar Co., Ltd | JKMS260PP-60 | 260 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 260 | 237.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5811 | 60 | 1 | N | 8.98 | 38.1 | 8.37 | 31.1 | 45.1 | -0.4249 | 0.0635 | -0.325 | 0.0161 | -0.437 | 1.55 | 30.7 | 6.69 | 28.2 | Rack | Flat Plate | 0.97 | 1.63 | 1 | 0.18302
Jinko Solar Co., Ltd | JKM265M-60B | 265 W Monocrystalline Module | UL 1703 | 265 | 239.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 9.19 | 38.2 | 8.5 | 31.2 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.66 | 30.6 | 6.77 | 28.71 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19168
Jinko Solar Co., Ltd | JKM265M-72B | 265 W Monocrystalline Module | UL 1703 | 265 | 237 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.06 | 45.1 | 7.36 | 36 | 47.3 | -0.4405 | 0.0732 | -0.3513 | 0.0163 | -0.3795 | 1.4459 | 35.6159 | 5.9398 | 32.8547 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19433
Jinko Solar Co., Ltd | JKM265M-96 | 265 W Monocrystalline Module | UL 1703 | 265 | 239.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7042 | 96 | 1 | N | 5.77 | 61.7 | 5.2 | 51 | 46.6 | -0.4326 | 0.0853 | -0.3853 | 0.0111 | -0.4346 | 1.0495 | 50.4266 | 4.2909 | 45.704 | Rack | Flat Plate | 1.082 | 1.575 | 1 | 0.19971
Jinko Solar Co., Ltd | JKM265P-60 | 265 W Polycrystalline Module | UL 1703 | 265 | 242.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7021 | 37.3469 | 6.8102 | 35.3833 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23987
Jinko Solar Co., Ltd | JKM265P-60B | 265 W Polycrystalline Module | UL 1703 | 265 | 240.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.67 | 30.16 | 6.75 | 28.82 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19006
Jinko Solar Co., Ltd | JKM265P-60-J4 | 265 W Polycrystalline Module | UL 1703 | 265 | 242.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7021 | 37.3469 | 6.8102 | 35.3833 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23987
Jinko Solar Co., Ltd | JKM265P-60-V | 265 W Polycrystalline Module | UL 1703 | 265 | 242.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.686 | 37.6691 | 6.823 | 35.8583 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23966
Jinko Solar Co., Ltd | JKM265P-72 | 265 W Polycrystalline Module | UL 1703 | 265 | 236.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.42 | 44.1 | 7.55 | 35.1 | 47.1 | -0.4575 | 0.0564 | -0.2743 | 0.0175 | -0.2338 | 1.4993 | 33.8914 | 6 | 32.8047 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19174
Jinko Solar Co., Ltd | JKM265P-72B | 265 W Polycrystalline Module | UL 1703 | 265 | 237.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.26 | 44.2 | 7.51 | 35.3 | 47.2 | -0.4422 | 0.0743 | -0.3672 | 0.0163 | -0.4179 | 1.5048 | 33.853 | 6.243 | 31.872 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19224
Jinko Solar Co., Ltd | JKM265PP-60 | 265 W Polycrystalline Module | UL 1703 | 265 | 242.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7021 | 37.3469 | 6.8102 | 35.3833 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23987
Jinko Solar Co., Ltd | JKM265PP-60(Plus) | 265 W Polycrystalline Module | UL 1703 | 265 | 239.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.67 | 30.17 | 6.77 | 29.55 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19013
Jinko Solar Co., Ltd | JKM265PP-60B | 265 W Polycrystalline Module | UL 1703 | 265 | 240.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.67 | 30.16 | 6.75 | 28.82 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19006
Jinko Solar Co., Ltd | JKM265PP-60-J4 | 265 W Polycrystalline Module | UL 1703 | 265 | 242.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7021 | 37.3469 | 6.8102 | 35.3833 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23987
Jinko Solar Co., Ltd | JKM265PP-60-V | 265 W Polycrystalline Module | UL 1703 | 265 | 242.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.686 | 37.6691 | 6.823 | 35.8583 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23966
Jinko Solar Co., Ltd | JKMS265M-60 | 265 W Monocrystalline Module with MX, SE or TG smart junction box | UL 1703 | 265 | 240.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 9.19 | 38.2 | 8.5 | 31.2 | 45.6 | -0.441 | 0.059 | -0.342 | 0.007 | -0.458 | 1.61 | 30.71 | 6.85 | 28.25 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18658
Jinko Solar Co., Ltd | JKMS265M-60B-EP | 265W Monocrystalline module，DC module' model number is JKM265M-60B，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 265 | 241.3 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.19 | 38.2 | 8.5 | 31.2 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.658 | 32.132 | 6.827 | 30.16 | [6 empty] | 2017-11-01
Jinko Solar Co., Ltd | JKMS265M-60B-MX | 265 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 265 | 241.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 8.96 | 29.6 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.5838 | 31.2864 | 6.5213 | 29.3663 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS265P-60 | 265 W Polycrystalline Module with MX,SE or TG smart junction box | UL 1703 | 265 | 239.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.637 | 60 |  | N | 9.51 | 36.7 | 8.88 | 29.8 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.73 | 29.3 | 7.15 | 26.92 | [6 empty] | 2015-10-01 | 2018-02-01
Jinko Solar Co., Ltd | JKMS265PP-60 | 265 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 265 | 241.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5811 | 60 | 1 | N | 9.03 | 38.6 | 8.44 | 31.4 | 45.1 | -0.4249 | 0.0635 | -0.325 | 0.0161 | -0.437 | 1.56 | 31 | 6.75 | 28.47 | Rack | Flat Plate | 0.97 | 1.63 | 1 | 0.18249
Jinko Solar Co., Ltd | JKMS265PP-60-MX | 265 W Polycrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 265 | 241.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  | N | 12 | 35 | 8.88 | 29.8 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.704 | 30.2081 | 6.9264 | 28.1297 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKM270M-60B | 270 W Monocrystalline Module | UL 1703 | 270 | 244.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 9.28 | 38.4 | 8.6 | 31.4 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.68 | 30.8 | 6.85 | 28.89 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19164
Jinko Solar Co., Ltd | JKM270M-60-V |  | UL 1703 | 270 | 247.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  |  | 9.28 | 38.4 | 8.6 | 31.4 | 45.1 | -0.4 | 0.066 | -0.312 | -0.005 | -0.396 | 2.047 | 32.28 | 7.477 | 29.99 | [6 empty] | 2017-08-01
Jinko Solar Co., Ltd | JKM270M-72 | 270 W Monocrystalline Module | UL 1703 | 270 | 242.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.35 | 45 | 7.52 | 35.9 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.6094 | 35.6139 | 6.016 | 33.489 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.21228
Jinko Solar Co., Ltd | JKM270M-72B | 270 W Monocrystalline Module | UL 1703 | 270 | 241.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.09 | 45.2 | 7.48 | 36.1 | 47.3 | -0.4405 | 0.0732 | -0.3513 | 0.0163 | -0.3795 | 1.4695 | 35.7149 | 6.0366 | 32.9459 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19438
Jinko Solar Co., Ltd | JKM270M-96 | 270 W Monocrystalline Module | UL 1703 | 270 | 243.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7042 | 96 | 1 | N | 5.82 | 62.3 | 5.24 | 51.5 | 46.6 | -0.4326 | 0.0853 | -0.3853 | 0.0111 | -0.4346 | 1.0442 | 51.1264 | 4.2905 | 46.6427 | Rack | Flat Plate | 1.082 | 1.575 | 1 | 0.19774
Jinko Solar Co., Ltd | JKM270P-60 | 270 W Polycrystalline Module | UL 1703 | 270 | 247.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.09 | 38.8 | 8.52 | 31.7 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7182 | 37.5404 | 6.8748 | 35.5667 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.2389
Jinko Solar Co., Ltd | JKM270P-60-J4 | 270 W Polycrystalline Module | UL 1703 | 270 | 247.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.09 | 38.8 | 8.52 | 31.7 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7182 | 37.5404 | 6.8748 | 35.5667 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.2389
Jinko Solar Co., Ltd | JKM270P-60-V | 270 W Polycrystalline Module | UL 1703 | 270 | 247.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.09 | 38.8 | 8.52 | 31.7 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.702 | 37.8643 | 6.8877 | 36.0441 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23869
Jinko Solar Co., Ltd | JKM270P-72 | 270 W Polycrystalline Module | UL 1703 | 270 | 240.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.59 | 44.2 | 7.67 | 35.2 | 47.1 | -0.4575 | 0.0564 | -0.2743 | 0.0175 | -0.2338 | 1.5231 | 33.988 | 6.0954 | 32.8981 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19173
Jinko Solar Co., Ltd | JKM270P-72B | 270 W Polycrystalline Module | UL 1703 | 270 | 241.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.32 | 44.3 | 7.63 | 35.4 | 47.2 | -0.4422 | 0.0743 | -0.3672 | 0.0163 | -0.4179 | 1.5289 | 33.9489 | 6.3427 | 31.9623 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19223
Jinko Solar Co., Ltd | JKM270PP-60 | 270 W Polycrystalline Module | UL 1703 | 270 | 247.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.09 | 38.8 | 8.52 | 31.7 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7182 | 37.5404 | 6.8748 | 35.5667 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.2389
Jinko Solar Co., Ltd | JKM270PP-60-J4 | 270 W Polycrystalline Module | UL 1703 | 270 | 247.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.09 | 38.8 | 8.52 | 31.7 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7182 | 37.5404 | 6.8748 | 35.5667 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.2389
Jinko Solar Co., Ltd | JKM270PP-60-V | 270 W Polycrystalline Module | UL 1703 | 270 | 247.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.09 | 38.8 | 8.52 | 31.7 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.702 | 37.8643 | 6.8877 | 36.0441 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.23869
Jinko Solar Co., Ltd | JKMS270M-60 | 270 W Monocrystalline Module | UL 1703 | 270 | 247.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.28 | 38.4 | 8.6 | 31.4 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.6783 | 30.6474 | 6.8584 | 29.073 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.1905
Jinko Solar Co., Ltd | JKMS270M-60B-EP | 270W Monocrystalline module，DC module' model number is JKM270M-60B，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 270 | 245.9 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.28 | 38.4 | 8.6 | 31.4 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.658 | 32.132 | 6.827 | 30.16 | [6 empty] | 2017-11-01
Jinko Solar Co., Ltd | JKMS270M-60B-MX | 270 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 270 | 245.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.07 | 29.8 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.6032 | 31.4978 | 6.6014 | 29.5647 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS270M-60-J4 | 270 W Monocrystalline Module | UL 1703 | 270 | 247.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.28 | 38.4 | 8.6 | 31.4 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.6783 | 30.6474 | 6.8584 | 29.073 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.1905
Jinko Solar Co., Ltd | JKMS270M-60-MX | 270 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 270 | 247.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.07 | 29.8 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.7597 | 30.0884 | 7.0314 | 28.012 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS270PP-60-MX | 270 W Polycrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 270 | 246.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  | N | 12 | 35 | 8.97 | 30.1 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.7213 | 30.5122 | 6.9966 | 28.4129 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKM275M-60 | 275 W Monocrystalline Module | UL 1703 | 275 | 252.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.4 | 38.5 | 8.7 | 31.6 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.7473 | 30.9638 | 6.8674 | 29.4388 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19674
Jinko Solar Co., Ltd | JKM275M-60B | 275 W Monocrystalline Module | UL 1703 | 275 | 250.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.4 | 38.5 | 8.7 | 31.6 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.6938 | 30.9376 | 6.9745 | 29.0389 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19056
Jinko Solar Co., Ltd | JKM275M-60B-J4 | 275 W Monocrystalline Module | UL 1703 | 275 | 250.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.4 | 38.5 | 8.7 | 31.6 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.6938 | 30.9376 | 6.9745 | 29.0389 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19056
Jinko Solar Co., Ltd | JKM275M-60-J4 | 275 W Monocrystalline Module | UL 1703 | 275 | 252.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.4 | 38.5 | 8.7 | 31.6 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.7473 | 30.9638 | 6.8674 | 29.4388 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19674
Jinko Solar Co., Ltd | JKM275M-60-V |  | UL 1703 | 275 | 252.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  |  | 9.4 | 38.5 | 8.7 | 31.6 | 45.1 | -0.4 | 0.066 | -0.312 | -0.005 | -0.396 | 2.047 | 32.28 | 7.477 | 29.99 | [6 empty] | 2017-08-01
Jinko Solar Co., Ltd | JKM275M-72 | 275 W Monocrystalline Module | UL 1703 | 275 | 247.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.37 | 45.3 | 7.61 | 36.1 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.6286 | 35.8124 | 6.088 | 33.6755 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.21209
Jinko Solar Co., Ltd | JKM275M-72B | 275 W Monocrystalline Module | UL 1703 | 275 | 246.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.19 | 45.4 | 7.58 | 36.3 | 47.3 | -0.4405 | 0.0732 | -0.3513 | 0.0163 | -0.3795 | 1.5324 | 35.1669 | 6.0838 | 33.338 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19596
Jinko Solar Co., Ltd | JKM275M-96 | 275 W Monocrystalline Module | UL 1703 | 275 | 248.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7042 | 96 | 1 | N | 5.84 | 62.8 | 5.3 | 51.9 | 46.6 | -0.4326 | 0.0853 | -0.3853 | 0.0111 | -0.4346 | 1.0562 | 51.5235 | 4.3396 | 47.005 | Rack | Flat Plate | 1.082 | 1.575 | 1 | 0.19789
Jinko Solar Co., Ltd | JKM275P-60 | 275 W Polycrystalline Module | UL 1703 | 275 | 251.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.15 | 39.1 | 8.61 | 32 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.7 | 31.4 | 6.89 | 29.24 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19411 | 2017-06-01
Jinko Solar Co., Ltd | JKM275P-72 | 275 W Polycrystalline Module | UL 1703 | 275 | 245.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.7 | 44.4 | 7.77 | 35.4 | 47.1 | -0.4575 | 0.0564 | -0.2743 | 0.0175 | -0.2338 | 1.5352 | 35.1311 | 6.2057 | 32.3023 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19612
Jinko Solar Co., Ltd | JKM275P-72B | 275 W Polycrystalline Module | UL 1703 | 275 | 246.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.41 | 44.5 | 7.73 | 35.6 | 47.2 | -0.4422 | 0.0743 | -0.3672 | 0.0163 | -0.4179 | 1.5062 | 35.0829 | 6.2209 | 31.7368 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19215
Jinko Solar Co., Ltd | JKM275PP-60 | 275 W Polycrystalline Module | UL 1703 | 275 | 251.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.15 | 39.1 | 8.61 | 32 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.7 | 31.4 | 6.89 | 29.24 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19411 | 2017-06-01
Jinko Solar Co., Ltd | JKM275PP-60H | 275 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 275 | 252.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.15 | 39.1 | 8.61 | 32 | 45.4 | -0.403 | 0.061 | -0.326 | 0.032 | -0.431 | 1.87 | 31.934 | 7.503 | 30.917 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM275PP-60H-V | 275 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 275 | 251.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.15 | 39.1 | 8.61 | 32 | 45.4 | -0.408 | 0.063 | -0.341 | 0.002 | -0.407 | 1.7815 | 30.2276 | 7.1441 | 29.2371
Jinko Solar Co., Ltd | JKM275PP-60-J4 | 275 W Polycrystalline Module | UL 1703 | 275 | 251.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.15 | 39.1 | 8.61 | 32 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.7 | 31.4 | 6.89 | 29.24 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19411 | 2017-06-01
Jinko Solar Co., Ltd | JKM275PP-60-V |  | UL 1703 | 275 | 250.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  |  | 9.15 | 39.1 | 8.61 | 32 | 45.3 | -0.429 | 0.076 | -0.326 | 0.007 | -0.437 | 2.034 | 31.14 | 7.309 | 28.84 | [6 empty] | 2017-08-01
Jinko Solar Co., Ltd | JKMS275M-60 | 275 W Monocrystalline Module | UL 1703 | 275 | 252.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.4 | 38.5 | 8.7 | 31.6 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.6978 | 30.8426 | 6.9381 | 29.2582 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19042
Jinko Solar Co., Ltd | JKMS275M-60B-EP | 275W Monocrystalline module，DC module' model number is JKM275M-60B，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 275 | 250.6 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.4 | 38.5 | 8.7 | 31.6 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.658 | 32.132 | 6.827 | 30.16 | [6 empty] | 2017-11-01
Jinko Solar Co., Ltd | JKMS275M-60B-MX | 275 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 275 | 250.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.17 | 30 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.6209 | 31.7092 | 6.6742 | 29.7632 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS275M-60-EP | 275W Monocrystalline module，DC module' model number is JKM275M-60，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 275 | 252.6 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.4 | 38.5 | 8.7 | 31.6 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.88 | 31.3 | 7.512 | 29.14 | [6 empty] | 2017-11-01
Jinko Solar Co., Ltd | JKMS275M-60-J4 | 275 W Monocrystalline Module | UL 1703 | 275 | 252.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.4 | 38.5 | 8.7 | 31.6 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.6978 | 30.8426 | 6.9381 | 29.2582 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19042
Jinko Solar Co., Ltd | JKMS275M-60-MX | 275 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 275 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.17 | 30 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.7791 | 30.2903 | 7.1089 | 28.2 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS275PP-60 | 275 W Polycrystalline Module | UL 1703 | 275 | 251.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.58 | 37.2 | 9.06 | 30.5 | 45.2 | -0.417 | 0.068 | -0.33 | -0.008 | -0.429 | 1.7606 | 30.3 | 7.2384 | 28.167 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19398
Jinko Solar Co., Ltd | JKMS275PP-60-J4 | 275 W Polycrystalline Module | UL 1703 | 275 | 251.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.58 | 37.2 | 9.06 | 30.5 | 45.2 | -0.417 | 0.068 | -0.33 | -0.008 | -0.429 | 1.7606 | 30.3 | 7.2384 | 28.167 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19398
Jinko Solar Co., Ltd | JKMS275PP-60-MX | 275 W Polycrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 275 | 251 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.06 | 30.5 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.7385 | 30.9177 | 7.0668 | 28.7904 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKM280M-60 | 280 W Monocrystalline Module | UL 1703 | 280 | 257.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.53 | 38.6 | 8.81 | 31.8 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.7694 | 31.1597 | 6.9542 | 29.6251 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.1969 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-60B | 280 W Monocrystalline Module | UL 1703 | 280 | 255.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.53 | 38.6 | 8.81 | 31.8 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7152 | 31.1334 | 7.0627 | 29.2227 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19072 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-60B-J4 | 280 W Monocrystalline Module | UL 1703 | 280 | 255.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.53 | 38.6 | 8.81 | 31.8 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7152 | 31.1334 | 7.0627 | 29.2227 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19072 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-60H | 280 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 280 | 257.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.49 | 38.6 | 8.81 | 31.8 | 45 | -0.404 | 0.06 | -0.338 | 0.005 | -0.403 | 1.88 | 31.739 | 7.482 | 31.18 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-60HB | 280 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 280 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.49 | 38.6 | 8.81 | 31.8 | 45.3 | -0.4 | 0.05 | -0.324 | 0.009 | -0.409 | 1.894 | 31.543 | 7.537 | 30.958 | [6 empty] | 2018-03-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-60HB-V | 280 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.49 | 38.6 | 8.81 | 31.8 | 45.3 | -0.407 | 0.071 | -0.343 | 0.015 | -0.421 | 1.7479 | 30.5849 | 7.0021 | 29.7908 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-60H-V | 280 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 280 | 256.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.49 | 38.6 | 8.81 | 31.8 | 45.2 | -0.406 | 0.062 | -0.334 | 0.021 | -0.424 | 1.7386 | 30.9607 | 7.0311 | 29.8602 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-60-J4 | 280 W Monocrystalline Module | UL 1703 | 280 | 257.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.53 | 38.6 | 8.81 | 31.8 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.7694 | 31.1597 | 6.9542 | 29.6251 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.1969 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-60-V |  | UL 1703 | 280 | 257.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  |  | 9.49 | 38.6 | 8.81 | 31.8 | 45.1 | -0.4 | 0.066 | -0.312 | -0.005 | -0.396 | 2.047 | 32.28 | 7.477 | 29.99 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-72 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.39 | 45.4 | 7.71 | 36.3 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.65 | 36.0108 | 6.168 | 33.8621 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.21221 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM280M-72B | 280 W Monocrystalline Module | UL 1703 | 280 | 250.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.24 | 45.6 | 7.65 | 36.6 | 47.3 | -0.4405 | 0.0732 | -0.3513 | 0.0163 | -0.3795 | 1.5466 | 35.4575 | 6.14 | 33.6135 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19585 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM280P-60 | 280 W Polycrystalline Module | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.2 | 39.4 | 8.69 | 32.3 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.71 | 31.69 | 6.96 | 29.51 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19354 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM280P-72 | 280 W Polycrystalline Module | UL 1703 | 280 | 250 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.81 | 44.5 | 7.89 | 35.5 | 47.1 | -0.4575 | 0.0564 | -0.2743 | 0.0175 | -0.2338 | 1.5589 | 35.2303 | 6.3016 | 32.3935 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19615 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM280P-72B | 280 W Polycrystalline Module | UL 1703 | 280 | 250.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.48 | 44.7 | 7.83 | 35.8 | 47.2 | -0.4422 | 0.0743 | -0.3672 | 0.0163 | -0.4179 | 1.5257 | 35.28 | 6.3014 | 31.9151 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19223 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM280PP-60 | 280 W Polycrystalline Module | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.2 | 39.4 | 8.69 | 32.3 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.71 | 31.69 | 6.96 | 29.51 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19354 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM280PP-60H | 280 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 280 | 256.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.2 | 39.4 | 8.69 | 32.3 | 45.4 | -0.403 | 0.061 | -0.326 | 0.032 | -0.431 | 1.87 | 31.934 | 7.503 | 30.917 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM280PP-60H-V | 280 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 280 | 256.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.2 | 39.4 | 8.69 | 32.3 | 45.4 | -0.408 | 0.063 | -0.341 | 0.002 | -0.407 | 1.7981 | 30.511 | 7.2105 | 29.5112 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM280PP-60-J4 | 280 W Polycrystalline Module | UL 1703 | 280 | 255.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.2 | 39.4 | 8.69 | 32.3 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.71 | 31.69 | 6.96 | 29.51 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19354 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM280PP-60-V |  | UL 1703 | 280 | 255.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  |  | 9.2 | 39.4 | 8.69 | 32.3 | 45.3 | -0.429 | 0.076 | -0.326 | 0.007 | -0.437 | 2.034 | 31.14 | 7.309 | 28.84 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS280M-60 | 280 W Monocrystalline Module | UL 1703 | 280 | 256.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.53 | 38.6 | 8.81 | 31.8 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7193 | 31.0378 | 7.0258 | 29.4433 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19058 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS280M-60B-EP | 280W Monocrystalline module，DC module' model number is JKM280M-60B，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 280 | 255.3 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.53 | 38.6 | 8.81 | 31.8 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.658 | 32.132 | 6.827 | 30.16 | [6 empty] | 2017-11-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS280M-60B-MX | 280 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 280 | 255.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.28 | 30.2 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.6403 | 31.9206 | 6.7542 | 29.9616 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS280M-60-EP | 280W Monocrystalline module，DC module' model number is JKM280M-60，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 280 | 257.3 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.53 | 38.6 | 8.81 | 31.8 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.88 | 31.3 | 7.512 | 29.14 | [6 empty] | 2017-11-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS280M-60-J4 | 280 W Monocrystalline Module | UL 1703 | 280 | 256.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.53 | 38.6 | 8.81 | 31.8 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7193 | 31.0378 | 7.0258 | 29.4433 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19058 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS280M-60-MX | 280 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 280 | 257.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.28 | 30.2 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8005 | 30.4923 | 7.1942 | 28.388 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS280PP-60-MX | 280 W Polycrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 280 | 255.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.15 | 30.7 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.7558 | 31.1204 | 7.137 | 28.9792 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKM285M-60 | 285 W Monocrystalline Module | UL 1703 | 285 | 262 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.54 | 38.7 | 8.9 | 32 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.7875 | 31.3557 | 7.0253 | 29.8114 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19666 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-60B | 285 W Monocrystalline Module | UL 1703 | 285 | 260 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.54 | 38.7 | 8.9 | 32 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7328 | 31.3292 | 7.1348 | 29.4065 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19048 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-60B-J4 | 285 W Monocrystalline Module | UL 1703 | 285 | 260 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.54 | 38.7 | 8.9 | 32 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7328 | 31.3292 | 7.1348 | 29.4065 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19048 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-60H | 285 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 285 | 261.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.51 | 38.7 | 8.9 | 32 | 45 | -0.404 | 0.06 | -0.338 | 0.005 | -0.403 | 1.88 | 31.739 | 7.482 | 31.18 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-60HB | 285 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 285 | 261.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.51 | 38.7 | 8.9 | 32 | 45.3 | -0.4 | 0.05 | -0.324 | 0.009 | -0.409 | 1.894 | 31.543 | 7.537 | 30.958 | [6 empty] | 2018-03-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-60HB-V | 285 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.51 | 38.7 | 8.9 | 32 | 45.3 | -0.407 | 0.071 | -0.343 | 0.015 | -0.421 | 1.7658 | 30.7772 | 7.0736 | 29.9782 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-60H-V | 285 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 285 | 261.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.51 | 38.7 | 8.9 | 32 | 45.2 | -0.406 | 0.062 | -0.334 | 0.021 | -0.424 | 1.7563 | 31.1554 | 7.103 | 30.048 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-60-J4 | 285 W Monocrystalline Module | UL 1703 | 285 | 262 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.54 | 38.7 | 8.9 | 32 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.7875 | 31.3557 | 7.0253 | 29.8114 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19666 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-60-V |  | UL 1703 | 285 | 262.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  |  | 9.51 | 38.7 | 8.9 | 32 | 45.1 | -0.4 | 0.066 | -0.312 | -0.005 | -0.396 | 2.047 | 32.28 | 7.477 | 29.99 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-72 | 285 W Monocrystalline Module | UL 1703 | 285 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.41 | 45.5 | 7.74 | 36.8 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.6565 | 36.5068 | 6.192 | 34.3285 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.21218 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM285M-72B | 285 W Monocrystalline Module | UL 1703 | 285 | 255.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.29 | 45.9 | 7.72 | 36.9 | 47.3 | -0.4405 | 0.0732 | -0.3513 | 0.0163 | -0.3795 | 1.5607 | 35.7481 | 6.1962 | 33.889 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19576 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM285P-60 | 285 W Polycrystalline Module | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.26 | 39.7 | 8.76 | 32.6 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.73 | 31.99 | 7.01 | 29.79 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19418 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM285P-72 | 285 W Polycrystalline Module | UL 1703 | 285 | 254.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.85 | 44.7 | 7.92 | 36 | 47.1 | -0.4575 | 0.0564 | -0.2743 | 0.0175 | -0.2338 | 1.5648 | 35.7265 | 6.3255 | 32.8497 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19616 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM285P-72B | 285 W Polycrystalline Module | UL 1703 | 285 | 255.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.55 | 44.9 | 7.9 | 36.1 | 47.2 | -0.4422 | 0.0743 | -0.3672 | 0.0163 | -0.4179 | 1.5393 | 35.5756 | 6.3577 | 32.1826 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19215 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM285PP-60 | 285 W Polycrystalline Module | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.26 | 39.7 | 8.76 | 32.6 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.73 | 31.99 | 7.01 | 29.79 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19418 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM285PP-60H | 285 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 285 | 261.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.26 | 39.6 | 8.77 | 32.5 | 45.4 | -0.403 | 0.061 | -0.326 | 0.032 | -0.431 | 1.87 | 31.934 | 7.503 | 30.917 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM285PP-60H-V | 285 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 285 | 261.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.26 | 39.6 | 8.77 | 32.5 | 45.4 | -0.408 | 0.063 | -0.341 | 0.002 | -0.407 | 1.8146 | 30.6999 | 7.2769 | 29.694 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM285PP-60-J4 | 285 W Polycrystalline Module | UL 1703 | 285 | 260.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.26 | 39.7 | 8.76 | 32.6 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.73 | 31.99 | 7.01 | 29.79 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19418 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM285PP-60-V |  | UL 1703 | 285 | 260.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  |  | 9.26 | 39.7 | 8.76 | 32.6 | 45.3 | -0.429 | 0.076 | -0.326 | 0.007 | -0.437 | 2.034 | 31.14 | 7.309 | 28.84 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS285M-60 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.54 | 38.7 | 8.9 | 32 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7369 | 31.233 | 7.0976 | 29.6285 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19034 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS285M-60B-EP | 285W Monocrystalline module，DC module' model number is JKM285M-60B，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 285 | 260 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.54 | 38.7 | 8.9 | 32 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.658 | 32.132 | 6.827 | 30.16 | [6 empty] | 2017-11-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS285M-60B-MX | 285 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 285 | 259.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.38 | 30.4 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.658 | 32.132 | 6.827 | 30.16 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS285M-60-EP | 285W Monocrystalline module，DC module' model number is JKM285M-60，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 285 | 262 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.54 | 38.7 | 8.9 | 32 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.88 | 31.3 | 7.512 | 29.14 | [6 empty] | 2017-11-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS285M-60-J4 | 285 W Monocrystalline Module | UL 1703 | 285 | 261.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.54 | 38.7 | 8.9 | 32 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7369 | 31.233 | 7.0976 | 29.6285 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19034 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS285M-60-MX | 285 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 285 | 261.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.38 | 30.4 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8199 | 30.6942 | 7.2717 | 28.576 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS285PP-60-MX | 285 W Polycrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 285 | 260.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.2 | 31 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.7654 | 31.4245 | 7.176 | 29.2624 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKM290M-60 | 290 W Monocrystalline Module | UL 1703 | 290 | 266.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.55 | 39.5 | 9.02 | 32.2 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8354 | 31.3097 | 7.3339 | 29.1491 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19816 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-60B | 290 W Monocrystalline Module | UL 1703 | 290 | 264.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.55 | 39.5 | 9.02 | 32.2 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7561 | 31.525 | 7.231 | 29.5902 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.1909 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-60B-J4 | 290 W Monocrystalline Module | UL 1703 | 290 | 264.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.55 | 39.5 | 9.02 | 32.2 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7561 | 31.525 | 7.231 | 29.5902 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.1909 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-60H | 290 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 290 | 266.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.55 | 39.5 | 9.02 | 32.2 | 45 | -0.404 | 0.06 | -0.338 | 0.005 | -0.403 | 1.88 | 31.739 | 7.482 | 31.18 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-60HB | 290 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 290 | 266.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.55 | 39.5 | 9.02 | 32.2 | 45.3 | -0.4 | 0.05 | -0.324 | 0.009 | -0.409 | 1.894 | 31.543 | 7.537 | 30.958 | [6 empty] | 2018-03-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-60HB-V | 290 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.55 | 39.5 | 9.02 | 32.2 | 45.3 | -0.407 | 0.071 | -0.343 | 0.015 | -0.421 | 1.7896 | 30.9696 | 7.169 | 30.1655 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-60H-V | 290 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 290 | 266.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.55 | 39.5 | 9.02 | 32.2 | 45.2 | -0.406 | 0.062 | -0.334 | 0.021 | -0.424 | 1.78 | 31.3501 | 7.1987 | 30.2358 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-60-J4 | 290 W Monocrystalline Module | UL 1703 | 290 | 266.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.55 | 39.5 | 9.02 | 32.2 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.8116 | 31.5517 | 7.12 | 29.9978 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19709 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-60-V |  | UL 1703 | 290 | 266.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  |  | 9.55 | 39.5 | 9.02 | 32.2 | 45.1 | -0.4 | 0.066 | -0.312 | -0.005 | -0.396 | 2.047 | 32.28 | 7.477 | 29.99 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-72 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.5 | 45.7 | 7.79 | 37.2 | 46.6 | -0.43507 | 0.04433 | -0.30372 | -0.039969 | -0.39965 | 1.6672 | 36.9036 | 6.232 | 34.7017 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.21215 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM290M-72B | 290 W Monocrystalline Module | UL 1703 | 290 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.47 | 45.2 | 7.9 | 36.7 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.59 | 35.24 | 6.34 | 33.87 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19321 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM290P-60 | 290 W Polycrystalline Module | UL 1703 | 290 | 265.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.32 | 39.9 | 8.82 | 32.8 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.74 | 32.18 | 7.06 | 29.97 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19308 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM290P-72 | 290 W Polycrystalline Module | UL 1703 | 290 | 264.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8818 | 72 | 1 | N | 8.69 | 44.9 | 8.11 | 35.8 | 45.1 | -0.4249 | 0.0635 | -0.325 | 0.0161 | -0.437 | 1.53 | 35.12 | 6.47 | 32.61 | Rack | Flat Plate | 0.97 | 1.94 | 1 | 0.18529 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM290P-72B | 290 W Polycrystalline Module | UL 1703 | 290 | 262.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.69 | 44.9 | 8.11 | 35.8 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.54 | 34.93 | 6.45 | 32.61 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18549 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM290PP-60 | 290 W Polycrystalline Module | UL 1703 | 290 | 265.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.32 | 39.9 | 8.82 | 32.8 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.74 | 32.18 | 7.06 | 29.97 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19308 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM290PP-60H | 290 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 290 | 266.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.32 | 39.8 | 8.86 | 32.8 | 45.4 | -0.403 | 0.061 | -0.326 | 0.032 | -0.431 | 1.87 | 31.934 | 7.503 | 30.917 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM290PP-60H-V | 290 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 290 | 266 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.32 | 39.8 | 8.86 | 32.8 | 45.4 | -0.408 | 0.063 | -0.341 | 0.002 | -0.407 | 1.8333 | 30.9833 | 7.3516 | 29.9681 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM290PP-60-J4 | 290 W Polycrystalline Module | UL 1703 | 290 | 265.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.54 | 60 | 1 | N | 9.32 | 39.9 | 8.82 | 32.8 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.74 | 32.18 | 7.06 | 29.97 |  | Flat Plate | 0.954 | 1.614 | 1 | 0.19308 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM290PP-60-V |  | UL 1703 | 290 | 264.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  |  | 9.32 | 39.9 | 8.82 | 32.8 | 45.3 | -0.429 | 0.076 | -0.326 | 0.007 | -0.437 | 2.034 | 31.14 | 7.309 | 28.84 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM290PP-72(Plus) | 290 W Polycrystalline Module | UL 1703 | 290 | 262 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.69 | 44.9 | 8.11 | 35.8 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.61 | 34.34 | 6.57 | 33.37 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19065 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM290PP-72B | 290 W Polycrystalline Module | UL 1703 | 290 | 262.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.69 | 44.9 | 8.11 | 35.8 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.54 | 34.93 | 6.45 | 32.61 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18549 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS290M-60 | 290 W Monocrystalline Module | UL 1703 | 290 | 266.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.55 | 39.5 | 9.02 | 32.2 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7603 | 31.4283 | 7.1933 | 29.8137 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19077 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS290M-60B-EP | 290W Monocrystalline module，DC module' model number is JKM290M-60B，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 290 | 264.7 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.55 | 39.5 | 9.02 | 32.2 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.658 | 32.132 | 6.827 | 30.16 | [6 empty] | 2017-11-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS290M-60B-MX | 290 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 290 | 264.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.49 | 30.6 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.6774 | 32.3434 | 6.9071 | 30.3584 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS290M-60-EP | 290W Monocrystalline module，DC module' model number is JKM290M-60，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 290 | 266.7 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.55 | 39.5 | 9.02 | 32.2 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.88 | 31.3 | 7.512 | 29.14 | [6 empty] | 2017-11-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS290M-60-J4 | 290 W Monocrystalline Module | UL 1703 | 290 | 266.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.55 | 39.5 | 9.02 | 32.2 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7603 | 31.4283 | 7.1933 | 29.8137 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19077 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS290M-60-MX | 290 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 290 | 266.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.49 | 30.6 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8412 | 30.8961 | 7.357 | 28.764 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS290M-72 | 290 W Monocrystalline Module with MX, SE or TG smart junction box | UL 1703 | 290 | 262.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.47 | 45.2 | 7.9 | 36.7 | 45.6 | -0.441 | 0.059 | -0.342 | 0.007 | -0.458 | 1.55 | 36.4 | 6.46 | 33.73 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19455 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS290P-72 | 290 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 290 | 261.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.15 | 42.7 | 8.54 | 34 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.68 | 32.89 | 6.9 | 31.41 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19054 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS290PP-60-MX | 290 W Polycrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 290 | 265.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.25 | 31.4 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.775 | 31.83 | 7.215 | 29.64 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS290PP-72 | 290 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 290 | 261.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.15 | 42.7 | 8.54 | 34 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.68 | 32.89 | 6.9 | 31.41 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19054 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-60 | 295 W Monocrystalline Module | UL 1703 | 295 | 271.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.61 | 39.7 | 9.1 | 32.4 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8517 | 31.5042 | 7.399 | 29.3301 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19775 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-60B | 295 W Monocrystalline Module | UL 1703 | 295 | 269.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.61 | 39.7 | 9.1 | 32.4 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7717 | 31.7208 | 7.2952 | 29.774 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19051 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-60B-J4 | 295 W Monocrystalline Module | UL 1703 | 295 | 269.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.61 | 39.7 | 9.1 | 32.4 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7717 | 31.7208 | 7.2952 | 29.774 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19051 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-60H | 295 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 295 | 271.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.61 | 39.7 | 9.1 | 32.4 | 45 | -0.404 | 0.06 | -0.338 | 0.005 | -0.403 | 1.88 | 31.739 | 7.482 | 31.18 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-60HB | 295 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 295 | 271.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.61 | 39.7 | 9.1 | 32.4 | 45.3 | -0.4 | 0.05 | -0.324 | 0.009 | -0.409 | 1.894 | 31.543 | 7.537 | 30.958 | [6 empty] | 2018-03-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-60HB-V | 295 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 295 | 270.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.61 | 39.7 | 9.1 | 32.4 | 45.3 | -0.407 | 0.071 | -0.343 | 0.015 | -0.421 | 1.8055 | 31.1619 | 7.2326 | 30.3529 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-60H-V | 295 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 295 | 271 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.61 | 39.7 | 9.1 | 32.4 | 45.2 | -0.406 | 0.062 | -0.334 | 0.021 | -0.424 | 1.7958 | 31.5448 | 7.2626 | 30.4236 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-60-J4 | 295 W Monocrystalline Module | UL 1703 | 295 | 271.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5398 | 60 | 1 | N | 9.61 | 39.7 | 9.1 | 32.4 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.8276 | 31.7477 | 7.1832 | 30.1841 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19669 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-60-V |  | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  |  | 9.61 | 39.7 | 9.1 | 32.4 | 45.1 | -0.4 | 0.066 | -0.312 | -0.005 | -0.396 | 2.047 | 32.28 | 7.477 | 29.99 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-72 | 295 W Monocrystalline Module | UL 1703 | 295 | 265.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.59 | 46 | 7.85 | 37.6 | 46.7 | -0.4388 | 0.0731 | -0.3574 | 0.0235 | -0.3993 | 1.623 | 35.9186 | 6.3977 | 33.8694 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19761 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295M-72B | 295 W Monocrystalline Module | UL 1703 | 295 | 266 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.55 | 45.3 | 8.02 | 36.8 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.62 | 35.33 | 6.43 | 33.96 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19402 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295P-72 | 295 W Polycrystalline Module | UL 1703 | 295 | 268.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8818 | 72 | 1 | N | 8.76 | 45.1 | 8.15 | 36.2 | 45.1 | -0.4249 | 0.0635 | -0.325 | 0.0161 | -0.437 | 1.53 | 35.52 | 6.5 | 32.97 | Rack | Flat Plate | 0.97 | 1.94 | 1 | 0.18422 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295P-72B | 295 W Polycrystalline Module | UL 1703 | 295 | 266.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.76 | 45.1 | 8.15 | 36.2 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.55 | 35.32 | 6.48 | 32.97 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18558 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295PP-60H | 295 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 295 | 271 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.37 | 40.1 | 8.95 | 33.1 | 45.4 | -0.403 | 0.061 | -0.326 | 0.032 | -0.431 | 1.87 | 31.934 | 7.503 | 30.917 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM295PP-60H-V | 295 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 295 | 270.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.37 | 40.1 | 8.95 | 33.1 | 45.4 | -0.408 | 0.063 | -0.341 | 0.002 | -0.407 | 1.8519 | 31.2667 | 7.4262 | 30.2422 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM295PP-72 | 295 W Polycrystalline Module | UL 1703 | 295 | 266.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.76 | 45.1 | 8.15 | 36.2 | 45.5 | -0.4452 | 0.0592 | -0.3354 | -0.0047 | -0.4415 | 1.63 | 34.73 | 6.58 | 32.48 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1919 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295PP-72(Plus) | 295 W Polycrystalline Module | UL 1703 | 295 | 266.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.76 | 45.1 | 8.15 | 36.2 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.62 | 34.72 | 6.6 | 33.74 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19067 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM295PP-72B | 295 W Monocrystalline Module | UL 1703 | 295 | 266 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.55 | 45.3 | 8.02 | 36.8 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.62 | 35.33 | 6.43 | 33.96 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19402 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS295M-60B-EP | 295W Monocrystalline module，DC module' model number is JKM295M-60B，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 295 | 269.4 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.61 | 39.7 | 9.1 | 32.4 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.658 | 32.132 | 6.827 | 30.16 | [6 empty] | 2017-11-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS295M-60B-MX | 295 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 295 | 269.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.58 | 30.8 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.6934 | 32.5548 | 6.9726 | 30.5568 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS295M-60-EP | 295W Monocrystalline module，DC module' model number is JKM295M-60，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 295 | 271.5 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.61 | 39.7 | 9.1 | 32.4 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.88 | 31.3 | 7.512 | 29.14 | [6 empty] | 2017-11-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS295M-60-MX | 295 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 295 | 271.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.58 | 30.8 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8587 | 31.0981 | 7.4267 | 28.952 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS295M-72 | 295 W Monocrystalline Module with MX, SE or TG smart junction box | UL 1703 | 295 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.55 | 45.3 | 8.02 | 36.8 | 45.6 | -0.441 | 0.059 | -0.342 | 0.007 | -0.458 | 1.57 | 36.5 | 6.56 | 33.82 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19425 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS295P-72 | 295 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 295 | 266.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.22 | 42.8 | 8.58 | 34.4 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.69 | 33.28 | 6.93 | 31.78 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19065 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS295PP-72 | 295 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 295 | 266.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.22 | 42.8 | 8.58 | 34.4 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.69 | 33.28 | 6.93 | 31.78 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19065 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM300M-60 | 300 W Monocrystalline Module | UL 1703 | 300 | 276.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.72 | 40.1 | 9.21 | 32.6 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8741 | 31.6987 | 7.4884 | 29.5112 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19802 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM300M-60B | 300 W, 60 cell Monocrystalline module, black substrate | UL 1703 | 300 | 275.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.72 | 40.1 | 9.21 | 32.6 | 45.8 | -0.405 | 0.066 | -0.308 | 0.009 | -0.413 | 1.7287 | 31.3702 | 7.2892 | 29.3498 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM300M-60BL | 300 W, 60 cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 300 | 276.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 9.72 | 40.1 | 9.21 | 32.6 | 45.4 | -0.383 | 0.058 | -0.297 | 0.006 | -0.388 | 1.8028 | 31.4738 | 7.4072 | 29.666 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM300M-60BL-Q | 300 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 300 | 277.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.98 | 40.1 | 9.21 | 32.6 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.8247 | 31.9841 | 7.2537 | 30.36 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM300M-60H | 300 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 300 | 276.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.72 | 40.1 | 9.21 | 32.6 | 45 | -0.404 | 0.06 | -0.338 | 0.005 | -0.403 | 1.88 | 31.739 | 7.482 | 31.18 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM300M-60HB | 300 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 300 | 276 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.72 | 40.1 | 9.21 | 32.6 | 45.3 | -0.4 | 0.05 | -0.324 | 0.009 | -0.409 | 1.894 | 31.543 | 7.537 | 30.958 | [6 empty] | 2018-03-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM300M-60HBL-Q | 300 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 300 | 274.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 9.98 | 39.4 | 9.29 | 32.3 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8165 | 31.3225 | 7.1809 | 30.6551 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM300M-60HB-V | 300 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 300 | 275.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.72 | 40.1 | 9.21 | 32.6 | 45.3 | -0.407 | 0.071 | -0.343 | 0.015 | -0.421 | 1.8273 | 31.3543 | 7.32 | 30.5403 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM300M-60H-V | 300 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 300 | 275.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.72 | 40.1 | 9.21 | 32.6 | 45.2 | -0.406 | 0.062 | -0.334 | 0.021 | -0.424 | 1.8175 | 31.7396 | 7.3504 | 30.6114 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM300M-60L-Q | 300 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 300 | 277.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.98 | 40.1 | 9.21 | 32.6 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.8326 | 31.7474 | 7.2728 | 30.2987 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM300M-60-V |  | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  |  | 9.72 | 40.1 | 9.21 | 32.6 | 45.1 | -0.4 | 0.066 | -0.312 | -0.005 | -0.396 | 2.047 | 32.28 | 7.477 | 29.99 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM300M-72 | 300 W Monocrystalline Module | UL 1703 | 300 | 270.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.67 | 46.4 | 7.9 | 38 | 46.7 | -0.4388 | 0.0731 | -0.3574 | 0.0235 | -0.3993 | 1.6333 | 36.3007 | 6.4385 | 34.2297 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19764 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM300M-72B | 300 W Monocrystalline Module | UL 1703 | 300 | 270.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.64 | 45.5 | 8.11 | 37 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.64 | 35.52 | 6.5 | 34.15 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19418 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM300P-72 | 300 W Polycrystalline Module | UL 1703 | 300 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8818 | 72 | 1 | N | 8.84 | 45.3 | 8.2 | 36.6 | 45.1 | -0.4249 | 0.0635 | -0.325 | 0.0161 | -0.437 | 1.54 | 35.91 | 6.54 | 33.34 | Rack | Flat Plate | 0.97 | 1.94 | 1 | 0.18434 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM300P-72B | 300 W Polycrystalline Module | UL 1703 | 300 | 271.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.84 | 45.3 | 8.2 | 36.6 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.56 | 35.71 | 6.52 | 33.34 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18569 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM300PP-60H | 300 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 300 | 275.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.43 | 40.3 | 9.03 | 33.4 | 45.4 | -0.403 | 0.061 | -0.326 | 0.032 | -0.431 | 1.87 | 31.934 | 7.503 | 30.917 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM300PP-60H-V | 300 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 300 | 275.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.43 | 40.3 | 9.03 | 33.4 | 45.4 | -0.408 | 0.063 | -0.341 | 0.002 | -0.407 | 1.8684 | 31.5501 | 7.4926 | 30.5163 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM300PP-72 | 300 W Polycrystalline Module | UL 1703 | 300 | 271.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.84 | 45.3 | 8.2 | 36.6 | 45.5 | -0.4452 | 0.0592 | -0.3354 | -0.0047 | -0.4415 | 1.64 | 35.11 | 6.62 | 32.84 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19193 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM300PP-72(Plus) | 300 W Polycrystalline Module | UL 1703 | 300 | 271.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.84 | 45.3 | 8.2 | 36.6 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.63 | 35.11 | 6.64 | 34.11 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19076 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM300PP-72B | 300 W Polycrystalline Module | UL 1703 | 300 | 271.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.84 | 45.3 | 8.2 | 36.6 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.56 | 35.71 | 6.52 | 33.34 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18569 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS300M-60BL-EP | 300W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM300M-60BL. Microinverter: IQ7-60-ACM-US. | UL 1741 | 300 | 276.9 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.72 | 40.1 | 9.21 | 32.6 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8028 | 31.4738 | 7.4072 | 29.666 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS300M-60BL-EP-Q | 300 W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM300M-60BL-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 300 | 277.2 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.98 | 40.1 | 9.21 | 32.6 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.8247 | 31.9841 | 7.2537 | 30.36 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS300M-60BL-MX3 | 300 W, 60 cell monocrystalline module with DC optimizer junction box, black backsheet, 1000V max system Vdc | UL 1741 | 300 | 276.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.72 | 40.1 | 9.21 | 32.6 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8028 | 31.4738 | 7.4072 | 29.666 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS300M-60BL-TI | 300 W, 60 cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 300 | 276.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.72 | 40.1 | 9.21 | 32.6 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8028 | 31.4738 | 7.4072 | 29.666 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS300M-60B-MX | 300 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 300 | 273.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.69 | 31 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7128 | 32.7662 | 7.0526 | 30.7553 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS300M-60-EP | 300W Monocrystalline module，DC module' model number is JKM300M-60，Model Number of microinverter is IQ6-60-ACM-US (240V) | UL 1741 | 300 | 276.2 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.54 | 60 |  | N | 9.72 | 40.1 | 9.21 | 32.6 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.88 | 31.3 | 7.512 | 29.14 | [6 empty] | 2017-11-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS300M-60-MX | 300 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 300 | 276 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 12 | 35 | 9.69 | 31 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.88 | 31.3 | 7.512 | 29.14 | [6 empty] | 2018-05-01
Jinko Solar Co., Ltd | JKMS300M-72 | 300 W Monocrystalline Module with MX, SE or TG smart junction box | UL 1703 | 300 | 271.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.64 | 45.5 | 8.11 | 37 | 45.6 | -0.441 | 0.059 | -0.342 | 0.007 | -0.458 | 1.59 | 36.7 | 6.63 | 34.01 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19451 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS300P-72 | 300 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.31 | 43 | 8.63 | 34.8 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.7 | 33.66 | 6.97 | 32.14 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19074 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS300PP-72 | 300 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 300 | 270.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.31 | 43 | 8.63 | 34.8 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.7 | 33.66 | 6.97 | 32.14 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19074 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305M-60 | 305 W Monocrystalline Module | UL 1703 | 305 | 281 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.5398 | 60 | 1 | N | 9.83 | 40.3 | 9.3 | 32.8 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8924 | 31.8931 | 7.5616 | 29.6922 | Rack | Flat Plate | 0.954 | 1.614 | 1 | 0.19789 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305M-60B | 305 W, 60 cell Monocrystalline module, black substrate | UL 1703 | 305 | 279.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.8 | -0.405 | 0.066 | -0.308 | 0.009 | -0.413 | 1.7456 | 31.5626 | 7.3605 | 29.5298 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM305M-60BL | 305 W, 60 cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 305 | 281.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.4 | -0.383 | 0.058 | -0.297 | 0.006 | -0.388 | 1.8204 | 31.6669 | 7.4796 | 29.848 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM305M-60BL-Q | 305 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 305 | 282 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.07 | 40.3 | 9.3 | 32.8 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.8425 | 32.1803 | 7.3246 | 30.5462 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM305M-60H | 305 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 305 | 280.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.83 | 40.3 | 9.3 | 32.8 | 45 | -0.404 | 0.06 | -0.338 | 0.005 | -0.403 | 1.88 | 31.739 | 7.482 | 31.18 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM305M-60HB | 305 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 305 | 280.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.3 | -0.4 | 0.05 | -0.324 | 0.009 | -0.409 | 1.894 | 31.543 | 7.537 | 30.958 | [6 empty] | 2018-03-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM305M-60HBL-Q | 305 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 305 | 279 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.07 | 39.6 | 9.38 | 32.52 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8341 | 31.5359 | 7.2504 | 30.8639 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM305M-60HB-V | 305 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 305 | 280.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.3 | -0.407 | 0.071 | -0.343 | 0.015 | -0.421 | 1.8452 | 31.5466 | 7.3915 | 30.7276 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM305M-60HL-Q | 305 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 1703 | 305 | 281.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.07 | 39.6 | 9.38 | 32.52 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.8316 | 31.8193 | 7.368 | 30.2174 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM305M-60H-V | 305 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 305 | 280.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.2 | -0.406 | 0.062 | -0.334 | 0.021 | -0.424 | 1.8353 | 31.9343 | 7.4222 | 30.7992 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM305M-60L | 305 W, 60 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 305 | 280.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.3 | -0.408 | 0.062 | -0.314 | 0.041 | -0.444 | 1.8135 | 32.0242 | 7.6126 | 29.9325 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM305M-60L-Q | 305 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 305 | 282.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.07 | 40.3 | 9.3 | 32.8 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.8505 | 31.9422 | 7.3439 | 30.4846 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM305M-60-V |  | UL 1703 | 305 | 281 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  |  | 9.83 | 40.3 | 9.3 | 32.8 | 45.1 | -0.4 | 0.066 | -0.312 | -0.005 | -0.396 | 2.047 | 32.28 | 7.477 | 29.99 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM305M-72 | 305 W Monocrystalline Module | UL 1703 | 305 | 275.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 8.72 | 46.8 | 7.99 | 38.2 | 46.5 | -0.432 | 0.0748 | -0.4095 | 0.0083 | -0.439 | 1.5705 | 38.0012 | 6.4347 | 34.2439 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19567 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305M-72B | 305 W Monocrystalline Module | UL 1703 | 305 | 275.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.72 | 45.7 | 8.2 | 37.2 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.65 | 35.72 | 6.58 | 34.33 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19324 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305P-72 | 305 W Polycrystalline Module | UL 1703 | 305 | 279.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.91 | 45.6 | 8.3 | 36.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6928 | 43.8289 | 6.8621 | 41.2208 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24326 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305P-72B | 305 W Polycrystalline Module | UL 1703 | 305 | 276.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.91 | 45.6 | 8.3 | 36.8 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.58 | 35.9 | 6.6 | 33.52 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18597 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305P-72-J4 | 305 W Polycrystalline Module | UL 1703 | 305 | 279.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.91 | 45.6 | 8.3 | 36.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6928 | 43.8289 | 6.8621 | 41.2208 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24326 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305P-72-V | 305 W Polycrystalline Module | UL 1703 | 305 | 278.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.91 | 45.6 | 8.3 | 36.8 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7159 | 43.3134 | 6.9462 | 40.6055 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24367 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305PP-60H | 305 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 305 | 280.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.49 | 40.6 | 9.11 | 33.6 | 45.4 | -0.403 | 0.061 | -0.326 | 0.032 | -0.431 | 1.87 | 31.934 | 7.503 | 30.917 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM305PP-60H-V | 305 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 305 | 280.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.49 | 40.6 | 9.11 | 33.6 | 45.4 | -0.408 | 0.063 | -0.341 | 0.002 | -0.407 | 1.885 | 31.739 | 7.559 | 30.699 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM305PP-72 | 305 W Polycrystalline Module | UL 1703 | 305 | 279.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.91 | 45.6 | 8.3 | 36.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6928 | 43.8289 | 6.8621 | 41.2208 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24326 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305PP-72(Plus) | 305 W Polycrystalline Module | UL 1703 | 305 | 275.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.91 | 45.6 | 8.3 | 36.8 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.65 | 35.3 | 6.72 | 34.3 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19097 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305PP-72B | 305 W Polycrystalline Module | UL 1703 | 305 | 276.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.91 | 45.6 | 8.3 | 36.8 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.58 | 35.9 | 6.6 | 33.52 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18597 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305PP-72-J4 | 305 W Polycrystalline Module | UL 1703 | 305 | 279.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.91 | 45.6 | 8.3 | 36.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.6928 | 43.8289 | 6.8621 | 41.2208 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24326 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM305PP-72-V | 305 W Polycrystalline Module | UL 1703 | 305 | 278.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.91 | 45.6 | 8.3 | 36.8 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7159 | 43.3134 | 6.9462 | 40.6055 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24367 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS305M-60BL-EP | 305W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM305M-60BL. Microinverter: IQ7-60-ACM-US. | UL 1741 | 305 | 281.7 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8204 | 31.6669 | 7.4796 | 29.848 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS305M-60BL-EP-Q | 305 W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM305M-60BL-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 305 | 282 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.07 | 40.3 | 9.3 | 32.8 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.8425 | 32.1803 | 7.3246 | 30.5462 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS305M-60BL-MX3 | 305 W, 60 cell monocrystalline module with DC optimizer junction box, black backsheet, 1000V max system Vdc | UL 1741 | 305 | 281.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8204 | 31.6669 | 7.4796 | 29.848 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS305M-60BL-TI | 305 W, 60 cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 305 | 281.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8204 | 31.6669 | 7.4796 | 29.848 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS305M-60L-EP | 305W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM305M-60L. Microinverter: IQ7-60-ACM-US. | UL 1741 | 305 | 280.3 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.8135 | 32.0242 | 7.6126 | 29.9325 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS305M-60L-EP-Q | 305 W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM305M-60L-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 305 | 282.2 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.07 | 40.3 | 9.3 | 32.8 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.8505 | 31.9422 | 7.3439 | 30.4846 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS305M-60L-MX3 | 305 W, 60 cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 305 | 280.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.8135 | 32.0242 | 7.6126 | 29.9325 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS305M-60L-TI | 305 W, 60 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 305 | 280.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.83 | 40.3 | 9.3 | 32.8 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.8135 | 32.0242 | 7.6126 | 29.9325 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS305M-72 | 305 W Monocrystalline Module with MX, SE or TG smart junction box | UL 1703 | 305 | 276.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.72 | 45.7 | 8.2 | 37.2 | 45.6 | -0.441 | 0.059 | -0.342 | 0.007 | -0.458 | 1.6 | 36.9 | 6.7 | 34.19 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19357 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS305P-72 | 305 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 305 | 275.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.38 | 43.3 | 8.74 | 34.9 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.72 | 33.76 | 7.06 | 32.24 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19038 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS305PP-72 | 305 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 305 | 275.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.38 | 43.3 | 8.74 | 34.9 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.72 | 33.76 | 7.06 | 32.24 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19038 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310M-60 | 310 W, 60 cell Monocrystalline module, white substrate | UL 1703 | 310 | 286.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.92 | 40.5 | 9.4 | 33 | 45.2 | -0.391 | 0.064 | -0.296 | 0.025 | -0.414 | 1.7643 | 32.2096 | 7.5572 | 29.5913 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM310M-60B | 310 W, 60 cell Monocrystalline module, black substrate | UL 1703 | 310 | 284.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.92 | 40.5 | 9.4 | 33 | 45.8 | -0.405 | 0.066 | -0.308 | 0.009 | -0.413 | 1.7643 | 31.7551 | 7.4396 | 29.7099 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM310M-60BL | 310 W, 60 cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 310 | 286.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.92 | 40.5 | 9.4 | 33 | 45.4 | -0.383 | 0.058 | -0.297 | 0.006 | -0.388 | 1.84 | 31.86 | 7.56 | 30.03 | [6 empty] | 2018-10-01 | 2019-09-16
Jinko Solar Co., Ltd | JKM310M-60BL-Q | 310 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 286.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.5 | 9.4 | 33 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.8624 | 32.3766 | 7.4034 | 30.7325 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM310M-60H | 310 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 310 | 285.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.92 | 40.5 | 9.4 | 33 | 45 | -0.404 | 0.06 | -0.338 | 0.005 | -0.403 | 1.88 | 31.739 | 7.482 | 31.18 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM310M-60HB | 310 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 310 | 285.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.92 | 40.5 | 9.4 | 33 | 45.3 | -0.4 | 0.05 | -0.324 | 0.009 | -0.409 | 1.894 | 31.543 | 7.537 | 30.958 | [6 empty] | 2018-03-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM310M-60HBL | 310 W, 120 half cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 310 | 284.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 9.92 | 40.5 | 9.4 | 33 | 45.5 | -0.407 | 0.05 | -0.317 | 0.024 | -0.428 | 1.845 | 31.5661 | 7.4967 | 30.1321 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM310M-60HBL-Q | 310 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 283.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.15 | 39.8 | 9.47 | 32.74 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8517 | 31.7492 | 7.32 | 31.0727 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM310M-60HB-V | 310 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 310 | 285 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.92 | 40.5 | 9.4 | 33 | 45.3 | -0.407 | 0.071 | -0.343 | 0.015 | -0.421 | 1.865 | 31.739 | 7.471 | 30.915 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM310M-60HL-BDVP | 310 W, 120 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 310 | 283.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.01 | 39.8 | 9.51 | 32.6 | 45.6 | -0.42 | 0.047 | -0.326 |  |  | 1.683 | 31.9168 | 7.3416 | 30.4556 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM310M-60HL-Q | 310 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 1703 | 310 | 286.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.15 | 39.8 | 9.47 | 32.74 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.8492 | 32.0345 | 7.4387 | 30.4218 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM310M-60H-V | 310 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 310 | 285.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 9.92 | 40.5 | 9.4 | 33 | 45.2 | -0.406 | 0.062 | -0.334 | 0.021 | -0.424 | 1.855 | 32.129 | 7.502 | 30.987 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM310M-60L | 310 W, 60 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 310 | 285 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 9.92 | 40.5 | 9.4 | 33 | 45.3 | -0.408 | 0.062 | -0.314 | 0.041 | -0.444 | 1.833 | 32.2195 | 7.6945 | 30.115 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM310M-60L-Q | 310 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 310 | 286.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.5 | 9.4 | 33 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.8704 | 32.1369 | 7.4228 | 30.6705 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM310M-72 | 310 W Monocrystalline Module | UL 1703 | 310 | 280.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9227 | 72 | 1 | N | 8.78 | 47.1 | 8.05 | 38.5 | 46.5 | -0.432 | 0.0748 | -0.4095 | 0.0083 | -0.439 | 1.5823 | 38.2996 | 6.6159 | 34.5129 | Rack | Flat Plate | 0.986 | 1.95 | 1 | 0.19549 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310M-72B | 310 W Monocrystalline Module | UL 1703 | 310 | 280 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.8 | 45.9 | 8.29 | 37.4 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.67 | 35.91 | 6.65 | 34.52 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19345 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310P-72 | 310 W Polycrystalline Module | UL 1703 | 310 | 284 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.96 | 45.9 | 8.38 | 37 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7091 | 44.1172 | 6.9282 | 41.4919 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24324 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310P-72B | 310 W Polycrystalline Module | UL 1703 | 310 | 280.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.96 | 45.9 | 8.38 | 37 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.59 | 36.1 | 6.67 | 33.7 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18516 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310P-72-J4 | 310 W Polycrystalline Module | UL 1703 | 310 | 284 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.96 | 45.9 | 8.38 | 37 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7091 | 44.1172 | 6.9282 | 41.4919 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24324 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310P-72-V | 310 W Polycrystalline Module | UL 1703 | 310 | 283.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.96 | 45.9 | 8.38 | 37 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7324 | 43.5983 | 7.0131 | 40.8727 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24364 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310PP-60H | 310 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 310 | 285.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.59 | 40.8 | 9.19 | 33.9 | 45.4 | -0.403 | 0.061 | -0.326 | 0.032 | -0.431 | 1.87 | 31.934 | 7.503 | 30.917 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM310PP-60H-V | 310 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 310 | 284.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.59 | 120 |  | N | 9.59 | 40.8 | 9.19 | 33.9 | 45.4 | -0.408 | 0.063 | -0.341 | 0.002 | -0.407 | 1.9016 | 32.0224 | 7.6254 | 30.9731 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM310PP-72 | 310 W Polycrystalline Module | UL 1703 | 310 | 284 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.96 | 45.9 | 8.38 | 37 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7091 | 44.1172 | 6.9282 | 41.4919 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24324 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310PP-72(Plus) | 310 W Polycrystalline Module | UL 1703 | 310 | 280.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.96 | 45.9 | 8.38 | 37 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.66 | 35.49 | 6.79 | 34.49 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19004 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310PP-72B | 310 W Polycrystalline Module | UL 1703 | 310 | 280.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.96 | 45.9 | 8.38 | 37 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.59 | 36.1 | 6.67 | 33.7 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18516 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310PP-72-J4 | 310 W Polycrystalline Module | UL 1703 | 310 | 284 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.96 | 45.9 | 8.38 | 37 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7091 | 44.1172 | 6.9282 | 41.4919 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24324 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM310PP-72-V | 310 W Polycrystalline Module | UL 1703 | 310 | 283.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 8.96 | 45.9 | 8.38 | 37 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7324 | 43.5983 | 7.0131 | 40.8727 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24364 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS310M-60BL-EP | 310W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM310M-60BL. Microinverter: IQ7-60-ACM-US. | UL 1741 | 310 | 286.4 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.92 | 40.5 | 9.4 | 33 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.84 | 31.86 | 7.56 | 30.03 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS310M-60BL-EP-Q | 310 W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM310M-60BL-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 310 | 286.7 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.5 | 9.4 | 33 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.8624 | 32.3766 | 7.4034 | 30.7325 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS310M-60BL-MX3 | 310 W, 60 cell monocrystalline module with DC optimizer junction box, black backsheet, 1000V max system Vdc | UL 1741 | 310 | 286.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.92 | 40.5 | 9.4 | 33 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.84 | 31.86 | 7.56 | 30.03 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS310M-60BL-TI | 310 W, 60 cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 310 | 286.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.92 | 40.5 | 9.4 | 33 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.84 | 31.86 | 7.56 | 30.03 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS310M-60HBL-MX3 | 310 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 310 | 284.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 9.92 | 40.5 | 9.4 | 33 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.845 | 31.5661 | 7.4967 | 30.1321 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS310M-60HBL-MX3-Q | 310 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 310 | 283.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.15 | 40.5 | 9.4 | 33 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8511 | 31.7552 | 7.318 | 31.0786 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS310M-60HBL-TI | 310 W, 120 half cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 310 | 284.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 9.92 | 40.5 | 9.4 | 33 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.845 | 31.5661 | 7.4967 | 30.1321 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS310M-60HBL-TI-Q | 310 W, 120 half cell monocrystalline module with rapid shutdown junction box, black substrate, 1000V max system Vdc | UL 1741 | 310 | 283.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.15 | 40.5 | 9.4 | 33 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8511 | 31.7552 | 7.318 | 31.0786 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS310M-60L-EP | 310W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM310M-60L. Microinverter: IQ7-60-ACM-US. | UL 1741 | 310 | 285 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.92 | 40.5 | 9.4 | 33 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.833 | 32.2195 | 7.6945 | 30.115 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS310M-60L-EP-Q | 310 W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM310M-60L-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 310 | 286.9 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.5 | 9.4 | 33 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.8704 | 32.1369 | 7.4228 | 30.6705 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS310M-60L-MX3 | 310 W, 60 cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 310 | 285 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.92 | 40.5 | 9.4 | 33 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.833 | 32.2195 | 7.6945 | 30.115 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS310M-60L-TI | 310 W, 60 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 310 | 285 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 9.92 | 40.5 | 9.4 | 33 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.833 | 32.2195 | 7.6945 | 30.115 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS310M-72 | 310 W Monocrystalline Module with MX, SE or TG smart junction box | UL 1703 | 310 | 280.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.8 | 45.9 | 8.29 | 37.4 | 45.6 | -0.441 | 0.059 | -0.342 | 0.007 | -0.458 | 1.62 | 37.1 | 6.78 | 34.38 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19388 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS310P-72 | 310 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 310 | 280.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.43 | 43.6 | 8.82 | 35.2 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.73 | 34.05 | 7.13 | 32.51 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19002 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS310PP-72 | 310 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 310 | 280.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.43 | 43.6 | 8.82 | 35.2 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.73 | 34.05 | 7.13 | 32.51 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19002 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315M-60 | 315 W, 60 cell Monocrystalline module, white substrate | UL 1703 | 315 | 291 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.2 | -0.391 | 0.064 | -0.296 | 0.025 | -0.414 | 1.7812 | 32.4048 | 7.6296 | 29.7707 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM315M-60B | 315 W, 60 cell Monocrystalline module, black substrate | UL 1703 | 315 | 289.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.8 | -0.405 | 0.066 | -0.308 | 0.009 | -0.413 | 1.7812 | 31.9475 | 7.5109 | 29.8899 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM315M-60BL | 315 W, 60 cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 315 | 291.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.4 | -0.383 | 0.058 | -0.297 | 0.006 | -0.388 | 1.8576 | 32.0531 | 7.6324 | 30.212 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM315M-60BL-Q | 315 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 315 | 291.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.23 | 40.7 | 9.49 | 33.2 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.8802 | 32.5728 | 7.4742 | 30.9187 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM315M-60H | 315 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 315 | 290.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 10.04 | 40.7 | 9.49 | 33.2 | 45 | -0.404 | 0.06 | -0.338 | 0.005 | -0.403 | 1.88 | 31.739 | 7.482 | 31.18 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM315M-60HB | 315 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 315 | 290.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.3 | -0.4 | 0.05 | -0.324 | 0.009 | -0.409 | 1.894 | 31.543 | 7.537 | 30.958 | [6 empty] | 2018-03-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM315M-60HBL | 315 W, 120 half cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 315 | 289.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.5 | -0.407 | 0.05 | -0.317 | 0.024 | -0.428 | 1.8627 | 31.7574 | 7.5685 | 30.3148 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM315M-60HBL-Q | 315 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 315 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.23 | 40 | 9.56 | 32.95 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8693 | 31.9529 | 7.3896 | 31.272 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM315M-60HB-V | 315 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 315 | 289.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.3 | -0.407 | 0.071 | -0.343 | 0.015 | -0.421 | 1.8829 | 31.9314 | 7.5425 | 31.1024 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM315M-60HL | 315 W, 120 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 315 | 289.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.4 | -0.405 | 0.058 | -0.325 | 0.001 | -0.405 | 1.8455 | 31.874 | 7.557 | 30.0961 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM315M-60HL-BDVP | 315 W, 120 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 315 | 288.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.09 | 39.9 | 9.63 | 32.7 | 45.6 | -0.42 | 0.047 | -0.326 |  |  | 1.7042 | 32.0147 | 7.4342 | 30.549 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM315M-60HL-Q | 315 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 1703 | 315 | 291.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.23 | 40 | 9.56 | 32.95 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.8668 | 32.24 | 7.5094 | 30.6169 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM315M-60HL-TV | 315 W, 120 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 315 | 290.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 9.99 | 39.9 | 9.63 | 32.7 | 45.2 | -0.396 | 0.068 | -0.327 |  |  | 1.7171 | 32.7701 | 7.6452 | 30.6204 | [6 empty] | 2019-11-01 | 2020-03-02
Jinko Solar Co., Ltd | JKM315M-60H-V | 315 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 315 | 290 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.2 | -0.406 | 0.062 | -0.334 | 0.021 | -0.424 | 1.8728 | 32.3237 | 7.5738 | 31.1748 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM315M-60L | 315 W, 60 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 315 | 289.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.3 | -0.408 | 0.062 | -0.314 | 0.041 | -0.444 | 1.8505 | 32.4147 | 7.7681 | 30.2975 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM315M-60L-Q | 315 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 291.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.23 | 40.7 | 9.49 | 33.2 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.8883 | 32.3317 | 7.4939 | 30.8564 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM315M-72B | 315 W Monocrystalline Module | UL 1703 | 315 | 284.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.87 | 46.1 | 8.38 | 37.6 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.69 | 36.1 | 6.72 | 34.7 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19368 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315N-60H-MBB-B | 315 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 315 | 286.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.34 | 39.82 | 9.57 | 32.92 | 46.07 | -0.43419 | 0.049935 | -0.30929 |  |  | 1.8976 | 31.1195 | 7.55 | 29.8578 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM315P-72 | 315 W Polycrystalline Module | UL 1703 | 315 | 288.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.01 | 46.2 | 8.48 | 37.2 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7295 | 44.4056 | 7.0109 | 41.7631 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24381 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315P-72B | 315 W Polycrystalline Module | UL 1703 | 315 | 285.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.01 | 46.2 | 8.48 | 37.2 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.61 | 36.3 | 6.75 | 33.88 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18553 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315P-72-J4 | 315 W Polycrystalline Module | UL 1703 | 315 | 288.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.01 | 46.2 | 8.48 | 37.2 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7295 | 44.4056 | 7.0109 | 41.7631 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24381 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315P-72-V | 315 W Polycrystalline Module | UL 1703 | 315 | 288.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.01 | 46.2 | 8.48 | 37.2 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7531 | 43.8833 | 7.0968 | 41.1398 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24422 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315PP-72 | 315 W Polycrystalline Module | UL 1703 | 315 | 288.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.01 | 46.2 | 8.48 | 37.2 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7295 | 44.4056 | 7.0109 | 41.7631 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24381 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315PP-72(Plus) | 315 W Polycrystalline Module | UL 1703 | 315 | 285.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.01 | 46.2 | 8.48 | 37.2 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.68 | 35.68 | 6.87 | 34.67 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19029 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315PP-72B | 315 W Polycrystalline Module | UL 1703 | 315 | 285.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.01 | 46.2 | 8.48 | 37.2 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.61 | 36.3 | 6.75 | 33.88 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18553 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315PP-72-J4 | 315 W Polycrystalline Module | UL 1703 | 315 | 288.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.01 | 46.2 | 8.48 | 37.2 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7295 | 44.4056 | 7.0109 | 41.7631 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24381 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM315PP-72-V | 315 W Polycrystalline Module | UL 1703 | 315 | 288.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.01 | 46.2 | 8.48 | 37.2 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7531 | 43.8833 | 7.0968 | 41.1398 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24422 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS315M-60BL-EP | 315W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM315M-60BL. Microinverter: IQ7-60-ACM-US. | UL 1741 | 315 | 291.2 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8576 | 32.0531 | 7.6324 | 30.212 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS315M-60BL-EP-Q | 315 W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM315M-60BL-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 315 | 291.5 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.23 | 40.7 | 9.49 | 33.2 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.8802 | 32.5728 | 7.4742 | 30.9187 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS315M-60BL-MX3 | 315 W, 60 cell monocrystalline module with DC optimizer junction box, black backsheet, 1000V max system Vdc | UL 1741 | 315 | 291.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8576 | 32.0531 | 7.6324 | 30.212 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS315M-60BL-TI | 315 W, 60 cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 315 | 291.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8576 | 32.0531 | 7.6324 | 30.212 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS315M-60HBL-MX3 | 315 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 315 | 289.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.8627 | 31.7574 | 7.5685 | 30.3148 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS315M-60HBL-MX3-Q | 315 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 315 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.23 | 40.7 | 9.49 | 33.2 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8689 | 31.9476 | 7.388 | 31.2669 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS315M-60HBL-TI | 315 W, 120 half cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 315 | 289.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.8627 | 31.7574 | 7.5685 | 30.3148 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS315M-60HBL-TI-Q | 315 W, 120 half cell monocrystalline module with rapid shutdown junction box, black substrate, 1000V max system Vdc | UL 1741 | 315 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.23 | 40.7 | 9.49 | 33.2 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8689 | 31.9476 | 7.388 | 31.2669 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS315M-60HL-MX3 | 315 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 315 | 289.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.8455 | 31.874 | 7.557 | 30.0961 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS315M-60HL-MX3-Q | 315 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 315 | 291.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.23 | 40.7 | 9.49 | 33.2 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.8662 | 32.2362 | 7.5073 | 30.6133 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS315M-60HL-TI | 315 W, 120 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 315 | 289.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.8455 | 31.874 | 7.557 | 30.0961 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS315M-60HL-TI-Q | 315 W, 120 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 315 | 291.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.23 | 40.7 | 9.49 | 33.2 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.8662 | 32.2362 | 7.5073 | 30.6133 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS315M-60L-EP | 315W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM315M-60L. Microinverter: IQ7-60-ACM-US. | UL 1741 | 315 | 289.7 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.8505 | 32.4147 | 7.7681 | 30.2975 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS315M-60L-EP-Q | 315 W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM315M-60L-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 315 | 291.7 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.23 | 40.7 | 9.49 | 33.2 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.8883 | 32.3317 | 7.4939 | 30.8564 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS315M-60L-MX3 | 315 W, 60 cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 315 | 289.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.8505 | 32.4147 | 7.7681 | 30.2975 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS315M-60L-TI | 315 W, 60 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 315 | 289.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.04 | 40.7 | 9.49 | 33.2 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.8505 | 32.4147 | 7.7681 | 30.2975 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS315M-72 | 315 W Monocrystalline Module with MX, SE or TG smart junction box | UL 1703 | 315 | 285.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.87 | 46.1 | 8.38 | 37.6 | 45.6 | -0.441 | 0.059 | -0.342 | 0.007 | -0.458 | 1.64 | 37.3 | 6.85 | 34.56 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1942 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS315P-72 | 315 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 315 | 284.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.48 | 43.9 | 8.93 | 35.3 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.76 | 34.15 | 7.22 | 32.61 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19081 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS315PP-72 | 315 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 315 | 284.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.48 | 43.9 | 8.93 | 35.3 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.76 | 34.15 | 7.22 | 32.61 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19081 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320M-60 | 320 W, 60 cell Monocrystalline module, white substrate | UL 1703 | 320 | 295.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.2 | -0.391 | 0.064 | -0.296 | 0.025 | -0.414 | 1.8 | 32.6 | 7.71 | 29.95 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM320M-60B | 320 W, 60 cell Monocrystalline module, black substrate | UL 1703 | 320 | 294.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.8 | -0.405 | 0.066 | -0.308 | 0.009 | -0.413 | 1.8 | 32.14 | 7.59 | 30.07 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM320M-60BL | 320 W, 60 cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 320 | 295.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.4 | -0.383 | 0.058 | -0.297 | 0.006 | -0.388 | 1.8772 | 32.2462 | 7.7128 | 30.394 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM320M-60BL-Q | 320 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 296.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.31 | 40.9 | 9.59 | 33.4 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.9 | 32.769 | 7.553 | 31.105 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM320M-60H | 320 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 320 | 295.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 10.15 | 40.9 | 9.59 | 33.4 | 45 | -0.404 | 0.06 | -0.338 | 0.005 | -0.403 | 1.88 | 31.739 | 7.482 | 31.18 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM320M-60HB | 320 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 320 | 295 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.3 | -0.4 | 0.05 | -0.324 | 0.009 | -0.409 | 1.894 | 31.543 | 7.537 | 30.958 | [6 empty] | 2018-03-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM320M-60HBL | 320 W, 120 half cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 320 | 294.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.5 | -0.407 | 0.05 | -0.317 | 0.024 | -0.428 | 1.8823 | 31.9487 | 7.6482 | 30.4974 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM320M-60HBL-Q | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 293.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.31 | 40.2 | 9.65 | 33.16 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8868 | 32.1565 | 7.4591 | 31.4714 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM320M-60HB-V | 320 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 320 | 294.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.3 | -0.407 | 0.071 | -0.343 | 0.015 | -0.421 | 1.9027 | 32.1237 | 7.622 | 31.2897 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM320M-60HL | 320 W, 120 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 320 | 294.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.4 | -0.405 | 0.058 | -0.325 | 0.001 | -0.405 | 1.865 | 32.066 | 7.6367 | 30.2774 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM320M-60HL-BDVP | 320 W, 120 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 320 | 292.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.17 | 40.1 | 9.73 | 32.9 | 45.6 | -0.42 | 0.047 | -0.326 |  |  | 1.7219 | 32.2105 | 7.5114 | 30.7359 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM320M-60HL-Q | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 1703 | 320 | 295.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.31 | 40.2 | 9.65 | 33.16 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.8843 | 32.4455 | 7.5801 | 30.8121 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM320M-60HL-TV | 320 W, 120 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 320 | 295 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.07 | 40.1 | 9.73 | 32.9 | 45.2 | -0.396 | 0.068 | -0.327 |  |  | 1.735 | 32.9706 | 7.7245 | 30.8077 | [6 empty] | 2019-11-01 | 2020-03-02
Jinko Solar Co., Ltd | JKM320M-60H-V | 320 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 320 | 294.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 120 |  | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.2 | -0.406 | 0.062 | -0.334 | 0.021 | -0.424 | 1.8925 | 32.5184 | 7.6536 | 31.3626 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM320M-60L | 320 W, 60 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 320 | 294.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.3 | -0.408 | 0.062 | -0.314 | 0.041 | -0.444 | 1.87 | 32.61 | 7.85 | 30.48 | [6 empty] | 2018-10-01 | 2019-09-16
Jinko Solar Co., Ltd | JKM320M-60L-Q | 320 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 320 | 296.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.31 | 40.9 | 9.59 | 33.4 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.9082 | 32.5265 | 7.5729 | 31.0422 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM320M-72B | 320 W Monocrystalline Module | UL 1703 | 320 | 289.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.95 | 46.3 | 8.47 | 37.8 | 45.9 | -0.448 | 0.033 | -0.323 | 0.012 | -0.457 | 1.71 | 36.29 | 6.79 | 34.88 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19392 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320N-60H-MBB | 320 W, 120 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 320 | 292.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.4 | 39.95 | 9.69 | 33.03 | 44.85 | -0.44299 | 0.037911 | -0.30841 |  |  | 1.9063 | 31.3609 | 7.6474 | 29.7143 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM320N-60H-MBB-B | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 320 | 291.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.4 | 39.95 | 9.69 | 33.03 | 46.07 | -0.43419 | 0.049935 | -0.30929 |  |  | 1.9214 | 31.2235 | 7.6447 | 29.9575 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM320N-60H-MBB-V | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 289.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.4 | 39.95 | 9.69 | 33.03 | 46.05 | -0.46864 | 0.037793 | -0.32307 |  |  | 1.9221 | 30.972 | 7.6092 | 29.9797 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM320P-72 | 320 W Polycrystalline Module | UL 1703 | 320 | 293.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.05 | 46.4 | 8.56 | 37.4 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7459 | 44.5978 | 7.0771 | 41.9439 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24332 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320P-72B | 320 W Polycrystalline Module | UL 1703 | 320 | 290.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 46.4 | 8.56 | 37.4 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.6251 | 36.4903 | 6.8107 | 34.0643 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18531 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320P-72-J4 | 320 W Polycrystalline Module | UL 1703 | 320 | 293.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.05 | 46.4 | 8.56 | 37.4 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7459 | 44.5978 | 7.0771 | 41.9439 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24332 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320P-72-V | 320 W Polycrystalline Module | UL 1703 | 320 | 292.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.05 | 46.4 | 8.56 | 37.4 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7696 | 44.0733 | 7.1638 | 41.3179 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24373 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320PP-72 | 320 W Polycrystalline Module | UL 1703 | 320 | 293.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.05 | 46.4 | 8.56 | 37.4 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7459 | 44.5978 | 7.0771 | 41.9439 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24332 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320PP-72(Plus) | 320 W Polycrystalline Module | UL 1703 | 320 | 289.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 46.4 | 8.56 | 37.4 | 46.1 | -0.435 | 0.047 | -0.33 | 0.011 | -0.451 | 1.7 | 35.88 | 6.93 | 34.86 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19061 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320PP-72B | 320 W Polycrystalline Module | UL 1703 | 320 | 290.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 46.4 | 8.56 | 37.4 | 46.1 | -0.432 | 0.057 | -0.339 | 0.003 | -0.469 | 1.6251 | 36.4903 | 6.8107 | 34.0643 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18531 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320PP-72-J4 | 320 W Polycrystalline Module | UL 1703 | 320 | 293.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.05 | 46.4 | 8.56 | 37.4 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7459 | 44.5978 | 7.0771 | 41.9439 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24332 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM320PP-72-V | 320 W Polycrystalline Module | UL 1703 | 320 | 292.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.05 | 46.4 | 8.56 | 37.4 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7696 | 44.0733 | 7.1638 | 41.3179 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24373 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS320M-60BL-EP | 320W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM320M-60BL. Microinverter: IQ7-60-ACM-US. | UL 1741 | 320 | 295.9 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8772 | 32.2462 | 7.7128 | 30.394 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS320M-60BL-EP-Q | 320 W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM320M-60BL-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 320 | 296.3 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.31 | 40.9 | 9.59 | 33.4 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.9 | 32.769 | 7.553 | 31.105 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS320M-60BL-MX3 | 320 W, 60 cell monocrystalline module with DC optimizer junction box, black backsheet, 1000V max system Vdc | UL 1741 | 320 | 295.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8772 | 32.2462 | 7.7128 | 30.394 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS320M-60BL-TI | 320 W, 60 cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 320 | 295.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8772 | 32.2462 | 7.7128 | 30.394 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS320M-60HBL-MX3 | 320 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 320 | 294.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.8823 | 31.9487 | 7.6482 | 30.4974 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS320M-60HBL-MX3-Q | 320 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 320 | 293.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.31 | 40.9 | 9.59 | 33.4 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8886 | 32.1401 | 7.4659 | 31.4553 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS320M-60HBL-TI | 320 W, 120 half cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 320 | 294.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.8823 | 31.9487 | 7.6482 | 30.4974 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS320M-60HBL-TI-Q | 320 W, 120 half cell monocrystalline module with rapid shutdown junction box, black substrate, 1000V max system Vdc | UL 1741 | 320 | 293.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.31 | 40.9 | 9.59 | 33.4 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.8886 | 32.1401 | 7.4659 | 31.4553 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS320M-60HL-MX3 | 320 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 320 | 294.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.865 | 32.066 | 7.6367 | 30.2774 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS320M-60HL-MX3-Q | 320 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 320 | 295.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.31 | 40.9 | 9.59 | 33.4 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.8859 | 32.4304 | 7.5864 | 30.7977 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS320M-60HL-TI | 320 W, 120 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 320 | 294.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.865 | 32.066 | 7.6367 | 30.2774 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS320M-60HL-TI-Q | 320 W, 120 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 320 | 295.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.31 | 40.9 | 9.59 | 33.4 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.8859 | 32.4304 | 7.5864 | 30.7977 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS320M-60L-EP | 320W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM320M-60L. Microinverter: IQ7-60-ACM-US. | UL 1741 | 320 | 294.5 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.87 | 32.61 | 7.85 | 30.48 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS320M-60L-EP-Q | 320 W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM320M-60L-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 320 | 296.5 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.31 | 40.9 | 9.59 | 33.4 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.9082 | 32.5265 | 7.5729 | 31.0422 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS320M-60L-MX3 | 320 W, 60 cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 320 | 294.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.87 | 32.61 | 7.85 | 30.48 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS320M-60L-TI | 320 W, 60 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 320 | 294.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.15 | 40.9 | 9.59 | 33.4 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.87 | 32.61 | 7.85 | 30.48 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS320M-72 | 320 W Monocrystalline Module with MX, SE or TG smart junction box | UL 1703 | 320 | 290.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.95 | 46.3 | 8.47 | 37.8 | 45.6 | -0.441 | 0.059 | -0.342 | 0.007 | -0.458 | 1.66 | 37.49 | 6.92 | 34.74 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19448 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS320P-72 | 320 W Polycrystalline Module with MX, SE or TG smart junction box | UL 1703 | 320 | 289.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.53 | 44.1 | 9.01 | 35.5 | 45.7 | -0.45 | 0.042 | -0.333 | -0.009 | -0.442 | 1.77 | 34.34 | 7.28 | 32.79 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18994 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS320PP-72 | 320 W Polycrystalline Module | UL 1703 | 320 | 292.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.53 | 44.1 | 9.01 | 35.5 | 45.2 | -0.417 | 0.068 | -0.33 | -0.008 | -0.429 | 1.7712 | 34.9131 | 7.1868 | 32.2811 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19325 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS320PP-72-J4 | 320 W Polycrystalline Module | UL 1703 | 320 | 292.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.53 | 44.1 | 9.01 | 35.5 | 45.2 | -0.417 | 0.068 | -0.33 | -0.008 | -0.429 | 1.7712 | 34.9131 | 7.1868 | 32.2811 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19325 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM325M-60BL | 325 W, 60 cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 325 | 300.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.4 | -0.383 | 0.058 | -0.297 | 0.006 | -0.388 | 1.8948 | 32.4393 | 7.7852 | 30.576 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM325M-60BL-Q | 325 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 325 | 301 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.5 | 41.1 | 9.68 | 33.6 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.9178 | 32.9652 | 7.6239 | 31.2913 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM325M-60HBL | 325 W, 120 half cell monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 325 | 298.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.5 | -0.407 | 0.05 | -0.317 | 0.024 | -0.428 | 1.9 | 32.14 | 7.72 | 30.68 | [6 empty] | 2018-11-15 | 2019-09-16
Jinko Solar Co., Ltd | JKM325M-60HBL-Q | 325 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 325 | 297.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.5 | 40.4 | 9.74 | 33.37 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9044 | 32.3601 | 7.5287 | 31.6707 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM325M-60HL | 325 W, 120 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 325 | 299.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.4 | -0.405 | 0.058 | -0.325 | 0.001 | -0.405 | 1.9 | 32.45 | 7.78 | 30.64 | [6 empty] | 2018-11-15 | 2019-09-16
Jinko Solar Co., Ltd | JKM325M-60HL-BDVP | 325 W, 120 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.25 | 40.3 | 9.82 | 33.1 | 45.6 | -0.42 | 0.047 | -0.326 |  |  | 1.7378 | 32.4063 | 7.5809 | 30.9227 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM325M-60HL-Q | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 1703 | 325 | 300.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.5 | 40.4 | 9.74 | 33.37 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9019 | 32.651 | 7.6508 | 31.0072 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM325M-60HL-TV | 325 W, 120 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 325 | 299.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.15 | 40.3 | 9.82 | 33.1 | 45.2 | -0.396 | 0.068 | -0.327 |  |  | 1.751 | 33.171 | 7.796 | 30.995 | [6 empty] | 2019-11-01 | 2021-02-22
Jinko Solar Co., Ltd | JKM325M-60L | 325 W, 60 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 325 | 299.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.3 | -0.408 | 0.062 | -0.314 | 0.041 | -0.444 | 1.8875 | 32.8053 | 7.9237 | 30.6625 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM325M-60L-Q | 325 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 325 | 301.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.5 | 41.1 | 9.68 | 33.6 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.9261 | 32.7212 | 7.6439 | 31.2281 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM325M-72 | 325 W Monocrystalline Module | UL 1703 | 325 | 298.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.03 | 46.5 | 8.55 | 38 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.6419 | 37.3637 | 6.8108 | 35.592 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.18876 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM325M-72-J4 | 325 W Monocrystalline Module | UL 1703 | 325 | 298.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.03 | 46.5 | 8.55 | 38 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.6419 | 37.3637 | 6.8108 | 35.592 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.18876 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM325N-60H-MBB | 325 W, 120 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 325 | 297.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.46 | 40.08 | 9.81 | 33.13 | 44.85 | -0.44299 | 0.037911 | -0.30841 |  |  | 1.9299 | 31.4558 | 7.7422 | 29.8042 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM325N-60H-MBB-B | 325 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 325 | 296.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.46 | 40.08 | 9.81 | 33.13 | 46.07 | -0.43419 | 0.049935 | -0.30929 |  |  | 1.9452 | 31.318 | 7.7393 | 30.0482 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM325N-60H-MBB-V | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 325 | 294 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.46 | 40.08 | 9.81 | 33.13 | 46.05 | -0.46864 | 0.037793 | -0.32307 |  |  | 1.9459 | 31.0658 | 7.7034 | 30.0705 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM325P-72 | 325 W Polycrystalline Module | UL 1703 | 325 | 298.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.1 | 46.7 | 8.66 | 37.6 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7663 | 44.8862 | 7.1597 | 42.2151 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24394 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM325P-72-J4 | 325 W Polycrystalline Module | UL 1703 | 325 | 298.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.1 | 46.7 | 8.66 | 37.6 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7663 | 44.8862 | 7.1597 | 42.2151 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24394 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM325P-72-V | 325 W Polycrystalline Module | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.1 | 46.7 | 8.66 | 37.6 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7903 | 44.3582 | 7.2475 | 41.5851 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24435 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM325PP-72 | 325 W Polycrystalline Module | UL 1703 | 325 | 298.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.1 | 46.7 | 8.66 | 37.6 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7663 | 44.8862 | 7.1597 | 42.2151 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24394 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM325PP-72-J4 | 325 W Polycrystalline Module | UL 1703 | 325 | 298.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.1 | 46.7 | 8.66 | 37.6 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7663 | 44.8862 | 7.1597 | 42.2151 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24394 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM325PP-72-V | 325 W Polycrystalline Module | UL 1703 | 325 | 297.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.1 | 46.7 | 8.66 | 37.6 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.7903 | 44.3582 | 7.2475 | 41.5851 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24435 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS325M-60BL-EP | 325W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM325M-60BL. Microinverter: IQ7-60-ACM-US. | UL 1741 | 325 | 300.7 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8948 | 32.4393 | 7.7852 | 30.576 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS325M-60BL-EP-Q | 325 W, Monocrystalline ACPV, black substrate, 1000V max system Vdc. DC Module: JKM325M-60BL-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 325 | 301 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.5 | 41.1 | 9.68 | 33.6 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.9178 | 32.9652 | 7.6239 | 31.2913 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS325M-60BL-MX3 | 325 W, 60 cell monocrystalline module with DC optimizer junction box, black backsheet, 1000V max system Vdc | UL 1741 | 325 | 300.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8948 | 32.4393 | 7.7852 | 30.576 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS325M-60BL-TI | 325 W, 60 cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 325 | 300.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.4 | -0.383 | 0.058 | -0.297 |  |  | 1.8948 | 32.4393 | 7.7852 | 30.576 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS325M-60HBL-MX3 | 325 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 325 | 298.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.9 | 32.14 | 7.72 | 30.68 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS325M-60HBL-MX3-Q | 325 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 325 | 297.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.5 | 41.1 | 9.68 | 33.6 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9063 | 32.3325 | 7.5359 | 31.6436 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS325M-60HBL-TI | 325 W, 120 half cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 325 | 298.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.9 | 32.14 | 7.72 | 30.68 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS325M-60HBL-TI-Q | 325 W, 120 half cell monocrystalline module with rapid shutdown junction box, black substrate, 1000V max system Vdc | UL 1741 | 325 | 297.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.5 | 41.1 | 9.68 | 33.6 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9063 | 32.3325 | 7.5359 | 31.6436 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS325M-60HL-MX3 | 325 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 325 | 299.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.9 | 32.45 | 7.78 | 30.64 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS325M-60HL-MX3-Q | 325 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 325 | 300.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.5 | 41.1 | 9.68 | 33.6 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9036 | 32.6246 | 7.6576 | 30.9822 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS325M-60HL-TI | 325 W, 120 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 325 | 299.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.8825 | 32.258 | 7.7083 | 30.4587 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS325M-60HL-TI-Q | 325 W, 120 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 325 | 300.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.5 | 41.1 | 9.68 | 33.6 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9036 | 32.6246 | 7.6576 | 30.9822 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS325M-60L-EP | 325W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM325M-60L. Microinverter: IQ7-60-ACM-US. | UL 1741 | 325 | 299.2 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.8875 | 32.8053 | 7.9237 | 30.6625 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS325M-60L-EP-Q | 325 W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM325M-60L-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 325 | 301.2 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.5 | 41.1 | 9.68 | 33.6 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.9261 | 32.7212 | 7.6439 | 31.2281 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS325M-60L-MX3 | 325 W, 60 cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 325 | 299.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.8875 | 32.8053 | 7.9237 | 30.6625 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS325M-60L-TI | 325 W, 60 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 325 | 299.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.2 | 41.1 | 9.68 | 33.6 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.8875 | 32.8053 | 7.9237 | 30.6625 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS325M-72 | 325 W Monocrystalline Module | UL 1703 | 325 | 297.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.03 | 46.5 | 8.55 | 38 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.6694 | 37.2539 | 6.8835 | 34.8489 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19136 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS325M-72-J4 | 325 W Monocrystalline Module | UL 1703 | 325 | 297.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.03 | 46.5 | 8.55 | 38 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.6694 | 37.2539 | 6.8835 | 34.8489 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19136 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS325PP-72 | 325 W Polycrystalline Module | UL 1703 | 325 | 297.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.55 | 44.5 | 9.12 | 35.7 | 45.2 | -0.417 | 0.068 | -0.33 | -0.008 | -0.429 | 1.7929 | 35.1098 | 7.2745 | 32.4629 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19368 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS325PP-72-J4 | 325 W Polycrystalline Module | UL 1703 | 325 | 297.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.55 | 44.5 | 9.12 | 35.7 | 45.2 | -0.417 | 0.068 | -0.33 | -0.008 | -0.429 | 1.7929 | 35.1098 | 7.2745 | 32.4629 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19368 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM330M-60BL-Q | 330 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 330 | 305.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.61 | 41.3 | 9.77 | 33.8 | 45.4 | -0.37746 | 0.05315 | -0.27718 |  |  | 1.9357 | 33.1614 | 7.6948 | 31.4775 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM330M-60HBL | 330 W, 120 half cell monocrystalline module, black substrate, 1000V max system Vdc | UL61730, UL 1703 | 330 | 303.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.61 | 40.6 | 9.84 | 33.54 | 45.4 | -0.40616 | 0.044908 | -0.30307 | 0.024 | -0.428 | 1.914 | 32.72 | 7.622 | 31.721 | [6 empty] | 2018-11-15 | 2021-02-01
Jinko Solar Co., Ltd | JKM330M-60HBL-Q | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 330 | 302.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.61 | 40.6 | 9.84 | 33.54 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.924 | 32.525 | 7.606 | 31.832 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM330M-60HL | 330 W, 120 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 330 | 304.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.61 | 40.6 | 9.84 | 33.54 | 45.6 | -0.39292 | 0.047315 | -0.30776 | 0.001 | -0.405 | 1.9551 | 32.5748 | 7.7174 | 31.4982 | [6 empty] | 2018-11-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM330M-60HL-BDVP | 330 W, 120 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 330 | 302.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.35 | 40.39 | 9.93 | 33.24 | 45.6 | -0.42 | 0.047 | -0.326 |  |  | 1.7573 | 32.5434 | 7.6658 | 31.0535 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM330M-60HL-Q | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 61730, UL 1703 | 330 | 305.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.61 | 40.6 | 9.84 | 33.54 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9214 | 32.8173 | 7.7293 | 31.1652 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM330M-60HL-TV | 330 W, 120 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 330 | 304.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.25 | 40.39 | 9.93 | 33.24 | 45.2 | -0.396 | 0.068 | -0.327 |  |  | 1.7706 | 33.3113 | 7.8833 | 31.1261 | [6 empty] | 2020-01-02 | 2021-02-22
Jinko Solar Co., Ltd | JKM330M-60L | 330 W, 60 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 330 | 304 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 |  | N | 10.31 | 41.3 | 9.77 | 33.8 | 45.3 | -0.408 | 0.062 | -0.314 | 0.041 | -0.444 | 1.9051 | 33.0005 | 7.9973 | 30.845 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM330M-60L-Q | 330 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 330 | 306 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.61 | 41.3 | 9.77 | 33.8 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.944 | 32.916 | 7.715 | 31.414 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM330M-6TL3 | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 330 | 305.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 10.92 | 39.31 | 10.11 | 32.64 | 45.4 | -0.374 | 0.0529 | -0.278 |  |  | 1.9483 | 31.6954 | 7.7557 | 30.5416 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM330M-6TL3-B | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 330 | 305.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 10.65 | 39.8 | 9.94 | 33.2 | 45.4 | -0.37469 | 0.067659 | -0.29152 |  |  | 1.9507 | 31.7866 | 7.7867 | 30.0516 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM330M-6TL3-V | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 330 | 305.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 10.92 | 39.31 | 10.11 | 32.64 | 45.3 | -0.374 | 0.0504 | -0.281 |  |  | 1.9529 | 31.6482 | 7.7417 | 30.4935 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM330M-72 | 330 W Monocrystalline Module | UL 1703 | 330 | 303.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.11 | 46.7 | 8.64 | 38.2 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.6592 | 37.5604 | 6.8825 | 35.7793 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.18885 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM330M-72-J4 | 330 W Monocrystalline Module | UL 1703 | 330 | 303.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.11 | 46.7 | 8.64 | 38.2 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.6592 | 37.5604 | 6.8825 | 35.7793 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.18885 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM330M-72-V | 330 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 330 | 302.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.11 | 46.7 | 8.64 | 38.2 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 1.9402 | 37.349 | 7.074 | 34.8152 | [6 empty] | 2017-08-01 | 2018-04-16
Jinko Solar Co., Ltd | JKM330N-60H-MBB | 330 W, 120 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 330 | 302.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.52 | 40.21 | 9.93 | 33.24 | 44.85 | -0.44299 | 0.037911 | -0.30841 |  |  | 1.9535 | 31.5603 | 7.8369 | 29.9032 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM330N-60H-MBB-B | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 330 | 301 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.52 | 40.21 | 9.93 | 33.24 | 46.07 | -0.43419 | 0.049935 | -0.30929 |  |  | 1.969 | 31.422 | 7.834 | 30.148 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM330N-60H-MBB-V | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 330 | 298.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.52 | 40.21 | 9.93 | 33.24 | 46.05 | -0.46864 | 0.037793 | -0.32307 |  |  | 1.9697 | 31.1689 | 7.7976 | 30.1703 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM330P-72 | 330 W Polycrystalline Module | UL 1703 | 330 | 302.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.14 | 46.9 | 8.74 | 37.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7826 | 45.0784 | 7.2259 | 42.3959 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.2435 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM330P-72-J4 | 330 W Polycrystalline Module | UL 1703 | 330 | 302.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.14 | 46.9 | 8.74 | 37.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7826 | 45.0784 | 7.2259 | 42.3959 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.2435 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM330P-72-V | 330 W Polycrystalline Module | UL 1703 | 330 | 302.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.14 | 46.9 | 8.74 | 37.8 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.8068 | 44.5482 | 7.3144 | 41.7632 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24391 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM330PP-72 | 330 W Polycrystalline Module | UL 1703 | 330 | 302.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.14 | 46.9 | 8.74 | 37.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7826 | 45.0784 | 7.2259 | 42.3959 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.2435 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM330PP-72H | 330 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 330 | 302.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.14 | 46.9 | 8.74 | 37.8 | 45.2 | -0.409 | 0.048 | -0.34 | 0.03 | -0.433 | 1.7405 | 37.0084 | 7.0315 | 35.4291 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM330PP-72H-V | 330 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 330 | 302.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.14 | 46.9 | 8.74 | 37.8 | 45.3 | -0.402 | 0.05 | -0.333 | 0.037 | -0.434 | 1.87 | 38.282 | 7.492 | 36.769 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM330PP-72-J4 | 330 W Polycrystalline Module | UL 1703 | 330 | 302.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.14 | 46.9 | 8.74 | 37.8 | 45.1 | -0.41 | 0.0623 | -0.306 | 0.0052 | -0.414 | 1.7826 | 45.0784 | 7.2259 | 42.3959 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.2435 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM330PP-72-V | 330 W Polycrystalline Module | UL 1703 | 330 | 302.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.14 | 46.9 | 8.74 | 37.8 | 45.3 | -0.413 | 0.0609 | -0.316 | 0.0137 | -0.425 | 1.8068 | 44.5482 | 7.3144 | 41.7632 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.24391 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS330M-60HBL-MX3 | 330 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 330 | 303.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.31 | 41.3 | 9.77 | 33.8 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.9177 | 32.3313 | 7.7918 | 30.8626 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS330M-60HBL-MX3-Q | 330 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 330 | 302.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.61 | 41.3 | 9.77 | 33.8 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.924 | 32.525 | 7.606 | 31.832 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS330M-60HBL-TI | 330 W, 120 half cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 330 | 303.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.31 | 41.3 | 9.77 | 33.8 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.9177 | 32.3313 | 7.7918 | 30.8626 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS330M-60HBL-TI-Q | 330 W, 120 half cell monocrystalline module with rapid shutdown junction box, black substrate, 1000V max system Vdc | UL 1741 | 330 | 302.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.61 | 41.3 | 9.77 | 33.8 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.924 | 32.525 | 7.606 | 31.832 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS330M-60HL-MX3 | 330 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 330 | 303.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.31 | 41.3 | 9.77 | 33.8 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.9 | 32.45 | 7.78 | 30.64 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS330M-60HL-MX3-Q | 330 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 330 | 305.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.61 | 41.3 | 9.77 | 33.8 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9213 | 32.8188 | 7.7288 | 31.1666 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS330M-60HL-TI | 330 W, 120 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 330 | 303.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.31 | 41.3 | 9.77 | 33.8 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.9 | 32.45 | 7.78 | 30.64 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS330M-60HL-TI-Q | 330 W, 120 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 330 | 305.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.61 | 41.3 | 9.77 | 33.8 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9213 | 32.8188 | 7.7288 | 31.1666 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS330M-60L-EP | 330W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM330M-60L. Microinverter: IQ7-60-ACM-US. | UL 1741 | 330 | 304 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.31 | 41.3 | 9.77 | 33.8 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.9051 | 33.0005 | 7.9973 | 30.845 | [6 empty] | 2019-07-15
Jinko Solar Co., Ltd | JKMS330M-60L-EP-Q | 330 W, Monocrystalline ACPV, white substrate, 1000V max system Vdc. DC Module: JKM330M-60L-Q. Microinverter: IQ7-60-x-ACM-US. | UL 1741 | 330 | 306 | This component is specific to ACPV and is not available as an individual unit. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.61 | 41.3 | 9.77 | 33.8 | 45.3 | -0.37605 | 0.046206 | -0.29863 |  |  | 1.944 | 32.916 | 7.715 | 31.414 | [6 empty] | 2020-02-11
Jinko Solar Co., Ltd | JKMS330M-60L-MX3 | 330 W, 60 cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 330 | 304 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.31 | 41.3 | 9.77 | 33.8 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.9051 | 33.0005 | 7.9973 | 30.845 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS330M-60L-TI | 330 W, 60 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 330 | 304 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.59 | 60 | 1 | N | 10.31 | 41.3 | 9.77 | 33.8 | 45.3 | -0.408 | 0.062 | -0.314 |  |  | 1.9051 | 33.0005 | 7.9973 | 30.845 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS330M-72 | 330 W Monocrystalline Module | UL 1703 | 330 | 302.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.11 | 46.7 | 8.64 | 38.2 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.687 | 37.45 | 6.9559 | 35.0323 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19145 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS330M-72-J4 | 330 W Monocrystalline Module | UL 1703 | 330 | 302.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.11 | 46.7 | 8.64 | 38.2 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.687 | 37.45 | 6.9559 | 35.0323 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19145 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS330PP-72 | 330 W Polycrystalline Module | UL 1703 | 330 | 302.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.57 | 44.7 | 9.2 | 35.9 | 45.2 | -0.417 | 0.068 | -0.33 | -0.008 | -0.429 | 1.8086 | 35.3065 | 7.3384 | 32.6448 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.1935 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS330PP-72-J4 | 330 W Polycrystalline Module | UL 1703 | 330 | 302.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.57 | 44.7 | 9.2 | 35.9 | 45.2 | -0.417 | 0.068 | -0.33 | -0.008 | -0.429 | 1.8086 | 35.3065 | 7.3384 | 32.6448 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.1935 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM335M-60HBL | 335 W, 120 half cell monocrystalline module, black substrate, 1000V max system Vdc | UL61730, UL 1703 | 335 | 308.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.73 | 40.8 | 9.93 | 33.74 | 45.4 | -0.40616 | 0.044908 | -0.30307 | 0.024 | -0.428 | 1.9315 | 32.9151 | 7.6917 | 31.9102 | [6 empty] | 2018-11-15 | 2021-02-01
Jinko Solar Co., Ltd | JKM335M-60HBL-Q | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 335 | 307.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.73 | 40.8 | 9.93 | 33.74 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9416 | 32.7189 | 7.6756 | 32.0218 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM335M-60HL | 335 W, 120 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 335 | 309.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.73 | 40.8 | 9.93 | 33.74 | 45.6 | -0.39292 | 0.047315 | -0.30776 | 0.001 | -0.405 | 1.973 | 32.769 | 7.788 | 31.686 | [6 empty] | 2018-11-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM335M-60HL-BDVP | 335 W, 120 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 335 | 307.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.44 | 40.46 | 10.03 | 33.4 | 45.6 | -0.42 | 0.047 | -0.326 |  |  | 1.775 | 32.7 | 7.743 | 31.203 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM335M-60HL-Q | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 61730, UL 1703 | 335 | 310.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.73 | 40.8 | 9.93 | 33.74 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.939 | 33.013 | 7.8 | 31.351 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM335M-60HL-TV | 335 W, 120 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 335 | 309.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.34 | 40.46 | 10.03 | 33.4 | 45.2 | -0.396 | 0.068 | -0.327 |  |  | 1.7838 | 33.3027 | 7.9419 | 31.1181 | [6 empty] | 2020-01-02 | 2021-02-22
Jinko Solar Co., Ltd | JKM335M-6TL3 | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 335 | 310.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.04 | 39.41 | 10.23 | 32.75 | 45.4 | -0.374 | 0.0529 | -0.278 |  |  | 1.9714 | 31.8022 | 7.8477 | 30.6445 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM335M-6TL3-B | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 335 | 310.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 10.77 | 39.9 | 10.06 | 33.3 | 45.4 | -0.37469 | 0.067659 | -0.29152 |  |  | 1.9743 | 31.8823 | 7.8807 | 30.1421 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM335M-6TL3-V | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 335 | 310.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.04 | 39.41 | 10.23 | 32.75 | 45.3 | -0.374 | 0.0504 | -0.281 |  |  | 1.9761 | 31.7549 | 7.8336 | 30.5962 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM335M-72 | 335 W Monocrystalline Module | UL 1703 | 335 | 307.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.18 | 46.9 | 8.72 | 38.4 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.7674 | 37.847 | 7.0289 | 35.0529 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19967 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM335M-72B | 335 W Monocrystalline Module | UL 1703 | 335 | 305.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.18 | 46.9 | 8.72 | 38.4 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7164 | 37.9891 | 6.9742 | 35.2008 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19464 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM335M-72B-J4 | 335 W Monocrystalline Module | UL 1703 | 335 | 305.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.18 | 46.9 | 8.72 | 38.4 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7164 | 37.9891 | 6.9742 | 35.2008 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19464 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM335M-72H | 335 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 335 | 307.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.18 | 46.9 | 8.72 | 38.4 | 45 | -0.402 | 0.052 | -0.336 | 0.028 | -0.426 | 1.7525 | 36.889 | 7.0502 | 35.762 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM335M-72HB | 360 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 335 | 307.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.18 | 46.9 | 8.72 | 38.4 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.7525 | 36.7957 | 7.0343 | 35.507 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM335M-72HB-V | 335 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 335 | 306.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.18 | 46.9 | 8.72 | 38.4 | 45.3 | -0.41 | 0.059 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM335M-72H-V | 335 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 335 | 307.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.18 | 46.9 | 8.72 | 38.4 | 44.9 | -0.412 | 0.058 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM335M-72-J4 | 335 W Monocrystalline Module | UL 1703 | 335 | 307.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.18 | 46.9 | 8.72 | 38.4 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.6746 | 37.757 | 6.9462 | 35.9666 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.18874 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM335M-72-V | 335 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 335 | 307.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.18 | 46.9 | 8.72 | 38.4 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 1.9582 | 37.5445 | 7.1395 | 34.9975 | [6 empty] | 2017-08-01 | 2018-04-16
Jinko Solar Co., Ltd | JKM335N-60H-MBB | 335 W, 120 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 335 | 306.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.58 | 40.34 | 10.04 | 33.37 | 44.85 | -0.44299 | 0.037911 | -0.30841 |  |  | 1.9751 | 31.6837 | 7.9237 | 30.0201 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM335N-60H-MBB-V | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 335 | 303.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.58 | 40.34 | 10.04 | 33.37 | 46.05 | -0.46864 | 0.037793 | -0.32307 |  |  | 1.9916 | 31.2908 | 7.884 | 30.2883 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM335P-72 | 335 W Polycrystalline Module | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.18 | 47.2 | 8.82 | 38 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.96 | 37.69 | 7.05 | 34.93 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.22051 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM335PP-72 | 335 W Polycrystalline Module | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.18 | 47.2 | 8.82 | 38 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.96 | 37.69 | 7.05 | 34.93 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.22051 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM335PP-72H | 335 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 335 | 307.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.18 | 47.2 | 8.82 | 38 | 45.2 | -0.409 | 0.048 | -0.34 | 0.03 | -0.433 | 1.7564 | 37.2042 | 7.0959 | 35.6165 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM335PP-72H-V | 335 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 335 | 307.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.18 | 47.2 | 8.82 | 38 | 45.3 | -0.402 | 0.05 | -0.333 | 0.037 | -0.434 | 1.87 | 38.282 | 7.492 | 36.769 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM335PP-72-J4 | 335 W Polycrystalline Module | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.18 | 47.2 | 8.82 | 38 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.96 | 37.69 | 7.05 | 34.93 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.22051 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM335PP-72-V |  | UL 1703 | 335 | 305 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.88 | 72 |  |  | 9.18 | 47.2 | 8.82 | 38 | 45.3 | -0.44 | 0.073 | -0.338 | 0.001 | -0.445 | 2.048 | 37.3 | 7.307 | 34.72 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS335M-60HBL-MX3 | 335 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 335 | 308.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.36 | 41.5 | 9.87 | 34 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.9373 | 32.5226 | 7.8715 | 31.0452 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS335M-60HBL-MX3-Q | 335 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 335 | 307.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.73 | 41.5 | 9.86 | 34 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9417 | 32.7175 | 7.6761 | 32.0204 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS335M-60HBL-TI | 335 W, 120 half cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 335 | 308.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.36 | 41.5 | 9.87 | 34 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.9373 | 32.5226 | 7.8715 | 31.0452 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS335M-60HBL-TI-Q | 335 W, 120 half cell monocrystalline module with rapid shutdown junction box, black substrate, 1000V max system Vdc | UL 1741 | 335 | 307.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.73 | 41.5 | 9.86 | 34 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9417 | 32.7175 | 7.6761 | 32.0204 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS335M-60HL-MX3 | 335 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 335 | 308.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.36 | 41.5 | 9.87 | 34 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.9194 | 32.642 | 7.8596 | 30.8213 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS335M-60HL-MX3-Q | 335 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 335 | 310.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.73 | 41.5 | 9.86 | 34 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.939 | 33.013 | 7.8 | 31.351 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS335M-60HL-TI | 335 W, 120 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 335 | 308.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.36 | 41.5 | 9.87 | 34 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.9194 | 32.642 | 7.8596 | 30.8213 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS335M-60HL-TI-Q | 335 W, 120 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 335 | 310.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.73 | 41.5 | 9.86 | 34 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.939 | 33.013 | 7.8 | 31.351 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS335M-72 | 335 W Monocrystalline Module | UL 1703 | 335 | 307.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.18 | 46.9 | 8.72 | 38.4 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7026 | 37.6461 | 7.0203 | 35.2157 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19133 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS335M-72-J4 | 335 W Monocrystalline Module | UL 1703 | 335 | 307.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.18 | 46.9 | 8.72 | 38.4 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7026 | 37.6461 | 7.0203 | 35.2157 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19133 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM340M-60HBL | 340 W, 120 half cell monocrystalline module, black substrate, 1000V max system Vdc | UL61730, UL 1703 | 340 | 313.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.82 | 41 | 10.02 | 33.93 | 45.4 | -0.40616 | 0.044908 | -0.30307 | 0.024 | -0.428 | 1.949 | 33.1005 | 7.7614 | 32.0898 | [6 empty] | 2018-11-15 | 2021-02-01
Jinko Solar Co., Ltd | JKM340M-60HBL-Q | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 340 | 312.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.82 | 41 | 10.02 | 33.93 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9592 | 32.9032 | 7.7451 | 32.2021 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM340M-60HL | 340 W, 120 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 340 | 313.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.82 | 41 | 10.02 | 33.93 | 45.6 | -0.39292 | 0.047315 | -0.30776 | 0.001 | -0.405 | 1.9909 | 32.9535 | 7.8586 | 31.8644 | [6 empty] | 2018-11-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM340M-60HL-Q | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 61730, UL 1703 | 340 | 314.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.82 | 41 | 10.02 | 33.93 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9566 | 33.1989 | 7.8707 | 31.5275 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM340M-60HL-TV | 340 W, 120 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 340 | 314 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.66 | 20 | 6 | N | 10.43 | 40.6 | 10.11 | 33.62 | 45.2 | -0.396 | 0.068 | -0.327 |  |  | 1.7993 | 33.4179 | 8.0111 | 31.2257 | [6 empty] | 2020-01-02 | 2021-02-22
Jinko Solar Co., Ltd | JKM340M-66HB | 340 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 340 | 314.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.01 | 43.6 | 9.3 | 36.56 | 45.3 | -0.37224 | 0.036979 | -0.29793 |  |  | 1.814 | 36.1227 | 7.0934 | 35.1093 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM340M-6TL3 | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 340 | 315.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.16 | 39.51 | 10.35 | 32.85 | 45.4 | -0.374 | 0.0529 | -0.278 |  |  | 1.9945 | 31.8993 | 7.9398 | 30.7381 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM340M-6TL3-B | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 340 | 315 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 10.89 | 40 | 10.18 | 33.4 | 45.4 | -0.37469 | 0.067659 | -0.29152 |  |  | 1.9978 | 31.9781 | 7.9747 | 30.2327 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM340M-6TL3-V | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 340 | 315.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.16 | 39.51 | 10.35 | 32.85 | 45.3 | -0.374 | 0.0504 | -0.281 |  |  | 1.9993 | 31.8519 | 7.9254 | 30.6896 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM340M-72 | 340 W Monocrystalline Module | UL 1703 | 340 | 312.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.24 | 47.1 | 8.79 | 38.7 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.7816 | 38.1427 | 7.0853 | 35.3267 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19986 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM340M-72B | 340 W Monocrystalline Module | UL 1703 | 340 | 310.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.24 | 47.1 | 8.79 | 38.7 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7302 | 38.2859 | 7.0302 | 35.4758 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19483 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM340M-72B-J4 | 340 W Monocrystalline Module | UL 1703 | 340 | 310.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.24 | 47.1 | 8.79 | 38.7 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7302 | 38.2859 | 7.0302 | 35.4758 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19483 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM340M-72H | 335 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 340 | 312.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.24 | 47.1 | 8.79 | 38.7 | 45 | -0.402 | 0.052 | -0.336 | 0.028 | -0.426 | 1.7665 | 37.1772 | 7.1068 | 36.0414 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM340M-72HB | 360 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 340 | 312.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.24 | 47.1 | 8.79 | 38.7 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.7665 | 37.0831 | 7.0907 | 35.7844 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM340M-72HB-V | 340 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 340 | 311.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.24 | 47.1 | 8.79 | 38.7 | 45.3 | -0.41 | 0.059 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM340M-72H-V | 340 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 340 | 312.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.24 | 47.1 | 8.79 | 38.7 | 44.9 | -0.412 | 0.058 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM340M-72-J4 | 340 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 340 | 312.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.24 | 47.1 | 8.79 | 38.7 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.688 | 38.052 | 7.002 | 36.2476 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.18892 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM340M-72-V | 340 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 340 | 312.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.24 | 47.1 | 8.79 | 38.7 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 1.9739 | 37.8378 | 7.1968 | 35.2709 | [6 empty] | 2017-08-01 | 2018-04-16
Jinko Solar Co., Ltd | JKM340N-60H-MBB | 340 W, 120 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 340 | 311.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.64 | 40.47 | 10.16 | 33.47 | 44.85 | -0.44299 | 0.037911 | -0.30841 |  |  | 1.9987 | 31.7786 | 8.0184 | 30.1101 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM340N-60H-MBB-V | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 340 | 308.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.64 | 40.47 | 10.16 | 33.47 | 46.05 | -0.46864 | 0.037793 | -0.32307 |  |  | 2.0154 | 31.3846 | 7.9782 | 30.3791 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM340PP-72H | 340 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 340 | 311.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.22 | 47.5 | 8.9 | 38.2 | 45.2 | -0.409 | 0.048 | -0.34 | 0.03 | -0.433 | 1.7723 | 37.4 | 7.1602 | 35.804 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM340PP-72H-V | 340 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 340 | 312.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.22 | 47.5 | 8.9 | 38.2 | 45.3 | -0.402 | 0.05 | -0.333 | 0.037 | -0.434 | 1.87 | 38.282 | 7.492 | 36.769 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM340PP-72-V |  | UL 1703 | 340 | 309.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.88 | 72 |  |  | 9.22 | 47.5 | 8.9 | 38.2 | 45.3 | -0.44 | 0.073 | -0.338 | 0.001 | -0.445 | 2.048 | 37.3 | 7.307 | 34.72 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS340M-60HBL-MX3 | 340 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 340 | 313.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.55 | 41.7 | 9.96 | 34.2 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.955 | 32.7139 | 7.9433 | 31.2279 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS340M-60HBL-MX3-Q | 340 W, 120 half cut cell monocrystalline module with DC optimizer junction box, black substrate, 1000V max system Vdc | UL 1741 | 340 | 312.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.82 | 41.7 | 9.95 | 34.2 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9594 | 32.9099 | 7.7461 | 32.2087 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS340M-60HBL-TI | 340 W, 120 half cell monocrystalline module with rapid shutdown device, black substrate, 1000V max system Vdc | UL 1741 | 340 | 313.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.55 | 41.7 | 9.96 | 34.2 | 45.5 | -0.407 | 0.05 | -0.317 |  |  | 1.955 | 32.7139 | 7.9433 | 31.2279 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS340M-60HBL-TI-Q | 340 W, 120 half cell monocrystalline module with rapid shutdown junction box, black substrate, 1000V max system Vdc | UL 1741 | 340 | 312.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.82 | 41.7 | 9.95 | 34.2 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9594 | 32.9099 | 7.7461 | 32.2087 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS340M-60HL-MX3 | 340 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 340 | 313.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.55 | 41.7 | 9.96 | 34.2 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.9369 | 32.834 | 7.9313 | 31.0026 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS340M-60HL-MX3-Q | 340 W, 120 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1000V max system Vdc | UL 1741 | 340 | 314.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.82 | 41.7 | 9.95 | 34.2 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9567 | 33.2072 | 7.8712 | 31.5354 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS340M-60HL-TI | 340 W, 120 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 340 | 313.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 20 | 6 | N | 10.55 | 41.7 | 9.96 | 34.2 | 45.4 | -0.405 | 0.058 | -0.325 |  |  | 1.9369 | 32.834 | 7.9313 | 31.0026 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS340M-60HL-TI-Q | 340 W, 120 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 340 | 314.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.82 | 41.7 | 9.95 | 34.2 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9567 | 33.2072 | 7.8712 | 31.5354 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS340M-72 | 340 W Monocrystalline Module | UL 1703 | 340 | 312 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.24 | 47.1 | 8.79 | 38.7 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7163 | 37.9402 | 7.0767 | 35.4908 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19152 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS340M-72-J4 | 340 W Monocrystalline Module | UL 1703 | 340 | 312 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.24 | 47.1 | 8.79 | 38.7 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7163 | 37.9402 | 7.0767 | 35.4908 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19152 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM340P-72 | 340 W Polycrystalline Module | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.22 | 47.5 | 8.9 | 38.2 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.98 | 37.89 | 7.12 | 35.11 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.21746 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM340PP-72 | 340 W Polycrystalline Module | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.22 | 47.5 | 8.9 | 38.2 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.98 | 37.89 | 7.12 | 35.11 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.21746 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM340PP-72-J4 | 340 W Polycrystalline Module | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.22 | 47.5 | 8.9 | 38.2 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 1.98 | 37.89 | 7.12 | 35.11 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.21746 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM345M-60HBL | 345 W, 120 half cell monocrystalline module, black substrate, 1000V max system Vdc | UL61730, UL 1703 | 345 | 318 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.91 | 41.2 | 10.11 | 34.12 | 45.4 | -0.40616 | 0.044908 | -0.30307 |  |  | 1.9665 | 33.2858 | 7.8311 | 32.2695 | [6 empty] | 2020-01-21 | 2021-02-01
Jinko Solar Co., Ltd | JKM345M-60HBL-Q | 345 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 345 | 316.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.91 | 41.2 | 10.11 | 34.12 | 45.4 | -0.42373 | 0.04866 | -0.3163 |  |  | 1.9768 | 33.0874 | 7.8147 | 32.3825 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM345M-60HL | 345 W, 120 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 345 | 318.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.91 | 41.2 | 10.11 | 34.12 | 45.6 | -0.39292 | 0.047315 | -0.30776 |  |  | 2.0088 | 33.1381 | 7.9292 | 32.0429 | [6 empty] | 2020-01-21 | 2020-08-03
Jinko Solar Co., Ltd | JKM345M-60HL-Q | 345 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 61730, UL 1703 | 345 | 319.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.91 | 41.2 | 10.11 | 34.12 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9741 | 33.3848 | 7.9414 | 31.7041 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM345M-66H | 345 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 345 | 319.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.27 | 43.32 | 9.41 | 36.67 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 1.8164 | 36.0246 | 7.2063 | 34.5511 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM345M-66HB | 345 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 345 | 319.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.13 | 43.63 | 9.42 | 36.63 | 45.3 | -0.37224 | 0.036979 | -0.29793 |  |  | 1.8374 | 36.1919 | 7.1849 | 35.1765 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM345M-66H-TV | 345 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 345 | 317 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 22 | 6 | N | 10.2 | 43.64 | 9.37 | 36.82 | 45.7 | -0.39847 | 0.065264 | -0.3165 |  |  | 1.8357 | 35.9702 | 7.624 | 33.4649 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM345M-66H-V | 345 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 345 | 319.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.27 | 43.32 | 9.41 | 36.67 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 1.8395 | 35.8331 | 7.2165 | 34.6003 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM345M-6TL3 | 345 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 345 | 319.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.28 | 39.61 | 10.47 | 32.95 | 45.4 | -0.374 | 0.0529 | -0.278 |  |  | 2.0176 | 31.9964 | 8.0318 | 30.8316 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM345M-6TL3-B | 345 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 345 | 319.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.01 | 40.1 | 10.3 | 33.5 | 45.4 | -0.37469 | 0.067659 | -0.29152 |  |  | 2.0214 | 32.0738 | 8.0687 | 30.3232 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM345M-6TL3-V | 345 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 345 | 320 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.28 | 39.61 | 10.47 | 32.95 | 45.3 | -0.374 | 0.0504 | -0.281 |  |  | 2.0225 | 31.9488 | 8.0173 | 30.7831 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM345M-72 | 345 W Monocrystalline Module | UL 1703 | 345 | 317.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.31 | 47.3 | 8.87 | 38.9 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.7978 | 38.3398 | 7.1498 | 35.5093 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19979 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM345M-72B | 345 W Monocrystalline Module | UL 1703 | 345 | 314.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.31 | 47.3 | 8.87 | 38.9 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.746 | 38.4837 | 7.0942 | 35.6592 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19476 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM345M-72B-J4 | 345 W Monocrystalline Module | UL 1703 | 345 | 314.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.31 | 47.3 | 8.87 | 38.9 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.746 | 38.4837 | 7.0942 | 35.6592 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19476 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM345M-72H | 340 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 345 | 317.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.31 | 47.3 | 8.87 | 38.9 | 45 | -0.402 | 0.052 | -0.336 | 0.028 | -0.426 | 1.7826 | 37.3693 | 7.1715 | 36.2277 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM345M-72HB | 365 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 345 | 316.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.31 | 47.3 | 8.87 | 38.9 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.7826 | 37.2748 | 7.1553 | 35.9693 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM345M-72HB-V | 345 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 345 | 316.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.31 | 47.3 | 8.87 | 38.9 | 45.3 | -0.41 | 0.059 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM345M-72H-V | 345 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 345 | 316.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.31 | 47.3 | 8.87 | 38.9 | 44.9 | -0.412 | 0.058 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM345M-72-J4 | 345 W Monocrystalline Module | UL 1703 | 345 | 317.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.31 | 47.3 | 8.87 | 38.9 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.7034 | 38.2487 | 7.0657 | 36.4349 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.18884 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM345M-72-V | 345 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 345 | 317 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.31 | 47.3 | 8.87 | 38.9 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 1.9919 | 38.0334 | 7.2623 | 35.4532 | [6 empty] | 2017-08-01 | 2018-04-16
Jinko Solar Co., Ltd | JKM345N-60H-MBB | 345 W, 120 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 345 | 316.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.7 | 40.6 | 10.27 | 33.6 | 44.85 | -0.44299 | 0.037911 | -0.30841 |  |  | 2.0204 | 31.9021 | 8.1052 | 30.227 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM345N-60H-MBB-V | 345 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 345 | 312.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.7 | 40.6 | 10.27 | 33.6 | 46.05 | -0.46864 | 0.037793 | -0.32307 |  |  | 2.0372 | 31.5065 | 8.0646 | 30.4971 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM345P-72 | 345 W Polycrystalline Module | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.29 | 47.8 | 8.98 | 38.4 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 2 | 38.09 | 7.18 | 35.3 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.22081 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM345PP-72 | 345 W Polycrystalline Module | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.29 | 47.8 | 8.98 | 38.4 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 2 | 38.09 | 7.18 | 35.3 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.22081 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM345PP-72H | 345 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 345 | 316.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.29 | 47.8 | 8.98 | 38.4 | 45.2 | -0.409 | 0.048 | -0.34 | 0.03 | -0.433 | 1.7883 | 37.5958 | 7.2246 | 35.9915 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM345PP-72H-V | 345 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 345 | 316.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.29 | 47.8 | 8.98 | 38.4 | 45.3 | -0.402 | 0.05 | -0.333 | 0.037 | -0.434 | 1.87 | 38.282 | 7.492 | 36.769 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM345PP-72-J4 | 345 W Polycrystalline Module | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.29 | 47.8 | 8.98 | 38.4 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 2 | 38.09 | 7.18 | 35.3 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.22081 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM345PP-72-V |  | UL 1703 | 345 | 314.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.88 | 72 |  |  | 9.29 | 47.8 | 8.98 | 38.4 | 45.3 | -0.44 | 0.073 | -0.338 | 0.001 | -0.445 | 2.048 | 37.3 | 7.307 | 34.72 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS345M-72 | 345 W Monocrystalline Module | UL 1703 | 345 | 316.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.31 | 47.3 | 8.87 | 38.9 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7319 | 38.1363 | 7.1411 | 35.6742 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19145 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS345M-72-J4 | 345 W Monocrystalline Module | UL 1703 | 345 | 316.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.31 | 47.3 | 8.87 | 38.9 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7319 | 38.1363 | 7.1411 | 35.6742 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19145 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM350M-60HL | 350 W, 120 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 350 | 323.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 11 | 41.4 | 10.2 | 34.31 | 45.6 | -0.39292 | 0.047315 | -0.30776 |  |  | 2.0266 | 33.3226 | 7.9998 | 32.2213 | [6 empty] | 2020-01-21 | 2020-08-03
Jinko Solar Co., Ltd | JKM350M-60HL-Q | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1000Vdc system rating | UL 61730, UL 1703 | 350 | 324.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 11 | 41.4 | 10.2 | 34.31 | 45.1 | -0.38696 | 0.071224 | -0.32224 |  |  | 1.9917 | 33.5707 | 8.0121 | 31.8806 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM350M-66H | 350 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 350 | 323.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.34 | 43.41 | 9.52 | 36.77 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 1.8376 | 36.1229 | 7.2906 | 34.6454 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM350M-66HB | 350 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 350 | 324.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.25 | 43.65 | 9.54 | 36.69 | 45.3 | -0.37224 | 0.036979 | -0.29793 |  |  | 1.8608 | 36.2512 | 7.2764 | 35.2341 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM350M-66H-TV | 350 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 350 | 321.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 22 | 6 | N | 10.28 | 43.67 | 9.48 | 36.92 | 45.7 | -0.39847 | 0.065264 | -0.3165 |  |  | 1.8572 | 36.0678 | 7.7135 | 33.5558 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM350M-66H-V | 350 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 350 | 323.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.34 | 43.41 | 9.52 | 36.77 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 1.861 | 35.9308 | 7.3008 | 34.6946 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM350M-6TL3 | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 350 | 324.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.4 | 39.71 | 10.59 | 33.05 | 45.4 | -0.374 | 0.0529 | -0.278 |  |  | 2.0408 | 32.0935 | 8.1239 | 30.9252 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM350M-6TL3-B | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 350 | 324.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.11 | 40.26 | 10.4 | 33.66 | 45.4 | -0.37469 | 0.067659 | -0.29152 |  |  | 2.041 | 32.227 | 8.147 | 30.468 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM350M-6TL3-V | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 324.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.4 | 39.71 | 10.59 | 33.05 | 45.3 | -0.374 | 0.0504 | -0.281 |  |  | 2.0456 | 32.0458 | 8.1092 | 30.8765 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM350M-72 | 350 W Monocrystalline Module | UL 1703 | 350 | 322 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.38 | 47.5 | 8.94 | 39.1 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.812 | 38.5369 | 7.2062 | 35.6918 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19951 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM350M-72B | 350 W Monocrystalline Module | UL 1703 | 350 | 319.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.38 | 47.5 | 8.94 | 39.1 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7597 | 38.6816 | 7.1502 | 35.8425 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19448 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM350M-72B-J4 | 350 W Monocrystalline Module | UL 1703 | 350 | 319.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.38 | 47.5 | 8.94 | 39.1 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7597 | 38.6816 | 7.1502 | 35.8425 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19448 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM350M-72H | 340 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 350 | 322.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.38 | 47.5 | 8.94 | 39.1 | 45 | -0.402 | 0.052 | -0.336 | 0.028 | -0.426 | 1.7967 | 37.5615 | 7.2281 | 36.414 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM350M-72HB | 365 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 350 | 321.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.38 | 47.5 | 8.94 | 39.1 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.7967 | 37.4664 | 7.2117 | 36.1543 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM350M-72HB-V | 350 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 350 | 321.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.38 | 47.5 | 8.94 | 39.1 | 45.3 | -0.41 | 0.059 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM350M-72H-V | 350 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 350 | 321.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.38 | 47.5 | 8.94 | 39.1 | 44.9 | -0.412 | 0.058 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM350M-72-J4 | 350 W Monocrystalline Module | UL 1703 | 350 | 322 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.38 | 47.5 | 8.94 | 39.1 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.7168 | 38.4453 | 7.1215 | 36.6223 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.18858 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM350M-72-V | 350 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 350 | 321.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.38 | 47.5 | 8.94 | 39.1 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 2.0076 | 38.2289 | 7.3196 | 35.6354 | [6 empty] | 2017-08-01 | 2018-04-16
Jinko Solar Co., Ltd | JKM350N-60H-MBB | 350 W, 120 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 350 | 321.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.76 | 40.73 | 10.38 | 33.72 | 44.85 | -0.44299 | 0.037911 | -0.30841 |  |  | 2.042 | 32.016 | 8.192 | 30.335 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM350N-60H-MBB-V | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 317.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 20 | 6 | N | 10.76 | 40.73 | 10.38 | 33.72 | 46.05 | -0.46864 | 0.037793 | -0.32307 |  |  | 2.059 | 31.619 | 8.151 | 30.606 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM350P-72 | 350 W Polycrystalline Module | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.36 | 48 | 9.07 | 38.6 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 2.02 | 38.28 | 7.25 | 35.48 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.22093 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM350PP-72 | 350 W Polycrystalline Module | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.36 | 48 | 9.07 | 38.6 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 2.02 | 38.28 | 7.25 | 35.48 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.22093 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM350PP-72H | 350 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 350 | 321.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.36 | 48 | 9.07 | 38.6 | 45.2 | -0.409 | 0.048 | -0.34 | 0.03 | -0.433 | 1.8062 | 37.7917 | 7.297 | 36.1789 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM350PP-72H-V | 350 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 350 | 321.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.36 | 48 | 9.07 | 38.6 | 45.3 | -0.402 | 0.05 | -0.333 | 0.037 | -0.434 | 1.87 | 38.282 | 7.492 | 36.769 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM350PP-72-J4 | 350 W Polycrystalline Module | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.835 | 72 | 1 | N | 9.36 | 48 | 9.07 | 38.6 | 45.3 | -0.426 | 0.065 | -0.325 | -0.003 | -0.443 | 2.02 | 38.28 | 7.25 | 35.48 |  | Flat Plate | 0.954 | 1.924 | 1 | 0.22093 | 2017-06-01 | 2018-04-02
Jinko Solar Co., Ltd | JKM350PP-72-V |  | UL 1703 | 350 | 319.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.88 | 72 |  |  | 9.36 | 48 | 9.07 | 38.6 | 45.3 | -0.44 | 0.073 | -0.338 | 0.001 | -0.445 | 2.048 | 37.3 | 7.307 | 34.72 | [6 empty] | 2017-08-01 | 2018-04-02
Jinko Solar Co., Ltd | JKMS350M-72 | 350 W Monocrystalline Module | UL 1703 | 350 | 321.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.38 | 47.5 | 8.94 | 39.1 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7456 | 38.3323 | 7.1975 | 35.8577 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19118 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS350M-72-J4 | 350 W Monocrystalline Module | UL 1703 | 350 | 321.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.38 | 47.5 | 8.94 | 39.1 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7456 | 38.3323 | 7.1975 | 35.8577 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19118 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM355M-66H | 355 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 355 | 328.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.41 | 43.49 | 9.63 | 36.87 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 1.8588 | 36.2211 | 7.3748 | 34.7396 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM355M-66HB | 355 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 355 | 329.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.37 | 43.68 | 9.66 | 36.76 | 45.3 | -0.37224 | 0.036979 | -0.29793 |  |  | 1.8842 | 36.3203 | 7.3679 | 35.3014 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM355M-66H-TV | 355 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 355 | 326.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 22 | 6 | N | 10.36 | 43.71 | 9.59 | 37.02 | 45.7 | -0.39847 | 0.065264 | -0.3165 |  |  | 1.8788 | 36.1655 | 7.803 | 33.6467 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM355M-66H-V | 355 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 355 | 328.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.41 | 43.49 | 9.63 | 36.87 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 1.8825 | 36.0285 | 7.3852 | 34.789 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM355M-6TL3 | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 355 | 329.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.52 | 39.81 | 10.71 | 33.15 | 45.4 | -0.374 | 0.0529 | -0.278 |  |  | 2.0639 | 32.1906 | 8.2159 | 31.0188 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM355M-6TL3-B | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 355 | 329.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.21 | 40.41 | 10.5 | 33.81 | 45.4 | -0.37469 | 0.067659 | -0.29152 |  |  | 2.0606 | 32.3706 | 8.2253 | 30.6038 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM355M-6TL3-V | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 329.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.52 | 39.81 | 10.71 | 33.15 | 45.3 | -0.374 | 0.0504 | -0.281 |  |  | 2.0688 | 32.1427 | 8.2011 | 30.9699 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM355M-72 | 355 W Monocrystalline Module | UL 1703 | 355 | 326.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.45 | 47.8 | 9.04 | 39.3 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8322 | 38.734 | 7.2868 | 35.8744 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19991 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM355M-72B | 355 W Monocrystalline Module | UL 1703 | 355 | 324.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.45 | 47.8 | 9.04 | 39.3 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7794 | 38.8795 | 7.2302 | 36.0258 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19488 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM355M-72B-J4 | 355 W Monocrystalline Module | UL 1703 | 355 | 324.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.45 | 47.8 | 9.04 | 39.3 | 46.2 | -0.417 | 0.069 | -0.308 | -0.009 | -0.415 | 1.7794 | 38.8795 | 7.2302 | 36.0258 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19488 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM355M-72H | 345 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 355 | 326.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.45 | 47.8 | 9.04 | 39.3 | 45 | -0.402 | 0.052 | -0.336 | 0.028 | -0.426 | 1.8168 | 37.7536 | 7.309 | 36.6002 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM355M-72HB | 370 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 355 | 326.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.45 | 47.8 | 9.04 | 39.3 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.8168 | 37.6581 | 7.2924 | 36.3392 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM355M-72HB-V | 355 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 355 | 325.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.45 | 47.8 | 9.04 | 39.3 | 45.3 | -0.41 | 0.059 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM355M-72H-V | 355 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 355 | 326.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.45 | 47.8 | 9.04 | 39.3 | 44.9 | -0.412 | 0.058 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM355M-72-J4 | 355 W Monocrystalline Module | UL 1703 | 355 | 326.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.45 | 47.8 | 9.04 | 39.3 | 44.9 | -0.41 | 0.0867 | -0.31 | 0.0298 | -0.436 | 1.736 | 38.642 | 7.2011 | 36.8096 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.18897 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM355M-72-V | 355 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 355 | 326.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.45 | 47.8 | 9.04 | 39.3 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 2.03 | 38.4245 | 7.4015 | 35.8177 | [6 empty] | 2017-08-01 | 2018-04-16
Jinko Solar Co., Ltd | JKM355PP-72H | 355 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 355 | 326 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.43 | 48.2 | 9.12 | 38.9 | 45.2 | -0.409 | 0.048 | -0.34 | 0.03 | -0.433 | 1.8161 | 38.0854 | 7.3372 | 36.4601 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM355PP-72H-V | 355 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 355 | 326.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.43 | 48.2 | 9.12 | 38.9 | 45.3 | -0.402 | 0.05 | -0.333 | 0.037 | -0.434 | 1.87 | 38.282 | 7.492 | 36.769 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKMS355M-72 | 355 W Monocrystalline Module | UL 1703 | 355 | 326.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.45 | 47.8 | 9.04 | 39.3 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7651 | 38.5284 | 7.278 | 36.0411 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19157 |  | 2018-04-02
Jinko Solar Co., Ltd | JKMS355M-72-J4 | 355 W Monocrystalline Module | UL 1703 | 355 | 326.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8355 | 72 | 1 | N | 9.45 | 47.8 | 9.04 | 39.3 | 45 | -0.416 | 0.0573 | -0.329 | 0.0102 | -0.424 | 1.7651 | 38.5284 | 7.278 | 36.0411 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19157 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM360M-66H | 360 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 360 | 333.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.48 | 43.58 | 9.74 | 36.97 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 1.8801 | 36.3193 | 7.459 | 34.8338 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM360M-66HB | 360 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 333.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.49 | 43.7 | 9.78 | 36.81 | 45.3 | -0.37224 | 0.036979 | -0.29793 |  |  | 1.9076 | 36.3697 | 7.4595 | 35.3494 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM360M-66H-TV | 360 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 360 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 22 | 6 | N | 10.44 | 43.75 | 9.7 | 37.12 | 45.7 | -0.39847 | 0.065264 | -0.3165 |  |  | 1.9003 | 36.2632 | 7.8925 | 33.7376 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM360M-66H-V | 360 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 360 | 333.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.48 | 43.58 | 9.74 | 36.97 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 1.904 | 36.1262 | 7.4696 | 34.8833 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM360M-6RL3-TV | 360 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 331.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 22 | 6 | N | 10.55 | 43.41 | 9.85 | 36.55 | 46.62 | -0.37388 | 0.03548 | -0.30273 |  |  | 1.8743 | 35.7629 | 7.2841 | 33.9695 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM360M-6TL3 | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 360 | 334.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.64 | 39.91 | 10.83 | 33.24 | 45.4 | -0.374 | 0.0529 | -0.278 |  |  | 2.087 | 32.278 | 8.308 | 31.103 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM360M-6TL3-B | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 334.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.31 | 40.57 | 10.6 | 33.97 | 45.4 | -0.37469 | 0.067659 | -0.29152 |  |  | 2.0802 | 32.5238 | 8.3037 | 30.7486 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM360M-6TL3-V | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 334.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.64 | 39.91 | 10.83 | 33.24 | 45.3 | -0.374 | 0.0504 | -0.281 |  |  | 2.092 | 32.23 | 8.293 | 31.054 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM360M-72 | 360 W Monocrystalline Module | UL 1703 | 360 | 331.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.51 | 48 | 9.12 | 39.5 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8484 | 38.9312 | 7.3513 | 36.057 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19989 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM360M-72H | 345 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 360 | 331.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.51 | 48 | 9.12 | 39.5 | 45 | -0.402 | 0.052 | -0.336 | 0.028 | -0.426 | 1.8328 | 37.9457 | 7.3736 | 36.7865 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM360M-72HB | 370 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 360 | 331.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.51 | 48 | 9.12 | 39.5 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.8328 | 37.8497 | 7.3569 | 36.5241 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM360M-72HB-V | 360 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 360 | 330.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.51 | 48 | 9.12 | 39.5 | 45.3 | -0.41 | 0.059 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM360M-72H-V | 360 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 360 | 331 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.51 | 48 | 9.12 | 39.5 | 44.9 | -0.412 | 0.058 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM360M-72-V | 360 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 360 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.51 | 48 | 9.12 | 39.5 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 2.048 | 38.62 | 7.467 | 36 | [6 empty] | 2017-08-01 | 2018-04-16
Jinko Solar Co., Ltd | JKM360N-6RL3-B | 360 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 332.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.44 | 44.12 | 9.86 | 36.51 | 46.62 | -0.36636 | 0.047539 | -0.30144 |  |  | 1.9284 | 35.2131 | 7.5848 | 33.1778 | [6 empty] | 2020-12-11 | 2021-02-22
Jinko Solar Co., Ltd | JKM360PP-72H | 360 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 360 | 330.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.51 | 48.5 | 9.21 | 39.1 | 45.2 | -0.409 | 0.048 | -0.34 | 0.03 | -0.433 | 1.8341 | 38.2812 | 7.4096 | 36.6475 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM360PP-72H-V | 360W Polycrystalline module | UL 1703 | 360 | 331.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.51 | 48.5 | 9.21 | 39.1 | 45.3 | -0.402 | 0.05 | -0.333 | 0.037 | -0.434 | 1.87 | 38.282 | 7.492 | 36.769 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM365M-66H | 365 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 365 | 338.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.55 | 43.66 | 9.85 | 37.06 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 1.9013 | 36.4078 | 7.5433 | 34.9186 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM365M-66HB | 365 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 338.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.61 | 43.73 | 9.9 | 36.87 | 45.3 | -0.37224 | 0.036979 | -0.29793 |  |  | 1.931 | 36.429 | 7.551 | 35.407 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM365M-66H-TV | 365 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 336 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 22 | 6 | N | 10.52 | 43.83 | 9.81 | 37.21 | 45.7 | -0.39847 | 0.065264 | -0.3165 |  |  | 1.9219 | 36.3512 | 7.982 | 33.8194 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM365M-66H-V | 365 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 338.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.55 | 43.66 | 9.85 | 37.06 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 1.9255 | 36.2142 | 7.5539 | 34.9682 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM365M-6RL3 | 365 W, 132 half-cut cell, monocrystalline module, 1000V max system Vdc | UL 61730 | 365 | 336.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.94 | 43.32 | 10.14 | 36 | 46.84 | -0.37396 | 0.033484 | -0.29983 | 1.936 | 35.5219 | 1.936 | 35.5219 | 7.5999 | 33.153 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM365M-6RL3-B | 365 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 337 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.79 | 43.92 | 9.97 | 36.61 | 46.72 | -0.36372 | 0.047134 | -0.29968 |  |  | 1.933 | 35.9889 | 7.6421 | 33.4431 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM365M-6RL3-TV | 365 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 336.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 22 | 6 | N | 10.65 | 43.49 | 9.97 | 36.61 | 46.62 | -0.37388 | 0.03548 | -0.30273 |  |  | 1.8972 | 35.8216 | 7.3728 | 34.0252 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM365M-6RL3-V | 365 W, 132 half-cut cell, monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 336.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.94 | 43.32 | 10.14 | 36 | 46.84 | -0.37396 | 0.033484 | -0.29983 |  |  | 1.936 | 35.5219 | 7.5999 | 33.153 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM365M-6TL3 | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 365 | 338.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.76 | 40.01 | 10.95 | 33.34 | 45.4 | -0.374 | 0.0529 | -0.278 |  |  | 2.1101 | 32.3751 | 8.4001 | 31.1966 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM365M-6TL3-B | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 338.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.41 | 40.72 | 10.7 | 34.12 | 45.4 | -0.37469 | 0.067659 | -0.29152 |  |  | 2.0999 | 32.6674 | 8.382 | 30.8844 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM365M-6TL3-V | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 339.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 20 | 6 | N | 11.76 | 40.01 | 10.95 | 33.34 | 45.3 | -0.374 | 0.0504 | -0.281 |  |  | 2.1152 | 32.327 | 8.3849 | 31.1474 | [6 empty] | 2020-12-11
Jinko Solar Co., Ltd | JKM365M-72 | 365 W Monocrystalline Module | UL 1703 | 365 | 336.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.8355 | 72 | 1 | N | 9.57 | 48.2 | 9.2 | 39.7 | 44.9 | -0.409 | 0.065 | -0.308 | 0.041 | -0.429 | 1.8647 | 39.1283 | 7.4158 | 36.2395 | Rack | Flat Plate | 0.954 | 1.924 | 1 | 0.19989 |  | 2018-04-02
Jinko Solar Co., Ltd | JKM365M-72H | 350 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 365 | 336.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.57 | 48.2 | 9.2 | 39.7 | 45 | -0.402 | 0.052 | -0.336 | 0.028 | -0.426 | 1.8489 | 38.1379 | 7.4383 | 36.9727 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM365M-72HB | 375 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 365 | 335.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.57 | 48.2 | 9.2 | 39.7 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.8489 | 38.0414 | 7.4215 | 36.7091 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM365M-72HB-V | 365 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 365 | 335.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.57 | 48.2 | 9.2 | 39.7 | 45.3 | -0.41 | 0.059 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM365M-72H-V | 365 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 365 | 335.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.57 | 48.2 | 9.2 | 39.7 | 44.9 | -0.412 | 0.058 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM365M-72-V | 365 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 365 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.57 | 48.2 | 9.2 | 39.7 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 2.066 | 38.8155 | 7.5325 | 36.1823 | [6 empty] | 2017-08-01 | 2018-04-16
Jinko Solar Co., Ltd | JKM365N-6RL3 | 365 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 365 | 336.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.03 | 43.95 | 10.2 | 35.79 | 46.64 | -0.37357 | 0.040072 | -0.30121 |  |  | 1.931 | 35.8423 | 7.5521 | 33.6144 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM365N-6RL3-B | 365 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 336.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.52 | 44.33 | 9.94 | 36.72 | 46.62 | -0.36636 | 0.047539 | -0.30144 |  |  | 1.9441 | 35.4157 | 7.6464 | 33.3687 | [6 empty] | 2020-12-11 | 2021-02-22
Jinko Solar Co., Ltd | JKM365N-6RL3-V | 365 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.03 | 43.95 | 10.2 | 35.79 | 46.58 | -0.38015 | 0.03911 | -0.30172 |  |  | 1.9291 | 35.6774 | 7.5391 | 33.3082 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM365PP-72H | 365 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 365 | 335.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.58 | 48.8 | 9.29 | 39.3 | 45.2 | -0.409 | 0.048 | -0.34 | 0.03 | -0.433 | 1.85 | 38.477 | 7.474 | 36.835 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM365PP-72H-V | 365 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 365 | 335.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.58 | 48.8 | 9.29 | 39.3 | 45.3 | -0.402 | 0.05 | -0.333 | 0.037 | -0.434 | 1.87 | 38.282 | 7.492 | 36.769 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM370M-66H | 370 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 370 | 342.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.62 | 43.75 | 9.96 | 37.15 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 1.9225 | 36.4962 | 7.6275 | 35.0034 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM370M-66H-TV | 370 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 340.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 22 | 6 | N | 10.6 | 43.92 | 9.92 | 37.3 | 45.7 | -0.39847 | 0.065264 | -0.3165 |  |  | 1.9434 | 36.4391 | 8.0715 | 33.9012 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM370M-66H-V | 370 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 342.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.62 | 43.75 | 9.96 | 37.15 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 1.947 | 36.3021 | 7.6383 | 35.0532 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM370M-6RL3 | 370 W, 132 half-cut cell, monocrystalline module, 1000V max system Vdc | UL 61730 | 370 | 340.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.03 | 43.41 | 10.25 | 36.1 | 46.84 | -0.37396 | 0.033484 | -0.29983 | 1.957 | 35.6206 | 1.957 | 35.6206 | 7.6823 | 33.2451 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM370M-6RL3-B | 370 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 370 | 341.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.9 | 44.02 | 10.08 | 36.71 | 46.72 | -0.36372 | 0.047134 | -0.29968 |  |  | 1.9543 | 36.0872 | 7.7264 | 33.5344 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM370M-6RL3-TV | 370 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 341 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 22 | 6 | N | 10.75 | 43.58 | 10.09 | 36.67 | 46.62 | -0.37388 | 0.03548 | -0.30273 |  |  | 1.92 | 35.8803 | 7.4616 | 34.081 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM370M-6RL3-V | 370 W, 132 half-cut cell, monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 340.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.03 | 43.41 | 10.25 | 36.1 | 46.84 | -0.37396 | 0.033484 | -0.29983 |  |  | 1.957 | 35.6206 | 7.6823 | 33.2451 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM370M-72 | 370 W, 72 cell Monocrystalline module, white substrate | UL 1703 | 370 | 341.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.61 | 48.5 | 9.28 | 39.9 | 44.9 | -0.396 | 0.058 | -0.314 | 0.016 | -0.419 | 1.7591 | 38.1759 | 7.5703 | 35.3977 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM370M-72BL | 370 W, 72 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 370 | 341.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.61 | 48.5 | 9.28 | 39.9 | 45.4 | -0.39107 | 0.04463 | -0.30935 |  |  | 1.8745 | 37.5127 | 7.3414 | 35.8955 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM370M-72H | 370 W, 144 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 370 | 341 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.61 | 48.5 | 9.28 | 39.9 | 45 | -0.402 | 0.05 | -0.336 | 0.028 | -0.426 | 1.865 | 38.33 | 7.503 | 37.159 | [6 empty] | 2018-04-02 | 2018-07-02
Jinko Solar Co., Ltd | JKM370M-72HB | 370 W, 144 half cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 370 | 340.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.61 | 48.5 | 9.28 | 39.9 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.865 | 38.233 | 7.486 | 36.894 | [6 empty] | 2018-04-02 | 2018-07-02
Jinko Solar Co., Ltd | JKM370M-72HBL | 370 W, 72 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 370 | 340.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 9.61 | 48.5 | 9.28 | 39.9 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.8647 | 37.4295 | 7.3264 | 36.1884 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM370M-72HBL-Q | 370 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 370 | 340.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.15 | 47.8 | 9.59 | 38.58 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.8686 | 37.4458 | 7.3039 | 36.4363 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM370M-72HB-V | 370 W, 144 half cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 370 | 340 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.61 | 48.5 | 9.28 | 39.9 | 45.3 | -0.41 | 0.06 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-07-02
Jinko Solar Co., Ltd | JKM370M-72H-V | 370 W, 144 half cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 340.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.61 | 48.5 | 9.28 | 39.9 | 44.9 | -0.412 | 0.06 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-07-02
Jinko Solar Co., Ltd | JKM370M-72L | 370 W, 72 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 370 | 339.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.61 | 48.5 | 9.28 | 39.9 | 45.6 | -0.406 | 0.067 | -0.311 | 0.012 | -0.416 | 1.7793 | 37.6801 | 7.54 | 34.7267 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM370M-72L-V | 370 W, 72 cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 370 | 340.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.61 | 48.5 | 9.28 | 39.9 | 45.5 | -0.402 | 0.05 | -0.3 | 0.01 | -0.411 | 1.8184 | 37.8705 | 7.4418 | 35.4076 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM370M-72-V | 370 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 370 | 340.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.61 | 48.5 | 9.28 | 39.9 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 2.0839 | 39.0111 | 7.598 | 36.3646 | [6 empty] | 2018-04-16
Jinko Solar Co., Ltd | JKM370N-6RL3 | 370 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 370 | 341.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.13 | 44.14 | 10.32 | 35.86 | 46.64 | -0.37357 | 0.040072 | -0.30121 |  |  | 1.9537 | 35.9124 | 7.6409 | 33.6801 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM370N-6RL3-B | 370 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 370 | 341.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.6 | 44.54 | 10.02 | 36.93 | 46.62 | -0.36636 | 0.047539 | -0.30144 |  |  | 1.9597 | 35.6182 | 7.7079 | 33.5595 | [6 empty] | 2020-12-11 | 2021-02-22
Jinko Solar Co., Ltd | JKM370N-6RL3-V | 370 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 340.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.13 | 44.14 | 10.32 | 35.86 | 46.58 | -0.38015 | 0.03911 | -0.30172 |  |  | 1.9518 | 35.7472 | 7.6278 | 33.3734 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM370PP-72H | 370 W Polycrystalline module, 1000V max system Vdc | UL 1703 | 370 | 340.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.63 | 49.1 | 9.37 | 39.5 | 45.2 | -0.409 | 0.048 | -0.34 | 0.03 | -0.433 | 1.8659 | 38.6728 | 7.5384 | 37.0225 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM370PP-72H-V | 370 W Polycrystalline module, 1500V max system Vdc | UL 1703 | 370 | 340.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9 | 144 |  | N | 9.63 | 49.1 | 9.37 | 39.5 | 45.3 | -0.402 | 0.05 | -0.333 | 0.037 | -0.434 | 1.87 | 38.282 | 7.492 | 36.769 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKMS370M-72L-TI | 370 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 370 | 339.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.61 | 48.5 | 9.28 | 39.9 | 45.6 | -0.406 | 0.067 | -0.311 |  |  | 1.7793 | 37.6801 | 7.54 | 34.7267 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS370M-72L-V-MX3 | 370 W, 72 cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 370 | 340.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.61 | 48.5 | 9.28 | 39.9 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8184 | 37.8705 | 7.4418 | 35.4076 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS370M-72L-V-TI | 370 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 370 | 340.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.61 | 48.5 | 9.28 | 39.9 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8184 | 37.8705 | 7.4418 | 35.4076 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKM375M-66H | 375 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 375 | 347.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.69 | 44.02 | 10.07 | 37.24 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 1.9438 | 36.5846 | 7.7118 | 35.0882 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM375M-66H-TV | 375 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 22 | 6 | N | 10.68 | 44 | 10.03 | 37.39 | 45.7 | -0.39847 | 0.065264 | -0.3165 |  |  | 1.965 | 36.527 | 8.161 | 33.983 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM375M-66H-V | 375 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 347.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.69 | 44.02 | 10.07 | 37.24 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 1.9685 | 36.3901 | 7.7226 | 35.1381 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM375M-6RL3 | 375 W, 132 half-cut cell, monocrystalline module, 1000V max system Vdc | UL 61730 | 375 | 345.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.12 | 43.49 | 10.36 | 36.2 | 46.84 | -0.37396 | 0.033484 | -0.29983 | 1.978 | 35.7192 | 1.978 | 35.7192 | 7.7648 | 33.3372 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM375M-6RL3-B | 375 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 375 | 346.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.01 | 44.12 | 10.19 | 36.8 | 46.72 | -0.36372 | 0.047134 | -0.29968 |  |  | 1.9757 | 36.1757 | 7.8107 | 33.6167 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM375M-6RL3-TV | 375 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 345.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 22 | 6 | N | 10.85 | 43.66 | 10.21 | 36.73 | 46.62 | -0.37388 | 0.03548 | -0.30273 |  |  | 1.9428 | 35.939 | 7.5503 | 34.1368 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM375M-6RL3-V | 375 W, 132 half-cut cell, monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 345.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.12 | 43.49 | 10.36 | 36.2 | 46.84 | -0.37396 | 0.033484 | -0.29983 |  |  | 1.978 | 35.7192 | 7.7648 | 33.3372 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM375M-72 | 375 W, 72 cell Monocrystalline module, white substrate | UL 1703 | 375 | 346.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 44.9 | -0.396 | 0.058 | -0.314 | 0.016 | -0.419 | 1.7686 | 38.463 | 7.6111 | 35.6639 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM375M-72BL | 375 W, 72 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 375 | 345.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.4 | -0.39107 | 0.04463 | -0.30935 |  |  | 1.8846 | 37.7948 | 7.381 | 36.1654 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM375M-72H | 355 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 375 | 345.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 45 | -0.402 | 0.052 | -0.336 | 0.028 | -0.426 | 1.875 | 38.6182 | 7.5434 | 37.4384 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM375M-72HB | 380 W Monocrystalline module, black substrate, 1000V max system Vdc | UL 1703 | 375 | 345.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.875 | 38.5205 | 7.5263 | 37.1714 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM375M-72HBL | 375 W, 72 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 375 | 345.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.8747 | 37.7109 | 7.3658 | 36.4605 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM375M-72HBL-Q | 375 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 375 | 345.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.23 | 48 | 9.65 | 38.86 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.8803 | 37.7176 | 7.3496 | 36.7008 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM375M-72HB-V | 375 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 375 | 344.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.3 | -0.41 | 0.059 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM375M-72HL | 375 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 375 | 346.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 144 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.1 | -0.39 | 0.063 | -0.34 | 0.022 | -0.412 | 1.8855 | 37.3646 | 7.6399 | 35.7042 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM375M-72HL-BDVP | 375 W, 144 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 375 | 344.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.14 | 47.92 | 9.56 | 39.25 | 45.3 | -0.409 | 0.056 | -0.313 |  |  | 1.7012 | 38.9498 | 7.4537 | 36.4583 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM375M-72HL-Q | 375 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 375 | 346.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.23 | 48 | 9.65 | 38.86 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9053 | 37.7416 | 7.3203 | 36.1314 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM375M-72HL-TV | 375 W, 144 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 375 | 344.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 9.92 | 47.92 | 9.56 | 39.25 | 45.2 | -0.412 | 0.048 | -0.322 |  |  | 1.7376 | 39.3328 | 7.594 | 37.2121 | [6 empty] | 2019-11-01 | 2020-03-02
Jinko Solar Co., Ltd | JKM375M-72HL-TV-Q | 375 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 375 | 343.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 9.92 | 47.92 | 9.56 | 39.25 | 45.2 | -0.42063 | 0.043554 | -0.30915 |  |  | 1.9525 | 38.2605 | 7.5812 | 36.3544 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM375M-72HL-V | 375 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 375 | 347.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 144 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.1 | -0.372 | 0.064 | -0.322 | 0.038 | -0.41 | 1.8855 | 37.3646 | 7.6594 | 35.6265 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM375M-72HL-V-Q | 375 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.23 | 48 | 9.65 | 38.86 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.8919 | 37.8346 | 7.5192 | 36.6925 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM375M-72H-V | 375 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 375 | 345.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 44.9 | -0.412 | 0.058 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM375M-72L | 375 W, 72 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 375 | 344.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.6 | -0.406 | 0.067 | -0.311 | 0.012 | -0.416 | 1.7889 | 37.9634 | 7.5806 | 34.9878 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM375M-72L-V | 375 W, 72 cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 375 | 344.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.5 | -0.402 | 0.05 | -0.3 | 0.01 | -0.411 | 1.8282 | 38.1553 | 7.4819 | 35.6738 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM375M-72-V | 375 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 375 | 345.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.68 | 48.7 | 9.33 | 40.2 | 45 | -0.408 | 0.064 | -0.306 | 0.013 | -0.42 | 2.0952 | 39.3044 | 7.6389 | 36.638 | [6 empty] | 2018-04-16
Jinko Solar Co., Ltd | JKM375N-6RL3 | 375 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 375 | 345.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.23 | 44.32 | 10.44 | 35.92 | 46.64 | -0.37357 | 0.040072 | -0.30121 |  |  | 1.9764 | 35.9725 | 7.7298 | 33.7365 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM375N-6RL3-B | 375 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 375 | 346.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.68 | 44.74 | 10.1 | 37.13 | 46.62 | -0.36636 | 0.047539 | -0.30144 |  |  | 1.9754 | 35.8111 | 7.7695 | 33.7413 | [6 empty] | 2020-12-11 | 2021-02-22
Jinko Solar Co., Ltd | JKM375N-6RL3-V | 375 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 345.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.23 | 44.32 | 10.44 | 35.92 | 46.58 | -0.38015 | 0.03911 | -0.30172 |  |  | 1.9745 | 35.807 | 7.7165 | 33.4292 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKMS375M-72HL-TI | 375 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 375 | 346.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.1 | -0.39 | 0.063 | -0.34 |  |  | 1.8855 | 37.3646 | 7.6399 | 35.7042 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS375M-72HL-TI-Q | 375 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 375 | 346.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.23 | 48.7 | 9.33 | 40.2 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9158 | 37.5125 | 7.619 | 35.912 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS375M-72HL-V-MX3 | 375 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 375 | 347.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.8855 | 37.3646 | 7.6594 | 35.6265 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS375M-72HL-V-MX3-Q | 375 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 375 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.23 | 48.7 | 9.33 | 40.2 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9024 | 37.6049 | 7.5606 | 36.4697 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS375M-72HL-V-TI | 375 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 375 | 347.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.8855 | 37.3646 | 7.6594 | 35.6265 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS375M-72HL-V-TI-Q | 375 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1500V max system Vdc | UL 1741 | 375 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.23 | 48.7 | 9.33 | 40.2 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9024 | 37.6049 | 7.5606 | 36.4697 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS375M-72L-TI | 375 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 375 | 344.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.6 | -0.406 | 0.067 | -0.311 |  |  | 1.7889 | 37.9634 | 7.5806 | 34.9878 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS375M-72L-V-MX3 | 375 W, 72 cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 375 | 344.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8282 | 38.1553 | 7.4819 | 35.6738 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS375M-72L-V-TI | 375 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 375 | 344.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.68 | 48.7 | 9.33 | 40.2 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8282 | 38.1553 | 7.4819 | 35.6738 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKM380M-66H | 380 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 380 | 352.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.77 | 44.09 | 10.18 | 37.33 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 1.965 | 36.673 | 7.796 | 35.173 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM380M-66H-TV | 380 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 350.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 22 | 6 | N | 10.76 | 44.11 | 10.14 | 37.48 | 45.7 | -0.39847 | 0.065264 | -0.3165 |  |  | 1.9866 | 36.6149 | 8.2505 | 34.0648 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM380M-66H-V | 380 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 352.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.77 | 44.09 | 10.18 | 37.33 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 1.99 | 36.478 | 7.807 | 35.223 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM380M-6RL3 | 380 W, 132 half-cut cell, monocrystalline module, 1000V max system Vdc | UL 61730 | 380 | 350.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.21 | 43.58 | 10.47 | 36.3 | 46.84 | -0.37396 | 0.033484 | -0.29983 | 1.999 | 35.8179 | 1.999 | 35.8179 | 7.8472 | 33.4293 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM380M-6RL3-B | 380 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 380 | 351.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.12 | 44.22 | 10.3 | 36.9 | 46.72 | -0.36372 | 0.047134 | -0.29968 |  |  | 1.997 | 36.274 | 7.895 | 33.708 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM380M-6RL3-TV | 380 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 350.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 22 | 6 | N | 10.95 | 43.75 | 10.33 | 36.79 | 46.62 | -0.37388 | 0.03548 | -0.30273 |  |  | 1.9657 | 35.9977 | 7.639 | 34.1925 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM380M-6RL3-V | 380 W, 132 half-cut cell, monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 350.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.21 | 43.58 | 10.47 | 36.3 | 46.84 | -0.37396 | 0.033484 | -0.29983 |  |  | 1.999 | 35.8179 | 7.8472 | 33.4293 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM380M-72 | 380 W, 72 cell Monocrystalline module, white substrate | UL 1703 | 380 | 351.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.75 | 48.9 | 9.39 | 40.5 | 44.9 | -0.396 | 0.058 | -0.314 | 0.016 | -0.419 | 1.78 | 38.75 | 7.66 | 35.93 | [6 empty] | 2018-06-15
Jinko Solar Co., Ltd | JKM380M-72BL | 380 W, 72 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 380 | 350.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.4 | -0.39107 | 0.04463 | -0.30935 |  |  | 1.8967 | 38.0768 | 7.4284 | 36.4353 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM380M-72H | 355 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 380 | 350.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.75 | 48.9 | 9.39 | 40.5 | 45 | -0.402 | 0.052 | -0.336 | 0.028 | -0.426 | 1.8871 | 38.9064 | 7.5919 | 37.7178 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM380M-72HB | 380 W Monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 380 | 350.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.8871 | 38.8079 | 7.5747 | 37.4488 | [6 empty] | 2018-04-02
Jinko Solar Co., Ltd | JKM380M-72HBL | 380 W, 72 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 380 | 350.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.8868 | 37.9923 | 7.4132 | 36.7326 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM380M-72HBL-Q | 380 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 380 | 349.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.3 | 48.2 | 9.72 | 39.1 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.8939 | 37.9505 | 7.4029 | 36.9275 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM380M-72HB-V | 380 W Monocrystalline module, black substrate, 1500V max system Vdc | UL 1703 | 380 | 349.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.3 | -0.41 | 0.059 | -0.33 | -0.02 | -0.428 | 1.87 | 38.33 | 7.517 | 36.712 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM380M-72HL | 380 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 380 | 350.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 144 |  | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.1 | -0.39 | 0.063 | -0.34 | 0.022 | -0.412 | 1.8977 | 37.6435 | 7.689 | 35.9707 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM380M-72HL-BDVP | 380 W, 144 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 380 | 349.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.23 | 47.96 | 9.66 | 39.36 | 45.3 | -0.409 | 0.056 | -0.313 |  |  | 1.719 | 39.059 | 7.5317 | 36.5605 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM380M-72HL-Q | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 380 | 351.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.3 | 48.2 | 9.72 | 39.1 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9191 | 37.9747 | 7.3734 | 36.3545 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM380M-72HL-TV | 380 W, 144 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 380 | 349 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.02 | 47.96 | 9.66 | 39.36 | 45.2 | -0.412 | 0.048 | -0.322 |  |  | 1.7557 | 39.443 | 7.6735 | 37.3164 | [6 empty] | 2019-11-01 | 2020-03-02
Jinko Solar Co., Ltd | JKM380M-72HL-TV-Q | 380 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 380 | 348.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.02 | 47.96 | 9.66 | 39.36 | 45.2 | -0.42063 | 0.043554 | -0.30915 |  |  | 1.9729 | 38.3677 | 7.6605 | 36.4562 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM380M-72HL-V | 380 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 380 | 352.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 144 |  | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.1 | -0.372 | 0.064 | -0.322 | 0.038 | -0.41 | 1.8977 | 37.6435 | 7.7086 | 35.8924 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM380M-72HL-V-Q | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 350.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.3 | 48.2 | 9.72 | 39.1 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9057 | 38.0683 | 7.5737 | 36.9191 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM380M-72H-V | 380 W Monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 380 | 349.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.75 | 48.9 | 9.39 | 40.5 | 44.9 | -0.412 | 0.058 | -0.337 | 0.028 | -0.438 | 1.87 | 38.282 | 7.463 | 36.914 | [6 empty] | 2018-02-15 | 2018-04-02
Jinko Solar Co., Ltd | JKM380M-72L | 380 W, 72 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 380 | 349.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.6 | -0.406 | 0.067 | -0.311 | 0.012 | -0.416 | 1.8004 | 38.2467 | 7.6294 | 35.2489 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM380M-72L-V | 380 W, 72 cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 380 | 349.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.5 | -0.402 | 0.05 | -0.3 | 0.01 | -0.411 | 1.84 | 38.44 | 7.53 | 35.94 | [6 empty] | 2018-10-01 | 2019-09-16
Jinko Solar Co., Ltd | JKM380M-72-V | 380 W, 72 cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 380 | 350.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.2 | -0.394 | 0.055 | -0.326 | 0.001 | -0.395 | 1.9 | 38.28 | 7.06 | 36.3 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM380N-6RL3 | 380 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 380 | 350.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.33 | 44.51 | 10.56 | 35.99 | 46.64 | -0.37357 | 0.040072 | -0.30121 |  |  | 1.9991 | 36.0426 | 7.8186 | 33.8022 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM380N-6RL3-B | 380 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 380 | 351.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.76 | 44.94 | 10.18 | 37.33 | 46.62 | -0.36636 | 0.047539 | -0.30144 |  |  | 1.991 | 36.004 | 7.831 | 33.923 | [6 empty] | 2020-12-11 | 2021-02-22
Jinko Solar Co., Ltd | JKM380N-6RL3-V | 380 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 350.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.33 | 44.51 | 10.56 | 35.99 | 46.58 | -0.38015 | 0.03911 | -0.30172 |  |  | 1.9972 | 35.8768 | 7.8052 | 33.4943 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM380N-72H-MBB-B | 380W Monocrystalline module with N-type solar cells and black color backsheet，1000V max system Vdc. | UL 61730 | 380 | 344.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.36 | 47.75 | 9.61 | 39.55 | 46.7 | -0.44106 | 0.049402 | -0.3206 |  |  | 1.8759 | 39.0225 | 7.6678 | 36.0453 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKMS380M-72HL-TI | 380 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 380 | 350.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.1 | -0.39 | 0.063 | -0.34 |  |  | 1.8977 | 37.6435 | 7.689 | 35.9707 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS380M-72HL-TI-Q | 380 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 380 | 351.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.3 | 48.9 | 9.39 | 40.5 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9281 | 37.7924 | 7.668 | 36.18 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS380M-72HL-V-MX3 | 380 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 380 | 352.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.8977 | 37.6435 | 7.7086 | 35.8924 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS380M-72HL-V-MX3-Q | 380 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 380 | 350.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.3 | 48.9 | 9.39 | 40.5 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9146 | 37.8856 | 7.6093 | 36.7419 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS380M-72HL-V-TI | 380 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 380 | 352.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.8977 | 37.6435 | 7.7086 | 35.8924 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS380M-72HL-V-TI-Q | 380 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1500V max system Vdc | UL 1741 | 380 | 350.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.3 | 48.9 | 9.39 | 40.5 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9146 | 37.8856 | 7.6093 | 36.7419 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS380M-72L-TI | 380 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 380 | 349.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.6 | -0.406 | 0.067 | -0.311 |  |  | 1.8004 | 38.2467 | 7.6294 | 35.2489 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS380M-72L-V-MX3 | 380 W, 72 cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 380 | 349.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.84 | 38.44 | 7.53 | 35.94 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS380M-72L-V-TI | 380 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 380 | 349.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.75 | 48.9 | 9.39 | 40.5 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.84 | 38.44 | 7.53 | 35.94 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKM385M-66H | 385 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 385 | 357.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.83 | 44.17 | 10.29 | 37.42 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 1.9862 | 36.7614 | 7.8802 | 35.2578 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM385M-66H-V | 385 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 357.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.83 | 44.17 | 10.29 | 37.42 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 2.0115 | 36.5659 | 7.8914 | 35.3079 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM385M-6RL3 | 385 W, 132 half-cut cell, monocrystalline module, 1000V max system Vdc | UL 61730 | 385 | 355.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.3 | 43.66 | 10.58 | 36.39 | 46.84 | -0.37396 | 0.033484 | -0.29983 | 2.02 | 35.9067 | 2.02 | 35.9067 | 7.9297 | 33.5121 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM385M-6RL3-B | 385 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 385 | 356 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.22 | 44.34 | 10.4 | 37.02 | 46.72 | -0.36372 | 0.047134 | -0.29968 |  |  | 2.0164 | 36.392 | 7.9717 | 33.8176 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM385M-6RL3-TV | 385 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 355.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 22 | 6 | N | 11.05 | 43.83 | 10.45 | 36.85 | 46.62 | -0.37388 | 0.03548 | -0.30273 |  |  | 1.9885 | 36.0564 | 7.7278 | 34.2483 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM385M-6RL3-V | 385 W, 132 half-cut cell, monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 355.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.3 | 43.66 | 10.58 | 36.39 | 46.84 | -0.37396 | 0.033484 | -0.29983 |  |  | 2.02 | 35.9067 | 7.9297 | 33.5121 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM385M-72BL | 385 W, 72 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 385 | 355.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.4 | -0.39107 | 0.04463 | -0.30935 |  |  | 1.9068 | 38.3589 | 7.468 | 36.7052 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM385M-72H | 385 W, 144 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 385 | 355.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.92 | 49.1 | 9.44 | 40.8 | 45 | -0.402 | 0.05 | -0.336 | 0.028 | -0.426 | 1.8972 | 39.1946 | 7.6324 | 37.9972 | [6 empty] | 2018-07-02
Jinko Solar Co., Ltd | JKM385M-72HB | 385 W, 144 half cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 385 | 354.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.3 | -0.402 | 0.056 | -0.331 | 0.035 | -0.43 | 1.8972 | 39.0954 | 7.6151 | 37.7262 | [6 empty] | 2018-07-02
Jinko Solar Co., Ltd | JKM385M-72HBL | 385 W, 72 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 385 | 354.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.8968 | 38.2737 | 7.4527 | 37.0047 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM385M-72HBL-Q | 385 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 385 | 354.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.38 | 48.4 | 9.78 | 39.37 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.9056 | 38.2126 | 7.4486 | 37.1824 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM385M-72HB-V | 385 W, 144 half cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 1703 | 385 | 354.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.3 | -0.41 | 0.06 | -0.33 | -0.02 | -0.428 | 1.9022 | 39.1946 | 7.6466 | 37.5401 | [6 empty] | 2018-07-02
Jinko Solar Co., Ltd | JKM385M-72HL | 385 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 385 | 355.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 144 |  | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.1 | -0.39 | 0.063 | -0.34 | 0.022 | -0.412 | 1.9078 | 37.9223 | 7.7299 | 36.2371 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM385M-72HL-BDVP | 385 W, 144 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 385 | 353.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.32 | 48.1 | 9.76 | 39.5 | 45.3 | -0.409 | 0.056 | -0.313 |  |  | 1.7368 | 39.1979 | 7.6096 | 36.6905 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM385M-72HL-Q | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 385 | 355.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.38 | 48.4 | 9.78 | 39.37 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9309 | 38.2369 | 7.4189 | 36.6055 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM385M-72HL-TV | 385 W, 144 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 385 | 353.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.08 | 48.1 | 9.76 | 39.5 | 45.2 | -0.412 | 0.048 | -0.322 |  |  | 1.7739 | 39.5833 | 7.7529 | 37.4491 | [6 empty] | 2019-11-01 | 2020-03-02
Jinko Solar Co., Ltd | JKM385M-72HL-TV-Q | 385 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 385 | 353.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.08 | 48.1 | 9.76 | 39.5 | 45.2 | -0.42063 | 0.043554 | -0.30915 |  |  | 1.9933 | 38.5042 | 7.7398 | 36.5859 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM385M-72HL-V | 385 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 385 | 357.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 144 |  | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.1 | -0.372 | 0.064 | -0.322 | 0.038 | -0.41 | 1.9078 | 37.9223 | 7.7497 | 36.1583 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM385M-72HL-V-Q | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 355 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.38 | 48.4 | 9.78 | 39.37 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9174 | 38.3312 | 7.6205 | 37.174 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM385M-72H-V | 385 W, 144 half cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 354.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 144 |  | N | 9.92 | 49.1 | 9.44 | 40.8 | 44.9 | -0.412 | 0.06 | -0.337 | 0.028 | -0.438 | 1.9022 | 39.1455 | 7.5917 | 37.7466 | [6 empty] | 2018-07-02
Jinko Solar Co., Ltd | JKM385M-72L | 385 W, 72 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 385 | 353.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.6 | -0.406 | 0.067 | -0.311 | 0.012 | -0.416 | 1.81 | 38.53 | 7.67 | 35.51 | [6 empty] | 2018-11-15 | 2019-09-03
Jinko Solar Co., Ltd | JKM385M-72L-V | 385 W, 72 cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 385 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.5 | -0.402 | 0.05 | -0.3 | 0.01 | -0.411 | 1.8498 | 38.7247 | 7.5701 | 36.2062 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM385M-72-V | 385 W, 72 cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 385 | 355.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 |  | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.2 | -0.394 | 0.055 | -0.326 | 0.001 | -0.395 | 1.9101 | 38.5636 | 7.0976 | 36.5689 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM385N-6RL3 | 385 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 385 | 355.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.43 | 44.69 | 10.68 | 36.05 | 46.64 | -0.37357 | 0.040072 | -0.30121 |  |  | 2.0218 | 36.1027 | 7.9075 | 33.8585 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM385N-6RL3-B | 385 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 385 | 356 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.84 | 45.14 | 10.26 | 37.53 | 46.62 | -0.36636 | 0.047539 | -0.30144 |  |  | 2.0066 | 36.1969 | 7.8925 | 34.1047 | [6 empty] | 2020-12-11 | 2021-02-22
Jinko Solar Co., Ltd | JKM385N-6RL3-V | 385 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 354.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.43 | 44.69 | 10.68 | 36.05 | 46.58 | -0.38015 | 0.03911 | -0.30172 |  |  | 2.0199 | 35.9366 | 7.8939 | 33.5502 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM385N-72H-MBB | 385 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 385 | 350.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.42 | 47.9 | 9.71 | 39.65 | 46.46 | -0.43521 | 0.037516 | -0.30533 |  |  | 1.9047 | 38.8767 | 7.8305 | 35.3538 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM385N-72H-MBB-B | 385 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 385 | 349.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.42 | 47.9 | 9.71 | 39.65 | 46.7 | -0.44106 | 0.049402 | -0.3206 |  |  | 1.8954 | 39.1211 | 7.7476 | 36.1365 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM385N-72H-MBB-V | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 350.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.42 | 47.9 | 9.71 | 39.65 | 45.89 | -0.4371 | 0.037545 | -0.31171 |  |  | 1.9028 | 39.0761 | 7.7755 | 35.8127 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKMS385M-72HL-TI | 385 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 385 | 355.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.1 | -0.39 | 0.063 | -0.34 |  |  | 1.9078 | 37.9223 | 7.7299 | 36.2371 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS385M-72HL-TI-Q | 385 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 385 | 355.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.38 | 49.1 | 9.44 | 40.8 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9383 | 38.0723 | 7.7088 | 36.448 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS385M-72HL-V-MX3 | 385 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 385 | 357.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.9078 | 37.9223 | 7.7497 | 36.1583 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS385M-72HL-V-MX3-Q | 385 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 385 | 355 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.38 | 49.1 | 9.44 | 40.8 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9248 | 38.1662 | 7.6498 | 37.014 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS385M-72HL-V-TI | 385 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 385 | 357.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.9078 | 37.9223 | 7.7497 | 36.1583 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS385M-72HL-V-TI-Q | 385 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1500V max system Vdc | UL 1741 | 385 | 355 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.38 | 49.1 | 9.44 | 40.8 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9248 | 38.1662 | 7.6498 | 37.014 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS385M-72L-TI | 385 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 385 | 353.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.6 | -0.406 | 0.067 | -0.311 |  |  | 1.81 | 38.53 | 7.67 | 35.51 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS385M-72L-V-MX3 | 385 W, 72 cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 385 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8498 | 38.7247 | 7.5701 | 36.2062 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS385M-72L-V-TI | 385 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 385 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 9.92 | 49.1 | 9.44 | 40.8 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8498 | 38.7247 | 7.5701 | 36.2062 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKM390M-66H | 390 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 390 | 362.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.93 | 44.29 | 10.39 | 37.54 | 45.2 | -0.38107 | 0.031896 | -0.31432 |  |  | 2.0055 | 36.8793 | 7.9568 | 35.3709 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM390M-66H-V | 390 W, 132 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 362 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 22 | 6 | N | 10.93 | 44.29 | 10.39 | 37.54 | 45.5 | -0.37646 | 0.032731 | -0.291 |  |  | 2.0311 | 36.6832 | 7.968 | 35.4211 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM390M-6RL3 | 390 W, 132 half-cut cell, monocrystalline module, 1000V max system Vdc | UL 61730 | 390 | 359.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.39 | 43.75 | 10.69 | 36.49 | 46.84 | -0.37396 | 0.033484 | -0.29983 | 2.041 | 36.0054 | 2.041 | 36.0054 | 8.0121 | 33.6042 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM390M-6RL3-B | 390 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 390 | 360.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.32 | 44.47 | 10.5 | 37.15 | 46.72 | -0.36372 | 0.047134 | -0.29968 |  |  | 2.0358 | 36.5198 | 8.0483 | 33.9364 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM390M-6RL3-TV | 390 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 360 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 22 | 6 | N | 11.15 | 43.92 | 10.57 | 36.9 | 46.62 | -0.37388 | 0.03548 | -0.30273 |  |  | 2.0113 | 36.1054 | 7.8165 | 34.2948 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM390M-6RL3-V | 390 W, 132 half-cut cell, monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 359.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.39 | 43.75 | 10.69 | 36.49 | 46.84 | -0.37396 | 0.033484 | -0.29983 |  |  | 2.041 | 36.0054 | 8.0121 | 33.6042 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM390M-72BL | 390 W, 72 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 390 | 360.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.4 | -0.39107 | 0.04463 | -0.30935 |  |  | 1.9169 | 38.6409 | 7.5075 | 36.9751 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM390M-72HBL | 390 W, 72 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 390 | 359.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.9069 | 38.5552 | 7.4922 | 37.2768 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM390M-72HBL-Q | 390 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 390 | 359.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.46 | 48.6 | 9.84 | 39.64 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.9173 | 38.4746 | 7.4943 | 37.4374 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM390M-72HL | 390 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 390 | 360.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 144 |  | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.1 | -0.39 | 0.063 | -0.34 | 0.022 | -0.412 | 1.9179 | 38.2012 | 7.7709 | 36.5036 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM390M-72HL-BDVP | 390 W, 144 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 358.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.41 | 48.14 | 9.84 | 39.62 | 45.3 | -0.409 | 0.056 | -0.313 |  |  | 1.751 | 39.317 | 7.672 | 36.802 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM390M-72HL-Q | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 390 | 360.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.46 | 48.6 | 9.84 | 39.64 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9428 | 38.4991 | 7.4644 | 36.8566 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM390M-72HL-TV | 390 W, 144 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 358.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.17 | 48.14 | 9.84 | 39.62 | 45.2 | -0.412 | 0.048 | -0.322 |  |  | 1.7885 | 39.7036 | 7.8165 | 37.5629 | [6 empty] | 2019-11-01 | 2020-03-02
Jinko Solar Co., Ltd | JKM390M-72HL-V | 390 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 390 | 361.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 144 |  | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.1 | -0.372 | 0.064 | -0.322 | 0.038 | -0.41 | 1.9179 | 38.2012 | 7.7907 | 36.4241 | [6 empty] | 2018-08-15
Jinko Solar Co., Ltd | JKM390M-72HL-V-Q | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 359.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.46 | 48.6 | 9.84 | 39.64 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9292 | 38.594 | 7.6672 | 37.429 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM390M-72L | 390 W, 72 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 390 | 358.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.6 | -0.406 | 0.067 | -0.311 | 0.012 | -0.416 | 1.8196 | 38.8133 | 7.7106 | 35.7711 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM390M-72L-V | 390 W, 72 cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 390 | 359.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.5 | -0.402 | 0.05 | -0.3 | 0.01 | -0.411 | 1.8596 | 39.0095 | 7.6102 | 36.4724 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM390N-6RL3 | 390 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 390 | 360.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.53 | 44.88 | 10.8 | 36.11 | 46.64 | -0.37357 | 0.040072 | -0.30121 |  |  | 2.0446 | 36.1628 | 7.9963 | 33.9149 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM390N-6RL3-B | 390 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 390 | 360.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 10.92 | 45.33 | 10.34 | 37.72 | 46.62 | -0.36636 | 0.047539 | -0.30144 |  |  | 2.0223 | 36.3801 | 7.9541 | 34.2774 | [6 empty] | 2020-12-11 | 2021-02-22
Jinko Solar Co., Ltd | JKM390N-6RL3-V | 390 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 359.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.53 | 44.88 | 10.8 | 36.11 | 46.58 | -0.38015 | 0.03911 | -0.30172 |  |  | 2.0426 | 35.9964 | 7.9826 | 33.606 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM390N-72H-MBB | 390 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 390 | 354.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.48 | 48.05 | 9.81 | 39.76 | 46.46 | -0.43521 | 0.037516 | -0.30533 |  |  | 1.9243 | 38.9845 | 7.9111 | 35.4519 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM390N-72H-MBB-B | 390 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 390 | 353.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.48 | 48.05 | 9.81 | 39.76 | 46.7 | -0.44106 | 0.049402 | -0.3206 |  |  | 1.915 | 39.2297 | 7.8274 | 36.2367 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM390N-72H-MBB-V | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 355.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.48 | 48.05 | 9.81 | 39.76 | 45.89 | -0.4371 | 0.037545 | -0.31171 |  |  | 1.9224 | 39.1845 | 7.8555 | 35.9121 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKMS390M-72HL-TI | 390 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 390 | 360.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.1 | -0.39 | 0.063 | -0.34 |  |  | 1.9179 | 38.2012 | 7.7709 | 36.5036 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS390M-72HL-TI-Q | 390 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 390 | 360.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.46 | 49.3 | 9.49 | 41.1 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9486 | 38.3523 | 7.7497 | 36.716 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS390M-72HL-V-MX3 | 390 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 390 | 361.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.9179 | 38.2012 | 7.7907 | 36.4241 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS390M-72HL-V-MX3-Q | 390 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 390 | 359.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.46 | 49.3 | 9.49 | 41.1 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.935 | 38.4468 | 7.6903 | 37.2862 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS390M-72HL-V-TI | 390 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 390 | 361.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.9179 | 38.2012 | 7.7907 | 36.4241 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS390M-72HL-V-TI-Q | 390 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1500V max system Vdc | UL 1741 | 390 | 359.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.46 | 49.3 | 9.49 | 41.1 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.935 | 38.4468 | 7.6903 | 37.2862 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS390M-72L-TI | 390 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 390 | 358.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.6 | -0.406 | 0.067 | -0.311 |  |  | 1.8196 | 38.8133 | 7.7106 | 35.7711 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS390M-72L-V-MX3 | 390 W, 72 cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 390 | 359.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8596 | 39.0095 | 7.6102 | 36.4724 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS390M-72L-V-TI | 390 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 390 | 359.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.12 | 49.3 | 9.49 | 41.1 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8596 | 39.0095 | 7.6102 | 36.4724 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKM395M-6RL3 | 395 W, 132 half-cut cell, monocrystalline module, 1000V max system Vdc | UL 61730 | 395 | 364.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.48 | 43.93 | 10.8 | 36.58 | 46.84 | -0.37396 | 0.033484 | -0.29983 | 2.062 | 36.0942 | 2.062 | 36.0942 | 8.0946 | 33.6871 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM395M-6RL3-B | 395 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 395 | 365.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.42 | 44.59 | 10.6 | 37.27 | 46.72 | -0.36372 | 0.047134 | -0.29968 |  |  | 2.0552 | 36.6377 | 8.125 | 34.046 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM395M-6RL3-TV | 395 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 364.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 22 | 6 | N | 11.25 | 44 | 10.69 | 36.95 | 46.62 | -0.37388 | 0.03548 | -0.30273 |  |  | 2.0342 | 36.1543 | 7.9053 | 34.3412 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM395M-6RL3-V | 395 W, 132 half-cut cell, monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 364.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.48 | 43.93 | 10.8 | 36.58 | 46.84 | -0.37396 | 0.033484 | -0.29983 |  |  | 2.062 | 36.0942 | 8.0946 | 33.6871 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM395M-72BL | 395 W, 72 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 395 | 364.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.23 | 49.5 | 9.55 | 41.4 | 45.4 | -0.39107 | 0.04463 | -0.30935 |  |  | 1.929 | 38.923 | 7.555 | 37.245 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM395M-72HBL | 395 W, 144 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL61730, UL 1703 | 395 | 364.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 48.8 | 9.9 | 39.9 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.9174 | 38.8647 | 7.5333 | 37.5761 | [6 empty] | 2019-12-02 | 2021-02-01
Jinko Solar Co., Ltd | JKM395M-72HBL-Q | 395 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 395 | 364.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 48.8 | 9.9 | 39.9 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.929 | 38.727 | 7.54 | 37.683 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM395M-72HL | 395 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 395 | 366.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 48.8 | 9.9 | 39.9 | 45.4 | -0.37035 | 0.050474 | -0.29932 | 0.022 | -0.412 | 1.9525 | 39.4214 | 7.7471 | 37.5333 | [6 empty] | 2018-08-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM395M-72HL-BDVP | 395 W, 144 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 363.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.5 | 48.26 | 9.92 | 39.83 | 45.3 | -0.409 | 0.056 | -0.313 |  |  | 1.7652 | 39.5254 | 7.7344 | 36.9971 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM395M-72HL-Q | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 395 | 365.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 48.8 | 9.9 | 39.9 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9546 | 38.7516 | 7.5099 | 37.0983 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM395M-72HL-TV | 395 W, 144 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 363.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.23 | 48.26 | 9.92 | 39.83 | 45.2 | -0.412 | 0.048 | -0.322 |  |  | 1.803 | 39.914 | 7.88 | 37.762 | [6 empty] | 2019-11-01 | 2021-02-22
Jinko Solar Co., Ltd | JKM395M-72HL-TV-Q | 395 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 395 | 362.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.23 | 48.26 | 9.92 | 39.83 | 45.2 | -0.42063 | 0.043554 | -0.30915 |  |  | 2.026 | 38.8259 | 7.8667 | 36.8916 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM395M-72HL-V | 395 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 363 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 48.8 | 9.9 | 39.9 | 45.3 | -0.41565 | 0.048629 | -0.30532 | 0.038 | -0.41 | 1.9525 | 39.4684 | 7.8483 | 37.2478 | [6 empty] | 2018-08-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM395M-72HL-V-Q | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 395 | 364.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 48.8 | 9.9 | 39.9 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9409 | 38.8472 | 7.714 | 37.6745 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM395M-72L | 395 W, 72 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 395 | 363.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 10.23 | 49.5 | 9.55 | 41.4 | 45.6 | -0.406 | 0.067 | -0.311 | 0.012 | -0.416 | 1.8311 | 39.0966 | 7.7594 | 36.0322 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM395M-72L-V | 395 W, 72 cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 395 | 363.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 10.23 | 49.5 | 9.55 | 41.4 | 45.5 | -0.402 | 0.05 | -0.3 | 0.01 | -0.411 | 1.8714 | 39.2942 | 7.6583 | 36.7387 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM395N-6RL3 | 395 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 395 | 364.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.63 | 45.07 | 10.92 | 36.18 | 46.64 | -0.37357 | 0.040072 | -0.30121 |  |  | 2.0673 | 36.2329 | 8.0852 | 33.9806 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM395N-6RL3-B | 395 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 395 | 365.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11 | 45.52 | 10.42 | 37.91 | 46.62 | -0.36636 | 0.047539 | -0.30144 |  |  | 2.0379 | 36.5634 | 8.0156 | 34.4501 | [6 empty] | 2020-12-11 | 2021-02-22
Jinko Solar Co., Ltd | JKM395N-6RL3-V | 395 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 364.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.63 | 45.07 | 10.92 | 36.18 | 46.58 | -0.38015 | 0.03911 | -0.30172 |  |  | 2.0653 | 36.0662 | 8.0713 | 33.6712 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM395N-72H-MBB | 395 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 395 | 359.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 48.2 | 9.91 | 39.86 | 46.46 | -0.43521 | 0.037516 | -0.30533 |  |  | 1.9439 | 39.0826 | 7.9918 | 35.5411 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM395N-72H-MBB-B | 395 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 395 | 358.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 48.2 | 9.91 | 39.86 | 46.7 | -0.44106 | 0.049402 | -0.3206 |  |  | 1.9345 | 39.3283 | 7.9072 | 36.3279 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM395N-72H-MBB-V | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 360.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 48.2 | 9.91 | 39.86 | 45.89 | -0.4371 | 0.037545 | -0.31171 |  |  | 1.942 | 39.2831 | 7.9356 | 36.0024 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKMS395M-72HL-TI | 395 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 395 | 365.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.23 | 49.5 | 9.55 | 41.4 | 45.1 | -0.39 | 0.063 | -0.34 |  |  | 1.93 | 38.48 | 7.82 | 36.77 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS395M-72HL-TI-Q | 395 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 395 | 365.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 49.5 | 9.55 | 41.4 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9609 | 38.6322 | 7.7987 | 36.984 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS395M-72HL-V-MX3 | 395 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 395 | 366.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.23 | 49.5 | 9.55 | 41.4 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.93 | 38.48 | 7.84 | 36.69 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS395M-72HL-V-MX3-Q | 395 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 395 | 364.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 49.5 | 9.55 | 41.4 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9472 | 38.7275 | 7.7389 | 37.5584 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS395M-72HL-V-TI | 395 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 395 | 366.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.23 | 49.5 | 9.55 | 41.4 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.93 | 38.48 | 7.84 | 36.69 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS395M-72HL-V-TI-Q | 395 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1500V max system Vdc | UL 1741 | 395 | 364.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.54 | 49.5 | 9.55 | 41.4 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9472 | 38.7275 | 7.7389 | 37.5584 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS395M-72L-TI | 395 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 395 | 363.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.23 | 49.5 | 9.55 | 41.4 | 45.6 | -0.406 | 0.067 | -0.311 |  |  | 1.8311 | 39.0966 | 7.7594 | 36.0322 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS395M-72L-V-MX3 | 395 W, 72 cell monocrystalline module with DC optimizer junction box, white substrate, 1500V max system Vdc | UL 1741 | 395 | 363.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.23 | 49.5 | 9.55 | 41.4 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8714 | 39.2942 | 7.6583 | 36.7387 | [6 empty] | 2019-09-16
Jinko Solar Co., Ltd | JKMS395M-72L-V-TI | 395 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 395 | 363.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.23 | 49.5 | 9.55 | 41.4 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8714 | 39.2942 | 7.6583 | 36.7387 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKM400M-6RL3 | 400 W, 132 half-cut cell, monocrystalline module, 1000V max system Vdc | UL 61730 | 400 | 369.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.57 | 44.12 | 10.91 | 36.67 | 46.84 | -0.37396 | 0.033484 | -0.29983 | 2.083 | 36.183 | 2.083 | 36.183 | 8.177 | 33.77 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM400M-6RL3-B | 400 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 400 | 370.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.52 | 44.71 | 10.7 | 37.39 | 46.72 | -0.36372 | 0.047134 | -0.29968 |  |  | 2.0746 | 36.7557 | 8.2016 | 34.1556 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM400M-6RL3-TV | 400 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 369.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.87 | 22 | 6 | N | 11.37 | 44.05 | 10.81 | 37.01 | 46.62 | -0.37388 | 0.03548 | -0.30273 |  |  | 2.057 | 36.213 | 7.994 | 34.397 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM400M-6RL3-V | 400 W, 132 half-cut cell, monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 369.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.57 | 44.12 | 10.91 | 36.67 | 46.84 | -0.37396 | 0.033484 | -0.29983 | 2.083 | 36.183 | 2.083 | 36.183 | 8.177 | 33.77 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM400M-72BL | 400 W, 72 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 400 | 369.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.36 | 49.8 | 9.6 | 41.7 | 45.4 | -0.39107 | 0.04463 | -0.30935 |  |  | 1.9391 | 39.2051 | 7.5946 | 37.5149 | [6 empty] | 2019-12-02
Jinko Solar Co., Ltd | JKM400M-72HBL | 400 W, 144 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL61730, UL 1703 | 400 | 369.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.61 | 49.1 | 9.96 | 40.16 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.929 | 39.118 | 7.579 | 37.821 | [6 empty] | 2019-12-02 | 2021-02-01
Jinko Solar Co., Ltd | JKM400M-72HBL-Q | 400 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 400 | 368.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.61 | 49.1 | 9.96 | 40.16 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.9407 | 38.9794 | 7.5857 | 37.9286 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM400M-72HL | 400 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 400 | 371.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.61 | 49.1 | 9.96 | 40.16 | 45.4 | -0.37035 | 0.050474 | -0.29932 | 0.022 | -0.412 | 1.9643 | 39.6782 | 7.7941 | 37.7778 | [6 empty] | 2018-08-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM400M-72HL-BDVP | 400 W, 144 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 400 | 368.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.59 | 48.35 | 10 | 40.01 | 45.3 | -0.409 | 0.056 | -0.313 |  |  | 1.7795 | 39.704 | 7.7967 | 37.1643 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM400M-72HL-Q | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 400 | 370.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.61 | 49.1 | 9.96 | 40.16 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9665 | 39.0042 | 7.5555 | 37.3401 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM400M-72HL-TV | 400 W, 144 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 400 | 368 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.32 | 48.35 | 10 | 40.01 | 45.2 | -0.412 | 0.048 | -0.322 |  |  | 1.8189 | 39.9884 | 7.9493 | 37.8324 | [6 empty] | 2020-01-02 | 2021-02-22
Jinko Solar Co., Ltd | JKM400M-72HL-TV-Q | 400 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 400 | 367.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.32 | 48.35 | 10 | 40.01 | 45.2 | -0.42063 | 0.043554 | -0.30915 |  |  | 2.0423 | 39.0013 | 7.9301 | 37.0583 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM400M-72HL-V | 400 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 61730, UL 1703 | 400 | 367.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.61 | 49.1 | 9.96 | 40.16 | 45.3 | -0.41565 | 0.048629 | -0.30532 | 0.038 | -0.41 | 1.9643 | 39.7256 | 7.8959 | 37.4906 | [6 empty] | 2018-08-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM400M-72HL-V-Q | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 400 | 369.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.61 | 49.1 | 9.96 | 40.16 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9527 | 39.1003 | 7.7607 | 37.9199 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM400M-72L | 400 W, 72 cell monocrystalline module, white substrate, 1000V max system Vdc | UL 1703 | 400 | 368.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 10.36 | 49.8 | 9.6 | 41.7 | 45.6 | -0.406 | 0.067 | -0.311 | 0.012 | -0.416 | 1.8407 | 39.3799 | 7.8 | 36.2933 | [6 empty] | 2018-11-15
Jinko Solar Co., Ltd | JKM400M-72L-V | 400 W, 72 cell monocrystalline module, white substrate, 1500V max system Vdc | UL 1703 | 400 | 368.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 |  | N | 10.36 | 49.8 | 9.6 | 41.7 | 45.5 | -0.402 | 0.05 | -0.3 | 0.01 | -0.411 | 1.8812 | 39.579 | 7.6984 | 37.0049 | [6 empty] | 2018-10-01
Jinko Solar Co., Ltd | JKM400N-6RL3 | 400 W, 132 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 400 | 369.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.73 | 45.25 | 11.04 | 36.24 | 46.64 | -0.37357 | 0.040072 | -0.30121 |  |  | 2.09 | 36.293 | 8.174 | 34.037 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM400N-6RL3-B | 400 W, 132 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 400 | 370.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.08 | 45.71 | 10.5 | 38.1 | 46.62 | -0.36636 | 0.047539 | -0.30144 |  |  | 2.0536 | 36.7466 | 8.0772 | 34.6227 | [6 empty] | 2020-12-11 | 2021-02-22
Jinko Solar Co., Ltd | JKM400N-6RL3-V | 400 W, 132 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 369.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.85 | 22 | 6 | N | 11.73 | 45.25 | 11.04 | 36.24 | 46.58 | -0.38015 | 0.03911 | -0.30172 |  |  | 2.088 | 36.126 | 8.16 | 33.727 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM400N-72H-MBB | 400 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 400 | 364.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.6 | 48.35 | 10.01 | 39.96 | 46.46 | -0.43521 | 0.037516 | -0.30533 |  |  | 1.9635 | 39.1806 | 8.0724 | 35.6303 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM400N-72H-MBB-B | 400 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 400 | 363.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.6 | 48.35 | 10.01 | 39.96 | 46.7 | -0.44106 | 0.049402 | -0.3206 |  |  | 1.954 | 39.427 | 7.987 | 36.419 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM400N-72H-MBB-V | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 365.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.6 | 48.35 | 10.01 | 39.96 | 45.89 | -0.4371 | 0.037545 | -0.31171 |  |  | 1.9616 | 39.3816 | 8.0157 | 36.0927 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKMS400M-72HL-TI | 400 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 400 | 370 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.36 | 49.8 | 9.6 | 41.7 | 45.1 | -0.39 | 0.063 | -0.34 |  |  | 1.9401 | 38.7588 | 7.8609 | 37.0364 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS400M-72HL-TI-Q | 400 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 400 | 370.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.61 | 49.8 | 9.6 | 41.7 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9712 | 38.9122 | 7.8395 | 37.252 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS400M-72HL-V-TI | 400 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 400 | 371.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.36 | 49.8 | 9.6 | 41.7 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.9401 | 38.7588 | 7.881 | 36.9559 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS400M-72HL-V-TI-Q | 400 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1500V max system Vdc | UL 1741 | 400 | 369.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.61 | 49.8 | 9.6 | 41.7 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9574 | 39.0081 | 7.7794 | 37.8305 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS400M-72L-TI | 400 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 400 | 368.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.36 | 49.8 | 9.6 | 41.7 | 45.6 | -0.406 | 0.067 | -0.311 |  |  | 1.8407 | 39.3799 | 7.8 | 36.2933 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKMS400M-72L-V-TI | 400 W, 72 cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 400 | 368.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 72 | 1 | N | 10.36 | 49.8 | 9.6 | 41.7 | 45.5 | -0.402 | 0.05 | -0.3 |  |  | 1.8812 | 39.579 | 7.6984 | 37.0049 | [6 empty] | 2019-09-03
Jinko Solar Co., Ltd | JKM405M-72HBL | 405 W, 144 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL61730, UL 1703 | 405 | 373.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.69 | 49.4 | 10.02 | 40.42 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.9406 | 39.3713 | 7.6247 | 38.0659 | [6 empty] | 2019-12-02 | 2021-02-01
Jinko Solar Co., Ltd | JKM405M-72HBL-Q | 405 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 405 | 373.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.69 | 49.4 | 10.02 | 40.42 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.9524 | 39.2317 | 7.6314 | 38.1741 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM405M-72HL | 405 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 405 | 375.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.69 | 49.4 | 10.02 | 40.42 | 45.4 | -0.37035 | 0.050474 | -0.29932 | 0.022 | -0.412 | 1.9762 | 39.9351 | 7.841 | 38.0224 | [6 empty] | 2018-11-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM405M-72HL-BDVP | 405 W, 144 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 405 | 372.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.68 | 48.45 | 10.08 | 40.19 | 45.3 | -0.409 | 0.056 | -0.313 |  |  | 1.7937 | 39.8826 | 7.8591 | 37.3315 | [6 empty] | 2019-11-01
Jinko Solar Co., Ltd | JKM405M-72HL-Q | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 405 | 374.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.69 | 49.4 | 10.02 | 40.42 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9783 | 39.2567 | 7.601 | 37.5818 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM405M-72HL-TV | 405 W, 144 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 405 | 372.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.42 | 48.45 | 10.08 | 40.19 | 45.2 | -0.412 | 0.048 | -0.322 |  |  | 1.8365 | 40.0711 | 8.0264 | 37.9107 | [6 empty] | 2020-01-02 | 2021-02-22
Jinko Solar Co., Ltd | JKM405M-72HL-TV-Q | 405 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 405 | 372 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.42 | 48.45 | 10.08 | 40.19 | 45.2 | -0.42063 | 0.043554 | -0.30915 |  |  | 2.0587 | 39.1768 | 7.9936 | 37.225 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM405M-72HL-V | 405 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 61730, UL 1703 | 405 | 372.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.69 | 49.4 | 10.02 | 40.42 | 45.3 | -0.41565 | 0.048629 | -0.30532 | 0.038 | -0.41 | 1.9762 | 39.9828 | 7.9434 | 37.7333 | [6 empty] | 2018-11-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM405M-72HL-V-Q | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 405 | 374 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.69 | 49.4 | 10.02 | 40.42 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9645 | 39.3535 | 7.8075 | 38.1654 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM405M-78H | 405 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 405 | 371.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.2 | 51.07 | 9.44 | 42.91 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.7648 | 42.156 | 7.177 | 40.5246 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM405M-78HB | 405 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 405 | 371.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.01 | 51.55 | 9.37 | 43.23 | 45.1 | -0.42421 | 0.029383 | -0.31882 |  |  | 1.7107 | 43.358 | 7.0963 | 41.4649 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM405M-78H-TV | 405 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 373.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.15 | 51.55 | 9.44 | 42.9 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.847 | 42.0601 | 7.4764 | 40.198 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM405M-78H-V | 405 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 373.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.2 | 51.07 | 9.44 | 42.91 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.6518 | 42.8689 | 7.154 | 40.3992 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM405N-72H-MBB | 405 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 405 | 369 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.66 | 48.5 | 10.11 | 40.06 | 46.46 | -0.43521 | 0.037516 | -0.30533 |  |  | 1.9832 | 39.2787 | 8.1531 | 35.7194 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM405N-72H-MBB-V | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 369.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.66 | 48.5 | 10.11 | 40.06 | 45.89 | -0.4371 | 0.037545 | -0.31171 |  |  | 1.9812 | 39.4802 | 8.0958 | 36.1831 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKMS405M-72HL-TI | 405 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 405 | 374.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.48 | 50.1 | 9.65 | 42 | 45.1 | -0.39 | 0.063 | -0.34 |  |  | 1.9502 | 39.0377 | 7.9019 | 37.3029 | [6 empty] | 2019-10-15
Jinko Solar Co., Ltd | JKMS405M-72HL-TI-Q | 405 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 405 | 374.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.69 | 50.1 | 9.65 | 42 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9815 | 39.1921 | 7.8803 | 37.52 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS405M-72HL-V-TI | 405 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 405 | 376.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.48 | 50.1 | 9.65 | 42 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.9502 | 39.0377 | 7.9221 | 37.2217 | [6 empty] | 2019-10-15
Jinko Solar Co., Ltd | JKMS405M-72HL-V-TI-Q | 405 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1500V max system Vdc | UL 1741 | 405 | 374 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.69 | 50.1 | 9.65 | 42 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9676 | 39.2887 | 7.82 | 38.1027 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKM410M-72HBL | 410 W, 144 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL61730, UL 1703 | 410 | 378.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.76 | 49.6 | 10.08 | 40.68 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.9522 | 39.6245 | 7.6703 | 38.3107 | [6 empty] | 2019-12-02 | 2021-02-01
Jinko Solar Co., Ltd | JKM410M-72HBL-Q | 410 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 410 | 378.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.76 | 49.6 | 10.08 | 40.68 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.9641 | 39.4841 | 7.6771 | 38.4197 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM410M-72HL | 410 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 410 | 380.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.76 | 49.6 | 10.08 | 40.68 | 45.4 | -0.37035 | 0.050474 | -0.29932 | 0.022 | -0.412 | 1.988 | 40.192 | 7.888 | 38.267 | [6 empty] | 2018-11-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM410M-72HL-Q | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 410 | 379.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.76 | 49.6 | 10.08 | 40.68 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9902 | 39.5092 | 7.6465 | 37.8236 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM410M-72HL-TV | 410 W, 144 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 410 | 377.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.51 | 48.56 | 10.16 | 40.38 | 45.2 | -0.412 | 0.048 | -0.322 |  |  | 1.8523 | 40.1621 | 8.0957 | 37.9967 | [6 empty] | 2020-01-02 | 2021-02-22
Jinko Solar Co., Ltd | JKM410M-72HL-TV-Q | 410 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 410 | 376.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.51 | 48.56 | 10.16 | 40.38 | 45.2 | -0.42063 | 0.043554 | -0.30915 |  |  | 2.075 | 39.362 | 8.057 | 37.401 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM410M-72HL-V | 410 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 61730, UL 1703 | 410 | 377.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.76 | 49.6 | 10.08 | 40.68 | 45.3 | -0.41565 | 0.048629 | -0.30532 | 0.038 | -0.41 | 1.988 | 40.24 | 7.991 | 37.976 | [6 empty] | 2018-11-15 | 2020-08-03
Jinko Solar Co., Ltd | JKM410M-72HL-V-Q | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 410 | 378.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.76 | 49.6 | 10.08 | 40.68 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9762 | 39.6066 | 7.8542 | 38.4109 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM410M-78H | 410 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 410 | 376.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.27 | 51.16 | 9.53 | 43.03 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.7817 | 42.2739 | 7.2454 | 40.6379 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM410M-78HB | 410 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 410 | 376 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.11 | 51.58 | 9.47 | 43.3 | 45.1 | -0.42421 | 0.029383 | -0.31882 |  |  | 1.729 | 43.4282 | 7.1721 | 41.532 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM410M-78H-TV | 410 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 377.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.2 | 51.58 | 9.53 | 43.03 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.8646 | 42.1876 | 7.5477 | 40.3198 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM410M-78H-V | 410 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 378.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.27 | 51.16 | 9.53 | 43.03 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.6675 | 42.9888 | 7.2222 | 40.5122 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM410N-72H-MBB | 410 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 410 | 373.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.72 | 48.65 | 10.21 | 40.16 | 46.46 | -0.43521 | 0.037516 | -0.30533 |  |  | 2.0028 | 39.3767 | 8.2337 | 35.8086 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM410N-72H-MBB-V | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 410 | 374.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.72 | 48.65 | 10.21 | 40.16 | 45.89 | -0.4371 | 0.037545 | -0.31171 |  |  | 2.0008 | 39.5787 | 8.1758 | 36.2734 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKMS410M-72HL-TI | 410 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1000V max system Vdc | UL 1741 | 410 | 379.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.6 | 50.4 | 9.69 | 42.3 | 45.1 | -0.39 | 0.063 | -0.34 |  |  | 1.9583 | 39.3165 | 7.9346 | 37.5693 | [6 empty] | 2019-10-15
Jinko Solar Co., Ltd | JKMS410M-72HL-TI-Q | 410 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1000V max system Vdc | UL 1741 | 410 | 379.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.76 | 50.3 | 9.7 | 42.3 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 1.9917 | 39.4721 | 7.9212 | 37.788 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKMS410M-72HL-V-TI | 410 W, 144 half cell monocrystalline module with rapid shutdown device, white substrate, 1500V max system Vdc | UL 1741 | 410 | 380.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.956 | 24 | 6 | N | 10.6 | 50.4 | 9.69 | 42.3 | 45.1 | -0.372 | 0.064 | -0.322 |  |  | 1.9583 | 39.3165 | 7.9549 | 37.4876 | [6 empty] | 2019-10-15
Jinko Solar Co., Ltd | JKMS410M-72HL-V-TI-Q | 410 W, 144 half cell monocrystalline module with rapid shutdown junction box, white substrate, 1500V max system Vdc | UL 1741 | 410 | 378.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.76 | 50.3 | 9.7 | 42.3 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9778 | 39.5694 | 7.8605 | 38.3748 | [6 empty] | 2020-02-21
Jinko Solar Co., Ltd | JKM415M-6TL4 | 415 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 415 | 379.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.43 | 40.62 | 12.5 | 33.2 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.3766 | 33.1001 | 9.5771 | 30.6251 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM415M-6TL4-V | 415 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 415 | 379.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.43 | 40.62 | 12.5 | 33.2 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.3766 | 33.1001 | 9.5771 | 30.6251 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM415M-72HBL | 415 W, 144 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL61730, UL 1703 | 415 | 383.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.82 | 49.9 | 10.14 | 40.93 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.9639 | 39.868 | 7.716 | 38.5462 | [6 empty] | 2020-01-21 | 2021-02-01
Jinko Solar Co., Ltd | JKM415M-72HBL-Q | 415 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 415 | 383.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.82 | 49.9 | 10.14 | 40.93 | 45.6 | -0.39519 | 0.055842 | -0.32693 |  |  | 1.9758 | 39.7267 | 7.7228 | 38.6558 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM415M-72HL | 415 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 415 | 385.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.82 | 49.9 | 10.14 | 40.93 | 45.4 | -0.37035 | 0.050474 | -0.29932 |  |  | 1.9998 | 40.439 | 7.935 | 38.5022 | [6 empty] | 2020-01-21 | 2020-08-03
Jinko Solar Co., Ltd | JKM415M-72HL-Q | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 415 | 384.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.82 | 49.9 | 10.14 | 40.93 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 2.002 | 39.752 | 7.692 | 38.056 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM415M-72HL-TV | 415 W, 144 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730, UL 1703 | 415 | 382.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.61 | 48.64 | 10.25 | 40.5 | 45.2 | -0.412 | 0.048 | -0.322 |  |  | 1.87 | 40.2283 | 8.1727 | 38.0593 | [6 empty] | 2020-01-02 | 2021-02-22
Jinko Solar Co., Ltd | JKM415M-72HL-TV-Q | 415 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 415 | 381.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.61 | 48.64 | 10.25 | 40.5 | 45.2 | -0.42063 | 0.043554 | -0.30915 |  |  | 2.0934 | 39.479 | 8.1284 | 37.5121 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM415M-72HL-V | 415 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 61730, UL 1703 | 415 | 382 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.82 | 49.9 | 10.14 | 40.93 | 45.3 | -0.41565 | 0.048629 | -0.30532 |  |  | 1.9998 | 40.4873 | 8.0386 | 38.2094 | [6 empty] | 2020-01-21 | 2020-08-03
Jinko Solar Co., Ltd | JKM415M-72HL-V-Q | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 415 | 383.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.82 | 49.9 | 10.14 | 40.93 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.988 | 39.85 | 7.901 | 38.647 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM415M-78H | 415 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 415 | 381 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.34 | 51.25 | 9.63 | 43.1 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.8004 | 42.3427 | 7.3214 | 40.704 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM415M-78HB | 415 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 415 | 380.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.21 | 51.61 | 9.57 | 43.37 | 45.1 | -0.42421 | 0.029383 | -0.31882 |  |  | 1.7472 | 43.4984 | 7.2478 | 41.5992 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM415M-78H-TV | 415 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 382.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.28 | 51.61 | 9.61 | 43.2 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.8802 | 42.3543 | 7.6111 | 40.4791 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM415M-78H-V | 415 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 382.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.34 | 51.25 | 9.63 | 43.1 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.685 | 43.0587 | 7.298 | 40.5781 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM415N-72H-MBB | 415 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 415 | 378.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.78 | 48.8 | 10.31 | 40.26 | 46.46 | -0.43521 | 0.037516 | -0.30533 |  |  | 2.0224 | 39.4748 | 8.3144 | 35.8978 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM415N-72H-MBB-V | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 415 | 379.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.78 | 48.8 | 10.31 | 40.26 | 45.89 | -0.4371 | 0.037545 | -0.31171 |  |  | 2.0204 | 39.6773 | 8.2559 | 36.3637 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM420M-60HL4 | 420 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 420 | 385.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.49 | 40.7 | 12.61 | 33.31 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4078 | 33.7061 | 9.6548 | 30.643 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM420M-60HL4-V | 420 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 385.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.49 | 40.7 | 12.61 | 33.31 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4078 | 33.7061 | 9.6548 | 30.643 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM420M-6TL4 | 420 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 420 | 384.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.49 | 40.7 | 12.61 | 33.31 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.3975 | 33.2098 | 9.6613 | 30.7265 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM420M-6TL4-V | 420 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 384.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.49 | 40.7 | 12.61 | 33.31 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.3975 | 33.2098 | 9.6613 | 30.7265 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM420M-72HBL | 420 W, 144 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL61730, UL 1703 | 420 | 388.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.88 | 50.2 | 10.2 | 41.18 | 45.6 | -0.39174 | 0.054695 | -0.31006 |  |  | 1.9755 | 40.1115 | 7.7616 | 38.7816 | [6 empty] | 2020-01-21 | 2021-02-01
Jinko Solar Co., Ltd | JKM420M-72HL | 420 W, 144 half cell monocrystalline module, white substrate, 1000V max system Vdc | UL 61730, UL 1703 | 420 | 390.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.88 | 50.2 | 10.2 | 41.18 | 45.4 | -0.37035 | 0.050474 | -0.29932 |  |  | 2.0117 | 40.686 | 7.9819 | 38.7373 | [6 empty] | 2020-01-21 | 2020-08-03
Jinko Solar Co., Ltd | JKM420M-72HL-Q | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 420 | 389.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.88 | 50.2 | 10.2 | 41.18 | 45.5 | -0.38013 | 0.048872 | -0.30923 |  |  | 2.0138 | 39.9948 | 7.7375 | 38.2884 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM420M-72HL-TV-Q | 420 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 420 | 386.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 24 | 6 | N | 10.7 | 48.74 | 10.33 | 40.65 | 45.2 | -0.42063 | 0.043554 | -0.30915 |  |  | 2.1097 | 39.6252 | 8.1918 | 37.6511 | [6 empty] | 2020-01-21
Jinko Solar Co., Ltd | JKM420M-72HL-V | 420 W, 144 half cell monocrystalline module, white substrate, 1500V max system Vdc | UL 61730, UL 1703 | 420 | 386.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.88 | 50.2 | 10.2 | 41.18 | 45.3 | -0.41565 | 0.048629 | -0.30532 |  |  | 2.0117 | 40.7346 | 8.0861 | 38.4428 | [6 empty] | 2020-01-21 | 2020-08-03
Jinko Solar Co., Ltd | JKM420M-72HL-V-Q | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 420 | 388.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.88 | 50.2 | 10.2 | 41.18 | 45.3 | -0.3963 | 0.044965 | -0.30327 |  |  | 1.9998 | 40.0934 | 7.9478 | 38.8831 | [6 empty] | 2020-01-21 | 2020-07-21
Jinko Solar Co., Ltd | JKM420M-78H | 420 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 420 | 385.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.41 | 51.34 | 9.73 | 43.17 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.819 | 42.4114 | 7.3975 | 40.7701 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM420M-78HB | 420 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 420 | 385.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.31 | 51.64 | 9.67 | 43.44 | 45.1 | -0.42421 | 0.029383 | -0.31882 |  |  | 1.7655 | 43.5686 | 7.3235 | 41.6663 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM420M-78H-TV | 420 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 420 | 387.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.36 | 51.64 | 9.69 | 43.35 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.8959 | 42.5013 | 7.6744 | 40.6197 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM420M-78H-V | 420 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 420 | 387.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.41 | 51.34 | 9.73 | 43.17 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.7025 | 43.1286 | 7.3738 | 40.644 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM420M-7RL3-TV | 420 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 386.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 10.63 | 51.1 | 9.82 | 42.77 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 1.9437 | 41.8005 | 7.5841 | 40.981 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM420N-72H-MBB | 420 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 420 | 383.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.84 | 48.95 | 10.41 | 40.35 | 46.46 | -0.43521 | 0.037516 | -0.30533 |  |  | 2.042 | 39.563 | 8.395 | 35.978 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM420N-72H-MBB-V | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 384 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.84 | 48.95 | 10.41 | 40.35 | 45.89 | -0.4371 | 0.037545 | -0.31171 |  |  | 2.04 | 39.766 | 8.336 | 36.445 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM425M-60HL4 | 425 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 425 | 390.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.55 | 40.78 | 12.72 | 33.42 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4288 | 33.8174 | 9.739 | 30.7442 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM425M-60HL4-B | 425 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 425 | 393.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.24 | 40.83 | 12.48 | 34.06 | 45.64 | -0.3783 | 0.05924 | -0.2937 |  |  | 2.4052 | 34.0264 | 9.7204 | 30.9271 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM425M-60HL4-V | 425 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 390.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.55 | 40.78 | 12.72 | 33.42 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4288 | 33.8174 | 9.739 | 30.7442 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM425M-6TL4 | 425 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 425 | 388.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.55 | 40.78 | 12.72 | 33.42 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.4184 | 33.3195 | 9.7456 | 30.828 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM425M-6TL4-V | 425 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 388.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.55 | 40.78 | 12.72 | 33.42 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.4184 | 33.3195 | 9.7456 | 30.828 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM425M-78H | 425 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 425 | 390.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.48 | 51.43 | 9.83 | 43.23 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.8377 | 42.4704 | 7.4735 | 40.8268 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM425M-78HB | 425 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 425 | 390.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.41 | 51.67 | 9.77 | 43.51 | 45.1 | -0.42421 | 0.029383 | -0.31882 |  |  | 1.7837 | 43.6388 | 7.3993 | 41.7334 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM425M-78H-TV | 425 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 392.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.44 | 51.67 | 9.77 | 43.5 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.9115 | 42.6484 | 7.7378 | 40.7602 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM425M-78H-V | 425 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 392.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.48 | 51.43 | 9.83 | 43.23 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.72 | 43.1886 | 7.4496 | 40.7005 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM425M-7RL3-TV | 425 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 390.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 10.72 | 51.2 | 9.92 | 42.85 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 1.9635 | 41.8787 | 7.6614 | 41.0577 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM425N-72H-MBB | 425 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 425 | 387.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.9 | 49.1 | 10.51 | 40.44 | 46.46 | -0.43521 | 0.037516 | -0.30533 |  |  | 2.0616 | 39.6512 | 8.4756 | 36.0582 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM425N-72H-MBB-V | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 388.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 24 | 6 | N | 10.9 | 49.1 | 10.51 | 40.44 | 45.89 | -0.4371 | 0.037545 | -0.31171 |  |  | 2.0596 | 39.8547 | 8.4161 | 36.5263 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM425N-7RL3-B | 425 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 425 | 394.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.42 | 52.26 | 9.84 | 43.2 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 1.9147 | 44.1663 | 7.5081 | 41.6255 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM430M-60HL4 | 430 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 430 | 394.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.61 | 40.86 | 12.83 | 33.52 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4498 | 33.9186 | 9.8232 | 30.8362 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM430M-60HL4-B | 430 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 430 | 397.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.32 | 41.01 | 12.56 | 34.24 | 45.64 | -0.3783 | 0.05924 | -0.2937 |  |  | 2.4206 | 34.2062 | 9.7827 | 31.0906 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM430M-60HL4-V | 430 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 394.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.61 | 40.86 | 12.83 | 33.52 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4498 | 33.9186 | 9.8232 | 30.8362 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM430M-6TL4 | 430 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 430 | 393.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.61 | 40.86 | 12.83 | 33.52 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.4393 | 33.4192 | 9.8299 | 30.9202 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM430M-6TL4-V | 430 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 393.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.61 | 40.86 | 12.83 | 33.52 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.4393 | 33.4192 | 9.8299 | 30.9202 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM430M-78H | 430 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 430 | 395.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.57 | 51.52 | 9.89 | 43.49 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.849 | 42.7258 | 7.5191 | 41.0723 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM430M-78HB | 430 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 430 | 395 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.51 | 51.7 | 9.87 | 43.57 | 45.1 | -0.42421 | 0.029383 | -0.31882 |  |  | 1.802 | 43.699 | 7.475 | 41.791 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM430M-78H-TV | 430 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 396.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.52 | 51.7 | 9.85 | 43.66 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.9272 | 42.8053 | 7.8012 | 40.9102 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM430M-78H-V | 430 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 397.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.57 | 51.52 | 9.89 | 43.49 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.7305 | 43.4483 | 7.495 | 40.9453 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM430M-7RL3 | 430 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 430 | 396.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.96 | 51.1 | 10.14 | 42.41 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9216 | 42.8519 | 7.675 | 41.0323 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM430M-7RL3-TV | 430 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 395.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 10.81 | 51.3 | 10.02 | 42.92 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 1.9832 | 41.9471 | 7.7386 | 41.1247 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM430M-7RL3-V | 430 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 396.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.96 | 51.1 | 10.14 | 42.41 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9216 | 42.8519 | 7.675 | 41.0323 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM430N-7RL3 | 430 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 430 | 396.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.82 | 51.72 | 10.1 | 42.58 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 1.899 | 42.4866 | 7.9177 | 39.7802 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM430N-7RL3-B | 430 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 430 | 399.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.49 | 52.44 | 9.91 | 43.39 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 1.9283 | 44.3605 | 7.5615 | 41.8085 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM430N-7RL3-V | 430 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 393.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.82 | 51.72 | 10.1 | 42.58 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 1.9302 | 42.8705 | 7.855 | 40.2119 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM435M-60HL4 | 435 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 435 | 399.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.67 | 40.94 | 12.94 | 33.62 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4708 | 34.0198 | 9.9074 | 30.9282 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM435M-60HL4-B | 435 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 435 | 402.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.4 | 41.19 | 12.64 | 34.42 | 45.64 | -0.3783 | 0.05924 | -0.2937 |  |  | 2.436 | 34.386 | 9.845 | 31.254 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM435M-60HL4-V | 435 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 399.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.67 | 40.94 | 12.94 | 33.62 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4708 | 34.0198 | 9.9074 | 30.9282 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM435M-6TL4 | 435 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 435 | 398.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.67 | 40.94 | 12.94 | 33.62 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.4603 | 33.5189 | 9.9142 | 31.0125 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM435M-6TL4-V | 435 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 398.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.67 | 40.94 | 12.94 | 33.62 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.4603 | 33.5189 | 9.9142 | 31.0125 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM435M-78H | 435 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 435 | 400 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.67 | 51.61 | 9.99 | 43.55 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.8677 | 42.7847 | 7.5951 | 41.129 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM435M-78HB | 435 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 435 | 399.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.61 | 51.73 | 9.97 | 43.64 | 45.1 | -0.42421 | 0.029383 | -0.31882 |  |  | 1.8203 | 43.7692 | 7.5507 | 41.8581 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM435M-78H-TV | 435 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 401.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.6 | 51.8 | 9.92 | 43.85 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.9409 | 42.9915 | 7.8566 | 41.0882 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM435M-78H-V | 435 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 401.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.67 | 51.61 | 9.99 | 43.55 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.748 | 43.5083 | 7.5708 | 41.0018 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM435M-7RL3 | 435 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 435 | 400.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.05 | 51.2 | 10.23 | 42.52 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9386 | 42.9631 | 7.7431 | 41.1387 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM435M-7RL3-TV | 435 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 400.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 10.9 | 51.4 | 10.12 | 42.99 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 2.003 | 42.0155 | 7.8158 | 41.1918 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM435M-7RL3-V | 435 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 435 | 400.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.05 | 51.2 | 10.23 | 42.52 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9386 | 42.9631 | 7.7431 | 41.1387 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM435N-7RL3 | 435 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 435 | 400.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.88 | 51.94 | 10.16 | 42.82 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 1.9103 | 42.726 | 7.9648 | 40.0044 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM435N-7RL3-B | 435 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 435 | 404.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.56 | 52.62 | 9.98 | 43.59 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 1.9419 | 44.565 | 7.6149 | 42.0013 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM435N-7RL3-V | 435 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 397.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.88 | 51.94 | 10.16 | 42.82 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 1.9417 | 43.1121 | 7.9017 | 40.4385 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM440M-60HL4 | 440 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 440 | 404.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.73 | 41.02 | 13.05 | 33.72 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4918 | 34.121 | 9.9917 | 31.0202 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM440M-60HL4-B | 440 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 440 | 407.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.48 | 41.36 | 12.72 | 34.59 | 45.64 | -0.3783 | 0.05924 | -0.2937 |  |  | 2.4514 | 34.5558 | 9.9073 | 31.4084 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM440M-60HL4-V | 440 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 404.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.73 | 41.02 | 13.05 | 33.72 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.4918 | 34.121 | 9.9917 | 31.0202 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM440M-6TL4 | 440 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 440 | 403.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.73 | 41.02 | 13.05 | 33.72 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.4812 | 33.6186 | 9.9984 | 31.1047 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM440M-6TL4-V | 440 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 403.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.73 | 41.02 | 13.05 | 33.72 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.4812 | 33.6186 | 9.9984 | 31.1047 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM440M-78H | 440 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 440 | 404.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.77 | 51.7 | 10.08 | 43.65 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.8845 | 42.883 | 7.6635 | 41.2235 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM440M-78H-TV | 440 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 406.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.68 | 51.9 | 10.02 | 43.92 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.9604 | 43.0602 | 7.9358 | 41.1538 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM440M-78H-V | 440 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 406.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.77 | 51.7 | 10.08 | 43.65 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.7638 | 43.6082 | 7.639 | 41.0959 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM440M-7RL3 | 440 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 440 | 405.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.14 | 51.3 | 10.32 | 42.64 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9557 | 43.0843 | 7.8113 | 41.2548 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM440M-7RL3-TV | 440 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 405.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 10.99 | 51.5 | 10.22 | 43.06 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 2.0228 | 42.0839 | 7.8931 | 41.2589 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM440M-7RL3-V | 440 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 405.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.14 | 51.3 | 10.32 | 42.64 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9557 | 43.0843 | 7.8113 | 41.2548 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM440N-7RL3 | 440 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 440 | 405.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.94 | 52.16 | 10.22 | 43.06 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 1.9216 | 42.9655 | 8.0118 | 40.2286 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM440N-7RL3-B | 440 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 440 | 409.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.63 | 52.8 | 10.05 | 43.78 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 1.9555 | 44.7592 | 7.6684 | 42.1843 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM440N-7RL3-V | 440 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 402.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.94 | 52.16 | 10.22 | 43.06 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 1.9531 | 43.3537 | 7.9483 | 40.6652 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM445M-60HL4 | 445 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 445 | 409.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.79 | 41.1 | 13.16 | 33.82 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.5128 | 34.2221 | 10.0759 | 31.1122 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM445M-60HL4-B | 445 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 445 | 412.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.56 | 41.54 | 12.8 | 34.77 | 45.64 | -0.3783 | 0.05924 | -0.2937 |  |  | 2.4668 | 34.7357 | 9.9696 | 31.5718 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM445M-60HL4-V | 445 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 409.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.79 | 41.1 | 13.16 | 33.82 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.5128 | 34.2221 | 10.0759 | 31.1122 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM445M-6TL4 | 445 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 445 | 407.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.79 | 41.1 | 13.16 | 33.82 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.5021 | 33.7183 | 10.0827 | 31.197 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM445M-6TL4-V | 445 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 407.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.79 | 41.1 | 13.16 | 33.82 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.5021 | 33.7183 | 10.0827 | 31.197 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM445M-78H | 445 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 445 | 409.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.84 | 52.04 | 10.18 | 43.72 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.9032 | 42.9518 | 7.7396 | 41.2896 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM445M-78H-TV | 445 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 411.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.78 | 52 | 10.12 | 43.98 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.98 | 43.119 | 8.015 | 41.21 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM445M-78H-V | 445 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 411.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.84 | 52.04 | 10.18 | 43.72 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.7813 | 43.6781 | 7.7148 | 41.1619 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM445M-7RL3 | 445 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 445 | 410.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.23 | 51.4 | 10.41 | 42.75 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9727 | 43.1955 | 7.8794 | 41.3612 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM445M-7RL3-TV | 445 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 409.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 11.08 | 51.6 | 10.32 | 43.13 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 2.0426 | 42.1523 | 7.9703 | 41.3259 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM445M-7RL3-V | 445 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 410.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.23 | 51.4 | 10.41 | 42.75 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9727 | 43.1955 | 7.8794 | 41.3612 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM445N-7RL3 | 445 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 445 | 410.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.99 | 52.38 | 10.28 | 43.29 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 1.9329 | 43.195 | 8.0589 | 40.4435 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM445N-7RL3-B | 445 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 445 | 414 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.7 | 52.98 | 10.12 | 43.98 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 1.9691 | 44.9637 | 7.7218 | 42.377 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM445N-7RL3-V | 445 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 407.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.99 | 52.38 | 10.28 | 43.29 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 1.9646 | 43.5853 | 7.995 | 40.8824 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM450M-60HL4 | 450 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 450 | 413.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.85 | 41.18 | 13.27 | 33.91 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.5338 | 34.3132 | 10.1601 | 31.195 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM450M-60HL4-V | 450 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 413.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.85 | 41.18 | 13.27 | 33.91 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.5338 | 34.3132 | 10.1601 | 31.195 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM450M-6TL4 | 450 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 450 | 412.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.85 | 41.18 | 13.27 | 33.91 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.523 | 33.808 | 10.167 | 31.28 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM450M-6TL4-V | 450 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 412.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.05 | 20 | 6 | N | 13.85 | 41.18 | 13.27 | 33.91 | 47.11 | -0.40289 | 0.045331 | -0.2978 |  |  | 2.523 | 33.808 | 10.167 | 31.28 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM450M-78H | 450 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 450 | 414.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.92 | 52.13 | 10.27 | 43.82 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.92 | 43.05 | 7.808 | 41.384 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM450M-78H-TV | 450 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 415.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 26 | 6 | N | 10.87 | 52.1 | 10.22 | 44.04 | 45.8 | -0.385 | 0.0461 | -0.302 |  |  | 1.9996 | 43.1778 | 8.0942 | 41.2662 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM450M-78H-V | 450 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 416.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 10.92 | 52.13 | 10.27 | 43.82 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.797 | 43.778 | 7.783 | 41.256 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM450M-7RL3 | 450 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 450 | 415.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.32 | 51.5 | 10.5 | 42.86 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9898 | 43.3066 | 7.9475 | 41.4676 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM450M-7RL3-TV | 450 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 414.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 11.17 | 51.7 | 10.42 | 43.19 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 2.0624 | 42.2109 | 8.0475 | 41.3834 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM450M-7RL3-V | 450 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 415.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.32 | 51.5 | 10.5 | 42.86 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 1.9898 | 43.3066 | 7.9475 | 41.4676 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM450N-7RL3 | 450 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 450 | 415.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.05 | 52.6 | 10.34 | 43.52 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 1.9442 | 43.4245 | 8.1059 | 40.6584 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM450N-7RL3-B | 450 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 450 | 418.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.77 | 53.16 | 10.19 | 44.16 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 1.9828 | 45.1477 | 7.7752 | 42.5505 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM450N-7RL3-V | 450 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 412.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.05 | 52.6 | 10.34 | 43.52 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 1.9761 | 43.8169 | 8.0417 | 41.0996 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM455M-60HL4 | 455 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 455 | 418.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.93 | 41.33 | 13.36 | 34.06 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.551 | 34.465 | 10.229 | 31.333 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM455M-60HL4-V | 455 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 418.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 13.93 | 41.33 | 13.36 | 34.06 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.551 | 34.465 | 10.229 | 31.333 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM455M-78H | 455 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 455 | 419 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 11 | 52.22 | 10.36 | 43.92 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.9368 | 43.1482 | 7.8764 | 41.4784 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM455M-78H-V | 455 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 421 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 11 | 52.22 | 10.36 | 43.92 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.8127 | 43.8779 | 7.8512 | 41.3501 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM455M-7RL3 | 455 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 455 | 419.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.41 | 51.6 | 10.59 | 42.97 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 2.0068 | 43.4178 | 8.0156 | 41.5741 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM455M-7RL3-TV | 455 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 419.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 11.26 | 51.8 | 10.52 | 43.25 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 2.0822 | 42.2696 | 8.1248 | 41.4409 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM455M-7RL3-V | 455 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 419.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.41 | 51.6 | 10.59 | 42.97 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 2.0068 | 43.4178 | 8.0156 | 41.5741 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM455N-7RL3 | 455 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 455 | 420 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.11 | 52.82 | 10.4 | 43.75 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 1.9554 | 43.654 | 8.1529 | 40.8732 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM455N-7RL3-B | 455 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 455 | 423.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.84 | 53.34 | 10.26 | 44.35 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 1.9964 | 45.342 | 7.8286 | 42.7336 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM455N-7RL3-V | 455 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 416.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.11 | 52.82 | 10.4 | 43.75 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 1.9875 | 44.0484 | 8.0883 | 41.3168 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM460M-60HL4 | 460 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 460 | 423.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 14.01 | 41.48 | 13.45 | 34.2 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.5682 | 34.6067 | 10.2979 | 31.4618 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM460M-60HL4-V | 460 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 460 | 423.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 20 | 6 | N | 14.01 | 41.48 | 13.45 | 34.2 | 46.51 | -0.39667 | 0.050106 | -0.30445 |  |  | 2.5682 | 34.6067 | 10.2979 | 31.4618 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM460M-78H | 460 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 460 | 423.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 11.08 | 52.32 | 10.45 | 44.02 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.9537 | 43.2465 | 7.9448 | 41.5729 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM460M-78H-V | 460 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 425.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 11.08 | 52.32 | 10.45 | 44.02 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.8285 | 43.9778 | 7.9194 | 41.4443 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM460M-7RL3 | 460 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 460 | 424.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.5 | 51.7 | 10.68 | 43.08 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 2.0239 | 43.5289 | 8.0838 | 41.6805 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM460M-7RL3-TV | 460 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 460 | 424.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 11.35 | 51.9 | 10.62 | 43.32 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 2.102 | 42.338 | 8.202 | 41.508 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM460M-7RL3-V | 460 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 424.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.5 | 51.7 | 10.68 | 43.08 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 2.0239 | 43.5289 | 8.0838 | 41.6805 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM460N-7RL3 | 460 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 460 | 424.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.17 | 53.04 | 10.46 | 43.98 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 1.9667 | 43.8835 | 8.2 | 41.0881 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM460N-7RL3-B | 460 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 460 | 428.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.91 | 53.52 | 10.33 | 44.53 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 2.01 | 45.526 | 7.882 | 42.907 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM460N-7RL3-V | 460 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 460 | 421.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.17 | 53.04 | 10.46 | 43.98 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 1.999 | 44.28 | 8.135 | 41.534 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM465M-78H | 465 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 465 | 428.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 11.16 | 52.43 | 10.54 | 44.12 | 45.2 | -0.41903 | 0.046676 | -0.31514 |  |  | 1.9705 | 43.3447 | 8.0133 | 41.6673 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM465M-78H-V | 465 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 465 | 430.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.09 | 26 | 6 | N | 11.16 | 52.43 | 10.54 | 44.12 | 45.4 | -0.39149 | 0.054727 | -0.3218 |  |  | 1.8442 | 44.0777 | 7.9876 | 41.5384 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM465M-7RL3 | 465 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 465 | 429.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.59 | 51.92 | 10.77 | 43.18 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 2.0409 | 43.63 | 8.1519 | 41.7772 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM465M-7RL3-TV | 465 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 465 | 428.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 11.44 | 52 | 10.72 | 43.38 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 2.1218 | 42.3966 | 8.2792 | 41.5655 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM465M-7RL3-V | 465 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 465 | 429.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.59 | 51.92 | 10.77 | 43.18 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 2.0409 | 43.63 | 8.1519 | 41.7772 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM465N-7RL3 | 465 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 465 | 429.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.22 | 53.26 | 10.52 | 44.21 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 1.978 | 44.113 | 8.247 | 41.303 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM465N-7RL3-B | 465 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 465 | 433.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 10.98 | 53.7 | 10.4 | 44.72 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 2.0236 | 45.7202 | 7.9354 | 43.0901 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM465N-7RL3-V | 465 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 465 | 426.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.22 | 53.26 | 10.52 | 44.21 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 2.0105 | 44.5116 | 8.1817 | 41.7512 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM470M-7RL3 | 470 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 470 | 434.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.68 | 52.14 | 10.86 | 43.28 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 2.058 | 43.731 | 8.22 | 41.874 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM470M-7RL3-TV | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 470 | 433.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 11.53 | 52.1 | 10.82 | 43.44 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 2.1416 | 42.4553 | 8.3565 | 41.623 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM470M-7RL3-V | 470 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 470 | 434.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.68 | 52.14 | 10.86 | 43.28 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 2.058 | 43.731 | 8.22 | 41.874 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM470N-7RL3 | 470 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 470 | 434.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.28 | 53.48 | 10.58 | 44.43 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 1.9893 | 44.3325 | 8.294 | 41.5085 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM470N-7RL3-B | 470 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 470 | 437.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.05 | 53.88 | 10.47 | 44.9 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 2.0372 | 45.9043 | 7.9888 | 43.2635 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM470N-7RL3-V | 470 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 470 | 431.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.28 | 53.48 | 10.58 | 44.43 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 2.0219 | 44.7331 | 8.2283 | 41.959 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM475M-7RL3 | 475 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 475 | 439 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.77 | 52.24 | 10.95 | 43.38 | 45.4 | -0.39787 | 0.025814 | -0.30765 | 2.0751 |  | 2.0751 | 43.832 | 8.2881 | 41.9708 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM475M-7RL3-TV | 475 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 475 | 438.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 26 | 6 | N | 11.63 | 52.16 | 10.92 | 43.5 | 45.2 | -0.40608 | 0.032397 | -0.31531 |  |  | 2.1614 | 42.5139 | 8.4337 | 41.6805 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM475M-7RL3-V | 475 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 475 | 439 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.77 | 52.24 | 10.95 | 43.38 | 45.4 | -0.39787 | 0.025814 | -0.30765 |  |  | 2.0751 | 43.832 | 8.2881 | 41.9708 | [6 empty] | 2020-09-11
Jinko Solar Co., Ltd | JKM475N-7RL3 | 475 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 475 | 439 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.34 | 53.7 | 10.64 | 44.65 | 45.3 | -0.39906 | 0.043409 | -0.3033 |  |  | 2.0006 | 44.552 | 8.3411 | 41.7141 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM475N-7RL3-B | 475 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 475 | 442.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.12 | 54.06 | 10.54 | 45.07 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 2.0509 | 46.0781 | 8.0422 | 43.4273 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM475N-7RL3-V | 475 W, 156 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 475 | 435.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.34 | 53.7 | 10.64 | 44.65 | 45.2 | -0.43668 | 0.073067 | -0.28786 |  |  | 2.0334 | 44.9546 | 8.275 | 42.1667 | [6 empty] | 2021-07-01
Jinko Solar Co., Ltd | JKM480N-7RL3-B | 480 W, 156 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 480 | 447.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 26 | 6 | N | 11.19 | 54.24 | 10.61 | 45.24 | 45.3 | -0.35826 | 0.061044 | -0.28575 |  |  | 2.0645 | 46.2519 | 8.0956 | 43.5911 | [6 empty] | 2021-02-22
Jinko Solar Co., Ltd | JKM495M-72HL4-TV | 495 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 495 | 463.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.18 | 48.82 | 12.39 | 39.96 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.3982 | 39.9502 | 9.6173 | 36.8245 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM495M-7TL4 | 495W Monocrystalline module，1000V max system Vdc. | UL 61730 | 495 | 453.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.22 | 48.7 | 12.37 | 40.02 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.3954 | 39.6539 | 9.6102 | 37.3372 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM495M-7TL4-TV | 495 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 495 | 454.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.18 | 48.82 | 12.39 | 39.96 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.3697 | 39.0655 | 9.7156 | 36.6105 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM495M-7TL4-V | 495 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 495 | 453.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.22 | 48.7 | 12.37 | 40.02 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.3954 | 39.6539 | 9.6102 | 37.3372 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM500M-72HL4 | 500 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 500 | 467.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.29 | 48.78 | 12.47 | 40.1 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.4716 | 39.7069 | 9.5504 | 37.0532 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM500M-72HL4-BDVP | 500 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 500 | 464.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.13 | 49.12 | 12.37 | 40.42 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.4267 | 39.4376 | 9.7323 | 37.8797 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM500M-72HL4-TV | 500 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 500 | 468.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.25 | 48.9 | 12.48 | 40.07 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.4156 | 40.0602 | 9.6871 | 36.9259 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM500M-72HL4-V | 500 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 500 | 467.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.29 | 48.78 | 12.47 | 40.1 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.4716 | 39.7069 | 9.5504 | 37.0532 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM500M-7TL4 | 500 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 500 | 458 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.29 | 48.78 | 12.47 | 40.1 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4148 | 39.7332 | 9.6879 | 37.4118 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM500M-7TL4-TV | 500 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 500 | 458.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.25 | 48.9 | 12.48 | 40.07 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.3869 | 39.1731 | 9.7861 | 36.7113 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM500M-7TL4-V | 500 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 500 | 458 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.29 | 48.78 | 12.47 | 40.1 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4148 | 39.7332 | 9.6879 | 37.4118 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM505M-72HL4 | 505 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 505 | 472.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.36 | 48.86 | 12.57 | 40.18 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.4914 | 39.7861 | 9.627 | 37.1271 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM505M-72HL4-BDVP | 505 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 505 | 469 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.23 | 49.18 | 12.47 | 40.5 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.4463 | 39.5157 | 9.8109 | 37.9547 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM505M-72HL4-TV | 505 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 505 | 473.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.32 | 48.98 | 12.57 | 40.18 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.4331 | 40.1702 | 9.757 | 37.0273 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM505M-72HL4-V | 505 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 505 | 472.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.36 | 48.86 | 12.57 | 40.18 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.4914 | 39.7861 | 9.627 | 37.1271 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM505M-7TL4 | 505 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 505 | 462.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.36 | 48.86 | 12.57 | 40.18 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4342 | 39.8125 | 9.7656 | 37.4865 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM505M-7TL4-TV | 505 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 505 | 463.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.32 | 48.98 | 12.57 | 40.18 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.4041 | 39.2806 | 9.8567 | 36.812 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM505M-7TL4-V | 505 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 505 | 462.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.36 | 48.86 | 12.57 | 40.18 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4342 | 39.8125 | 9.7656 | 37.4865 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM510M-72HL4 | 510 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 510 | 477.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.43 | 48.94 | 12.67 | 40.26 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5112 | 39.8653 | 9.7036 | 37.201 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM510M-72HL4-BDVP | 510 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 510 | 473.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.33 | 49.24 | 12.57 | 40.58 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.4659 | 39.5937 | 9.8896 | 38.0296 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM510M-72HL4-TV | 510 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 510 | 478.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.4 | 49.05 | 12.66 | 40.29 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.4505 | 40.2802 | 9.8268 | 37.1286 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM510M-72HL4-V | 510 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 510 | 477.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.43 | 48.94 | 12.67 | 40.26 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5112 | 39.8653 | 9.7036 | 37.201 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM510M-7TL4 | 510 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 510 | 467.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.43 | 48.94 | 12.67 | 40.26 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4535 | 39.8917 | 9.8432 | 37.5611 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM510M-7TL4-TV | 510 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 510 | 468.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.4 | 49.05 | 12.66 | 40.29 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.4214 | 39.3882 | 9.9273 | 36.9128 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM510M-7TL4-V | 510 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 510 | 467.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.43 | 48.94 | 12.67 | 40.26 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4535 | 39.8917 | 9.8432 | 37.5611 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM515M-72HL4 | 515 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 515 | 482 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.5 | 49.02 | 12.77 | 40.33 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5311 | 39.9346 | 9.7801 | 37.2657 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM515M-72HL4-BDVP | 515 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 515 | 478.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.43 | 49.3 | 12.67 | 40.65 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.4855 | 39.662 | 9.9683 | 38.0952 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM515M-72HL4-TV | 515 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 515 | 482.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.47 | 49.12 | 12.75 | 40.4 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.4679 | 40.3901 | 9.8967 | 37.23 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM515M-72HL4-V | 515 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 515 | 482 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.5 | 49.02 | 12.77 | 40.33 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5311 | 39.9346 | 9.7801 | 37.2657 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM515M-7TL4 | 515 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 515 | 472.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.5 | 49.02 | 12.77 | 40.33 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4729 | 39.9611 | 9.9209 | 37.6264 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM515M-7TL4-TV | 515 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 515 | 473 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.47 | 49.12 | 12.75 | 40.4 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.4386 | 39.4957 | 9.9979 | 37.0136 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM515M-7TL4-V | 515 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 515 | 472.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.5 | 49.02 | 12.77 | 40.33 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4729 | 39.9611 | 9.9209 | 37.6264 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM520M-72HL4 | 520 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 520 | 486.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.57 | 49.1 | 12.87 | 40.41 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5509 | 40.0138 | 9.8567 | 37.3396 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM520M-72HL4-BDVP | 520 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 520 | 483.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.53 | 49.36 | 12.77 | 40.73 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.5051 | 39.7401 | 10.047 | 38.1702 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM520M-72HL4-TV | 520 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 520 | 487.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.54 | 49.2 | 12.84 | 40.5 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.4853 | 40.4901 | 9.9666 | 37.3222 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM520M-72HL4-V | 520 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 520 | 486.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.57 | 49.1 | 12.87 | 40.41 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5509 | 40.0138 | 9.8567 | 37.3396 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM520M-7TL4 | 520 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 520 | 476.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.57 | 49.1 | 12.87 | 40.41 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4923 | 40.0404 | 9.9986 | 37.7011 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM520M-7TL4-TV | 520 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 520 | 477.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.54 | 49.2 | 12.84 | 40.5 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.4558 | 39.5935 | 10.0684 | 37.1052 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM520M-7TL4-V | 520 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 520 | 476.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.57 | 49.1 | 12.87 | 40.41 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.4923 | 40.0404 | 9.9986 | 37.7011 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM525M-72HL4 | 525 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 525 | 491.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.64 | 49.18 | 12.97 | 40.48 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5707 | 40.0831 | 9.9333 | 37.4043 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM525M-72HL4-BDVP | 525 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 525 | 488.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.63 | 49.42 | 12.87 | 40.8 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.5248 | 39.8084 | 10.1256 | 38.2358 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM525M-72HL4-TV | 525 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 525 | 492.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.64 | 49.27 | 12.93 | 40.61 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.5027 | 40.6001 | 10.0364 | 37.4235 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM525M-72HL4-V | 525 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 525 | 491.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.64 | 49.18 | 12.97 | 40.48 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5707 | 40.0831 | 9.9333 | 37.4043 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM525M-7TL4 | 525 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 525 | 481.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.64 | 49.18 | 12.97 | 40.48 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.5116 | 40.1097 | 10.0763 | 37.7664 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM525M-7TL4-TV | 525 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 525 | 482.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.64 | 49.27 | 12.93 | 40.61 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.473 | 39.701 | 10.139 | 37.206 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM525M-7TL4-V | 525 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 525 | 481.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.64 | 49.18 | 12.97 | 40.48 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.5116 | 40.1097 | 10.0763 | 37.7664 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM530M-72HL4 | 530 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 530 | 496.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.71 | 49.26 | 13.07 | 40.56 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5905 | 40.1624 | 10.0099 | 37.4782 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM530M-72HL4-BDVP | 530 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 530 | 492.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.73 | 49.48 | 12.97 | 40.87 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.5444 | 39.8767 | 10.2043 | 38.3014 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM530M-72HL4-TV | 530 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 530 | 497.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.71 | 49.35 | 13.02 | 40.71 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.5202 | 40.7 | 10.1063 | 37.5157 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM530M-72HL4-V | 530 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 530 | 496.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.71 | 49.26 | 13.07 | 40.56 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.5905 | 40.1624 | 10.0099 | 37.4782 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM530M-7TL4 | 530 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 530 | 486.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.71 | 49.26 | 13.07 | 40.56 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.531 | 40.189 | 10.154 | 37.841 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM530M-7TL4-TV | 530 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 530 | 487.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.71 | 49.35 | 13.02 | 40.71 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.4902 | 39.7988 | 10.2096 | 37.2976 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM530M-7TL4-V | 530 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 530 | 486.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.71 | 49.26 | 13.07 | 40.56 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.531 | 40.189 | 10.154 | 37.841 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM535M-72HL4 | 535 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 535 | 501.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.79 | 49.34 | 13.17 | 40.63 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.6103 | 40.2317 | 10.0865 | 37.5429 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM535M-72HL4-BDVP | 535 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 497.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.83 | 49.54 | 13.07 | 40.94 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.564 | 39.945 | 10.283 | 38.367 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM535M-72HL4-TV | 535 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 502.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.79 | 49.42 | 13.11 | 40.81 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.5376 | 40.8 | 10.1761 | 37.6078 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM535M-72HL4-V | 535 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 501.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.79 | 49.34 | 13.17 | 40.63 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.6103 | 40.2317 | 10.0865 | 37.5429 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM535M-7RL4 | 535 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 535 | 495.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 12.92 | 53.04 | 12.31 | 43.46 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.3736 | 42.9706 | 9.6379 | 40.2896 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM535M-7RL4-TV | 535 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 495.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.06 | 53.02 | 12.34 | 43.36 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.4233 | 41.9613 | 9.5972 | 40.5264 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM535M-7RL4-V | 535 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 495.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 12.92 | 53.04 | 12.31 | 43.46 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.3736 | 42.9706 | 9.6379 | 40.2896 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM535M-7TL4 | 535 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 535 | 491.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.79 | 49.34 | 13.17 | 40.63 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.5504 | 40.2584 | 10.2317 | 37.9063 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM535M-7TL4-TV | 535 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 492 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.79 | 49.42 | 13.11 | 40.81 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.5074 | 39.8965 | 10.2801 | 37.3892 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM535M-7TL4-V | 535 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 491.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.79 | 49.34 | 13.17 | 40.63 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.5504 | 40.2584 | 10.2317 | 37.9063 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM540M-72HL4 | 540 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 540 | 506.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.85 | 49.42 | 13.27 | 40.7 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.6302 | 40.301 | 10.1631 | 37.6076 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM540M-72HL4-BDVP | 540 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 502.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.89 | 49.73 | 13.13 | 41.13 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.5758 | 40.1304 | 10.3302 | 38.5451 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM540M-72HL4-TV | 540 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 507 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.87 | 49.49 | 13.2 | 40.91 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.555 | 40.9 | 10.246 | 37.7 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM540M-72HL4-V | 540 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 506.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.85 | 49.42 | 13.27 | 40.7 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.6302 | 40.301 | 10.1631 | 37.6076 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM540M-7RL4 | 540 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 540 | 500.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13 | 53.14 | 12.39 | 43.59 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.389 | 43.0991 | 9.7006 | 40.4101 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM540M-7RL4-TV | 540 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 500.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.13 | 53.1 | 12.42 | 43.48 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.439 | 42.0775 | 9.6595 | 40.6386 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM540M-7RL4-V | 540 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 500.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13 | 53.14 | 12.39 | 43.59 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.389 | 43.0991 | 9.7006 | 40.4101 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM540M-7TL4 | 540 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 540 | 495.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.85 | 49.42 | 13.27 | 40.7 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.5697 | 40.3277 | 10.3094 | 37.9716 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM540M-7TL4-TV | 540 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 496.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.87 | 49.49 | 13.2 | 40.91 | 45.3 | -0.423 | 0.0465 | -0.326 |  |  | 2.5246 | 39.9943 | 10.3507 | 37.4809 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM540M-7TL4-V | 540 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 495.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.46 | 24 | 6 | N | 13.85 | 49.42 | 13.27 | 40.7 | 46.1 | -0.415 | 0.0472 | -0.315 |  |  | 2.5697 | 40.3277 | 10.3094 | 37.9716 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM545M-72HL4-BDVP | 545 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 545 | 507.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.95 | 49.92 | 13.19 | 41.32 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.5875 | 40.3158 | 10.3774 | 38.7231 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM545M-72HL4-TV | 545 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 545 | 511.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.94 | 49.65 | 13.27 | 41.07 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.5685 | 41.06 | 10.3003 | 37.8474 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM545M-72HL4-V | 545 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 545 | 510.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 13.94 | 49.52 | 13.36 | 40.8 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.648 | 40.4 | 10.232 | 37.7 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM545M-7RL4 | 545 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 545 | 505.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.08 | 53.24 | 12.47 | 43.71 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4044 | 43.2178 | 9.7632 | 40.5213 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM545M-7RL4-TV | 545 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 545 | 505.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.2 | 53.19 | 12.5 | 43.6 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.4547 | 42.1936 | 9.7217 | 40.7507 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM545M-7RL4-V | 545 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 545 | 505.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.08 | 53.24 | 12.47 | 43.71 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4044 | 43.2178 | 9.7632 | 40.5213 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM550M-72HL4 | 550 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 550 | 515.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 14.03 | 49.62 | 13.45 | 40.9 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.6658 | 40.499 | 10.3009 | 37.7924 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM550M-72HL4-BDVP | 550 W, 144 half-cut cell dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 550 | 512 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 14.01 | 50.11 | 13.25 | 41.51 | 46.3 | -0.3479 | 0.0444 | -0.2685 |  |  | 2.5993 | 40.5011 | 10.4246 | 38.9012 | [6 empty] | 2021-05-03
Jinko Solar Co., Ltd | JKM550M-72HL4-TV | 550 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 550 | 516.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 14.01 | 49.81 | 13.34 | 41.23 | 45.24 | -0.32208 | 0.037296 | -0.25576 |  |  | 2.5821 | 41.2199 | 10.3547 | 37.9949 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM550M-72HL4-V | 550 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 550 | 515.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 14.03 | 49.62 | 13.45 | 40.9 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.6658 | 40.499 | 10.3009 | 37.7924 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM550M-7RL4 | 550 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 550 | 509.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.17 | 53.34 | 12.55 | 43.83 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4199 | 43.3364 | 9.8258 | 40.6326 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM550M-7RL4-TV | 550 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 550 | 510.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.27 | 53.27 | 12.58 | 43.72 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.4704 | 42.3097 | 9.7839 | 40.8629 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM550M-7RL4-V | 550 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 550 | 509.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.17 | 53.34 | 12.55 | 43.83 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4199 | 43.3364 | 9.8258 | 40.6326 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM555M-72HL4 | 555 W, 144 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 555 | 520.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 14.12 | 49.72 | 13.54 | 40.99 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.6837 | 40.5881 | 10.3699 | 37.8756 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM555M-72HL4-V | 555 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 555 | 520.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.5 | 24 | 6 | N | 14.12 | 49.72 | 13.54 | 40.99 | 44.6 | -0.34204 | 0.045669 | -0.29501 |  |  | 2.6837 | 40.5881 | 10.3699 | 37.8756 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM555M-7RL4 | 555 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 555 | 514.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.26 | 53.44 | 12.63 | 43.95 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4353 | 43.4551 | 9.8885 | 40.7438 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM555M-7RL4-TV | 555 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 555 | 514.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.34 | 53.36 | 12.66 | 43.84 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.4862 | 42.4258 | 9.8461 | 40.9751 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM555M-7RL4-V | 555 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 555 | 514.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.26 | 53.44 | 12.63 | 43.95 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4353 | 43.4551 | 9.8885 | 40.7438 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM560M-7RL4 | 560 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 560 | 519.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.35 | 53.54 | 12.71 | 44.06 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4507 | 43.5638 | 9.9511 | 40.8458 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM560M-7RL4-TV | 560 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 560 | 519.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.41 | 53.44 | 12.74 | 43.96 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.5019 | 42.542 | 9.9083 | 41.0872 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM560M-7RL4-V | 560 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 560 | 519.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.35 | 53.54 | 12.71 | 44.06 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4507 | 43.5638 | 9.9511 | 40.8458 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM565M-7RL4 | 565 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 565 | 524.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.44 | 53.64 | 12.79 | 44.18 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4661 | 43.6825 | 10.0137 | 40.957 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM565M-7RL4-TV | 565 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 565 | 524.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.48 | 53.53 | 12.82 | 44.08 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.5176 | 42.6581 | 9.9706 | 41.1994 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM565M-7RL4-V | 565 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 565 | 524.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.44 | 53.64 | 12.79 | 44.18 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4661 | 43.6825 | 10.0137 | 40.957 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM570M-7RL4 | 570 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 570 | 529 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.52 | 53.74 | 12.87 | 44.29 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4816 | 43.7912 | 10.0764 | 41.059 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM570M-7RL4-TV | 570 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 570 | 529.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.55 | 53.61 | 12.9 | 44.19 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.5333 | 42.7645 | 10.0328 | 41.3022 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM570M-7RL4-V | 570 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 570 | 529 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.52 | 53.74 | 12.87 | 44.29 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.4816 | 43.7912 | 10.0764 | 41.059 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM575M-7RL4 | 575 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 575 | 533.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.61 | 53.84 | 12.95 | 44.4 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.497 | 43.9 | 10.139 | 41.161 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM575M-7RL4-TV | 575 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 575 | 534 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.62 | 53.7 | 12.98 | 44.3 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.549 | 42.871 | 10.095 | 41.405 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM575M-7RL4-V | 575 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 575 | 533.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.61 | 53.84 | 12.95 | 44.4 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.497 | 43.9 | 10.139 | 41.161 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM580M-7RL4 | 580 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 580 | 538.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.68 | 53.94 | 13.03 | 44.52 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.5124 | 44.0186 | 10.2016 | 41.2722 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM580M-7RL4-TV | 580 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 580 | 538.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.7 | 53.81 | 13.06 | 44.41 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.5647 | 42.9775 | 10.1572 | 41.5078 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM580M-7RL4-V | 580 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 580 | 538.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.68 | 53.94 | 13.03 | 44.52 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.5124 | 44.0186 | 10.2016 | 41.2722 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM585M-7RL4 | 585 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 585 | 543.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.75 | 54.04 | 13.11 | 44.63 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.5279 | 44.1274 | 10.2643 | 41.3742 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM585M-7RL4-TV | 585 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 585 | 543.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.78 | 53.92 | 13.14 | 44.52 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.5804 | 43.0839 | 10.2194 | 41.6106 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM585M-7RL4-V | 585 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 585 | 543.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.75 | 54.04 | 13.11 | 44.63 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.5279 | 44.1274 | 10.2643 | 41.3742 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM590M-7RL4 | 590 W, 156 half-cut cell monocrystalline module, 1000V max system Vdc | UL 61730 | 590 | 548.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.81 | 54.14 | 13.19 | 44.73 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.5433 | 44.2263 | 10.3269 | 41.4669 | [6 empty] | 2021-04-01
Jinko Solar Co., Ltd | JKM590M-7RL4-TV | 590 W, 156 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 590 | 548.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.86 | 54.03 | 13.22 | 44.63 | 45.5 | -0.37122 | 0.062194 | -0.27053 |  |  | 2.5961 | 43.1904 | 10.2817 | 41.7134 | [6 empty] | 2021-03-01
Jinko Solar Co., Ltd | JKM590M-7RL4-V | 590 W, 156 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 590 | 548.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.66 | 26 | 6 | N | 13.81 | 54.14 | 13.19 | 44.73 | 45.7 | -0.36887 | 0.06687 | -0.26551 |  |  | 2.5433 | 44.2263 | 10.3269 | 41.4669 | [6 empty] | 2021-04-01
Jinzhou Jinmao Photovoltaic Technology | JMPV-5M/36-85 | 85 W Monocrystalline Module | UL 1703 | 85 | 74.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.66425 | 36 | 1 | N | 5.08 | 22 | 4.81 | 17.66 | 46.1 | -0.5597 | 0.037 | -0.4164 | -0.0499 | -0.5597 | 0.94291 | 16.9334 | 3.7707 | 15.9385 | Rack | Flat Plate | 0.554 | 1.199 | 1 | 0.18784
Jinzhou Jinmao Photovoltaic Technology | JMPV-5M/36-90 | 90 W Monocrystalline Module | UL 1703 | 90 | 78.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.66425 | 36 | 1 | N | 5.29 | 22.2 | 4.99 | 18.03 | 46.1 | -0.5597 | 0.037 | -0.4164 | -0.0499 | -0.5597 | 1.0048 | 17.6666 | 3.9862 | 16.1612 | Rack | Flat Plate | 0.554 | 1.199 | 1 | 0.19724
Jinzhou Jinmao Photovoltaic Technology | JMPV-5M/36-95 | 95 W Monocrystalline Module | UL 1703 | 95 | 83.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.66425 | 36 | 1 | N | 5.49 | 22.39 | 5.16 | 18.4 | 46.1 | -0.5597 | 0.037 | -0.4164 | -0.0499 | -0.5597 | 1.039 | 18.0291 | 4.122 | 16.4928 | Rack | Flat Plate | 0.554 | 1.199 | 1 | 0.19719
Jinzhou Jinmao Photovoltaic Technology | JMPV-5M/72-165 | 165 W Monocrystalline Module | UL 1703 | 165 | 142.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.2 | 43.51 | 4.79 | 34.45 | 45.9 | -0.6046 | 0.0344 | -0.4186 | -0.0453 | -0.5596 | 0.93224 | 32.8086 | 3.8001 | 30.7834 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18537
Jinzhou Jinmao Photovoltaic Technology | JMPV-5M/72-170 | 170 W Monocrystalline Module | UL 1703 | 170 | 146.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.29 | 43.75 | 4.87 | 34.89 | 45.9 | -0.6046 | 0.0344 | -0.4186 | -0.0453 | -0.5596 | 0.94781 | 33.2276 | 3.8636 | 31.1766 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18526
Jinzhou Jinmao Photovoltaic Technology | JMPV-5M/72-175 | 175 W Monocrystalline Module | UL 1703 | 175 | 151.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.39 | 43.99 | 4.95 | 35.33 | 45.9 | -0.6046 | 0.0344 | -0.4186 | -0.0453 | -0.5596 | 0.96338 | 33.6467 | 3.927 | 31.5698 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18523
Jinzhou Jinmao Photovoltaic Technology | JMPV-5M/72-180 | 180 W Monocrystalline Module | UL 1703 | 180 | 155.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.48 | 44.23 | 5.03 | 35.77 | 45.9 | -0.6046 | 0.0344 | -0.4186 | -0.0453 | -0.5596 | 1.0113 | 35.0398 | 4.0138 | 31.8632 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19687
Jinzhou Jinmao Photovoltaic Technology | JMPV-5M/72-185 | 185 W Monocrystalline Module | UL 1703 | 185 | 160.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.57 | 44.47 | 5.11 | 36.21 | 45.9 | -0.6046 | 0.0344 | -0.4186 | -0.0453 | -0.5596 | 1.0274 | 35.4708 | 4.0776 | 32.2552 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19699
Jinzhou Jinmao Photovoltaic Technology | JMPV-5M/72-190 | 190 W Monocrystalline Module | UL 1703 | 190 | 164.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.66 | 44.71 | 5.18 | 36.65 | 45.9 | -0.6046 | 0.0344 | -0.4186 | -0.0453 | -0.5596 | 1.0415 | 35.9018 | 4.1335 | 32.6471 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19679
Juli New Energy | JLS155M | 155 W Monocrystalline Module | UL 1703 | 155 | 132.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 4.96 | 42 | 4.43 | 35 | 47.1 | -0.59432 | 0.04901 | -0.44615 | -0.033635 | -0.56584 | 0.85955 | 35.9651 | 3.5174 | 31.1494 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19944
Juli New Energy | JLS160M | 160 W Monocrystalline Module | UL 1703 | 160 | 137 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.12 | 42 | 4.57 | 35 | 47.1 | -0.59432 | 0.04901 | -0.44615 | -0.033635 | -0.56584 | 0.88672 | 35.9651 | 3.6285 | 31.1494 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19932
Juli New Energy | JLS165M | 165 W Monocrystalline Module | UL 1703 | 165 | 141.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.28 | 42 | 4.71 | 35 | 47.1 | -0.59432 | 0.04901 | -0.44615 | -0.033635 | -0.56584 | 0.91388 | 35.9651 | 3.7397 | 31.1494 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.1992
Juli New Energy | JLS170M | 170 W Monocrystalline Module | UL 1703 | 170 | 148.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.36 | 42.6 | 4.79 | 35.5 | 46.5 | -0.54243 | 0.041431 | -0.39283 | -0.054934 | -0.48941 | 0.96775 | 35.4132 | 3.8476 | 31.3542 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20159
Juli New Energy | JLS175M | 175 W Monocrystalline Module | UL 1703 | 175 | 153.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.52 | 42.6 | 4.93 | 35.5 | 46.5 | -0.54243 | 0.041431 | -0.39283 | -0.054934 | -0.48941 | 0.99603 | 35.4132 | 3.96 | 31.3542 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20156
Juli New Energy | JLS180M | 180 W Monocrystalline Module | UL 1703 | 180 | 157.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.6 | 43.2 | 5 | 36 | 46.5 | -0.54243 | 0.041431 | -0.39283 | -0.054934 | -0.48941 | 1.0102 | 35.912 | 4.0163 | 31.7958 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20154
Juli New Energy | JLS200M | 200 W Monocrystalline Module | UL 1703 | 200 | 177.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 60 | 1 | N | 7.86 | 34.2 | 7.02 | 28.5 | 47.7 | -0.47102 | 0.083468 | -0.35233 | -0.01328 | -0.45669 | 1.3294 | 29.8529 | 5.7185 | 25.2609 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19844
Juli New Energy | JLS205M | 205 W Monocrystalline Module | UL 1703 | 205 | 182.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 60 | 1 | N | 8.05 | 34.2 | 7.16 | 28.5 | 47.7 | -0.47102 | 0.083468 | -0.35233 | -0.01328 | -0.45669 | 1.3559 | 29.8529 | 5.8326 | 25.2609 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19746
Juli New Energy | JLS210M | 210 W Monocrystalline Module | UL 1703 | 210 | 187 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 60 | 1 | N | 8.11 | 34.8 | 7.24 | 29 | 47.7 | -0.47102 | 0.083468 | -0.35233 | -0.01328 | -0.45669 | 1.3711 | 30.3766 | 5.8978 | 25.7041 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19833
Juli New Energy | JLS215P | 215 W Polycrystalline Module | UL 1703 | 215 | 188.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 60 | 1 | N | 8.3 | 34.8 | 7.41 | 29 | 47.7 | -0.53034 | 0.067002 | -0.38244 | 0.00638 | -0.54101 | 1.4968 | 29.7395 | 5.8991 | 25.9721 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20704
Juli New Energy | JLS220P | 220 W Polycrystalline Module | UL 1703 | 220 | 191.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.36 | 35.4 | 7.46 | 29.5 | 47.7 | -0.53034 | 0.067002 | -0.38244 | 0.00638 | -0.54101 | 1.4968 | 30.2522 | 5.8991 | 26.4199 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20582
Juli New Energy | JLS225P | 225 W Polycrystalline Module | UL 1703 | 225 | 196 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.55 | 35.4 | 7.63 | 29.5 | 47.7 | -0.53034 | 0.067002 | -0.38244 | 0.00638 | -0.54101 | 1.5412 | 30.2522 | 6.0742 | 26.4199 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20722
Juli New Energy | JLS230P | 230 W Polycrystalline Module | UL 1703 | 230 | 200.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.59 | 36 | 7.67 | 30 | 47.7 | -0.53034 | 0.067002 | -0.38244 | 0.00638 | -0.54101 | 1.5493 | 30.765 | 6.1061 | 26.8677 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20723
Juli New Energy | JLS60P240WH(156) | 240 W Polycrystalline Module | UL 1703 | 240 | 212.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.56 | 37.2 | 8.01 | 30 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.6 | 28.71 | 6.49 | 27.52 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.1914
Juli New Energy | JLS60P245WH(156) | 245 W Polycrystalline Module | UL 1703 | 245 | 217.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.69 | 37.4 | 8.12 | 30.2 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.62 | 28.91 | 6.58 | 27.71 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19116
Juli New Energy | JLS60M250WH(156) | 250 W Monocrystalline Module | UL 1703 | 250 | 221.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.79 | 38 | 8.14 | 30.7 | 47 | -0.493 | 0.053 | -0.365 | 0.006 | -0.498 | 1.58 | 29.83 | 6.6 | 27.41 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18853
Juli New Energy | JLS60P250WH(156) | 250 W Polycrystalline Module | UL 1703 | 250 | 222 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.81 | 37.6 | 8.23 | 30.4 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.64 | 29.1 | 6.67 | 27.89 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.1909
Juli New Energy | JLS60M255WH(156) | 255 W Monocrystalline Module | UL 1703 | 255 | 226.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.81 | 38.5 | 8.23 | 31 | 47 | -0.493 | 0.053 | -0.365 | 0.006 | -0.498 | 1.6 | 30.12 | 6.67 | 27.68 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18899
Juli New Energy | JLS60P255WH(156) | 255 W Polycrystalline Module | UL 1703 | 255 | 226.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.83 | 37.8 | 8.25 | 30.9 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.64 | 29.58 | 6.69 | 28.35 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19024
Juli New Energy | JLS60M260WH(156) | 260 W Monocrystalline Module | UL 1703 | 260 | 230.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.86 | 39 | 8.25 | 31.5 | 47 | -0.493 | 0.053 | -0.365 | 0.006 | -0.498 | 1.6 | 30.6 | 6.69 | 28.13 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18831
Juli New Energy | JLS60P260WH(156) | 260 W Polycrystalline Module | UL 1703 | 260 | 231.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.85 | 37.9 | 8.26 | 31.5 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.65 | 30.15 | 6.69 | 28.9 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.19134
Juli New Energy | JLS60M265WH(156) | 265 W Monocrystalline Module | UL 1703 | 265 | 235.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6368 | 60 | 1 | N | 8.95 | 39.1 | 8.41 | 31.5 | 47 | -0.493 | 0.053 | -0.365 | 0.006 | -0.498 | 1.63 | 30.6 | 6.81 | 28.13 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.18822
Juli New Energy | JLS72P290WH(156) | 290 W Polycrystalline Module | UL 1703 | 290 | 257.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 44.9 | 8.1 | 35.8 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.54 | 34.7 | 6.53 | 32.02 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18427
Juli New Energy | JLS72P295WH(156) | 295 W Polycrystalline Module | UL 1703 | 295 | 261.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.71 | 45 | 8.15 | 36.2 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.55 | 35.09 | 6.57 | 32.38 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18437
Juli New Energy | JLS72M300WH(156) | 300 W Monocrystalline Module | UL 1703 | 300 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.81 | 45.5 | 8.21 | 36.5 | 47 | -0.493 | 0.053 | -0.365 | 0.006 | -0.498 | 1.58 | 35.37 | 6.65 | 32.49 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18628
Juli New Energy | JLS72P300WH(156) | 300 W Polycrystalline Module | UL 1703 | 300 | 266.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.8 | 45.1 | 8.21 | 36.5 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.56 | 35.38 | 6.62 | 32.65 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18398
Juli New Energy | JLS72M305WH(156) | 305 W Monocrystalline Module | UL 1703 | 305 | 270.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.85 | 45.7 | 8.25 | 37 | 47 | -0.493 | 0.053 | -0.365 | 0.006 | -0.498 | 1.59 | 35.86 | 6.68 | 32.93 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18694
Juli New Energy | JLS72P305WH(156) | 305 W Polycrystalline Module | UL 1703 | 305 | 271.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.82 | 45.5 | 8.23 | 37.1 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.57 | 35.96 | 6.64 | 33.19 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18511
Juli New Energy | JLS72M310WH(156) | 310 W Monocrystalline Module | UL 1703 | 310 | 275.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.93 | 45.8 | 8.34 | 37.2 | 47 | -0.493 | 0.053 | -0.365 | 0.006 | -0.498 | 1.61 | 36.05 | 6.75 | 33.11 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18723
Juli New Energy | JLS72P310WH(156) | 310 W Polycrystalline Module | UL 1703 | 310 | 275.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.84 | 45.7 | 8.25 | 37.6 | 47.1 | -0.484 | 0.054 | -0.346 | 0.003 | -0.485 | 1.57 | 36.45 | 6.65 | 33.63 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1846
Juli New Energy | JLS72M315WH(156) | 315 W Monocrystalline Module | UL 1703 | 315 | 279.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.95 | 46 | 8.39 | 37.6 | 47 | -0.493 | 0.053 | -0.365 | 0.006 | -0.498 | 1.61 | 36.44 | 6.79 | 33.47 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18625
Juli New Energy | JLS72M320WH(156) | 320 W Monocrystalline Module | UL 1703 | 320 | 284.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.97 | 46.1 | 8.43 | 37.9 | 47 | -0.493 | 0.053 | -0.365 | 0.006 | -0.498 | 1.62 | 36.73 | 6.83 | 33.73 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18595
KOSOL ENERGIE PVT. LTD. | KE200 | 200 W, 48 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 200 | 181.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.31 | 48 | 1 | N | 8.64 | 29.62 | 8.17 | 24.71 | 45.88 | -0.4229 | 0.0226 | -0.3086 | -0.0302 | -0.3904 | 1.6496 | 23.1265 | 6.5789 | 22.0318 | [6 empty] | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE205 | 205 W, 48 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 205 | 186.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.31 | 48 | 1 | N | 8.73 | 29.81 | 8.28 | 24.95 | 45.88 | -0.4229 | 0.0226 | -0.3086 | -0.0302 | -0.3904 | 1.6718 | 23.3511 | 6.6675 | 22.2458 | [6 empty] | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE210 | 210 W, 48 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 210 | 190.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.31 | 48 | 1 | N | 8.8 | 30.18 | 8.37 | 25.28 | 45.88 | -0.4229 | 0.0226 | -0.3086 | -0.0302 | -0.3904 | 1.69 | 23.66 | 6.74 | 22.54 | [6 empty] | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE225 | 225 W, 54 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 225 | 202.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.46 | 54 | 1 | N | 8.64 | 33.32 | 8.17 | 27.8 | 45.88 | -0.4567 | 0.0192 | -0.3379 | -0.0395 | -0.4198 | 1.6458 | 26.3529 | 6.5928 | 24.896 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19276 |  | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE230 | 230 W, 54 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 230 | 207.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.46 | 54 | 1 | N | 8.73 | 33.53 | 8.28 | 28.07 | 45.88 | -0.4567 | 0.0192 | -0.3379 | -0.0395 | -0.4198 | 1.6679 | 26.6088 | 6.6816 | 25.1378 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19296 |  | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE235 | 235 W, 54 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 235 | 211.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.46 | 54 | 1 | N | 8.78 | 33.72 | 8.34 | 28.24 | 45.88 | -0.4567 | 0.0192 | -0.3379 | -0.0395 | -0.4198 | 1.68 | 26.77 | 6.73 | 25.29 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19138 |  | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE240 | 240 W Polycrystalline Module | UL 1703 | 240 | 219.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.48 | 37.14 | 7.93 | 30.27 | 47.7 | -0.3431 | 0.0288 | -0.244 | -0.0176 | -0.3105 | 1.6484 | 29.3168 | 6.5326 | 27.5457 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.20136 |  | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE245 | 245 W Polycrystalline Module | UL 1703 | 245 | 224.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.55 | 37.53 | 8 | 30.65 | 47.7 | -0.3431 | 0.0288 | -0.244 | -0.0176 | -0.3105 | 1.663 | 29.6849 | 6.5902 | 27.8915 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.20149 |  | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE250 | 250 W, 60 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 250 | 225.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 8.64 | 37.02 | 8.17 | 30.89 | 45.88 | -0.4422 | 0.0274 | -0.3216 | -0.029 | -0.4123 | 1.636 | 29.2419 | 6.5438 | 27.8602 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19135 |  | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE255 | 255 W, 60 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 255 | 230.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 8.68 | 37.2 | 8.22 | 31.07 | 45.88 | -0.4422 | 0.0274 | -0.3216 | -0.029 | -0.4123 | 1.646 | 29.4123 | 6.5839 | 28.0226 | [6 empty] | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE260 | 260 W, 60 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 260 | 235.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 8.78 | 37.37 | 8.34 | 31.3 | 45.88 | -0.4422 | 0.0274 | -0.3216 | -0.029 | -0.4123 | 1.67 | 29.63 | 6.68 | 28.23 | [6 empty] | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE265 | 265 W, 60 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 265 | 239.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 8.88 | 37.61 | 8.46 | 31.54 | 45.88 | -0.4422 | 0.0274 | -0.3216 | -0.029 | -0.4123 | 1.694 | 29.8572 | 6.7761 | 28.4465 | [6 empty] | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE300 | 300 W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 300 | 273.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 | 1 | N | 8.64 | 44.42 | 8.17 | 37.07 | 45.88 | -0.405 | 0.0278 | -0.3078 | -0.0219 | -0.3893 | 1.6301 | 34.7238 | 6.4423 | 32.7393 | [6 empty] | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE305 | 305 W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 305 | 278.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 | 1 | N | 8.68 | 44.64 | 8.22 | 37.28 | 45.88 | -0.405 | 0.0278 | -0.3078 | -0.0219 | -0.3893 | 1.6401 | 34.9205 | 6.4817 | 32.9248 | [6 empty] | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE310 | 310 W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 310 | 282.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 | 1 | N | 8.78 | 44.85 | 8.34 | 37.56 | 45.88 | -0.405 | 0.0278 | -0.3078 | -0.0219 | -0.3893 | 1.664 | 35.1828 | 6.5763 | 33.1721 | [6 empty] | 2019-03-01
KOSOL ENERGIE PVT. LTD. | KE315 | 315 W, 72 cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 287.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 | 1 | N | 8.8 | 45.27 | 8.37 | 37.92 | 45.88 | -0.405 | 0.0278 | -0.3078 | -0.0219 | -0.3893 | 1.67 | 35.52 | 6.6 | 33.49 | [6 empty] | 2019-03-01
La Solar LLC | LS430HC | 430 W, 144 half-cut cell monodrystalline module, 1500V max system Vdc | UL 61730 | 430 | 401.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2092 | 72 | 2 | N | 11.24 | 48.8 | 10.66 | 40.3 | 44.1 | -0.3583 | 0.0488 | -0.3743 |  |  | 2.0242 | 40.6165 | 8.0659 | 40.0995 | [6 empty] | 2021-08-23
La Solar LLC | LS435HC | 435 W, 144 half-cut cell monodrystalline module, 1500V max system Vdc | UL 61730 | 435 | 406.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2092 | 72 | 2 | N | 11.31 | 49 | 10.74 | 40.5 | 44.1 | -0.3583 | 0.0488 | -0.3743 |  |  | 2.0394 | 40.8181 | 8.1264 | 40.2985 | [6 empty] | 2021-08-23
La Solar LLC | LS440HC | 440 W, 144 half-cut cell monodrystalline module, 1500V max system Vdc | UL 61730 | 440 | 410.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2092 | 72 | 2 | N | 11.39 | 49.2 | 10.82 | 40.7 | 44.1 | -0.3583 | 0.0488 | -0.3743 |  |  | 2.0546 | 41.0196 | 8.1869 | 40.4975 | [6 empty] | 2021-08-23
La Solar LLC | LS445HC | 445 W, 144 half-cut cell monodrystalline module, 1500V max system Vdc | UL 61730 | 445 | 415.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2092 | 72 | 2 | N | 11.46 | 49.4 | 10.9 | 40.8 | 44.1 | -0.3583 | 0.0488 | -0.3743 |  |  | 2.0698 | 41.1204 | 8.2475 | 40.597 | [6 empty] | 2021-08-23
La Solar LLC | LS450HC | 450 W, 144 half-cut cell monodrystalline module, 1500V max system Vdc | UL 61730 | 450 | 420.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2092 | 72 | 2 | N | 11.53 | 49.6 | 10.98 | 41 | 44.1 | -0.3583 | 0.0488 | -0.3743 |  |  | 2.085 | 41.322 | 8.308 | 40.796 | [6 empty] | 2021-08-23
LDK Solar | LDK-170D-24 | 170 W Monocrystalline Module | UL 1703 | 170 | 152.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2815 | 72 | 1 | N | 5.42 | 44.5 | 4.76 | 35.4 | 46.2 | -0.445 | 0.051268 | -0.3366 | 0.013972 | -0.45394 | 0.75933 | 30.0857 | 3.126 | 28.755 | Rack | Flat Plate | 0.808 | 1.586 | 1 | 0.13438
LDK Solar | LDK-175D-24 | 175 W Monocrystalline Module | UL 1703 | 175 | 157.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2815 | 72 | 1 | N | 5.43 | 44.7 | 4.87 | 35.9 | 46.2 | -0.445 | 0.051268 | -0.3366 | 0.013972 | -0.45394 | 0.76126 | 31.0469 | 3.1339 | 29.6737 | Rack | Flat Plate | 0.808 | 1.586 | 1 | 0.13506
LDK Solar | LDK-180D-24 | 180 W Monocrystalline Module | UL 1703 | 180 | 161.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2815 | 72 | 1 | N | 5.46 | 44.9 | 4.98 | 36.2 | 46.2 | -0.445 | 0.051268 | -0.3366 | 0.013972 | -0.45394 | 0.76513 | 31.5275 | 3.1498 | 30.133 | Rack | Flat Plate | 0.808 | 1.586 | 1 | 0.13401
LDK Solar | LDK-180P-24(S) | 180 W Polycrystalline Module | UL 1703 | 180 | 160.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 5.45 | 44.5 | 5.04 | 35.8 | 47.7 | -0.4521 | 0.0782 | -0.3215 | 0.0068 | -0.4449 | 1.0311 | 35.2294 | 4.0902 | 31.805 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20181
LDK Solar | LDK-185P-24(S) | 185 W Polycrystalline Module | UL 1703 | 185 | 164.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 5.5 | 44.9 | 5.11 | 36.3 | 47.7 | -0.4521 | 0.0782 | -0.3215 | 0.0068 | -0.4449 | 1.0455 | 35.7215 | 4.147 | 32.2492 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20187
LDK Solar | LDK-190D-24(S) | 190 W Monocrystalline Module | UL 1703 | 190 | 170.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.69 | 44.9 | 5.3 | 36 | 47 | -0.45197 | 0.0459 | -0.31996 | -0.0307 | -0.425 | 1.068 | 35.6005 | 4.2549 | 32.1737 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.20011
LDK Solar | LDK-190P-18 | 190 W Polycrystalline Module | UL 1703 | 190 | 166.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4751 | 72 | 1 | N | 7.97 | 32.6 | 7.11 | 26.7 | 47.4 | -0.51441 | 0.061305 | -0.36957 | -0.041918 | -0.47856 | 1.4799 | 26.7405 | 5.6524 | 24.0959 | Rack | Flat Plate | 0.994 | 1.484 | 1 | 0.20828
LDK Solar | LDK-190P-24(S) | 190 W Polycrystalline Module | UL 1703 | 190 | 169.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2766 | 72 | 1 | N | 5.54 | 45.4 | 5.17 | 36.8 | 47.7 | -0.4521 | 0.0782 | -0.3215 | 0.0068 | -0.4449 | 1.0577 | 36.2135 | 4.1957 | 32.6934 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.2016
LDK Solar | LDK-195D-24(S) | 195 W Monocrystalline Module | UL 1703 | 195 | 174.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.74 | 45.2 | 5.37 | 36.4 | 47 | -0.45197 | 0.0459 | -0.31996 | -0.0307 | -0.425 | 1.0821 | 35.996 | 4.3111 | 32.5312 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19975
LDK Solar | LDK-200D-24(S) | 200 W Monocrystalline Module | UL 1703 | 200 | 179.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.8 | 45.4 | 5.44 | 36.9 | 47 | -0.45197 | 0.0459 | -0.31996 | -0.0307 | -0.425 | 1.0962 | 36.4905 | 4.3673 | 32.978 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.2
LDK Solar | LDK-200P-18 | 200 W Polycrystalline Module | UL 1703 | 200 | 175.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4751 | 72 | 1 | N | 8.25 | 32.8 | 7.44 | 26.9 | 47.4 | -0.51441 | 0.061305 | -0.36957 | -0.041918 | -0.47856 | 1.5486 | 26.9408 | 5.9148 | 24.2764 | Rack | Flat Plate | 0.994 | 1.484 | 1 | 0.20861
LDK Solar | LDK-210P-18 | 210 W Polycrystalline Module | UL 1703 | 210 | 184.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4751 | 72 | 1 | N | 8.47 | 33.2 | 7.75 | 27.1 | 47.4 | -0.51441 | 0.061305 | -0.36957 | -0.041918 | -0.47856 | 1.6131 | 27.1411 | 6.1612 | 24.4569 | Rack | Flat Plate | 0.994 | 1.484 | 1 | 0.20849
LDK Solar | LDK-210P-20 | 210 W Polycrystalline Module | UL 1703 | 210 | 183 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6321 | 72 | 1 | N | 7.83 | 36.1 | 7.07 | 29.7 | 47.9 | -0.51679 | 0.061713 | -0.37232 | -0.027686 | -0.48998 | 1.4075 | 30.9615 | 5.6868 | 26.2183 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.20751
LDK Solar | LDK-220D-20 | 220 W Monocrystalline Module | UL 1703 | 220 | 189.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6321 | 72 | 1 | N | 8.01 | 36.9 | 7.05 | 31.2 | 47.8 | -0.56103 | 0.044498 | -0.398 | -0.029697 | -0.53477 | 1.4437 | 31.2527 | 5.6273 | 27.4396 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.20509
LDK Solar | LDK-220P-20 | 220 W Polycrystalline Module | UL 1703 | 220 | 192 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6321 | 72 | 1 | N | 8.14 | 36.5 | 7.4 | 29.8 | 47.9 | -0.51679 | 0.061713 | -0.37232 | -0.027686 | -0.48998 | 1.4732 | 31.0657 | 5.9522 | 26.3066 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.20802
LDK Solar | LDK-225P-20 | 225 W Polycrystalline Module | UL 1703 | 225 | 200.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6321 | 60 | 1 | N | 8.36 | 36.6 | 7.78 | 29 | 47.7 | -0.4521 | 0.0782 | -0.3215 | 0.0068 | -0.4449 | 1.6142 | 29.1022 | 6.2855 | 25.9141 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.20879
LDK Solar | LDK-230D-20 | 230 W Monocrystalline Module | UL 1703 | 230 | 206.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6321 | 60 | 1 | N | 8.21 | 37.2 | 7.23 | 31.8 | 46.5 | -0.45197 | 0.045949 | -0.31996 | -0.03079 | -0.425 | 1.3969 | 30.5663 | 5.7508 | 29.2143 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.18565
LDK Solar | LDK-230P-20 | 230 W Polycrystalline Module | UL 1703 | 230 | 204.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6321 | 60 | 1 | N | 8.43 | 36.9 | 7.88 | 29.3 | 47.7 | -0.4521 | 0.0782 | -0.3215 | 0.0068 | -0.4449 | 1.635 | 29.4033 | 6.3663 | 26.1822 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.20902
LDK Solar | LDK-235D-20 | 235 W Monocrystalline Module | UL 1703 | 235 | 210.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6321 | 60 | 1 | N | 8.3 | 37.2 | 7.35 | 32 | 46.5 | -0.45197 | 0.045949 | -0.31996 | -0.03079 | -0.425 | 1.4201 | 30.7585 | 5.8463 | 29.3981 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.18588
LDK Solar | LDK-235P-20 | 235 W Polycrystalline Module | UL 1703 | 235 | 209.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6321 | 60 | 1 | N | 8.5 | 37.1 | 7.98 | 29.5 | 47.7 | -0.4521 | 0.0782 | -0.3215 | 0.0068 | -0.4449 | 1.6557 | 29.604 | 6.4471 | 26.3609 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.20858
LDK Solar | LDK-240D-20 | 240 W Monocrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6321 | 60 | 1 | N | 8.39 | 37.3 | 7.45 | 32.2 | 46.5 | -0.45197 | 0.045949 | -0.31996 | -0.03079 | -0.425 | 1.4394 | 30.9508 | 5.9258 | 29.5818 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.18563
LDK Solar | LDK-240P-20 | 240 W Polycrystalline Module | UL 1703 | 240 | 214 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6321 | 60 | 1 | N | 8.56 | 37.3 | 8.08 | 29.8 | 47.7 | -0.4521 | 0.0782 | -0.3215 | 0.0068 | -0.4449 | 1.6765 | 29.905 | 6.5279 | 26.629 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.2089
LDK Solar | LDK-245D-20 | 245 W Monocrystalline Module | UL 1703 | 245 | 220 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6321 | 60 | 1 | N | 8.48 | 37.4 | 7.56 | 32.4 | 46.5 | -0.45197 | 0.045949 | -0.31996 | -0.03079 | -0.425 | 1.4607 | 31.143 | 6.0133 | 29.7656 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.18568
LDK Solar | LDK-245P-20 | 245 W Polycrystalline Module | UL 1703 | 245 | 216.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6321 | 60 | 1 | N | 8.63 | 37.5 | 8.18 | 30 | 48 | -0.4859 | 0.06073 | -0.3592 | 0.00598 | -0.48489 | 1.7036 | 29.6108 | 6.5717 | 26.6568 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.2059
LDK Solar | LDK-250D-20 | 250 W Monocrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6321 | 60 | 1 | N | 8.57 | 37.5 | 7.67 | 32.6 | 46.5 | -0.45197 | 0.045949 | -0.31996 | -0.03079 | -0.425 | 1.4819 | 31.3353 | 6.1008 | 29.9493 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.18575
LDK Solar | LDK-250P-20 | 250 W Polycrystalline Module | UL 1703 | 250 | 220.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6321 | 60 | 1 | N | 8.69 | 37.7 | 8.27 | 30.3 | 48 | -0.4859 | 0.06073 | -0.3592 | 0.00598 | -0.48489 | 1.7224 | 29.9069 | 6.644 | 26.9234 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.20604
LDK Solar | LDK-255D-20 | 255 W Monocrystalline Module | UL 1703 | 255 | 226.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6321 | 60 | 1 | N | 8.93 | 38.1 | 8.43 | 30.3 | 48 | -0.4726 | 0.04809 | -0.35 | 0.006843 | -0.47167 | 1.7451 | 29.3887 | 6.8127 | 27.0992 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.20112
LDK Solar | LDK-255P-20 | 255 W Polycrystalline Module | UL 1703 | 255 | 225.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6321 | 60 | 1 | N | 8.76 | 37.9 | 8.37 | 30.5 | 48 | -0.4859 | 0.06073 | -0.3592 | 0.00598 | -0.48489 | 1.7432 | 30.1043 | 6.7243 | 27.1011 | Rack | Flat Plate | 0.994 | 1.642 | 1 | 0.20579
LDK Solar | LDK-260P-24 | 260 W Polycrystalline Module | UL 1703 | 260 | 228 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9463 | 72 | 1 | N | 8.06 | 44.2 | 7.23 | 36 | 47.6 | -0.50494 | 0.055758 | -0.36384 | -0.017038 | -0.48631 | 1.4526 | 35.7285 | 5.8778 | 32.2089 | Rack | Flat Plate | 0.994 | 1.958 | 1 | 0.19962
LDK Solar | LDK-270P-24 | 270 W Polycrystalline Module | UL 1703 | 270 | 237 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9463 | 72 | 1 | N | 8.21 | 44.2 | 7.47 | 36.2 | 47.6 | -0.50494 | 0.055758 | -0.36384 | -0.017038 | -0.48631 | 1.5009 | 35.927 | 6.0729 | 32.3879 | Rack | Flat Plate | 0.994 | 1.958 | 1 | 0.19971
LDK Solar | LDK-275P-24 | 275 W Polycrystalline Module | UL 1703 | 275 | 242.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9463 | 72 | 1 | N | 8.41 | 44.3 | 7.92 | 34.8 | 48 | -0.4859 | 0.06073 | -0.3592 | 0.00598 | -0.48489 | 1.6129 | 34.1323 | 6.3374 | 31.6001 | Rack | Flat Plate | 0.994 | 1.958 | 1 | 0.20019
LDK Solar | LDK-280P-24 | 280 W Polycrystalline Module | UL 1703 | 280 | 251.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9463 | 72 | 1 | N | 8.36 | 44.3 | 7.72 | 36.3 | 46.4 | -0.45297 | 0.054099 | -0.32113 | -0.02249 | -0.43278 | 1.4916 | 34.8917 | 6.1406 | 33.3485 | Rack | Flat Plate | 0.994 | 1.958 | 1 | 0.18587
LDK Solar | LDK-285P-24 | 285 W Polycrystalline Module | UL 1703 | 285 | 255.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9463 | 72 | 1 | N | 8.44 | 44.4 | 7.83 | 36.4 | 46.4 | -0.45297 | 0.054099 | -0.32113 | -0.02249 | -0.43278 | 1.5129 | 34.9878 | 6.2281 | 33.4403 | Rack | Flat Plate | 0.994 | 1.958 | 1 | 0.18573
LDK Solar | LDK-290P-24 | 290 W Polycrystalline Module | UL 1703 | 290 | 260.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9463 | 72 | 1 | N | 8.52 | 44.4 | 7.95 | 36.5 | 46.4 | -0.45297 | 0.054099 | -0.32113 | -0.02249 | -0.43278 | 1.536 | 35.084 | 6.3235 | 33.5322 | Rack | Flat Plate | 0.994 | 1.958 | 1 | 0.18583
LDK Solar | LDK-295P-24 | 295 W Polycrystalline Module | UL 1703 | 295 | 265 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9463 | 72 | 1 | N | 8.6 | 44.5 | 8.06 | 36.6 | 46.4 | -0.45297 | 0.054099 | -0.32113 | -0.02249 | -0.43278 | 1.5573 | 35.1801 | 6.411 | 33.6241 | Rack | Flat Plate | 0.994 | 1.958 | 1 | 0.18572
LG Electronics Inc. | LG210P1C-G2 | 210 W Polycrystalline Module | UL 1703 | 210 | 188.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 7.99 | 35.7 | 7.32 | 28.7 | 45.7 | -0.46 | -0.001 | -0.312 | -0.001 | -0.397 | 1.6713 | 29.4917 | 5.8821 | 26.7999 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.23471 |  | 2018-02-15
LG Electronics Inc. | LG210P1W-G1 | 210 W Polycrystalline Module | UL 1703 | 210 | 188.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6375 | 60 | 1 | N | 7.99 | 35.7 | 7.32 | 28.7 | 44.7 | -0.467 | 0.015 | -0.323 | 0.016 | -0.411 | 1.518 | 27.0941 | 6.1298 | 27.2911 | Rack | Flat Plate | 0.993 | 1.649 | 1 | 0.19584 |  | 2018-02-15
LG Electronics Inc. | LG215P1C-G2 | 215 W Polycrystalline Module | UL 1703 | 215 | 192.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.1 | 35.8 | 7.46 | 28.9 | 45.7 | -0.46 | -0.001 | -0.312 | -0.001 | -0.397 | 1.7032 | 29.6972 | 5.9946 | 26.9866 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.23526 |  | 2018-02-15
LG Electronics Inc. | LG215P1W | 215 W Polycrystalline Module | UL 1703 | 215 | 191 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6464 | 60 | 1 | N | 7.99 | 36 | 7.39 | 29.1 | 45.4 | -0.505 | 0.038 | -0.339 | 0.04 | -0.429 | 1.6811 | 28.2097 | 5.8162 | 26.6292 | Rack | Flat Plate | 0.993 | 1.658 | 1 | 0.22057 |  | 2018-02-15
LG Electronics Inc. | LG215P1W-G1 | 215 W Polycrystalline Module | UL 1703 | 215 | 193.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6375 | 60 | 1 | N | 8.1 | 35.8 | 7.46 | 28.9 | 44.7 | -0.467 | 0.015 | -0.323 | 0.016 | -0.411 | 1.547 | 27.2829 | 6.247 | 27.4813 | Rack | Flat Plate | 0.993 | 1.649 | 1 | 0.19631 |  | 2018-02-15
LG Electronics Inc. | LG220M1C-G2 | 220 W Monocrystalline Module | UL 1703 | 220 | 196.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6097 | 60 | 1 | N | 8.2 | 36.2 | 7.51 | 29.3 | 43.8 | -0.525 | -0.018 | -0.337 | -0.019 | -0.429 | 1.6825 | 29.3 | 5.9497 | 26.6183 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.22407 |  | 2018-02-15
LG Electronics Inc. | LG220P1C-G2 | 220 W Polycrystalline Module | UL 1703 | 220 | 197.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.21 | 36.1 | 7.62 | 28.9 | 45.7 | -0.46 | -0.001 | -0.312 | -0.001 | -0.397 | 1.7398 | 29.6972 | 6.1232 | 26.9866 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.23485 |  | 2018-02-15
LG Electronics Inc. | LG220P1W | 220 W Polycrystalline Module | UL 1703 | 220 | 195.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6464 | 60 | 1 | N | 8 | 36.6 | 7.39 | 29.2 | 45.4 | -0.505 | 0.038 | -0.339 | 0.04 | -0.429 | 1.7152 | 28.3066 | 5.9342 | 26.7207 | Rack | Flat Plate | 0.993 | 1.658 | 1 | 0.22069 |  | 2018-02-15
LG Electronics Inc. | LG220P1W-G1 | 220 W Polycrystalline Module | UL 1703 | 220 | 198.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6375 | 60 | 1 | N | 8.21 | 36.1 | 7.62 | 28.9 | 44.7 | -0.467 | 0.015 | -0.323 | 0.016 | -0.411 | 1.5802 | 27.2829 | 6.381 | 27.4813 | Rack | Flat Plate | 0.993 | 1.649 | 1 | 0.19596 |  | 2018-02-15
LG Electronics Inc. | LG220R1C-G2 | 220 W Polycrystalline Module | UL 1703 | 220 | 193.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.06 | 36 | 7.69 | 28.7 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.4826 | 28.5281 | 6.0393 | 25.6448 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19226 |  | 2018-02-15
LG Electronics Inc. | LG220R1W-G2 | 220 W Polycrystalline Module | UL 1703 | 220 | 193.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.06 | 36 | 7.69 | 28.7 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.4826 | 28.5281 | 6.0393 | 25.6448 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19226 |  | 2018-02-15
LG Electronics Inc. | LG225M1C-G2 | 225 W Monocrystalline Module | UL 1703 | 225 | 201.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6097 | 60 | 1 | N | 8.29 | 36.5 | 7.65 | 29.5 | 43.8 | -0.525 | -0.018 | -0.337 | -0.019 | -0.429 | 1.7138 | 29.5 | 6.0606 | 26.8 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.2247 |  | 2018-02-15
LG Electronics Inc. | LG225P1C-G2 | 225 W Polycrystalline Module | UL 1703 | 225 | 202.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.3 | 36.3 | 7.76 | 29 | 45.7 | -0.46 | -0.001 | -0.312 | -0.001 | -0.397 | 1.7717 | 29.8 | 6.2357 | 27.08 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.23466 |  | 2018-02-15
LG Electronics Inc. | LG225P1W | 225 W Polycrystalline Module | UL 1703 | 225 | 200.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6464 | 60 | 1 | N | 8.24 | 36.13 | 7.39 | 29 | 45.4 | -0.505 | 0.038 | -0.339 | 0.04 | -0.429 | 1.7653 | 28.1128 | 6.1074 | 26.5376 | Rack | Flat Plate | 0.993 | 1.658 | 1 | 0.22056 |  | 2018-02-15
LG Electronics Inc. | LG225P1W-G1 | 225 W Polycrystalline Module | UL 1703 | 225 | 202.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6375 | 60 | 1 | N | 8.3 | 36.3 | 7.76 | 29 | 44.7 | -0.467 | 0.015 | -0.323 | 0.016 | -0.411 | 1.6092 | 27.3773 | 6.4983 | 27.5764 | Rack | Flat Plate | 0.993 | 1.649 | 1 | 0.1958 |  | 2018-02-15
LG Electronics Inc. | LG225R1C-G2 | 225 W Polycrystalline Module | UL 1703 | 225 | 197.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.21 | 36.4 | 7.8 | 28.9 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.5039 | 28.7269 | 6.1257 | 25.8235 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19201 |  | 2018-02-15
LG Electronics Inc. | LG225R1W-G2 | 225 W Polycrystalline Module | UL 1703 | 225 | 197.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.21 | 36.4 | 7.8 | 28.9 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.5039 | 28.7269 | 6.1257 | 25.8235 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19201 |  | 2018-02-15
LG Electronics Inc. | LG230M1C-G2 | 230 W Monocrystalline Module | UL 1703 | 230 | 205.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6097 | 60 | 1 | N | 8.37 | 36.6 | 7.81 | 29.5 | 43.8 | -0.525 | -0.018 | -0.337 | -0.019 | -0.429 | 1.7497 | 29.5 | 6.1874 | 26.8 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.22441 |  | 2018-02-15
LG Electronics Inc. | LG230N8K-G4 | 230 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 230 | 212.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.274 | 48 | 1 | N | 9.9 | 30 | 9.71 | 23.7 | 44.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.9546 | 23.1654 | 7.7659 | 22.0071 | Rack | Flat Plate | 0.98 | 1.3 | 1 | 0.19687 |  | 2018-02-15
LG Electronics Inc. | LG230P1C-G2 | 230 W Polycrystalline Module | UL 1703 | 230 | 206.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6097 | 60 | 1 | N | 8.39 | 36.4 | 7.91 | 29.1 | 45.7 | -0.46 | -0.001 | -0.312 | -0.001 | -0.397 | 1.806 | 29.9028 | 6.3563 | 27.1734 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.2348 |  | 2018-02-15
LG Electronics Inc. | LG230P1W | 230 W Polycrystalline Module | UL 1703 | 230 | 204.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6464 | 60 | 1 | N | 8.26 | 36.4 | 7.39 | 29.5 | 45.4 | -0.505 | 0.038 | -0.339 | 0.04 | -0.429 | 1.7766 | 28.5975 | 6.1467 | 26.9952 | Rack | Flat Plate | 0.993 | 1.658 | 1 | 0.2209 |  | 2018-02-15
LG Electronics Inc. | LG230P1W-G1 | 230 W Polycrystalline Module | UL 1703 | 230 | 207.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6375 | 60 | 1 | N | 8.39 | 36.4 | 7.91 | 29.1 | 44.7 | -0.467 | 0.015 | -0.323 | 0.016 | -0.411 | 1.6403 | 27.4717 | 6.6239 | 27.6715 | Rack | Flat Plate | 0.993 | 1.649 | 1 | 0.19592 |  | 2018-02-15
LG Electronics Inc. | LG230R1C-G2 | 230 W Polycrystalline Module | UL 1703 | 230 | 202.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.35 | 36.6 | 7.93 | 29.1 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.5289 | 28.9257 | 6.2278 | 26.0022 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19228 |  | 2018-02-15
LG Electronics Inc. | LG230R1W-G2 | 230 W Polycrystalline Module | UL 1703 | 230 | 202.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.35 | 36.6 | 7.93 | 29.1 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.5289 | 28.9257 | 6.2278 | 26.0022 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19228 |  | 2018-02-15
LG Electronics Inc. | LG235M1C-G2 | 235 W Monocrystalline Module | UL 1703 | 235 | 210.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6097 | 60 | 1 | N | 8.49 | 36.8 | 7.94 | 29.6 | 43.8 | -0.525 | -0.018 | -0.337 | -0.019 | -0.429 | 1.7788 | 29.6 | 6.2904 | 26.8908 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.22405 |  | 2018-02-15
LG Electronics Inc. | LG235N8K-G4 | 235 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 235 | 217.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.274 | 48 | 1 | N | 9.96 | 30.2 | 9.76 | 24.1 | 44.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.9647 | 23.5564 | 7.8059 | 22.3786 | Rack | Flat Plate | 0.98 | 1.3 | 1 | 0.19694 |  | 2018-02-15
LG Electronics Inc. | LG235P1W | 235 W Polycrystalline Module | UL 1703 | 235 | 209.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6464 | 60 | 1 | N | 8.3 | 36.3 | 7.39 | 29.8 | 45.4 | -0.505 | 0.038 | -0.339 | 0.04 | -0.429 | 1.7948 | 28.8883 | 6.2097 | 27.2697 | Rack | Flat Plate | 0.993 | 1.658 | 1 | 0.22064 |  | 2018-02-15
LG Electronics Inc. | LG235R1C-G2 | 235 W Polycrystalline Module | UL 1703 | 235 | 206.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.48 | 36.9 | 7.97 | 29.5 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.5366 | 29.3234 | 6.2592 | 26.3596 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19174 |  | 2018-02-15
LG Electronics Inc. | LG235R1W-G2 | 235 W Polycrystalline Module | UL 1703 | 235 | 206.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.48 | 36.9 | 7.97 | 29.5 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.5366 | 29.3234 | 6.2592 | 26.3596 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19174 |  | 2018-02-15
LG Electronics Inc. | LG240M1C-G2 | 240 W Monocrystalline Module | UL 1703 | 240 | 215 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6097 | 60 | 1 | N | 8.58 | 36.9 | 8.1 | 29.7 | 43.8 | -0.525 | -0.018 | -0.337 | -0.019 | -0.429 | 1.8146 | 29.7 | 6.4171 | 26.9817 | Rack | Flat Plate | 0.99 | 1.626 | 1 | 0.22456 |  | 2018-02-15
LG Electronics Inc. | LG240N8K-G4 | 240 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 240 | 222.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.274 | 48 | 1 | N | 10.01 | 30.5 | 9.8 | 24.5 | 44.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.9727 | 23.9474 | 7.8379 | 22.75 | Rack | Flat Plate | 0.98 | 1.3 | 1 | 0.19684 |  | 2018-02-15
LG Electronics Inc. | LG240R1C-G2 | 240 W Polycrystalline Module | UL 1703 | 240 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.61 | 37.2 | 8.02 | 30 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.5463 | 29.8204 | 6.2985 | 26.8064 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19213 |  | 2018-02-15
LG Electronics Inc. | LG240R1W-G2 | 240 W Polycrystalline Module | UL 1703 | 240 | 211.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5935 | 60 | 1 | N | 8.61 | 37.2 | 8.02 | 30 | 46.2 | -0.5367 | 0.0494 | -0.3978 | -0.0347 | -0.5053 | 1.5463 | 29.8204 | 6.2985 | 26.8064 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19213 |  | 2018-02-15
LG Electronics Inc. | LG240S1C-G2 | 240 W Monocrystalline Module | UL 1703 | 240 | 215.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5935 | 60 | 1 | N | 8.58 | 36.9 | 8.1 | 29.7 | 45.2 | -0.47243 | 0.041667 | -0.33803 | 0.0035253 | -0.47785 | 1.6562 | 29.3013 | 6.6152 | 26.9094 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.2022 |  | 2018-02-15
LG Electronics Inc. | LG240S1K-G3 | 240 W Monocrystalline Module | UL 1703 | 240 | 213.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 8.42 | 37.96 | 7.91 | 30.37 | 48.8 | -0.4447 | 0.0496 | -0.3247 | -0.022406 | -0.71914 | 1.6137 | 29.7686 | 6.4362 | 27.0624 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.20016 |  | 2018-02-15
LG Electronics Inc. | LG245M1C-G2 | 245 W Monocrystalline Module | UL 1703 | 245 | 213.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5935 | 60 | 1 | N | 8.67 | 37 | 8.23 | 29.8 | 45.5 | -0.6023 | 0.0418 | -0.4321 | -0.0345 | -0.5082 | 1.6857 | 29.7332 | 6.4793 | 26.1967 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.20457 |  | 2018-02-15
LG Electronics Inc. | LG245M1W-G2 | 245 W Monocrystalline Module | UL 1703 | 245 | 213.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5935 | 60 | 1 | N | 8.67 | 37 | 8.23 | 29.8 | 45.5 | -0.6023 | 0.0418 | -0.4321 | -0.0345 | -0.5082 | 1.6857 | 29.7332 | 6.4793 | 26.1967 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.20457 |  | 2018-02-15
LG Electronics Inc. | LG245N8K-G4 | 245 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 245 | 227.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.274 | 48 | 1 | N | 10.06 | 30.8 | 9.84 | 24.9 | 44.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.9808 | 24.3383 | 7.8699 | 23.1214 | Rack | Flat Plate | 0.98 | 1.3 | 1 | 0.19677 |  | 2018-02-15
LG Electronics Inc. | LG245S1C-G2 | 245 W Monocrystalline Module | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5935 | 60 | 1 | N | 8.67 | 37 | 8.23 | 29.8 | 45.2 | -0.47243 | 0.041667 | -0.33803 | 0.0035253 | -0.47785 | 1.6827 | 29.4 | 6.7213 | 27 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.20193 |  | 2018-02-15
LG Electronics Inc. | LG245S1C-G3 | 245 W Monocrystalline Module | UL 1703 | 245 | 221.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 8.52 | 38.11 | 8.02 | 30.57 | 44.9 | -0.4589 | 0.053377 | -0.34206 | 0.0536 | -0.3426 | 1.7106 | 30.3655 | 6.5244 | 28.5252 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.21201 |  | 2018-02-15
LG Electronics Inc. | LG245S1K-G3 | 245 W Monocrystalline Module | UL 1703 | 245 | 217.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 8.52 | 38.11 | 8.02 | 30.57 | 48.8 | -0.4447 | 0.0496 | -0.3247 | -0.022406 | -0.71914 | 1.6362 | 29.9647 | 6.5257 | 27.2406 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.20011 |  | 2018-02-15
LG Electronics Inc. | LG250N8K-G4 | 250 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 250 | 231.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.274 | 48 | 1 | N | 10.1 | 31.1 | 9.89 | 25.3 | 44.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.9908 | 24.7293 | 7.9099 | 23.4929 | Rack | Flat Plate | 0.98 | 1.3 | 1 | 0.19693 |  | 2018-02-15
LG Electronics Inc. | LG250S1C-G2 | 250 W Monocrystalline Module | UL 1703 | 250 | 225.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5935 | 60 | 1 | N | 8.76 | 37.1 | 8.37 | 29.9 | 45.2 | -0.47243 | 0.041667 | -0.33803 | 0.0035253 | -0.47785 | 1.7114 | 29.4987 | 6.8357 | 27.0906 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.20193 |  | 2018-02-15
LG Electronics Inc. | LG250S1C-G3 | 250 W Monocrystalline Module | UL 1703 | 250 | 226.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 8.62 | 38.26 | 8.13 | 30.77 | 44.9 | -0.4589 | 0.053377 | -0.34206 | 0.0536 | -0.3426 | 1.734 | 30.5642 | 6.6139 | 28.7118 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.212 |  | 2018-02-15
LG Electronics Inc. | LG250S1K-A3 | 250 W Monocrystalline Module | UL 1703 | 250 | 225.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.68 | 37.6 | 8.13 | 30.8 | 46.8 | -0.43 | 0.05 | -0.31 | -0.01 | -0.42 | 1.6411 | 28.389 | 6.4795 | 28.1 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18636 |  | 2018-02-15
LG Electronics Inc. | LG250S1K-B3 | 250 W Monocrystalline Module | UL 1703 | 250 | 227.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.68 | 37.6 | 8.13 | 30.8 | 44.8 | -0.44 | 0.04 | -0.31 | -0.02 | -0.42 | 1.63 | 29.8 | 7.14 | 28.09 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1943 |  | 2018-02-15
LG Electronics Inc. | LG250S1K-G3 | 250 W Monocrystalline Module | UL 1703 | 250 | 222.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 8.62 | 38.26 | 8.13 | 30.77 | 48.8 | -0.4447 | 0.0496 | -0.3247 | -0.022406 | -0.71914 | 1.6586 | 30.1607 | 6.6152 | 27.4188 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.2001 |  | 2018-02-15
LG Electronics Inc. | LG255S1C-A3 | 255 W Monocrystalline Module | UL 1703 | 255 | 231.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.98 | 38 | 8.27 | 30.9 | 46.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.6694 | 28.8778 | 6.5911 | 28.1912 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18905 |  | 2018-02-15
LG Electronics Inc. | LG255S1C-B3 | 255 W Monocrystalline Module | UL 1703 | 255 | 233.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.98 | 38 | 8.27 | 30.9 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.64 | 29.99 | 6.57 | 28.48 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19288 |  | 2018-02-15
LG Electronics Inc. | LG255S1C-G2 | 255 W Monocrystalline Module | UL 1703 | 255 | 229.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5935 | 60 | 1 | N | 8.85 | 37.2 | 8.5 | 30 | 45.2 | -0.47243 | 0.041667 | -0.33803 | 0.0035253 | -0.47785 | 1.738 | 29.5973 | 6.9418 | 27.1812 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.20172 |  | 2018-02-15
LG Electronics Inc. | LG255S1C-G3 | 255 W Monocrystalline Module | UL 1703 | 255 | 230.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 8.72 | 38.41 | 8.24 | 30.97 | 44.9 | -0.4589 | 0.053377 | -0.34206 | 0.0536 | -0.3426 | 1.7575 | 30.7628 | 6.7034 | 28.8984 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.21202 |  | 2018-02-15
LG Electronics Inc. | LG255S1K-A3 | 255 W Monocrystalline Module | UL 1703 | 255 | 230.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.78 | 37.9 | 8.26 | 30.9 | 46.8 | -0.43 | 0.05 | -0.31 | -0.01 | -0.42 | 1.6673 | 28.8429 | 6.5831 | 28.1912 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18859 |  | 2018-02-15
LG Electronics Inc. | LG255S1K-B3 | 255 W Monocrystalline Module | UL 1703 | 255 | 232 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.78 | 37.9 | 8.26 | 30.9 | 44.8 | -0.44 | 0.04 | -0.31 | -0.02 | -0.42 | 1.65 | 29.89 | 6.58 | 28.18 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19341 |  | 2018-02-15
LG Electronics Inc. | LG255S1K-G3 | 255 W Monocrystalline Module | UL 1703 | 255 | 227 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 8.72 | 38.41 | 8.24 | 30.97 | 48.8 | -0.4447 | 0.0496 | -0.3247 | -0.022406 | -0.71914 | 1.681 | 30.3567 | 6.7047 | 27.597 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.20012 |  | 2018-02-15
LG Electronics Inc. | LG255S1W-A3 | 255 W Monocrystalline Module | UL 1703 | 255 | 231.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.98 | 38 | 8.27 | 30.9 | 46.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.6694 | 28.8778 | 6.5911 | 28.1912 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18905 |  | 2018-02-15
LG Electronics Inc. | LG255S1W-B3 | 255 W Monocrystalline Module | UL 1703 | 255 | 233.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.98 | 38 | 8.27 | 30.9 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.64 | 29.99 | 6.57 | 28.48 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19288 |  | 2018-02-15
LG Electronics Inc. | LG260N9K-G4 | 260 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 260 | 241.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4308 | 54 | 1 | N | 9.55 | 35.2 | 8.88 | 29.3 | 43.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.7702 | 28.2221 | 7.0807 | 27.4381 | Rack | Flat Plate | 0.98 | 1.46 | 1 | 0.19215 |  | 2018-02-15
LG Electronics Inc. | LG260S1C-A3 | 260 W Monocrystalline Module | UL 1703 | 260 | 235.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.05 | 38.1 | 8.38 | 31.1 | 46.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.6916 | 29.2619 | 6.6787 | 28.3737 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19038 |  | 2018-02-15
LG Electronics Inc. | LG260S1C-B3 | 260 W Monocrystalline Module | UL 1703 | 260 | 238.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.05 | 38.1 | 8.38 | 31.1 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.67 | 30.19 | 6.66 | 28.67 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19391 |  | 2018-02-15
LG Electronics Inc. | LG260S1C-G2 | 260 W Monocrystalline Module | UL 1703 | 260 | 234.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5935 | 60 | 1 | N | 8.94 | 37.3 | 8.64 | 30.1 | 45.2 | -0.47243 | 0.041667 | -0.33803 | 0.0035253 | -0.47785 | 1.7666 | 29.696 | 7.0562 | 27.2718 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.20177 |  | 2018-02-15
LG Electronics Inc. | LG260S1C-G3 | 260 W Monocrystalline Module | UL 1703 | 260 | 235 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.82 | 38.56 | 8.35 | 31.17 | 46.3 | -0.44 | 0.05 | -0.32 | -0.02 | -0.42 | 1.6855 | 30.2592 | 6.6645 | 28.3364 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19616 |  | 2018-02-15
LG Electronics Inc. | LG260S1K-A3 | 260 W Monocrystalline Module | UL 1703 | 260 | 234.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.88 | 38.2 | 8.34 | 31.2 | 46.8 | -0.43 | 0.05 | -0.31 | -0.01 | -0.42 | 1.6835 | 29.1223 | 6.6468 | 28.4649 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18856 |  | 2018-02-15
LG Electronics Inc. | LG260S1K-B3 | 260 W Monocrystalline Module | UL 1703 | 260 | 236.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.88 | 38.2 | 8.34 | 31.2 | 44.8 | -0.44 | 0.04 | -0.31 | -0.02 | -0.42 | 1.67 | 30.18 | 6.64 | 28.46 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19385 |  | 2018-02-15
LG Electronics Inc. | LG260S1K-G3 | 260 W Monocrystalline Module | UL 1703 | 260 | 231.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 8.82 | 38.56 | 8.35 | 31.17 | 48.8 | -0.4447 | 0.0496 | -0.3247 | -0.022406 | -0.71914 | 1.7035 | 30.5528 | 6.7942 | 27.7752 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.20018 |  | 2018-02-15
LG Electronics Inc. | LG260S1W-A3 | 260 W Monocrystalline Module | UL 1703 | 260 | 235.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.05 | 38.1 | 8.38 | 31.1 | 46.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.6916 | 29.2619 | 6.6787 | 28.3737 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19038 |  | 2018-02-15
LG Electronics Inc. | LG260S1W-B3 | 260 W Monocrystalline Module | UL 1703 | 260 | 238.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.05 | 38.1 | 8.38 | 31.1 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.67 | 30.19 | 6.66 | 28.67 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19391 |  | 2018-02-15
LG Electronics Inc. | LG260S1W-G2 | 260 W Monocrystalline Module | UL 1703 | 260 | 230.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5935 | 60 | 1 | N | 8.94 | 37.3 | 8.64 | 30.1 | 46.1 | -0.524 | 0.0363 | -0.3845 | -0.0259 | -0.5009 | 1.7406 | 29.1496 | 6.826 | 26.7882 | Rack | Flat Plate | 0.98 | 1.626 | 1 | 0.19514 |  | 2018-02-15
LG Electronics Inc. | LG260S1W-G3 | 260 W Monocrystalline Module | UL 1703 | 260 | 235 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.82 | 38.56 | 8.35 | 31.17 | 46.3 | -0.44 | 0.05 | -0.32 | -0.02 | -0.42 | 1.6855 | 30.2592 | 6.6645 | 28.3364 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19616 |  | 2018-02-15
LG Electronics Inc. | LG265N9K-G4 | 265 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 265 | 246.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4308 | 54 | 1 | N | 9.6 | 35.5 | 8.93 | 29.7 | 43.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.7801 | 28.6074 | 7.1205 | 27.8127 | Rack | Flat Plate | 0.98 | 1.46 | 1 | 0.19217 |  | 2018-02-15
LG Electronics Inc. | LG265S1C-A3 | 265 W Monocrystalline Module | UL 1703 | 265 | 240.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.11 | 38.3 | 8.49 | 31.3 | 46.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.7138 | 29.6461 | 6.7664 | 28.5562 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19172 |  | 2018-02-15
LG Electronics Inc. | LG265S1C-B3 | 265 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 265 | 243.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.11 | 38.3 | 8.49 | 31.3 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.69 | 30.38 | 6.74 | 28.85 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19374 |  | 2018-02-15
LG Electronics Inc. | LG265S1C-G3 | 265 W Monocrystalline Module | UL 1703 | 265 | 239.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.92 | 38.71 | 8.46 | 31.37 | 46.3 | -0.44 | 0.05 | -0.32 | -0.02 | -0.42 | 1.7077 | 30.4533 | 6.7523 | 28.5182 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19625 |  | 2018-02-15
LG Electronics Inc. | LG265S1K-A3 | 265 W Monocrystalline Module | UL 1703 | 265 | 239.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.03 | 38.4 | 8.42 | 31.5 | 46.8 | -0.43 | 0.05 | -0.31 | -0.01 | -0.42 | 1.6996 | 29.4016 | 6.7106 | 28.7386 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18857 |  | 2018-02-15
LG Electronics Inc. | LG265S1K-B3 | 265 W Monocrystalline Module | UL 1703 | 265 | 241.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.03 | 38.4 | 8.42 | 31.5 | 44.8 | -0.44 | 0.04 | -0.31 | -0.02 | -0.42 | 1.68 | 30.47 | 6.71 | 28.73 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19317 |  | 2018-02-15
LG Electronics Inc. | LG265S1W-A3 | 265 W Monocrystalline Module | UL 1703 | 265 | 240.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.11 | 38.3 | 8.49 | 31.3 | 46.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.7138 | 29.6461 | 6.7664 | 28.5562 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19172 |  | 2018-02-15
LG Electronics Inc. | LG265S1W-B3 | 265 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 265 | 243.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.11 | 38.3 | 8.49 | 31.3 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.69 | 30.38 | 6.74 | 28.85 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19374 |  | 2018-02-15
LG Electronics Inc. | LG265S1W-G3 | 265 W Monocrystalline Module | UL 1703 | 265 | 239.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 8.92 | 38.71 | 8.46 | 31.37 | 46.3 | -0.44 | 0.05 | -0.32 | -0.02 | -0.42 | 1.7077 | 30.4533 | 6.7523 | 28.5182 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19625 |  | 2018-02-15
LG Electronics Inc. | LG270N1C-G3 | 270 W Monocrystalline Module | UL 1703 | 270 | 244.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 9.31 | 38.57 | 8.74 | 31.21 | 46.5 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7519 | 31.0086 | 6.9593 | 28.6931 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.20119 |  | 2018-02-15
LG Electronics Inc. | LG270N1W-G3 | 270 W Monocrystalline Module | UL 1703 | 270 | 244.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 9.31 | 38.57 | 8.74 | 31.21 | 46.5 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7519 | 31.0086 | 6.9593 | 28.6931 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.20119 |  | 2018-02-15
LG Electronics Inc. | LG270N9K-G4 | 270 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 270 | 251.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4308 | 54 | 1 | N | 9.65 | 35.8 | 8.98 | 30.1 | 43.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.7901 | 28.9926 | 7.1604 | 28.1873 | Rack | Flat Plate | 0.98 | 1.46 | 1 | 0.19222 |  | 2018-02-15
LG Electronics Inc. | LG270S1C-A3 | 270 W Monocrystalline Module | UL 1703 | 270 | 245.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.17 | 38.5 | 8.58 | 31.5 | 46.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.7319 | 29.9603 | 6.8381 | 28.7386 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19218 |  | 2018-02-15
LG Electronics Inc. | LG270S1C-B3 | 270 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 270 | 247.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.17 | 38.5 | 8.58 | 31.5 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.71 | 30.58 | 6.82 | 29.04 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19367 |  | 2018-02-15
LG Electronics Inc. | LG270S1C-G3 | 270 W Monocrystalline Module | UL 1703 | 270 | 244.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.02 | 38.86 | 8.57 | 31.57 | 46.3 | -0.44 | 0.05 | -0.32 | -0.02 | -0.42 | 1.7299 | 30.6475 | 6.8401 | 28.7 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19636 |  | 2018-02-15
LG Electronics Inc. | LG270S1C-G4 | 270 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 270 | 247.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.17 | 38.5 | 8.58 | 31.5 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7064 | 30.7933 | 6.8447 | 29.1779 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19461 |  | 2018-02-15
LG Electronics Inc. | LG270S1C-L4 | 270 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 270 | 246.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.17 | 38.2 | 8.7 | 31.1 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.7225 | 29.9227 | 6.9191 | 28.4511 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19089 |  | 2018-02-15
LG Electronics Inc. | LG270S1K-B3 | 270 W Monocrystalline Module | UL 1703 | 270 | 241.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.12 | 38.6 | 8.52 | 31.7 | 49.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.69 | 30.58 | 8.49 | 31.5 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19141 |  | 2018-02-15
LG Electronics Inc. | LG270S1W-A3 | 270 W Monocrystalline Module | UL 1703 | 270 | 245.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.17 | 38.5 | 8.58 | 31.5 | 46.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.7319 | 29.9603 | 6.8381 | 28.7386 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19218 |  | 2018-02-15
LG Electronics Inc. | LG270S1W-B3 | 270 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 270 | 247.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.17 | 38.5 | 8.58 | 31.5 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.71 | 30.58 | 6.82 | 29.04 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19367 |  | 2018-02-15
LG Electronics Inc. | LG270S1W-G3 | 270 W Monocrystalline Module | UL 1703 | 270 | 244.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.02 | 38.86 | 8.57 | 31.57 | 46.3 | -0.44 | 0.05 | -0.32 | -0.02 | -0.42 | 1.7299 | 30.6475 | 6.8401 | 28.7 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19636 |  | 2018-02-15
LG Electronics Inc. | LG270S1W-G4 | 270 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 270 | 247.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.17 | 38.5 | 8.58 | 31.5 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7064 | 30.7933 | 6.8447 | 29.1779 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19461 |  | 2018-02-15
LG Electronics Inc. | LG270S1W-L4 | 270 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 270 | 246.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.17 | 38.2 | 8.7 | 31.1 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.7225 | 29.9227 | 6.9191 | 28.4511 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19089 |  | 2018-02-15
LG Electronics Inc. | LG275N1C-G3 | 275 W Monocrystalline Module | UL 1703 | 275 | 249.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 9.44 | 38.72 | 8.85 | 31.36 | 46.5 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7739 | 31.1577 | 7.0469 | 28.831 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.20098 |  | 2018-02-15
LG Electronics Inc. | LG275N1K-A3 | 275 W Monocrystalline Module | UL 1703 | 275 | 248 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 72 | 1 | N | 9.35 | 39.2 | 8.8 | 31.3 | 49.3 | -0.4 | 0.04 | -0.29 | -0.003 | -0.4 | 1.7719 | 30.91 | 7.0579 | 28.3748 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19917 |  | 2018-02-15
LG Electronics Inc. | LG275N1K-B3 | 275 W Monocrystalline Module | UL 1703 | 275 | 245.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.35 | 39.18 | 8.8 | 31.33 | 50.9 | -0.41 | 0.04 | -0.29 | -0.01 | -0.4 | 1.77 | 30.46 | 6.99 | 28.23 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19605 |  | 2018-02-15
LG Electronics Inc. | LG275N1W-G3 | 275 W Monocrystalline Module | UL 1703 | 275 | 249.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6242 | 60 | 1 | N | 9.44 | 38.72 | 8.85 | 31.36 | 46.5 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7739 | 31.1577 | 7.0469 | 28.831 | Rack | Flat Plate | 0.994 | 1.634 | 1 | 0.20098 |  | 2018-02-15
LG Electronics Inc. | LG275N9K-G4 | 275 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 275 | 256 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4308 | 54 | 1 | N | 9.7 | 36.1 | 9.02 | 30.5 | 43.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.7981 | 29.3779 | 7.1923 | 28.5619 | Rack | Flat Plate | 0.98 | 1.46 | 1 | 0.19209 |  | 2018-02-15
LG Electronics Inc. | LG275S1C-B3 | 275 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 275 | 252.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.26 | 38.7 | 8.68 | 31.7 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.73 | 30.77 | 6.89 | 29.22 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19357 |  | 2018-02-15
LG Electronics Inc. | LG275S1C-G4 | 275 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 275 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.26 | 38.7 | 8.68 | 31.7 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7262 | 30.9888 | 6.9245 | 29.3631 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19452 |  | 2018-02-15
LG Electronics Inc. | LG275S1C-L4 | 275 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 275 | 251.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.28 | 38.4 | 8.8 | 31.3 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.7423 | 30.1151 | 6.9987 | 28.6341 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1908 |  | 2018-02-15
LG Electronics Inc. | LG275S1K-B3 | 275 W Monocrystalline Module | UL 1703 | 275 | 246.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.23 | 38.8 | 8.63 | 31.9 | 49.1 | -0.43 | 0.04 | -0.31 | -0.02 | -0.42 | 1.71 | 30.77 | 8.6 | 31.69 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19133 |  | 2018-02-15
LG Electronics Inc. | LG275S1W-B3 | 275 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 275 | 252.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.26 | 38.7 | 8.68 | 31.7 | 43.7 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.73 | 30.77 | 6.89 | 29.22 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19357 |  | 2018-02-15
LG Electronics Inc. | LG275S1W-G4 | 275 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 275 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.26 | 38.7 | 8.68 | 31.7 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7262 | 30.9888 | 6.9245 | 29.3631 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19452 |  | 2018-02-15
LG Electronics Inc. | LG275S1W-L4 | 275 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 275 | 251.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.28 | 38.4 | 8.8 | 31.3 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.7423 | 30.1151 | 6.9987 | 28.6341 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1908 |  | 2018-02-15
LG Electronics Inc. | LG280N1C-G3 | 280 W Monocrystalline Module | UL 1703 | 280 | 257.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.56 | 38.9 | 8.97 | 31.5 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7017 | 31 | 7.1625 | 29.2 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1884 |  | 2018-02-15
LG Electronics Inc. | LG280N1K-A3 | 280 W Monocrystalline Module | UL 1703 | 280 | 252.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 72 | 1 | N | 9.46 | 39.3 | 8.92 | 31.5 | 49.3 | -0.4 | 0.04 | -0.29 | -0.003 | -0.4 | 1.7961 | 31.1075 | 7.1542 | 28.5561 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19954 |  | 2018-02-15
LG Electronics Inc. | LG280N1K-B3 | 280 W Monocrystalline Module | UL 1703 | 280 | 250.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.46 | 39.33 | 8.92 | 31.49 | 50.9 | -0.41 | 0.04 | -0.29 | -0.01 | -0.4 | 1.79 | 30.61 | 7.09 | 28.37 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19569 |  | 2018-02-15
LG Electronics Inc. | LG280N1W-G3 | 280 W Monocrystalline Module | UL 1703 | 280 | 257.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.56 | 38.9 | 8.97 | 31.5 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7017 | 31 | 7.1625 | 29.2 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1884 |  | 2018-02-15
LG Electronics Inc. | LG280N9K-G4 | 280 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 280 | 260.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4308 | 54 | 1 | N | 9.75 | 36.4 | 9.07 | 30.9 | 43.6 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.808 | 29.7632 | 7.2322 | 28.9365 | Rack | Flat Plate | 0.98 | 1.46 | 1 | 0.19219 |  | 2018-02-15
LG Electronics Inc. | LG280S1C-A5 | 280 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6593 | 60 | 1 | N | 9.87 | 37.7 | 9.31 | 30.1 | 47.9 | -0.422 | 0.04 | -0.31 | -0.02 | -0.4 | 1.8502 | 29.4225 | 7.4106 | 27.39 | Rack | Flat Plate | 0.996 | 1.666 | 1 | 0.19442 |  | 2018-02-15
LG Electronics Inc. | LG280S1C-B3 | 280 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 280 | 255.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.33 | 38.8 | 8.78 | 31.9 | 45.5 | -0.43 | 0.04 | -0.31 | -0.01 | -0.42 | 1.74 | 31.08 | 7.01 | 28.92 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19314 |  | 2018-02-15
LG Electronics Inc. | LG280S1C-G4 | 280 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.33 | 38.8 | 8.78 | 31.9 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7461 | 31.1843 | 7.0043 | 29.5484 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19447 |  | 2018-02-15
LG Electronics Inc. | LG280S1C-L4 | 280 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 280 | 256.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.39 | 38.6 | 8.9 | 31.5 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.7621 | 30.3076 | 7.0782 | 28.817 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19073 |  | 2018-02-15
LG Electronics Inc. | LG280S1W-A5 | 280 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 280 | 252.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6593 | 60 | 1 | N | 9.87 | 37.7 | 9.31 | 30.1 | 47.9 | -0.422 | 0.04 | -0.31 | -0.02 | -0.4 | 1.8502 | 29.4225 | 7.4106 | 27.39 | Rack | Flat Plate | 0.996 | 1.666 | 1 | 0.19442 |  | 2018-02-15
LG Electronics Inc. | LG280S1W-B3 | 280 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 280 | 255.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.33 | 38.8 | 8.78 | 31.9 | 45.5 | -0.43 | 0.04 | -0.31 | -0.01 | -0.42 | 1.74 | 31.08 | 7.01 | 28.92 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19314 |  | 2018-02-15
LG Electronics Inc. | LG280S1W-G4 | 280 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.33 | 38.8 | 8.78 | 31.9 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7461 | 31.1843 | 7.0043 | 29.5484 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19447 |  | 2018-02-15
LG Electronics Inc. | LG280S1W-L4 | 280 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 280 | 256.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.39 | 38.6 | 8.9 | 31.5 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.7621 | 30.3076 | 7.0782 | 28.817 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19073 |  | 2018-02-15
LG Electronics Inc. | LG285N1C-A3 | 285 W Monocrystalline Module | UL 1703 | 285 | 259.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.59 | 39.47 | 9.03 | 31.63 | 46.3 | -0.42 | 0.03 | -0.29 | -0.02 | -0.4 | 1.83 | 31.33 | 7.19 | 29.26 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.20117 |  | 2018-02-15
LG Electronics Inc. | LG285N1C-B3 | 285 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 285 | 258.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.59 | 39.5 | 9.03 | 31.6 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.81 | 31.11 | 7.22 | 28.55 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19758 |  | 2018-02-15
LG Electronics Inc. | LG285N1C-G3 | 285 W Monocrystalline Module | UL 1703 | 285 | 262.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.68 | 39 | 9.09 | 31.6 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7245 | 31.0984 | 7.2584 | 29.2927 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18817 |  | 2018-02-15
LG Electronics Inc. | LG285N1K-A3 | 285 W Monocrystalline Module | UL 1703 | 285 | 257.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 72 | 1 | N | 9.59 | 39.5 | 9.03 | 31.6 | 49.3 | -0.4 | 0.04 | -0.29 | -0.003 | -0.4 | 1.8183 | 31.2062 | 7.2424 | 28.6467 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19909 |  | 2018-02-15
LG Electronics Inc. | LG285N1K-B3 | 285 W Monocrystalline Module | UL 1703 | 285 | 254.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.59 | 39.47 | 9.03 | 31.63 | 50.9 | -0.41 | 0.04 | -0.29 | -0.01 | -0.4 | 1.81 | 30.75 | 7.18 | 28.5 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19529 |  | 2018-02-15
LG Electronics Inc. | LG285N1W-A3 | 285 W Monocrystalline Module | UL 1703 | 285 | 259.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.59 | 39.47 | 9.03 | 31.63 | 46.3 | -0.42 | 0.03 | -0.29 | -0.02 | -0.4 | 1.83 | 31.33 | 7.19 | 29.26 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.20117 |  | 2018-02-15
LG Electronics Inc. | LG285N1W-B3 | 285 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 285 | 258.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.59 | 39.5 | 9.03 | 31.6 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.81 | 31.11 | 7.22 | 28.55 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19758 |  | 2018-02-15
LG Electronics Inc. | LG285N1W-G3 | 285 W Monocrystalline Module | UL 1703 | 285 | 262.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.68 | 39 | 9.09 | 31.6 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7245 | 31.0984 | 7.2584 | 29.2927 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18817 |  | 2018-02-15
LG Electronics Inc. | LG285S1C-A5 | 285 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 285 | 259.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 9.92 | 38 | 9.35 | 30.5 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8541 | 29.8222 | 7.4661 | 27.9825 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19402 |  | 2018-02-15
LG Electronics Inc. | LG285S1C-G4 | 285 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.38 | 38.9 | 8.88 | 32.1 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.766 | 31.3798 | 7.084 | 29.7337 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19445 |  | 2018-02-15
LG Electronics Inc. | LG285S1C-L4 | 285 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 285 | 260.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.5 | 38.8 | 9 | 31.7 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.7819 | 30.5 | 7.1577 | 29 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19069 |  | 2018-02-15
LG Electronics Inc. | LG285S1W-A5 | 285 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 285 | 259.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 9.92 | 38 | 9.35 | 30.5 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8541 | 29.8222 | 7.4661 | 27.9825 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19402 |  | 2018-02-15
LG Electronics Inc. | LG285S1W-G4 | 285 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.38 | 38.9 | 8.88 | 32.1 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.766 | 31.3798 | 7.084 | 29.7337 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19445 |  | 2018-02-15
LG Electronics Inc. | LG285S1W-L4 | 285 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 285 | 260.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.5 | 38.8 | 9 | 31.7 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.7819 | 30.5 | 7.1577 | 29 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19069 |  | 2018-02-15
LG Electronics Inc. | LG290N1C-A3 | 290 W Monocrystalline Module | UL 1703 | 290 | 265.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.7 | 39.6 | 9.15 | 31.8 | 46.6 | -0.4 | 0.03 | -0.29 | -0.02 | -0.39 | 1.8535 | 31.2111 | 7.2867 | 29.0519 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19949 |  | 2018-04-02
LG Electronics Inc. | LG290N1C-B3 | 290 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 290 | 262.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.7 | 39.6 | 9.15 | 31.8 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.84 | 31.3 | 7.31 | 28.73 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19859 |  | 2018-02-15
LG Electronics Inc. | LG290N1C-G3 | 290 W Monocrystalline Module | UL 1703 | 290 | 267 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.8 | 39.2 | 9.19 | 31.8 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7434 | 31.2952 | 7.3382 | 29.4781 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18814 |  | 2018-02-15
LG Electronics Inc. | LG290N1K-A3 | 290 W Monocrystalline Module | UL 1703 | 290 | 261.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 72 | 1 | N | 9.7 | 39.6 | 9.15 | 31.8 | 49.3 | -0.4 | 0.04 | -0.29 | -0.003 | -0.4 | 1.8424 | 31.4037 | 7.3386 | 28.828 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19951 |  | 2018-02-15
LG Electronics Inc. | LG290N1K-B3 | 290 W Monocrystalline Module | UL 1703 | 290 | 259.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.85 | 39.68 | 9.28 | 31.83 | 50.9 | -0.41 | 0.04 | -0.29 | -0.01 | -0.4 | 1.86 | 30.94 | 7.37 | 28.68 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19844 |  | 2018-02-15
LG Electronics Inc. | LG290N1K-Z4 | 290 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 290 | 269.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.61 | 38.9 | 9.16 | 31.7 | 43.5 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.8439 | 30.6622 | 7.4945 | 29.5301 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19496 |  | 2018-02-15
LG Electronics Inc. | LG290N1T-A4 | 290 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 290 | 265.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6366 | 60 | 1 | N | 9.61 | 39.5 | 9.04 | 32.1 | 48.1 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.81 | 31.1446 | 7.1616 | 29.425 | Rack | Flat Plate | 0.98 | 1.67 | 1 | 0.19438 |  | 2018-02-15
LG Electronics Inc. | LG290N1W-A3 | 290 W Monocrystalline Module | UL 1703 | 290 | 265.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 72 | 1 | N | 9.7 | 39.6 | 9.15 | 31.8 | 46.6 | -0.4 | 0.03 | -0.29 | -0.02 | -0.39 | 1.8535 | 31.2111 | 7.2867 | 29.0519 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19949 |  | 2018-02-15
LG Electronics Inc. | LG290N1W-B3 | 290 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 290 | 262.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.7 | 39.6 | 9.15 | 31.8 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.84 | 31.3 | 7.31 | 28.73 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19859 |  | 2018-02-15
LG Electronics Inc. | LG290N1W-G3 | 290 W Monocrystalline Module | UL 1703 | 290 | 267 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.8 | 39.2 | 9.19 | 31.8 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7434 | 31.2952 | 7.3382 | 29.4781 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18814 |  | 2018-02-15
LG Electronics Inc. | LG290S1C-A5 | 290 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 290 | 264 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 9.97 | 38.3 | 9.36 | 31 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8561 | 30.3111 | 7.4741 | 28.4413 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.194 |  | 2018-02-15
LG Electronics Inc. | LG290S1C-G4 | 290 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 290 | 266.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.43 | 39 | 8.98 | 32.3 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7859 | 31.5753 | 7.1638 | 29.9189 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19445 |  | 2018-02-15
LG Electronics Inc. | LG290S1C-L4 | 290 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 290 | 265.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.61 | 39 | 9.1 | 31.9 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.8017 | 30.6924 | 7.2372 | 29.183 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19068 |  | 2018-02-15
LG Electronics Inc. | LG290S1W-A5 | 290 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 290 | 264 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 9.97 | 38.3 | 9.36 | 31 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8561 | 30.3111 | 7.4741 | 28.4413 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.194 |  | 2018-02-15
LG Electronics Inc. | LG290S1W-G4 | 290 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 290 | 266.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.43 | 39 | 8.98 | 32.3 | 44.2 | -0.43 | 0.03 | -0.31 | -0.02 | -0.41 | 1.7859 | 31.5753 | 7.1638 | 29.9189 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19445 |  | 2018-02-15
LG Electronics Inc. | LG290S1W-L4 | 290 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 290 | 265.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.61 | 39 | 9.1 | 31.9 | 45.6 | -0.41 | 0.03 | -0.31 | -0.02 | -0.4 | 1.8017 | 30.6924 | 7.2372 | 29.183 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19068 |  | 2018-02-15
LG Electronics Inc. | LG295A1C-B3 | 295 W DC, Monocrystalline ACPV Module | UL 1741 | 295 | 267.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.85 | 39.68 | 9.28 | 31.83 | 47.9 | -0.41 | 0.03 | -0.29 | -0.02 | -0.4 | 1.86 | 31.33 | 7.42 | 28.76 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19754 |  | 2018-02-15
LG Electronics Inc. | LG295A1W-B3 | 295 W DC, Monocrystalline ACPV Module | UL 1741 | 295 | 267.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.85 | 39.68 | 9.28 | 31.83 | 47.9 | -0.41 | 0.03 | -0.29 | -0.02 | -0.4 | 1.86 | 31.33 | 7.42 | 28.76 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19754 |  | 2018-02-15
LG Electronics Inc. | LG295N1C-A3 | 295 W Monocrystalline Module | UL 1703 | 295 | 269.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.85 | 39.7 | 9.28 | 31.8 | 46.6 | -0.4 | 0.03 | -0.29 | -0.02 | -0.39 | 1.8799 | 31.2111 | 7.3902 | 29.0519 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19889 |  | 2018-04-02
LG Electronics Inc. | LG295N1C-B3 | 295 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 295 | 267.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.85 | 39.7 | 9.28 | 31.8 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.86 | 31.3 | 7.42 | 28.73 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19735 |  | 2018-02-15
LG Electronics Inc. | LG295N1C-G3 | 295 W Monocrystalline Module | UL 1703 | 295 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.94 | 39.3 | 9.34 | 31.8 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7719 | 31.2952 | 7.458 | 29.4781 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18797 |  | 2018-02-15
LG Electronics Inc. | LG295N1C-G4 | 295 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 295 | 268.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.87 | 39.5 | 9.28 | 31.8 | 48.8 | -0.38 | 0.03 | -0.28 | -0.02 | -0.36 | 1.85 | 31.13 | 7.39 | 29.11 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19522 |  | 2018-02-15
LG Electronics Inc. | LG295N1K-A3 | 295 W Monocrystalline Module | UL 1703 | 295 | 266.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 72 | 1 | N | 9.85 | 39.7 | 9.28 | 31.8 | 49.3 | -0.4 | 0.04 | -0.29 | -0.003 | -0.4 | 1.8686 | 31.4037 | 7.4429 | 28.828 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19892 |  | 2018-02-15
LG Electronics Inc. | LG295N1K-B3 | 295 W Monocrystalline Module | UL 1703 | 295 | 264 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.98 | 39.82 | 9.4 | 31.98 | 50.9 | -0.41 | 0.04 | -0.29 | -0.01 | -0.4 | 1.89 | 31.09 | 7.47 | 28.81 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19919 |  | 2018-02-15
LG Electronics Inc. | LG295N1K-G4 | 295 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 295 | 275.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.66 | 39.3 | 9.21 | 32.1 | 43.9 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8599 | 31.4293 | 7.3799 | 30.0878 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19815 |  | 2018-02-15
LG Electronics Inc. | LG295N1K-Z4 | 295 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 295 | 274.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.66 | 39.3 | 9.21 | 32.1 | 43.5 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.854 | 31.0491 | 7.5355 | 29.9027 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19513 |  | 2018-02-15
LG Electronics Inc. | LG295N1T-A4 | 295 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 295 | 270.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6366 | 60 | 1 | N | 9.65 | 39.9 | 9.08 | 32.5 | 48.1 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.818 | 31.5327 | 7.1932 | 29.7917 | Rack | Flat Plate | 0.98 | 1.67 | 1 | 0.19432 |  | 2018-02-15
LG Electronics Inc. | LG295N1W-A3 | 295 W Monocrystalline Module | UL 1703 | 295 | 269.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 72 | 1 | N | 9.85 | 39.7 | 9.28 | 31.8 | 46.6 | -0.4 | 0.03 | -0.29 | -0.02 | -0.39 | 1.8799 | 31.2111 | 7.3902 | 29.0519 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19889 |  | 2018-02-15
LG Electronics Inc. | LG295N1W-B3 | 295 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 295 | 267.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.85 | 39.7 | 9.28 | 31.8 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.86 | 31.3 | 7.42 | 28.73 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19735 |  | 2018-02-15
LG Electronics Inc. | LG295N1W-G3 | 295 W Monocrystalline Module | UL 1703 | 295 | 271.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.94 | 39.3 | 9.34 | 31.8 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7719 | 31.2952 | 7.458 | 29.4781 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18797 |  | 2018-02-15
LG Electronics Inc. | LG295N1W-G4 | 295 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 295 | 268.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.87 | 39.5 | 9.28 | 31.8 | 48.8 | -0.38 | 0.03 | -0.28 | -0.02 | -0.36 | 1.85 | 31.13 | 7.39 | 29.11 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19522 |  | 2018-02-15
LG Electronics Inc. | LG295S1C-A5 | 295 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 295 | 268.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.02 | 38.6 | 9.43 | 31.3 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.87 | 30.6044 | 7.53 | 28.7165 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.194 |  | 2018-02-15
LG Electronics Inc. | LG295S1C-G4 | 295 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 295 | 266.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.48 | 39.1 | 9.08 | 32.5 | 48.4 | -0.42 | 0.03 | -0.3 | -0.02 | -0.4 | 1.81 | 31.57 | 7.23 | 29.41 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1937 |  | 2018-02-15
LG Electronics Inc. | LG295S1W-A5 | 295 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 295 | 268.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.02 | 38.6 | 9.43 | 31.3 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.87 | 30.6044 | 7.53 | 28.7165 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.194 |  | 2018-02-15
LG Electronics Inc. | LG295S1W-G4 | 295 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 295 | 266.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.48 | 39.1 | 9.08 | 32.5 | 48.4 | -0.42 | 0.03 | -0.3 | -0.02 | -0.4 | 1.81 | 31.57 | 7.23 | 29.41 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1937 |  | 2018-02-15
LG Electronics Inc. | LG300A1C-B3 | 300 W DC, Monocrystalline ACPV Module | UL 1741 | 300 | 272.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.98 | 39.82 | 9.4 | 31.98 | 47.9 | -0.41 | 0.03 | -0.29 | -0.02 | -0.4 | 1.89 | 31.48 | 7.51 | 28.89 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19832 |  | 2018-02-15
LG Electronics Inc. | LG300A1W-B3 | 300 W DC, Monocrystalline ACPV Module | UL 1741 | 300 | 272.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.98 | 39.82 | 9.4 | 31.98 | 47.9 | -0.41 | 0.03 | -0.29 | -0.02 | -0.4 | 1.89 | 31.48 | 7.51 | 28.89 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19832 |  | 2018-02-15
LG Electronics Inc. | LG300N1C-A3 | 300 W Monocrystalline Module | UL 1703 | 300 | 274.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.98 | 39.8 | 9.4 | 32 | 46.6 | -0.4 | 0.03 | -0.29 | -0.02 | -0.39 | 1.9042 | 31.4074 | 7.4857 | 29.2346 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19935 |  | 2018-04-02
LG Electronics Inc. | LG300N1C-B3 | 300 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 300 | 272.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.98 | 39.8 | 9.4 | 32 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.89 | 31.5 | 7.51 | 28.91 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19845 |  | 2018-02-15
LG Electronics Inc. | LG300N1C-G3 | 300 W Monocrystalline Module | UL 1703 | 300 | 276.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.05 | 39.5 | 9.46 | 32 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7947 | 31.4921 | 7.5538 | 29.6635 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18839 |  | 2018-02-15
LG Electronics Inc. | LG300N1C-G4 | 300 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 300 | 279.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.9 | 39.8 | 9.34 | 32.2 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.8859 | 31.4287 | 7.4641 | 30.9467 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19757 |  | 2018-02-15
LG Electronics Inc. | LG300N1C-Z4 | 300 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 300 | 278.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.9 | 39.8 | 9.34 | 32.2 | 44.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8819 | 31.3375 | 7.4878 | 29.9 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19658 |  | 2018-02-15
LG Electronics Inc. | LG300N1K-G4 | 300 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 300 | 279.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.7 | 39.7 | 9.26 | 32.5 | 43.9 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.87 | 31.8209 | 7.42 | 30.4627 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19835 |  | 2018-02-15
LG Electronics Inc. | LG300N1K-Z4 | 300 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 300 | 279.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.7 | 39.7 | 9.26 | 32.5 | 43.5 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.864 | 31.436 | 7.5764 | 30.2753 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19533 |  | 2018-02-15
LG Electronics Inc. | LG300N1T-A4 | 300 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 300 | 275.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6366 | 60 | 1 | N | 9.69 | 40.3 | 9.12 | 32.9 | 48.1 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.826 | 31.9208 | 7.2249 | 30.1583 | Rack | Flat Plate | 0.98 | 1.67 | 1 | 0.19429 |  | 2018-02-15
LG Electronics Inc. | LG300N1W-A3 | 300 W Monocrystalline Module | UL 1703 | 300 | 274.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 72 | 1 | N | 9.98 | 39.8 | 9.4 | 32 | 46.6 | -0.4 | 0.03 | -0.29 | -0.02 | -0.39 | 1.9042 | 31.4074 | 7.4857 | 29.2346 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19935 |  | 2018-02-15
LG Electronics Inc. | LG300N1W-B3 | 300 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 300 | 272.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.98 | 39.8 | 9.4 | 32 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.89 | 31.5 | 7.51 | 28.91 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19845 |  | 2018-02-15
LG Electronics Inc. | LG300N1W-G3 | 300 W Monocrystalline Module | UL 1703 | 300 | 276.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.05 | 39.5 | 9.46 | 32 | 43.5 | -0.43 | 0.03 | -0.3 | -0.02 | -0.41 | 1.7947 | 31.4921 | 7.5538 | 29.6635 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.18839 |  | 2018-02-15
LG Electronics Inc. | LG300N1W-G4 | 300 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 300 | 279.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.9 | 39.8 | 9.34 | 32.2 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.8859 | 31.4287 | 7.4641 | 30.9467 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19757 |  | 2018-02-15
LG Electronics Inc. | LG300S1C-A5 | 300 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 300 | 273.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.07 | 38.9 | 9.47 | 31.7 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8779 | 30.9956 | 7.5619 | 29.0835 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19403 |  | 2018-02-15
LG Electronics Inc. | LG300S1W-A5 | 300 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 300 | 273.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.07 | 38.9 | 9.47 | 31.7 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8779 | 30.9956 | 7.5619 | 29.0835 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19403 |  | 2018-02-15
LG Electronics Inc. | LG305A1C-B3 | 305 W DC, Monocrystalline ACPV Module | UL 1741 | 305 | 276.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.1 | 40 | 9.52 | 32.1 | 47.9 | -0.41 | 0.03 | -0.29 | -0.02 | -0.4 | 1.91 | 31.6 | 7.61 | 29 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19789 |  | 2018-02-15
LG Electronics Inc. | LG305A1W-B3 | 305 W DC, Monocrystalline ACPV Module | UL 1741 | 305 | 276.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.1 | 40 | 9.52 | 32.1 | 47.9 | -0.41 | 0.03 | -0.29 | -0.02 | -0.4 | 1.91 | 31.6 | 7.61 | 29 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19789 |  | 2018-02-15
LG Electronics Inc. | LG305N1C-B3 | 305 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 305 | 276.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.1 | 40 | 9.52 | 32.1 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.91 | 31.6 | 7.61 | 29 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19789 |  | 2018-02-15
LG Electronics Inc. | LG305N1C-G4 | 305 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 305 | 284.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.93 | 40.1 | 9.39 | 32.5 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.896 | 31.7216 | 7.504 | 31.235 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19719 |  | 2018-02-15
LG Electronics Inc. | LG305N1C-Z4 | 305 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 305 | 283.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.93 | 40.1 | 9.39 | 32.5 | 44.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8919 | 31.6295 | 7.5279 | 30.1786 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1962 |  | 2018-02-15
LG Electronics Inc. | LG305N1K-G4 | 305 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 305 | 284.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.74 | 40.1 | 9.28 | 32.9 | 43.9 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.874 | 32.2125 | 7.436 | 30.8376 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19793 |  | 2018-02-15
LG Electronics Inc. | LG305N1K-Z4 | 305 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 305 | 284 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.74 | 40.1 | 9.28 | 32.9 | 43.5 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.8681 | 31.8229 | 7.5927 | 30.6479 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19491 |  | 2018-02-15
LG Electronics Inc. | LG305N1T-A4 | 305 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 305 | 279.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6366 | 60 | 1 | N | 9.73 | 40.7 | 9.16 | 33.3 | 48.1 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.834 | 32.3089 | 7.2566 | 30.525 | Rack | Flat Plate | 0.98 | 1.67 | 1 | 0.19428 |  | 2018-02-15
LG Electronics Inc. | LG305N1T-A5 | 305 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 305 | 280.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.706 | 60 | 1 | N | 10.04 | 40.6 | 9.37 | 32.6 | 47.3 | -0.36 | 0.02 | -0.27 | -0.02 | -0.34 | 1.8701 | 31.5576 | 7.4609 | 30.136 | Rack | Flat Plate | 1 | 1.706 | 1 | 0.19349 |  | 2018-02-15
LG Electronics Inc. | LG305N1W-B3 | 305 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 305 | 276.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.1 | 40 | 9.52 | 32.1 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.91 | 31.6 | 7.61 | 29 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19789 |  | 2018-02-15
LG Electronics Inc. | LG305N1W-G4 | 305 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 305 | 284.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.93 | 40.1 | 9.39 | 32.5 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.896 | 31.7216 | 7.504 | 31.235 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19719 |  | 2018-02-15
LG Electronics Inc. | LG305S1C-A5 | 305 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 305 | 278.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.12 | 39.2 | 9.54 | 32 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8918 | 31.2889 | 7.6178 | 29.3587 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19407 |  | 2018-02-15
LG Electronics Inc. | LG305S1W-A5 | 305 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 305 | 278.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.12 | 39.2 | 9.54 | 32 | 46.7 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8918 | 31.2889 | 7.6178 | 29.3587 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19407 |  | 2018-02-15
LG Electronics Inc. | LG310N1C-B3 | 310 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 310 | 281.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.19 | 40.1 | 9.61 | 32.3 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.93 | 31.8 | 7.68 | 29.18 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19798 |  | 2018-02-15
LG Electronics Inc. | LG310N1C-G4 | 310 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 310 | 289.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.96 | 40.4 | 9.45 | 32.8 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.9081 | 32.0144 | 7.552 | 31.5234 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19705 |  | 2018-02-15
LG Electronics Inc. | LG310N1C-V5 | 310 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 310 | 287.6 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.29 | 40.5 | 9.67 | 32.1 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.9369 | 31.3743 | 1.9369 | 31.3743 | 7.6948 | 29.867 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG310N1C-Z4 | 310 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 310 | 287.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.96 | 40.4 | 9.45 | 32.8 | 44.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.904 | 31.9214 | 7.576 | 30.4571 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19606 |  | 2018-02-15
LG Electronics Inc. | LG310N1K-A5 | 310 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 310 | 285.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.11 | 40.6 | 9.55 | 32.5 | 47.7 | -0.357 | 0.02 | -0.26 | -0.02 | -0.34 | 1.9061 | 31.742 | 7.6145 | 30.0364 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19517 |  | 2018-02-15
LG Electronics Inc. | LG310N1K-G4 | 310 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 310 | 289.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.78 | 40.5 | 9.31 | 33.3 | 43.9 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8801 | 32.6042 | 7.4601 | 31.2125 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19774 |  | 2018-02-15
LG Electronics Inc. | LG310N1K-L5 | 310 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 310 | 287.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.36 | 40.3 | 9.94 | 31.2 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9448 | 31.3207 | 7.7359 | 30.2157 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG310N1K-V5 | 310 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 310 | 284.6 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.11 | 40.6 | 9.55 | 32.5 | 48.5 | -0.353 | 0.036 | -0.261 |  |  | 1.9278 | 32.0689 | 7.6895 | 30.0765 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG310N1K-Z4 | 310 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 310 | 288.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.78 | 40.5 | 9.31 | 33.3 | 43.5 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.8741 | 32.2098 | 7.6173 | 31.0205 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19472 |  | 2018-02-15
LG Electronics Inc. | LG310N1T-A4 | 310 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 310 | 284.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6366 | 60 | 1 | N | 9.77 | 41.1 | 9.2 | 33.7 | 48.1 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.842 | 32.697 | 7.2883 | 30.8917 | Rack | Flat Plate | 0.98 | 1.67 | 1 | 0.19428 |  | 2018-02-15
LG Electronics Inc. | LG310N1T-A5 | 310 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 310 | 285.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.706 | 60 | 1 | N | 10.08 | 40.7 | 9.38 | 33.1 | 47.3 | -0.36 | 0.02 | -0.27 | -0.02 | -0.34 | 1.8721 | 32.0416 | 7.4689 | 30.5983 | Rack | Flat Plate | 1 | 1.706 | 1 | 0.1935 |  | 2018-02-15
LG Electronics Inc. | LG310N1T-L5 | 310 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 310 | 286 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.22 | 40.6 | 9.61 | 32.3 | 46.5 | -0.3605 | 0.03358 | -0.2696 |  |  | 1.9201 | 31.6406 | 7.656 | 30.1499 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG310N1T-V5 | 310 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 310 | 285.1 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 | 1 | N | 10.14 | 40.2 | 9.52 | 32.6 | 48.5 | -0.346 | 0.0385 | -0.26 |  |  | 1.8972 | 32.4139 | 7.5517 | 30.4984 | [6 empty] | 2019-10-01
LG Electronics Inc. | LG310N1W-B3 | 310 W Monocrystalline Module, 600V or 1000 V System Voltage | UL 1703 | 310 | 281.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.19 | 40.1 | 9.61 | 32.3 | 47.9 | -0.41 | 0.03 | -0.32 | -0.02 | -0.4 | 1.93 | 31.8 | 7.68 | 29.18 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19798 |  | 2018-02-15
LG Electronics Inc. | LG310N1W-G4 | 310 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 310 | 289.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.96 | 40.4 | 9.45 | 32.8 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.9081 | 32.0144 | 7.552 | 31.5234 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19705 |  | 2018-02-15
LG Electronics Inc. | LG310N1W-V5 | 310 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 310 | 287.6 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.29 | 40.5 | 9.67 | 32.1 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.9369 | 31.3743 | 1.9369 | 31.3743 | 7.6948 | 29.867 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG315E1K-A5 | 315 W DC, ACPV module | UL 1741 | 315 | 290 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 |  | N | 10.15 | 40.7 | 9.58 | 32.9 | 47.7 | -0.356 | 0.03 | -0.26 | -0.01 | -0.34 | 1.94 | 33.5 | 7.75 | 31.7 | [6 empty] | 2017-08-01 | 2018-02-15
LG Electronics Inc. | LG315N1C-G4 | 315 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 315 | 293.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.02 | 40.6 | 9.5 | 33.2 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.9182 | 32.4048 | 7.5919 | 31.9078 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19733 |  | 2018-02-15
LG Electronics Inc. | LG315N1C-L5 | 315 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 315 | 291.6 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.48 | 40.4 | 10.07 | 31.3 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 1.9767 |  | 1.9767 | 30.887 | 7.8599 | 29.813 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG315N1C-V5 | 315 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 315 | 292.4 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.33 | 40.6 | 9.7 | 32.5 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.943 | 31.7652 | 1.943 | 31.7652 | 7.7187 | 30.2391 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG315N1C-Z4 | 315 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 315 | 292.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.02 | 40.6 | 9.5 | 33.2 | 44.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.9141 | 32.3107 | 7.6161 | 30.8286 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19634 |  | 2018-02-15
LG Electronics Inc. | LG315N1K-A5 | 315 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 315 | 289.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.15 | 40.7 | 9.58 | 32.9 | 47.7 | -0.357 | 0.02 | -0.26 | -0.02 | -0.34 | 1.9121 | 32.1327 | 7.6384 | 30.4061 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19505 |  | 2018-02-15
LG Electronics Inc. | LG315N1K-G4 | 315 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 315 | 294.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.82 | 40.6 | 9.35 | 33.7 | 43.9 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8882 | 32.9958 | 7.4921 | 31.5875 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19778 |  | 2018-02-15
LG Electronics Inc. | LG315N1K-L5 | 315 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 315 | 292.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.4 | 40.4 | 9.97 | 31.6 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9507 | 31.7223 | 7.7593 | 30.6031 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG315N1K-V5 | 315W, 60 cell monocrystalline Module, black backsheet, 1000V max system Voltage | UL 1703 | 315 | 289.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 | 1 | N | 10.15 | 40.7 | 9.58 | 32.9 | 48.5 | -0.3535 | 0.0365 | -0.2615 | -0.0055 | -0.348 | 1.9339 | 32.4636 | 7.7136 | 30.4467 | [6 empty] | 2018-10-15 | 2019-01-15
LG Electronics Inc. | LG315N1K-Z4 | 315 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 315 | 293.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.82 | 40.6 | 9.35 | 33.7 | 43.5 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.8821 | 32.5967 | 7.65 | 31.3932 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19477 |  | 2018-02-15
LG Electronics Inc. | LG315N1T-A4 | 315 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 315 | 289.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6366 | 60 | 1 | N | 9.81 | 41.5 | 9.24 | 34.1 | 48.1 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.85 | 33.0851 | 7.32 | 31.2583 | Rack | Flat Plate | 0.98 | 1.67 | 1 | 0.19431 |  | 2018-02-15
LG Electronics Inc. | LG315N1T-A5 | 315 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 315 | 289.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.706 | 60 | 1 | N | 10.12 | 40.8 | 9.41 | 33.5 | 47.3 | -0.36 | 0.02 | -0.27 | -0.02 | -0.34 | 1.8781 | 32.4288 | 7.4928 | 30.968 | Rack | Flat Plate | 1 | 1.706 | 1 | 0.19335 |  | 2018-02-15
LG Electronics Inc. | LG315N1T-L5 | 315 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 315 | 290.7 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.26 | 40.7 | 9.67 | 32.6 | 46.5 | -0.3605 | 0.03358 | -0.2696 |  |  | 1.932 | 31.9345 | 7.7038 | 30.4299 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG315N1T-V5 | 315 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 315 | 289.9 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 | 1 | N | 10.18 | 40.3 | 9.58 | 32.9 | 48.5 | -0.346 | 0.0385 | -0.26 |  |  | 1.9091 | 32.7121 | 7.5993 | 30.779 | [6 empty] | 2019-10-01
LG Electronics Inc. | LG315N1W-G4 | 315 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 315 | 293.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.02 | 40.6 | 9.5 | 33.2 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.9182 | 32.4048 | 7.5919 | 31.9078 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19733 |  | 2018-02-15
LG Electronics Inc. | LG315N1W-L5 | 315 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 315 | 291.6 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.48 | 40.4 | 10.07 | 31.3 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 1.9767 | 30.887 | 7.8599 | 29.813 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG315N1W-V5 | 315 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 315 | 292.4 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.33 | 40.6 | 9.7 | 32.5 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.943 | 31.7652 | 1.943 | 31.7652 | 7.7187 | 30.2391 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG320E1K-A5 | 320 W DC, ACPV module | UL 1741 | 320 | 294.7 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 |  | N | 10.19 | 40.8 | 9.62 | 33.3 | 47.7 | -0.356 | 0.03 | -0.26 | -0.01 | -0.34 | 1.94 | 33.5 | 7.75 | 31.7 | [6 empty] | 2017-08-01 | 2018-02-15
LG Electronics Inc. | LG320N1C-A5 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.37 | 40.7 | 9.74 | 32.9 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.95 | 32.0392 | 7.7801 | 30.6047 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19524 |  | 2018-02-15
LG Electronics Inc. | LG320N1C-G4 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 298.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.05 | 40.9 | 9.53 | 33.6 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.9242 | 32.7952 | 7.6159 | 32.2922 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1972 |  | 2018-02-15
LG Electronics Inc. | LG320N1C-L5 | 320 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 320 | 296.4 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.52 | 40.5 | 10.1 | 31.7 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 1.9826 |  | 1.9826 | 31.2817 | 7.8833 | 30.194 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG320N1C-N5 | 320 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 320 | 298.4 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.53 | 40.8 | 10.04 | 31.9 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0011 | 31.1646 | 7.9154 | 30.0522 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG320N1C-V5 | 320W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 320 | 297.2 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.37 | 40.7 | 9.74 | 32.9 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.951 | 32.1562 | 7.7505 | 30.6113 | [6 empty] | 2019-06-03
LG Electronics Inc. | LG320N1C-Z4 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 297.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.05 | 40.9 | 9.53 | 33.6 | 44.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.9201 | 32.7 | 7.6402 | 31.2 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19622 |  | 2018-02-15
LG Electronics Inc. | LG320N1C-Z5 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 295.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.654 | 60 | 1 | N | 10.37 | 40.7 | 9.74 | 32.9 | 46.6 | -0.362 | 0.03 | -0.26 | -0.02 | -0.35 | 1.948 | 32.1327 | 7.7623 | 30.502 | Rack | Flat Plate | 0.994 | 1.664 | 1 | 0.19561 |  | 2018-02-15
LG Electronics Inc. | LG320N1K-A5 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 294.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.19 | 40.8 | 9.62 | 33.3 | 47.7 | -0.357 | 0.02 | -0.26 | -0.02 | -0.34 | 1.92 | 32.5233 | 7.6703 | 30.7758 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19514 |  | 2018-02-15
LG Electronics Inc. | LG320N1K-G4 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 299 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.86 | 40.9 | 9.39 | 34.1 | 43.9 | -0.36 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8963 | 33.3875 | 7.5242 | 31.9624 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19785 |  | 2018-02-15
LG Electronics Inc. | LG320N1K-L5 | 320 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 320 | 297.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.44 | 40.5 | 10.01 | 32 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9585 | 32.1238 | 7.7904 | 30.9905 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG320N1K-V5 | 320W, 60 cell monocrystalline Module, black backsheet, 1000V max system Voltage | UL 1703 | 320 | 294 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 | 1 | N | 10.19 | 40.8 | 9.62 | 33.3 | 48.5 | -0.3535 | 0.0365 | -0.2615 | -0.0055 | -0.348 | 1.9419 | 32.8583 | 7.7458 | 30.8168 | [6 empty] | 2018-10-15 | 2019-01-15
LG Electronics Inc. | LG320N1K-Z4 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 298.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 9.86 | 40.9 | 9.39 | 34.1 | 43.5 | -0.38 | 0.03 | -0.28 | -0.01 | -0.37 | 1.8902 | 32.9836 | 7.6827 | 31.7658 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19483 |  | 2018-02-15
LG Electronics Inc. | LG320N1T-A5 | 320 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 320 | 294.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.706 | 60 | 1 | N | 10.16 | 40.9 | 9.45 | 33.9 | 47.3 | -0.36 | 0.02 | -0.27 | -0.02 | -0.34 | 1.8861 | 32.816 | 7.5246 | 31.3378 | Rack | Flat Plate | 1 | 1.706 | 1 | 0.19342 |  | 2018-02-15
LG Electronics Inc. | LG320N1T-L5 | 320 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 320 | 295.4 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.3 | 40.8 | 9.73 | 32.9 | 46.5 | -0.3605 | 0.03358 | -0.2696 |  |  | 1.944 | 32.2284 | 7.7516 | 30.7099 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG320N1T-V5 | 320 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 320 | 294.6 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 | 1 | N | 10.22 | 40.4 | 9.65 | 33.2 | 48.5 | -0.346 | 0.0385 | -0.26 |  |  | 1.9231 | 33.0104 | 7.6548 | 31.0597 | [6 empty] | 2019-10-01
LG Electronics Inc. | LG320N1W-A5 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.37 | 40.7 | 9.74 | 32.9 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.95 | 32.0392 | 7.7801 | 30.6047 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19524 |  | 2018-02-15
LG Electronics Inc. | LG320N1W-G4 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 298.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.05 | 40.9 | 9.53 | 33.6 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.9242 | 32.7952 | 7.6159 | 32.2922 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.1972 |  | 2018-02-15
LG Electronics Inc. | LG320N1W-L5 | 320 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 320 | 296.4 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.52 | 40.5 | 10.1 | 31.7 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 1.9826 | 31.2817 | 7.8833 | 30.194 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG320N1W-N5 | 320 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 320 | 298.4 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.53 | 40.8 | 10.04 | 31.9 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0011 | 31.1646 | 7.9154 | 30.0522 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG320N1W-V5 | 320W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 320 | 297.2 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.37 | 40.7 | 9.74 | 32.9 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.951 | 32.1562 | 7.7505 | 30.6113 | [6 empty] | 2019-06-03
LG Electronics Inc. | LG320S2C-G4 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 294.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.28 | 45.6 | 8.66 | 37 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.7203 | 36.313 | 6.9397 | 34.252 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19522 |  | 2018-02-15
LG Electronics Inc. | LG320S2W-G4 | 320 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 320 | 294.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.28 | 45.6 | 8.66 | 37 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.7203 | 36.313 | 6.9397 | 34.252 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19522 |  | 2018-02-15
LG Electronics Inc. | LG325E1C-A5 | 325 W DC, ACPV module | UL 1741 | 325 | 301.3 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 |  | N | 10.41 | 40.8 | 9.77 | 33.3 | 45.9 | -0.36 | 0.02 | -0.26 | -0.02 | -0.34 | 1.97 | 33.5 | 7.86 | 32 | [6 empty] | 2017-08-01 | 2018-02-15
LG Electronics Inc. | LG325E1K-A5 | 325 W DC, ACPV module | UL 1741 | 325 | 299.5 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 |  | N | 10.23 | 40.9 | 9.65 | 33.7 | 47.7 | -0.356 | 0.03 | -0.26 | -0.01 | -0.34 | 1.94 | 33.5 | 7.75 | 31.7 | [6 empty] | 2017-08-01 | 2018-02-15
LG Electronics Inc. | LG325N1C-A5 | 325 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 325 | 301.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.41 | 40.8 | 9.77 | 33.3 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.956 | 32.4288 | 7.8041 | 30.9767 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19517 |  | 2018-02-15
LG Electronics Inc. | LG325N1C-G4 | 325 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 325 | 303.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.08 | 41.2 | 9.57 | 34 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.9323 | 33.1856 | 7.6479 | 32.6766 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19731 |  | 2018-02-15
LG Electronics Inc. | LG325N1C-L5 | 325 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 325 | 301.1 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.56 | 40.6 | 10.13 | 32.1 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 1.9885 |  | 1.9885 | 31.6764 | 7.9067 | 30.575 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG325N1C-N5 | 325 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 325 | 303.2 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.57 | 40.9 | 10.07 | 32.3 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0071 | 31.5553 | 7.9391 | 30.429 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG325N1C-V5 | 325W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 325 | 301.9 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.41 | 40.8 | 9.77 | 33.3 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.957 | 32.5471 | 7.7744 | 30.9835 | [6 empty] | 2018-10-15 | 2019-06-03
LG Electronics Inc. | LG325N1C-Z4 | 325 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 325 | 302.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.08 | 41.2 | 9.57 | 34 | 44.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.9282 | 33.0893 | 7.6722 | 31.5714 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19632 |  | 2018-02-15
LG Electronics Inc. | LG325N1C-Z5 | 325 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 325 | 300.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.654 | 60 | 1 | N | 10.41 | 40.8 | 9.77 | 33.3 | 46.6 | -0.362 | 0.03 | -0.26 | -0.02 | -0.35 | 1.954 | 32.5233 | 7.7862 | 30.8729 | Rack | Flat Plate | 0.994 | 1.664 | 1 | 0.19554 |  | 2018-02-15
LG Electronics Inc. | LG325N1K-A5 | 325 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 325 | 299.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.23 | 40.9 | 9.65 | 33.7 | 47.7 | -0.357 | 0.02 | -0.26 | -0.02 | -0.34 | 1.926 | 32.914 | 7.6942 | 31.1455 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19506 |  | 2018-02-15
LG Electronics Inc. | LG325N1K-L5 | 325 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 325 | 302.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.48 | 40.6 | 10.04 | 32.4 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9643 | 32.5254 | 7.8137 | 31.3779 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG325N1K-V5 | 325 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 325 | 298.8 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.23 | 40.9 | 9.65 | 33.7 | 48.5 | -0.353 | 0.036 | -0.261 | -0.0055 | -0.348 | 1.948 | 33.253 | 7.77 | 31.187 | [6 empty] | 2018-10-15 | 2019-08-15
LG Electronics Inc. | LG325N1T-A5 | 325 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 325 | 299.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.706 | 60 | 1 | N | 10.2 | 41 | 9.48 | 34.3 | 47.3 | -0.36 | 0.02 | -0.27 | -0.02 | -0.34 | 1.8921 | 33.2032 | 7.5485 | 31.7076 | Rack | Flat Plate | 1 | 1.706 | 1 | 0.1933 |  | 2018-02-15
LG Electronics Inc. | LG325N1T-L5 | 325 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 325 | 300.2 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.34 | 40.9 | 9.79 | 33.2 | 46.5 | -0.3605 | 0.03358 | -0.2696 |  |  | 1.956 | 32.5222 | 7.7994 | 30.9899 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG325N1T-V5 | 325 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 325 | 299.3 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 | 1 | N | 10.26 | 40.5 | 9.7 | 33.5 | 48.5 | -0.346 | 0.0385 | -0.26 |  |  | 1.9331 | 33.3087 | 7.6945 | 31.3403 | [6 empty] | 2019-10-01
LG Electronics Inc. | LG325N1W-A5 | 325 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 325 | 301.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.41 | 40.8 | 9.77 | 33.3 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.956 | 32.4288 | 7.8041 | 30.9767 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19517 |  | 2018-02-15
LG Electronics Inc. | LG325N1W-G4 | 325 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 325 | 303.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.08 | 41.2 | 9.57 | 34 | 43.2 | -0.38 | 0.03 | -0.27 | -0.02 | -0.36 | 1.9323 | 33.1856 | 7.6479 | 32.6766 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19731 |  | 2018-02-15
LG Electronics Inc. | LG325N1W-L5 | 325 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 325 | 301.1 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.56 | 40.6 | 10.13 | 32.1 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 1.9885 | 31.6764 | 7.9067 | 30.575 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG325N1W-N5 | 325 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 325 | 303.2 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.57 | 40.9 | 10.07 | 32.3 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0071 | 31.5553 | 7.9391 | 30.429 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG325N1W-V5 | 325W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 325 | 301.9 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.41 | 40.8 | 9.77 | 33.3 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.957 | 32.5471 | 7.7744 | 30.9835 | [6 empty] | 2018-10-15 | 2019-06-03
LG Electronics Inc. | LG325S2C-G4 | 325 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 325 | 299.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.35 | 45.8 | 8.75 | 37.2 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.7382 | 36.5093 | 7.0118 | 34.4371 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19526 |  | 2018-02-15
LG Electronics Inc. | LG325S2W-G4 | 325 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 325 | 299.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.35 | 45.8 | 8.75 | 37.2 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.7382 | 36.5093 | 7.0118 | 34.4371 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19526 |  | 2018-02-15
LG Electronics Inc. | LG330E1C-A5 | 330 W DC, ACPV module | UL 1741 | 330 | 306 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 |  | N | 10.45 | 40.9 | 9.8 | 33.7 | 45.9 | -0.36 | 0.02 | -0.26 | -0.02 | -0.34 | 1.97 | 33.5 | 7.86 | 32 | [6 empty] | 2017-08-01 | 2018-02-15
LG Electronics Inc. | LG330N1C-A5 | 330 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 330 | 306.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.45 | 40.9 | 9.8 | 33.7 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.962 | 32.8183 | 7.828 | 31.3488 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19512 |  | 2018-02-15
LG Electronics Inc. | LG330N1C-L5 | 330 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 330 | 305.9 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.6 | 40.7 | 10.16 | 32.5 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 1.9944 |  | 1.9944 | 32.0711 | 7.9301 | 30.956 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG330N1C-N5 | 330 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 330 | 307.9 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.61 | 41 | 10.1 | 32.7 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0131 | 31.9461 | 7.9627 | 30.8059 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG330N1C-V5 | 330W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 330 | 306.7 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.45 | 40.9 | 9.8 | 33.7 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.963 | 32.9381 | 7.7983 | 31.3557 | [6 empty] | 2018-10-15 | 2019-06-03
LG Electronics Inc. | LG330N1C-Z4 | 330 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 330 | 307 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5876 | 60 | 1 | N | 10.11 | 41.5 | 9.63 | 34.3 | 44.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.9403 | 33.3813 | 7.7203 | 31.85 | Rack | Flat Plate | 0.98 | 1.62 | 1 | 0.19627 |  | 2018-02-15
LG Electronics Inc. | LG330N1C-Z5 | 330 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 330 | 305.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.654 | 60 | 1 | N | 10.45 | 40.9 | 9.8 | 33.7 | 46.6 | -0.362 | 0.03 | -0.26 | -0.02 | -0.35 | 1.96 | 32.914 | 7.8102 | 31.2437 | Rack | Flat Plate | 0.994 | 1.664 | 1 | 0.19549 |  | 2018-02-15
LG Electronics Inc. | LG330N1K-A5 | 330 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 330 | 304.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.27 | 41 | 9.69 | 34.1 | 47.7 | -0.357 | 0.02 | -0.26 | -0.02 | -0.34 | 1.934 | 33.3047 | 7.7261 | 31.5152 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19519 |  | 2018-02-15
LG Electronics Inc. | LG330N1K-L5 | 330 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 330 | 306.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.52 | 40.7 | 10.07 | 32.8 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9702 | 32.9269 | 7.8371 | 31.7652 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG330N1K-V5 | 330W, 60 cell monocrystalline Module, black backsheet, 1000V max system Voltage | UL 1703 | 330 | 303.6 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.27 | 41 | 9.69 | 34.1 | 48.5 | -0.353 | 0.036 | -0.261 |  |  | 1.9561 | 33.6477 | 7.8022 | 31.5572 | [6 empty] | 2019-05-01
LG Electronics Inc. | LG330N1T-A5 | 330 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 330 | 304.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.706 | 60 | 1 | N | 10.24 | 41.1 | 9.52 | 34.7 | 47.3 | -0.36 | 0.02 | -0.27 | -0.02 | -0.34 | 1.9 | 33.5904 | 7.5804 | 32.0773 | Rack | Flat Plate | 1 | 1.706 | 1 | 0.1934 |  | 2018-02-15
LG Electronics Inc. | LG330N1T-L5 | 330 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 330 | 304.9 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.38 | 41 | 9.85 | 33.5 | 46.5 | -0.3605 | 0.03358 | -0.2696 |  |  | 1.968 | 32.8161 | 7.8472 | 31.27 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG330N1T-V5 | 330 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 330 | 304.1 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 | 1 | N | 10.3 | 40.6 | 9.77 | 33.8 | 48.5 | -0.346 | 0.0385 | -0.26 |  |  | 1.947 | 33.607 | 7.75 | 31.621 | [6 empty] | 2019-10-01
LG Electronics Inc. | LG330N1W-A5 | 330 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 330 | 306.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.45 | 40.9 | 9.8 | 33.7 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.962 | 32.8183 | 7.828 | 31.3488 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19512 |  | 2018-02-15
LG Electronics Inc. | LG330N1W-L5 | 330 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 330 | 305.9 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.6 | 40.7 | 10.16 | 32.5 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 1.9944 | 32.0711 | 7.9301 | 30.956 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG330N1W-N5 | 330 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 330 | 307.9 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.61 | 41 | 10.1 | 32.7 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0131 | 31.9461 | 7.9627 | 30.8059 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG330N1W-V5 | 330W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 330 | 306.7 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.45 | 40.9 | 9.8 | 33.7 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.963 | 32.9381 | 7.7983 | 31.3557 | [6 empty] | 2018-10-15 | 2019-06-03
LG Electronics Inc. | LG330Q1C-V5 | 330 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 330 | 310.4 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.73 | 42.5 | 9.38 | 35.2 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.8571 | 33.7325 | 1.8571 | 33.7325 | 7.4503 | 33.0132 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG330Q1K-A5 | 330 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 330 | 306.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.73 | 42.5 | 9.45 | 35.2 | 48.7 | -0.31 | 0.04 | -0.24 | 0.01 | -0.32 | 1.8861 | 32.8087 | 7.5934 | 32.1391 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18751 |  | 2018-02-15
LG Electronics Inc. | LG330S2C-G4 | 330 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 330 | 303.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.41 | 46 | 8.85 | 37.3 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.7581 | 36.6074 | 7.0919 | 34.5297 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19503 |  | 2018-02-15
LG Electronics Inc. | LG330S2W-G4 | 330 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 330 | 303.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.41 | 46 | 8.85 | 37.3 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.7581 | 36.6074 | 7.0919 | 34.5297 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19503 |  | 2018-02-15
LG Electronics Inc. | LG333N1C-A5 | 333W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 333 | 309.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.47 | 41 | 9.81 | 34 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.964 | 33.1105 | 7.836 | 31.6279 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19528 |  | 2018-02-15
LG Electronics Inc. | LG333N1C-V5 | 333 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 333 | 309.6 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.47 | 40.9 | 9.83 | 33.9 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.969 | 33.1336 | 1.969 | 33.1336 | 7.8221 | 31.5417 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG333N1W-A5 | 333W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 333 | 309.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.47 | 41 | 9.81 | 34 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.964 | 33.1105 | 7.836 | 31.6279 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19528 |  | 2018-02-15
LG Electronics Inc. | LG333N1W-V5 | 333 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 333 | 309.6 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.47 | 40.9 | 9.83 | 33.9 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.969 | 33.1336 | 1.969 | 33.1336 | 7.8221 | 31.5417 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG335E1C-A5 | 335 W DC, ACPV module | UL 1741 | 335 | 310.8 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 |  | N | 10.49 | 41 | 9.83 | 34.1 | 45.9 | -0.36 | 0.02 | -0.26 | -0.02 | -0.34 | 1.97 | 33.5 | 7.86 | 32 | [6 empty] | 2017-08-01 | 2018-02-15
LG Electronics Inc. | LG335N1C-A5 | 335 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 335 | 311.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.49 | 41 | 9.83 | 34.1 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.968 | 33.2078 | 7.852 | 31.7209 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19508 |  | 2018-02-15
LG Electronics Inc. | LG335N1C-L5 | 335 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 335 | 310.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.64 | 40.8 | 10.19 | 32.9 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 2.0003 |  | 2.0003 | 32.4658 | 7.9536 | 31.337 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG335N1C-N5 | 335 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 335 | 312.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.65 | 41.1 | 10.13 | 33.1 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0191 | 32.3369 | 7.9864 | 31.1827 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG335N1C-V5 | 335W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 335 | 311.5 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.49 | 41 | 9.83 | 34.1 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.969 | 33.329 | 7.8221 | 31.7278 | [6 empty] | 2018-10-15 | 2019-06-03
LG Electronics Inc. | LG335N1C-Z5 | 335 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 335 | 309.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.654 | 60 | 1 | N | 10.49 | 41 | 9.83 | 34.1 | 46.6 | -0.362 | 0.03 | -0.26 | -0.02 | -0.35 | 1.966 | 33.3047 | 7.8341 | 31.6146 | Rack | Flat Plate | 0.994 | 1.664 | 1 | 0.19545 |  | 2018-02-15
LG Electronics Inc. | LG335N1K-A5 | 335 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 335 | 308.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.31 | 41.1 | 9.72 | 34.5 | 47.7 | -0.357 | 0.02 | -0.26 | -0.02 | -0.34 | 1.94 | 33.6953 | 7.75 | 31.8848 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19513 |  | 2018-02-15
LG Electronics Inc. | LG335N1K-L5 | 335 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 335 | 311.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.56 | 40.8 | 10.1 | 33.2 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9761 | 33.3285 | 7.8604 | 32.1526 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG335N1K-V5 | 335W, 60 cell monocrystalline Module, black backsheet, 1000V max system Voltage | UL 1703 | 335 | 308.3 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.31 | 41.1 | 9.72 | 34.5 | 48.5 | -0.353 | 0.036 | -0.261 |  |  | 1.9621 | 34.0424 | 7.8264 | 31.9273 | [6 empty] | 2019-05-01
LG Electronics Inc. | LG335N1T-A5 | 335 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 335 | 308.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.706 | 60 | 1 | N | 10.28 | 41.2 | 9.55 | 35.1 | 47.3 | -0.36 | 0.02 | -0.27 | -0.02 | -0.34 | 1.906 | 33.9776 | 7.6043 | 32.4471 | Rack | Flat Plate | 1 | 1.706 | 1 | 0.19332 |  | 2018-02-15
LG Electronics Inc. | LG335N1T-L5 | 335 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 335 | 309.7 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.42 | 41.1 | 9.91 | 33.8 | 46.5 | -0.3605 | 0.03358 | -0.2696 |  |  | 1.98 | 33.11 | 7.895 | 31.55 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG335N1T-V5 | 335 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 335 | 308.8 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 | 1 | N | 10.34 | 40.7 | 9.83 | 34.1 | 48.5 | -0.346 | 0.0385 | -0.26 |  |  | 1.959 | 33.9053 | 7.7976 | 31.9017 | [6 empty] | 2019-10-01
LG Electronics Inc. | LG335N1W-A5 | 335 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 335 | 311.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.49 | 41 | 9.83 | 34.1 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.968 | 33.2078 | 7.852 | 31.7209 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19508 |  | 2018-02-15
LG Electronics Inc. | LG335N1W-L5 | 335 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 335 | 310.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.64 | 40.8 | 10.19 | 32.9 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 2.0003 | 32.4658 | 7.9536 | 31.337 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG335N1W-N5 | 335 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 335 | 312.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.65 | 41.1 | 10.13 | 33.1 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0191 | 32.3369 | 7.9864 | 31.1827 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG335N1W-V5 | 335W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 335 | 311.5 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.49 | 41 | 9.83 | 34.1 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.969 | 33.329 | 7.8221 | 31.7278 | [6 empty] | 2018-10-15 | 2019-06-03
LG Electronics Inc. | LG335Q1C-V5 | 335 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 335 | 315.2 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.74 | 42.6 | 9.47 | 35.4 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.875 | 33.9242 | 1.875 | 33.9242 | 7.5217 | 33.2008 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG335Q1K-A5 | 335 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 335 | 311.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.74 | 42.6 | 9.53 | 35.4 | 48.7 | -0.31 | 0.04 | -0.24 | 0.01 | -0.32 | 1.902 | 32.9951 | 7.6577 | 32.3217 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18734 |  | 2018-02-15
LG Electronics Inc. | LG335S2C-G4 | 335 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 335 | 308.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.48 | 46.2 | 8.94 | 37.5 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.776 | 36.8037 | 7.164 | 34.7149 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19511 |  | 2018-02-15
LG Electronics Inc. | LG335S2W-G4 | 335 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 335 | 308.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.48 | 46.2 | 8.94 | 37.5 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.776 | 36.8037 | 7.164 | 34.7149 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19511 |  | 2018-02-15
LG Electronics Inc. | LG340M1K-L5 | 340 W, monocrystalline ACPV module, white backsheet. DC Module : LG340N1K-L5. Microinverter : LM320UE-A2. | UL 1741 | 340 | 316.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.6 | 40.9 | 10.12 | 33.6 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.98 | 33.73 | 7.876 | 32.54 | [6 empty] | 2020-08-21
LG Electronics Inc. | LG340N1C-A5 | 340 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 340 | 315.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.53 | 41.1 | 9.86 | 34.5 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.974 | 33.5974 | 7.876 | 32.093 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19506 |  | 2018-02-15
LG Electronics Inc. | LG340N1C-L5 | 340 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 340 | 315.4 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.68 | 40.9 | 10.22 | 33.3 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 2.0062 |  | 2.0062 | 32.8606 | 7.977 | 31.718 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG340N1C-N5 | 340 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 340 | 317.5 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.69 | 41.2 | 10.16 | 33.5 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0251 | 32.7277 | 8.01 | 31.5595 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG340N1C-V5 | 340 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 340 | 316.3 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.53 | 41.1 | 9.86 | 34.5 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.975 | 33.72 | 1.975 | 33.72 | 7.846 | 32.1 | [6 empty] | 2018-10-15 | 2019-08-15
LG Electronics Inc. | LG340N1C-Z5 | 340 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 340 | 314.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.654 | 60 | 1 | N | 10.53 | 41.1 | 9.86 | 34.5 | 46.6 | -0.362 | 0.03 | -0.26 | -0.02 | -0.35 | 1.972 | 33.6953 | 7.858 | 31.9854 | Rack | Flat Plate | 0.994 | 1.664 | 1 | 0.19543 |  | 2018-02-15
LG Electronics Inc. | LG340N1K-L5 | 340 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 340 | 316.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.6 | 40.9 | 10.12 | 33.6 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.98 | 33.73 | 7.876 | 32.54 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG340N1K-V5 | 340 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 340 | 313 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.35 | 41.2 | 9.75 | 34.9 | 48.5 | -0.353 | 0.036 | -0.261 |  |  | 1.9682 | 34.4371 | 7.8505 | 32.2975 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG340N1T-L5 | 340 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 340 | 314.4 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.46 | 41.2 | 9.97 | 34.1 | 46.5 | -0.3605 | 0.03358 | -0.2696 |  |  | 1.992 | 33.4039 | 7.9428 | 31.83 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG340N1T-V5 | 340 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 340 | 313.6 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.65 | 60 | 1 | N | 10.38 | 40.8 | 9.89 | 34.4 | 48.5 | -0.346 | 0.0385 | -0.26 |  |  | 1.9709 | 34.2036 | 7.8452 | 32.1823 | [6 empty] | 2019-10-01
LG Electronics Inc. | LG340N1W-A5 | 340 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 340 | 315.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.53 | 41.1 | 9.86 | 34.5 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.974 | 33.5974 | 7.876 | 32.093 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19506 |  | 2018-02-15
LG Electronics Inc. | LG340N1W-L5 | 340 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 340 | 315.4 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.68 | 40.9 | 10.22 | 33.3 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 2.0062 | 32.8606 | 7.977 | 31.718 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG340N1W-N5 | 340 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 340 | 317.5 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.69 | 41.2 | 10.16 | 33.5 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0251 | 32.7277 | 8.01 | 31.5595 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG340N1W-V5 | 340W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 340 | 316.3 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.53 | 41.1 | 9.86 | 34.5 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.975 | 33.72 | 7.846 | 32.1 | [6 empty] | 2018-10-15 | 2019-06-03
LG Electronics Inc. | LG340Q1C-A5 | 340 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 340 | 318.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.75 | 42.6 | 9.57 | 35.6 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.8716 | 33.5462 | 7.6213 | 33.1549 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18466 |  | 2018-02-15
LG Electronics Inc. | LG340Q1C-V5 | 340W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 340 | 320 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.75 | 42.6 | 9.56 | 35.6 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.8928 | 34.1159 | 1.8928 | 34.1159 | 7.5932 | 33.3883 | [6 empty] | 2019-06-03
LG Electronics Inc. | LG340Q1K-A5 | 340 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 340 | 316 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.75 | 42.6 | 9.6 | 35.7 | 48.7 | -0.31 | 0.04 | -0.24 | 0.01 | -0.32 | 1.916 | 33.2747 | 7.7139 | 32.5957 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18751 |  | 2018-02-15
LG Electronics Inc. | LG340S2C-G4 | 340 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 340 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.54 | 46.4 | 9.02 | 37.7 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.7919 | 37 | 7.2281 | 34.9 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.195 |  | 2018-02-15
LG Electronics Inc. | LG340S2W-A5 | 340 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 340 | 307.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 1 | N | 9.91 | 45.9 | 9.35 | 36.4 | 47.6 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8661 | 35.6276 | 7.4445 | 33.2138 | Rack | Flat Plate | 1.004 | 2.004 | 1 | 0.19554 |  | 2018-02-15
LG Electronics Inc. | LG340S2W-G4 | 340 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 340 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.54 | 46.4 | 9.02 | 37.7 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.7919 | 37 | 7.2281 | 34.9 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.195 |  | 2018-02-15
LG Electronics Inc. | LG345M1K-L5 | 345 W, monocrystalline ACPV module, white backsheet. DC Module : LG345N1K-L5. Microinverter : LM320UE-A2. | UL 1741 | 345 | 321.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.64 | 41 | 10.15 | 34 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9859 | 34.1315 | 7.8993 | 32.9274 | [6 empty] | 2020-08-21
LG Electronics Inc. | LG345N1C-A5 | 345 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 345 | 320.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.57 | 41.2 | 9.89 | 34.9 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.98 | 33.9869 | 7.8999 | 32.4651 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19506 |  | 2018-02-15
LG Electronics Inc. | LG345N1C-L5 | 345 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 345 | 320.2 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.72 | 41 | 10.24 | 33.7 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 2.0101 |  | 2.0101 | 33.2553 | 7.9926 | 32.099 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG345N1C-N5 | 345 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 345 | 322.3 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.72 | 41.3 | 10.19 | 33.9 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.031 | 33.1184 | 8.0337 | 31.9363 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG345N1C-V5 | 345W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 345 | 321 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.57 | 41.2 | 9.89 | 34.9 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.981 | 34.111 | 7.8699 | 32.4722 | [6 empty] | 2019-05-01 | 2019-06-03
LG Electronics Inc. | LG345N1C-Z5 | 345 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 345 | 319.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.654 | 60 | 1 | N | 10.57 | 41.2 | 9.89 | 34.9 | 46.6 | -0.362 | 0.03 | -0.26 | -0.02 | -0.35 | 1.978 | 34.086 | 7.8819 | 32.3563 | Rack | Flat Plate | 0.994 | 1.664 | 1 | 0.19543 |  | 2018-02-15
LG Electronics Inc. | LG345N1K-A6 | 345 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 345 | 319.2 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 10.76 | 41.4 | 10.32 | 33.5 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.0819 | 32.747 | 8.3265 | 31.154 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG345N1K-B6 | 345 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 345 | 318.6 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.64 | 41.3 | 10.09 | 34.2 | 48 | -0.3383 | 0.0279 | -0.2572 |  |  | 2.0041 | 33.1642 | 8.0263 | 31.5813 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG345N1K-L5 | 345 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 345 | 321.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.64 | 41 | 10.15 | 34 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9859 | 34.1315 | 7.8993 | 32.9274 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG345N1T-L5 | 345 W, 60 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 345 | 319.2 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.5 | 41.3 | 10.03 | 34.4 | 46.5 | -0.3605 | 0.03358 | -0.2696 |  |  | 2.004 | 33.6978 | 7.9906 | 32.1101 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG345N1W-A5 | 345 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 345 | 320.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.57 | 41.2 | 9.89 | 34.9 | 45.9 | -0.356 | 0.03 | -0.26 | -0.02 | -0.34 | 1.98 | 33.9869 | 7.8999 | 32.4651 | Rack | Flat Plate | 0.992 | 1.662 | 1 | 0.19506 |  | 2018-02-15
LG Electronics Inc. | LG345N1W-L5 | 345 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 345 | 320.2 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.72 | 41 | 10.24 | 33.7 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 2.0101 | 33.2553 | 7.9926 | 32.099 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG345N1W-N5 | 345 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 345 | 322.3 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.72 | 41.3 | 10.19 | 33.9 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.031 | 33.1184 | 8.0337 | 31.9363 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG345N1W-V5 | 345W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 345 | 321 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.57 | 41.2 | 9.89 | 34.9 | 45.95 | -0.349 | 0.02644 | -0.2588 |  |  | 1.981 | 34.111 | 7.8699 | 32.4722 | [6 empty] | 2019-05-01 | 2019-06-03
LG Electronics Inc. | LG345Q1C-A5 | 345 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 345 | 323.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.76 | 42.6 | 9.64 | 35.8 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.8852 | 33.7346 | 7.677 | 33.3412 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18434 |  | 2018-02-15
LG Electronics Inc. | LG345Q1C-V5 | 345W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 345 | 324.8 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.76 | 42.6 | 9.64 | 35.8 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.9086 | 34.3075 | 1.9086 | 34.3075 | 7.6568 | 33.5759 | [6 empty] | 2019-06-03
LG Electronics Inc. | LG345Q1K-A5 | 345 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 345 | 320.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.76 | 42.6 | 9.68 | 35.9 | 48.7 | -0.31 | 0.04 | -0.24 | 0.01 | -0.32 | 1.932 | 33.4611 | 7.7782 | 32.7783 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18738 |  | 2018-02-15
LG Electronics Inc. | LG345Q1K-V5 | 345 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 345 | 320.7 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.34 | 42.7 | 9.61 | 36 | 49.01 | -0.3064 | 0.0317 | -0.2427 |  |  | 1.8619 | 35.2088 | 7.6023 | 33.9429 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG345S2C-G4 | 345 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 345 | 318 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.61 | 46.6 | 9.11 | 37.9 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8097 | 37.1963 | 7.3003 | 35.0851 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19512 |  | 2018-02-15
LG Electronics Inc. | LG345S2W-A5 | 345 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 345 | 312.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 1 | N | 9.96 | 46.1 | 9.41 | 36.7 | 47.6 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.878 | 35.9212 | 7.4922 | 33.4875 | Rack | Flat Plate | 1.004 | 2.004 | 1 | 0.19554 |  | 2018-02-15
LG Electronics Inc. | LG345S2W-G4 | 345 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 345 | 318 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.61 | 46.6 | 9.11 | 37.9 | 44.1 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.8097 | 37.1963 | 7.3003 | 35.0851 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19512 |  | 2018-02-15
LG Electronics Inc. | LG350M1K-L5 | 350 W, monocrystalline ACPV module, white backsheet. DC Module : LG350N1K-L5. Microinverter : LM320UE-A2. | UL 1741 | 350 | 326 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.68 | 41.1 | 10.18 | 34.4 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9917 | 34.5331 | 7.9227 | 33.3148 | [6 empty] | 2020-08-21
LG Electronics Inc. | LG350N1C-L5 | 350 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 350 | 325 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.76 | 41.1 | 10.27 | 34.1 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 2.016 |  | 2.016 | 33.65 | 8.016 | 32.48 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG350N1C-N5 | 350 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 350 | 327.1 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.76 | 41.4 | 10.22 | 34.3 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.037 | 33.5092 | 8.0573 | 32.3132 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG350N1C-V5 | 350 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 350 | 325.8 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.61 | 41.3 | 9.92 | 35.3 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.987 | 34.5019 | 1.987 | 34.5019 | 7.8937 | 32.8443 | [6 empty] | 2019-06-03 | 2019-08-15
LG Electronics Inc. | LG350N1K-A6 | 350 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 350 | 323.9 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 10.8 | 41.5 | 10.35 | 33.9 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.0879 | 33.138 | 8.3507 | 31.526 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG350N1K-B6 | 350 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 350 | 323.4 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.68 | 41.4 | 10.12 | 34.6 | 48 | -0.3383 | 0.0279 | -0.2572 |  |  | 2.01 | 33.5521 | 8.0501 | 31.9506 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG350N1K-E6 | 350 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 350 | 325 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 10.83 | 40.6 | 10.35 | 33.9 | 47.2 | -0.3309 | 0.0257 | -0.2581 | 2.0219 | 32.8995 | 2.0219 | 32.8995 | 8.1144 | 31.763 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG350N1K-L5 | 350 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 350 | 326 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.68 | 41.1 | 10.18 | 34.4 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9917 | 34.5331 | 7.9227 | 33.3148 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG350N1W-L5 | 350 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 350 | 325 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.76 | 41.1 | 10.27 | 34.1 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 2.016 | 33.65 | 8.016 | 32.48 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG350N1W-N5 | 350 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 350 | 327.1 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.76 | 41.4 | 10.22 | 34.3 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.037 | 33.5092 | 8.0573 | 32.3132 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG350N1W-V5 | 350 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 350 | 325.8 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.61 | 41.3 | 9.92 | 35.3 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.987 | 34.5019 | 1.987 | 34.5019 | 7.8937 | 32.8443 | [6 empty] | 2019-06-03 | 2019-08-15
LG Electronics Inc. | LG350N2C-B3 | 350 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 350 | 319.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.74 | 48.1 | 9.24 | 37.9 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.85 | 37.32 | 7.38 | 34.9 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19726 |  | 2018-02-15
LG Electronics Inc. | LG350N2T-A4 | 350 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 350 | 321.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9502 | 72 | 1 | N | 9.62 | 47.6 | 9.03 | 38.8 | 46.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8297 | 37.5515 | 7.22 | 35.8228 | Rack | Flat Plate | 0.98 | 1.99 | 1 | 0.19631 |  | 2018-02-15
LG Electronics Inc. | LG350N2W-B3 | 350 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 350 | 319.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.74 | 48.1 | 9.24 | 37.9 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.85 | 37.32 | 7.38 | 34.9 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19726 |  | 2018-02-15
LG Electronics Inc. | LG350Q1C-A5 | 350 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 350 | 328 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.77 | 42.7 | 9.71 | 36 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.8989 | 33.9231 | 7.7328 | 33.5275 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18405 |  | 2018-02-15
LG Electronics Inc. | LG350Q1C-V5 | 350W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 350 | 329.7 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.77 | 42.7 | 9.7 | 36.1 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.9205 | 34.595 | 1.9205 | 34.595 | 7.7044 | 33.8573 | [6 empty] | 2019-04-15 | 2019-06-03
LG Electronics Inc. | LG350Q1K-A5 | 350 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 350 | 325.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.77 | 42.7 | 9.75 | 36.2 | 48.7 | -0.31 | 0.04 | -0.24 | 0.01 | -0.32 | 1.9459 | 33.7408 | 7.8345 | 33.0522 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18759 |  | 2018-02-15
LG Electronics Inc. | LG350Q1K-V5 | 350 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 350 | 325.5 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.39 | 42.9 | 9.68 | 36.2 | 49.01 | -0.3064 | 0.0317 | -0.2427 |  |  | 1.8755 | 35.4044 | 7.6577 | 34.1314 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG350S2W-A5 | 350 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 350 | 317.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 1 | N | 10.02 | 46.3 | 9.44 | 37.1 | 47.6 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.884 | 36.3127 | 7.5161 | 33.8525 | Rack | Flat Plate | 1.004 | 2.004 | 1 | 0.19547 |  | 2018-02-15
LG Electronics Inc. | LG355A1C-A5 | 355 W Monocrystalline ACPV module. DC Module: LG355Q1C-A5. Microinverter: LM320UE-A2 | UL 1741 | 355 | 332.8 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 10.78 | 42.7 | 9.79 | 36.3 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.9146 | 34.2058 | 7.7965 | 33.8069 | [6 empty] | 2018-02-15
LG Electronics Inc. | LG355M1C-N5 | 355 W, monocrystalline ACPV module, white backsheet. DC Module : LG355N1C-N5. . Microinverter : LM320UE-A2. | UL 1741 | 355 | 331.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.8 | 41.5 | 10.25 | 34.7 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.043 | 33.9 | 8.081 | 32.69 | [6 empty] | 2020-08-21
LG Electronics Inc. | LG355M1K-A6 | 355 W, monocrystalline ACPV module, black backsheet. DC Module: LG355N1K-A6. Microinverter: LM320UE-A2. | UL 1741 | 355 | 328.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.84 | 41.6 | 10.37 | 34.3 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.092 | 33.529 | 8.3669 | 31.898 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG355N1C-A6 | 355 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 328.3 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.19 | 41.4 | 10.54 | 33.7 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.1149 | 32.3062 | 8.43 | 30.7596 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG355N1C-E6 | 355 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 328.3 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.15 | 39.8 | 10.65 | 33.4 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.0888 | 32.1059 | 2.0888 | 32.1059 | 8.4101 | 30.9164 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG355N1C-L5 | 355 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 329.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.8 | 41.2 | 10.29 | 34.5 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 2.0199 |  | 2.0199 | 34.0447 | 8.0316 | 32.861 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG355N1C-N5 | 355 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 331.9 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.8 | 41.5 | 10.25 | 34.7 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.043 | 33.9 | 8.081 | 32.69 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG355N1C-V5 | 355 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 355 | 330.6 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.65 | 41.4 | 9.95 | 35.7 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.993 | 34.8929 | 1.993 | 34.8929 | 7.9176 | 33.2165 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG355N1K-A6 | 355 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 328.7 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 10.84 | 41.6 | 10.37 | 34.3 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.092 | 33.529 | 8.3669 | 31.898 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG355N1K-B6 | 355 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 328.1 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.72 | 41.5 | 10.15 | 35 | 48 | -0.3383 | 0.0279 | -0.2572 |  |  | 2.016 | 33.94 | 8.074 | 32.32 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG355N1K-E6 | 355 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 329.7 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 10.93 | 40.8 | 10.44 | 34 | 47.2 | -0.3309 | 0.0257 | -0.2581 | 2.0394 | 32.9966 | 2.0394 | 32.9966 | 8.185 | 31.8567 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG355N1K-L5 | 355 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 330.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.72 | 41.2 | 10.21 | 34.8 | 45.83 | -0.3433 | 0.02505 | -0.2583 |  |  | 1.9976 | 34.9346 | 7.946 | 33.7021 | [6 empty] | 2020-01-02 | 2020-08-03
LG Electronics Inc. | LG355N1W-A6 | 355 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 355 | 328.3 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.19 | 41.4 | 10.54 | 33.7 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.1149 | 32.3062 | 8.43 | 30.7596 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG355N1W-E6 | 355 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 355 | 328.3 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.15 | 39.8 | 10.65 | 33.4 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.0888 | 32.1059 | 2.0888 | 32.1059 | 8.4101 | 30.9164 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG355N1W-L5 | 355 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 355 | 329.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.8 | 41.2 | 10.29 | 34.5 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 2.0199 | 34.0447 | 8.0316 | 32.861 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG355N1W-N5 | 355 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 355 | 331.9 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.8 | 41.5 | 10.25 | 34.7 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.043 | 33.9 | 8.081 | 32.69 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG355N1W-V5 | 355 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 355 | 330.6 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6487 | 60 | 1 | N | 10.65 | 41.4 | 9.95 | 35.7 | 45.95 | -0.349 | 0.02644 | -0.2588 | 1.993 | 34.8929 | 1.993 | 34.8929 | 7.9176 | 33.2165 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG355N2C-B3 | 355 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 355 | 324.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.79 | 48.2 | 9.32 | 38.1 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.87 | 37.52 | 7.44 | 35.09 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19764 |  | 2018-02-15
LG Electronics Inc. | LG355N2T-A4 | 355 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 355 | 326.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9502 | 72 | 1 | N | 9.66 | 47.9 | 9.08 | 39.1 | 46.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8399 | 37.8418 | 7.26 | 36.0998 | Rack | Flat Plate | 0.98 | 1.99 | 1 | 0.19612 |  | 2018-02-15
LG Electronics Inc. | LG355N2W-B3 | 355 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 355 | 324.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.79 | 48.2 | 9.32 | 38.1 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.87 | 37.52 | 7.44 | 35.09 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19764 |  | 2018-02-15
LG Electronics Inc. | LG355Q1C-A5 | 355 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 355 | 332.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.78 | 42.7 | 9.79 | 36.3 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.9146 | 34.2058 | 7.7965 | 33.8069 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18448 |  | 2018-02-15
LG Electronics Inc. | LG355Q1C-V5 | 355W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 355 | 334.5 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.78 | 42.7 | 9.79 | 36.3 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.9383 | 34.7867 | 1.9383 | 34.7867 | 7.7759 | 34.0449 | [6 empty] | 2019-04-15 | 2019-06-03
LG Electronics Inc. | LG355Q1K-A5 | 355 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 355 | 330.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.79 | 42.7 | 9.82 | 36.4 | 48.7 | -0.31 | 0.04 | -0.24 | 0.01 | -0.32 | 1.9599 | 33.9272 | 7.8907 | 33.2348 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18731 |  | 2018-02-15
LG Electronics Inc. | LG355Q1K-V5 | 355 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 355 | 330.3 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.44 | 43.1 | 9.76 | 36.4 | 49.01 | -0.3064 | 0.0317 | -0.2427 |  |  | 1.891 | 35.6 | 7.721 | 34.32 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG355S2W-A5 | 355 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 355 | 321.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 1 | N | 10.07 | 46.4 | 9.5 | 37.4 | 47.6 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.896 | 36.6064 | 7.5639 | 34.1263 | Rack | Flat Plate | 1.004 | 2.004 | 1 | 0.19551 |  | 2018-02-15
LG Electronics Inc. | LG360A1C-A5 | 360 W Monocrystalline ACPV module. DC Module: LG360Q1C-A5. Microinverter: LM320UE-A2 | UL 1741 | 360 | 337.6 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 10.79 | 42.7 | 9.87 | 36.5 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.9146 | 34.2058 | 7.7965 | 33.8069 | [6 empty] | 2018-02-15
LG Electronics Inc. | LG360A1K-V5 | 360 W, monocrystalline ACPV module, white backsheet. DC Module: LG360Q1K-V5. Microinverter: LM320UE-A2. | UL 1741 | 360 | 335.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.5 | 43.3 | 9.82 | 36.7 | 49.01 | -0.3064 | 0.0317 | -0.2427 |  |  | 1.9026 | 35.8934 | 7.7685 | 34.6029 | [6 empty] | 2020-05-01
LG Electronics Inc. | LG360M1C-N5 | 360 W, monocrystalline ACPV module, white backsheet. DC Module : LG360N1C-N5. Microinverter : LM320UE-A2. | UL 1741 | 360 | 336.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.84 | 41.6 | 10.28 | 35.1 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.049 | 34.2908 | 8.1047 | 33.0668 | [6 empty] | 2020-08-21
LG Electronics Inc. | LG360M1K-A6 | 360 W, monocrystalline ACPV module, black backsheet. DC Module: LG360N1K-A6. Microinverter: LM320UE-A2. | UL 1741 | 360 | 333.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.88 | 41.7 | 10.39 | 34.7 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.096 | 33.92 | 8.383 | 32.27 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG360N1C-A6 | 360 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 360 | 333.1 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.23 | 41.5 | 10.56 | 34.1 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.119 | 32.6896 | 8.446 | 31.1247 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG360N1C-E6 | 360 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 360 | 333 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.19 | 40.2 | 10.68 | 33.8 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.0947 | 32.4904 | 2.0947 | 32.4904 | 8.4338 | 31.2867 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG360N1C-L5 | 360 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 360 | 334.5 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.84 | 41.3 | 10.32 | 34.9 | 46.48 | -0.3467 | 0.02326 | -0.2584 | 2.0258 |  | 2.0258 | 34.4394 | 8.055 | 33.242 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG360N1C-N5 | 360 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 360 | 336.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.84 | 41.6 | 10.28 | 35.1 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.049 | 34.2908 | 8.1047 | 33.0668 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG360N1K-A6 | 360 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 360 | 333.4 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 10.88 | 41.7 | 10.39 | 34.7 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.096 | 33.92 | 8.383 | 32.27 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG360N1K-B6 | 360 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 360 | 332.9 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.76 | 41.6 | 10.18 | 35.4 | 48 | -0.3383 | 0.0279 | -0.2572 |  |  | 2.022 | 34.3279 | 8.0979 | 32.6894 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG360N1K-E6 | 360 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 360 | 334.5 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.03 | 41 | 10.51 | 34.3 | 47.2 | -0.3309 | 0.0257 | -0.2581 | 2.0531 | 33.2877 | 2.0531 | 33.2877 | 8.2398 | 32.1378 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG360N1W-A6 | 360 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 360 | 333.1 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.23 | 41.5 | 10.56 | 34.1 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.119 | 32.6896 | 8.446 | 31.1247 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG360N1W-E6 | 360 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 360 | 333 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.19 | 40.2 | 10.68 | 33.8 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.0947 | 32.4904 | 2.0947 | 32.4904 | 8.4338 | 31.2867 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG360N1W-L5 | 360 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 360 | 334.5 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.84 | 41.3 | 10.32 | 34.9 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 2.0258 | 34.4394 | 8.055 | 33.242 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG360N1W-N5 | 360 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 360 | 336.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.84 | 41.6 | 10.28 | 35.1 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.049 | 34.2908 | 8.1047 | 33.0668 | [6 empty] | 2020-02-03 | 2020-08-11
LG Electronics Inc. | LG360N2C-B3 | 360 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 360 | 328.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.84 | 48.3 | 9.39 | 38.4 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.88 | 37.81 | 7.5 | 35.36 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19745 |  | 2018-02-15
LG Electronics Inc. | LG360N2C-G4 | 360 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 360 | 332.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.86 | 47.4 | 9.33 | 38.6 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.864 | 37.7315 | 7.4362 | 35.6085 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19537 |  | 2018-02-15
LG Electronics Inc. | LG360N2K-G4 | 360 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 360 | 332.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.69 | 47.9 | 9.21 | 39.1 | 45.7 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.84 | 38.1225 | 7.3501 | 36.1675 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19485 |  | 2018-02-15
LG Electronics Inc. | LG360N2T-A4 | 360 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 360 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9502 | 72 | 1 | N | 9.7 | 48.2 | 9.12 | 39.5 | 46.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.848 | 38.229 | 7.292 | 36.4691 | Rack | Flat Plate | 0.98 | 1.99 | 1 | 0.19624 |  | 2018-02-15
LG Electronics Inc. | LG360N2W-B3 | 360 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 360 | 328.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.84 | 48.3 | 9.39 | 38.4 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.88 | 37.81 | 7.5 | 35.36 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19745 |  | 2018-02-15
LG Electronics Inc. | LG360N2W-G4 | 360 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 360 | 332.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.86 | 47.4 | 9.33 | 38.6 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.864 | 37.7315 | 7.4362 | 35.6085 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19537 |  | 2018-02-15
LG Electronics Inc. | LG360Q1C-A5 | 360 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 360 | 337.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.79 | 42.7 | 9.86 | 36.5 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.9283 | 34.3942 | 7.8522 | 33.9931 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18423 |  | 2018-02-15
LG Electronics Inc. | LG360Q1C-V5 | 360W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 360 | 339.3 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.79 | 42.7 | 9.87 | 36.5 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.9542 | 34.9783 | 1.9542 | 34.9783 | 7.8395 | 34.2324 | [6 empty] | 2019-04-15 | 2019-06-03
LG Electronics Inc. | LG360Q1K-A5 | 360 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 360 | 335.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.8 | 42.8 | 9.9 | 36.6 | 48.7 | -0.31 | 0.04 | -0.24 | 0.01 | -0.32 | 1.9759 | 34.1136 | 7.955 | 33.4174 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18723 |  | 2018-02-15
LG Electronics Inc. | LG360Q1K-V5 | 360 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 360 | 335.1 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.5 | 43.3 | 9.82 | 36.7 | 49.01 | -0.3064 | 0.0317 | -0.2427 |  |  | 1.9026 | 35.8934 | 7.7685 | 34.6029 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG360S2W-A5 | 360 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 360 | 326.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 1 | N | 10.12 | 46.6 | 9.56 | 37.7 | 47.6 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.908 | 36.9 | 7.6117 | 34.4 | Rack | Flat Plate | 1.004 | 2.004 | 1 | 0.19557 |  | 2018-02-15
LG Electronics Inc. | LG365A1C-A5 | 365 W Monocrystalline ACPV module. DC Module: LG365Q1C-A5. Microinverter: LM320UE-A2 | UL 1741 | 365 | 342.4 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 10.8 | 42.8 | 9.95 | 36.7 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.9146 | 34.2058 | 7.7965 | 33.8069 | [6 empty] | 2018-02-15
LG Electronics Inc. | LG365A1C-V5 | 365 W, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1C-V5. Microinverter: LM320UE-A2. | UL 1741 | 365 | 344.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.8 | 42.8 | 9.95 | 36.7 | 44.53 | -0.3134 | 0.02868 | -0.243 |  |  | 1.97 | 35.17 | 7.903 | 34.42 | [6 empty] | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG365A1K-V5 | 365 W, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1K-V5. Microinverter: LM320UE-A2. | UL 1741 | 365 | 339.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.55 | 43.5 | 9.9 | 36.9 | 49.01 | -0.3064 | 0.0317 | -0.2427 |  |  | 1.9181 | 36.089 | 7.8318 | 34.7914 | [6 empty] | 2020-05-01
LG Electronics Inc. | LG365M1C-N5 | 365 W, monocrystalline ACPV module, white backsheet. DC Module : LG365N1C-N5. Microinverter : LM320UE-A2. | UL 1741 | 365 | 341.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.88 | 41.7 | 10.3 | 35.5 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.053 | 34.6816 | 8.1204 | 33.4437 | [6 empty] | 2020-08-21
LG Electronics Inc. | LG365M1K-A6 | 365 W, monocrystalline ACPV module, black backsheet. DC Module: LG365N1K-A6. Microinverter: LM320UE-A2. | UL 1741 | 365 | 338.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.92 | 41.8 | 10.41 | 35.1 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.1 | 34.311 | 8.3991 | 32.642 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG365N1C-A6 | 365 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 365 | 337.8 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.27 | 41.6 | 10.58 | 34.5 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.123 | 33.0731 | 8.462 | 31.4898 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG365N1C-E6 | 365 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 365 | 337.8 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.25 | 40.5 | 10.73 | 34.1 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1045 | 32.7787 | 2.1045 | 32.7787 | 8.4732 | 31.5644 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG365N1C-L5 | 365 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 365 | 339.3 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.88 | 41.4 | 10.34 | 35.3 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 2.0297 | 34.8342 | 8.0706 | 33.623 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG365N1C-N5 | 365 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 365 | 341.5 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.88 | 41.7 | 10.3 | 35.5 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.053 | 34.6816 | 8.1204 | 33.4437 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG365N1K-A6 | 365 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 365 | 338.2 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 10.92 | 41.8 | 10.41 | 35.1 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.1 | 34.311 | 8.3991 | 32.642 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG365N1K-B6 | 365 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 365 | 337.6 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.8 | 41.7 | 10.21 | 35.8 | 48 | -0.3383 | 0.0279 | -0.2572 |  |  | 2.0279 | 34.7158 | 8.1217 | 33.0587 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG365N1K-E6 | 365 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 365 | 339.3 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.13 | 41.2 | 10.6 | 34.5 | 47.2 | -0.3309 | 0.0257 | -0.2581 | 2.0707 | 33.4818 | 2.0707 | 33.4818 | 8.3104 | 32.3252 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG365N1W-A6 | 365 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 365 | 337.8 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.27 | 41.6 | 10.58 | 34.5 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.123 | 33.0731 | 8.462 | 31.4898 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG365N1W-E6 | 365 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 365 | 337.8 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.25 | 40.5 | 10.73 | 34.1 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1045 | 32.7787 | 2.1045 | 32.7787 | 8.4732 | 31.5644 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG365N1W-L5 | 365 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 365 | 339.3 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.88 | 41.4 | 10.34 | 35.3 | 46.48 | -0.3467 | 0.02326 | -0.2584 |  |  | 2.0297 | 34.8342 | 8.0706 | 33.623 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG365N1W-N5 | 365 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 365 | 341.5 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.88 | 41.7 | 10.3 | 35.5 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.053 | 34.6816 | 8.1204 | 33.4437 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG365N2C-B3 | 365 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 365 | 333.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.89 | 48.4 | 9.46 | 38.6 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.89 | 38.01 | 7.56 | 35.55 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19682 |  | 2018-02-15
LG Electronics Inc. | LG365N2C-G4 | 365 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 365 | 337.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.92 | 47.7 | 9.39 | 38.9 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.876 | 38.0247 | 7.4841 | 35.8852 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19544 |  | 2018-02-15
LG Electronics Inc. | LG365N2K-G4 | 365 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 365 | 337.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.76 | 48.2 | 9.27 | 39.4 | 45.7 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.852 | 38.415 | 7.398 | 36.445 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19492 |  | 2018-02-15
LG Electronics Inc. | LG365N2T-A4 | 365 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 365 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9502 | 72 | 1 | N | 9.74 | 48.5 | 9.16 | 39.9 | 46.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8561 | 38.6161 | 7.324 | 36.8384 | Rack | Flat Plate | 0.98 | 1.99 | 1 | 0.19637 |  | 2018-02-15
LG Electronics Inc. | LG365N2W-B3 | 365 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 365 | 333.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.89 | 48.4 | 9.46 | 38.6 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.89 | 38.01 | 7.56 | 35.55 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19682 |  | 2018-02-15
LG Electronics Inc. | LG365N2W-G4 | 365 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 365 | 337.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.92 | 47.7 | 9.39 | 38.9 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.876 | 38.0247 | 7.4841 | 35.8852 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19544 |  | 2018-02-15
LG Electronics Inc. | LG365Q1C-A5 | 365 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 365 | 342.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.8 | 42.8 | 9.94 | 36.8 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.9439 | 34.6769 | 7.9159 | 34.2725 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18468 |  | 2018-02-15
LG Electronics Inc. | LG365Q1C-V5 | 365 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 365 | 344.1 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.8 | 42.8 | 9.95 | 36.7 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.97 | 35.17 | 1.97 | 35.17 | 7.903 | 34.42 | [6 empty] | 2019-04-15 | 2019-08-15
LG Electronics Inc. | LG365Q1K-V5 | 365 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 365 | 339.9 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.55 | 43.5 | 9.9 | 36.9 | 49.01 | -0.3064 | 0.0317 | -0.2427 |  |  | 1.9181 | 36.089 | 7.8318 | 34.7914 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG365S2W-A5 | 365 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 365 | 331.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 1 | N | 10.18 | 46.7 | 9.61 | 38 | 47.6 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.9179 | 37.1936 | 7.6515 | 34.6737 | Rack | Flat Plate | 1.004 | 2.004 | 1 | 0.19544 |  | 2018-02-15
LG Electronics Inc. | LG370A1C-A5 | 370 W Monocrystalline ACPV module. DC Module: LG370Q1C-A5. Microinverter: LM320UE-A2 | UL 1741 | 370 | 347.2 | This component is specific to ACPV and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 |  | N | 10.82 | 42.8 | 10.01 | 37 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.9146 | 34.2058 | 7.7965 | 33.8069 | [6 empty] | 2018-02-15
LG Electronics Inc. | LG370A1C-V5 | 370 W, monocrystalline ACPV module, white backsheet. DC Module: LG370Q1C-V5. Microinverter: LM320UE-A2. | UL 1741 | 370 | 349 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.82 | 42.8 | 10.01 | 37 | 44.53 | -0.3134 | 0.02868 | -0.243 |  |  | 1.9819 | 35.4575 | 7.9507 | 34.7014 | [6 empty] | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG370M1C-N5 | 370 W, monocrystalline ACPV module, white backsheet. DC Module : LG370N1C-N5. Microinverter : LM320UE-A2. | UL 1741 | 370 | 346.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.92 | 41.8 | 10.34 | 35.8 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0609 | 34.9746 | 8.152 | 33.7263 | [6 empty] | 2020-08-21
LG Electronics Inc. | LG370M1K-A6 | 370 W, monocrystalline ACPV module, black backsheet. DC Module: LG370N1K-A6. Microinverter: LM320UE-A2. | UL 1741 | 370 | 343 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 19.96 | 41.9 | 10.43 | 35.5 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.1041 | 34.702 | 8.4153 | 33.014 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG370N1C-A6 | 370 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 370 | 342.6 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.31 | 41.7 | 10.61 | 34.9 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.129 | 33.4565 | 8.486 | 31.8549 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG370N1C-E6 | 370 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 370 | 342.6 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.3 | 40.9 | 10.76 | 34.4 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1103 | 33.0671 | 2.1103 | 33.0671 | 8.4969 | 31.8421 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG370N1C-N5 | 370 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 370 | 346.3 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.92 | 41.8 | 10.34 | 35.8 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0609 | 34.9746 | 8.152 | 33.7263 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG370N1K-A6 | 370 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 370 | 342.9 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 10.96 | 41.9 | 10.43 | 35.5 | 47.15 | -0.3442 | 0.0293 | -0.2599 |  |  | 2.1041 | 34.702 | 8.4153 | 33.014 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG370N1K-B6 | 370 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 370 | 342.4 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.84 | 41.8 | 10.24 | 36.2 | 48 | -0.3383 | 0.0279 | -0.2572 |  |  | 2.0339 | 35.1037 | 8.1456 | 33.4281 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG370N1K-E6 | 370 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 370 | 344.1 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.23 | 41.4 | 10.68 | 34.7 | 47.2 | -0.3309 | 0.0257 | -0.2581 | 2.0863 | 33.6759 | 2.0863 | 33.6759 | 8.3731 | 32.5126 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG370N1W-A6 | 370 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 370 | 342.6 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.31 | 41.7 | 10.61 | 34.9 | 47.43 | -0.3444 | 0.0239 | -0.2586 | 0.0239 |  | 2.129 | 33.4565 | 8.486 | 31.8549 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG370N1W-E6 | 370 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 370 | 342.6 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.3 | 40.9 | 10.76 | 34.4 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1103 | 33.0671 | 2.1103 | 33.0671 | 8.4969 | 31.8421 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG370N1W-N5 | 370 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 370 | 346.3 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.7255 | 60 | 1 | N | 10.92 | 41.8 | 10.34 | 35.8 | 44.94 | -0.342 | 0.03162 | -0.2574 |  |  | 2.0609 | 34.9746 | 8.152 | 33.7263 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG370N2C-B3 | 370 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 370 | 338.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.94 | 48.5 | 9.54 | 38.8 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.91 | 38.21 | 7.62 | 35.73 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19725 |  | 2018-02-15
LG Electronics Inc. | LG370N2C-G4 | 370 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 370 | 342.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.98 | 48 | 9.44 | 39.2 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.886 | 38.318 | 7.5239 | 36.162 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19532 |  | 2018-02-15
LG Electronics Inc. | LG370N2K-G4 | 370 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 370 | 342.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.82 | 48.5 | 9.33 | 39.7 | 45.7 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.864 | 38.7075 | 7.4459 | 36.7225 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.195 |  | 2018-02-15
LG Electronics Inc. | LG370N2T-A4 | 370 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 370 | 340.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9502 | 72 | 1 | N | 9.78 | 48.8 | 9.2 | 40.3 | 46.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8642 | 39.0032 | 7.356 | 37.2077 | Rack | Flat Plate | 0.98 | 1.99 | 1 | 0.19651 |  | 2018-02-15
LG Electronics Inc. | LG370N2T-A5 | 370 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 370 | 340.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 1 | N | 9.99 | 48.8 | 9.33 | 39.7 | 47.8 | -0.355 | 0.03 | -0.26 | -0.02 | -0.34 | 1.8621 | 38.5437 | 7.4582 | 36.6165 | Rack | Flat Plate | 1 | 2.04 | 1 | 0.19398 |  | 2018-02-15
LG Electronics Inc. | LG370N2W-B3 | 370 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 370 | 338.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.94 | 48.5 | 9.54 | 38.8 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.91 | 38.21 | 7.62 | 35.73 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19725 |  | 2018-02-15
LG Electronics Inc. | LG370N2W-G4 | 370 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 370 | 342.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.98 | 48 | 9.44 | 39.2 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.886 | 38.318 | 7.5239 | 36.162 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19532 |  | 2018-02-15
LG Electronics Inc. | LG370Q1C-A5 | 370 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 370 | 347.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.82 | 42.8 | 10.01 | 37 | 45.7 | -0.32 | 0.03 | -0.24 | -0.03 | -0.29 | 1.9576 | 34.8654 | 7.9717 | 34.4588 | Rack | Flat Plate | 0.996 | 1.68 | 1 | 0.18447 |  | 2018-02-15
LG Electronics Inc. | LG370Q1C-V5 | 370W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 370 | 349 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.82 | 42.8 | 10.01 | 37 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.9819 | 35.4575 | 1.9819 | 35.4575 | 7.9507 | 34.7014 | [6 empty] | 2019-04-15 | 2019-06-03
LG Electronics Inc. | LG370Q1K-V5 | 370 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 1703 | 370 | 344.7 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.61 | 43.7 | 9.97 | 37.2 | 49.01 | -0.3064 | 0.0317 | -0.2427 |  |  | 1.9317 | 36.3824 | 7.8871 | 35.0743 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG370S2W-A5 | 370 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 370 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.012 | 72 | 1 | N | 10.23 | 46.9 | 9.67 | 38.3 | 47.6 | -0.41 | 0.03 | -0.3 | -0.02 | -0.4 | 1.9299 | 37.4873 | 7.6992 | 34.9475 | Rack | Flat Plate | 1.004 | 2.004 | 1 | 0.19553 |  | 2018-02-15
LG Electronics Inc. | LG375A1C-V5 | 375 W, monocrystalline ACPV module, white backsheet. DC Module: LG375Q1C-V5. Microinverter: LM320UE-A2. | UL 1741 | 375 | 353.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.83 | 42.8 | 10.09 | 37.2 | 44.53 | -0.3134 | 0.02868 | -0.243 |  |  | 1.9977 | 35.6492 | 8.0142 | 34.8889 | [6 empty] | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG375M1C-A6 | 370 W, monocrystalline ACPV module, white backsheet. DC Module: LG375N1C-A6. Microinverter: LM320UE-A2. | UL 1741 | 375 | 347.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.35 | 41.8 | 10.63 | 35.3 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.133 | 33.84 | 8.502 | 32.22 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG375M1K-A6 | 375 W, monocrystalline ACPV module, black backsheet. DC Module : LG375N1K-A6. Microinverter : LM320UE-A2. | UL 1741 | 375 | 346.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11 | 42 | 10.45 | 35.9 | 48.71 | -0.3424 | 0.026 | -0.255 |  |  | 2.088 | 34.02 | 8.296 | 32.21 | [6 empty] | 2021-09-13
LG Electronics Inc. | LG375N1C-A6 | 375 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 375 | 347.3 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.35 | 41.8 | 10.63 | 35.3 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.133 | 33.84 | 8.502 | 32.22 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG375N1C-E6 | 375 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 375 | 347.3 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.35 | 41.3 | 10.8 | 34.8 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1182 | 33.4516 | 2.1182 | 33.4516 | 8.5285 | 32.2123 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG375N1K-A6 | 385 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 375 | 346.1 |  | 2021-04-12 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11 | 42 | 10.45 | 35.9 | 48.71 | -0.3424 | 0.026 | -0.255 |  |  | 2.088 | 34.02 | 8.296 | 32.21 | [6 empty] | 2021-07-01
LG Electronics Inc. | LG375N1K-E6 | 375 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 375 | 348.8 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.33 | 41.5 | 10.75 | 34.9 | 47.2 | -0.3309 | 0.0257 | -0.2581 | 2.1 | 33.87 | 2.1 | 33.87 | 8.428 | 32.7 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG375N1W-A6 | 375 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 375 | 347.3 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.35 | 41.8 | 10.63 | 35.3 | 47.43 | -0.3444 | 0.0239 | -0.2586 | 0.0239 |  | 2.133 | 33.84 | 8.502 | 32.22 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG375N1W-E6 | 375 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 375 | 347.3 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.35 | 41.3 | 10.8 | 34.8 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1182 | 33.4516 | 2.1182 | 33.4516 | 8.5285 | 32.2123 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG375N2C-B3 | 375 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 375 | 343.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.99 | 48.6 | 9.62 | 39 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.93 | 38.4 | 7.68 | 35.92 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19763 |  | 2018-02-15
LG Electronics Inc. | LG375N2C-G4 | 375 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 375 | 346.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 10.04 | 48.3 | 9.5 | 39.5 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.898 | 38.6113 | 7.5717 | 36.4387 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19542 |  | 2018-02-15
LG Electronics Inc. | LG375N2K-A5 | 375 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 375 | 346 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.09 | 48.9 | 9.62 | 39 | 47.2 | -0.353 | 0.03 | -0.26 | -0.02 | -0.34 | 1.9161 | 37.8668 | 7.7039 | 36.0726 | Rack | Flat Plate | 1 | 2 | 1 | 0.19348 |  | 2018-02-15
LG Electronics Inc. | LG375N2K-G4 | 375 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 375 | 347.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.88 | 48.8 | 9.38 | 40 | 45.7 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.874 | 39 | 7.4858 | 37 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19489 |  | 2018-02-15
LG Electronics Inc. | LG375N2T-A4 | 375 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 375 | 345.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9502 | 72 | 1 | N | 9.82 | 49.1 | 9.24 | 40.6 | 46.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8723 | 39.2936 | 7.388 | 37.4847 | Rack | Flat Plate | 0.98 | 1.99 | 1 | 0.19618 |  | 2018-02-15
LG Electronics Inc. | LG375N2T-A5 | 375 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 375 | 344.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 1 | N | 10.03 | 48.9 | 9.34 | 40.2 | 47.8 | -0.355 | 0.03 | -0.26 | -0.02 | -0.34 | 1.8641 | 39.0291 | 7.4662 | 37.0777 | Rack | Flat Plate | 1 | 2.04 | 1 | 0.19401 |  | 2018-02-15
LG Electronics Inc. | LG375N2W-B3 | 375 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 375 | 343.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.99 | 48.6 | 9.62 | 39 | 47.5 | -0.39 | 0.02 | -0.28 | -0.02 | -0.37 | 1.93 | 38.4 | 7.68 | 35.92 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19763 |  | 2018-02-15
LG Electronics Inc. | LG375N2W-G4 | 375 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 375 | 346.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 10.04 | 48.3 | 9.5 | 39.5 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.898 | 38.6113 | 7.5717 | 36.4387 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19542 |  | 2018-02-15
LG Electronics Inc. | LG375Q1C-V5 | 375W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 375 | 353.8 |  | 2019-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.83 | 42.8 | 10.09 | 37.2 | 44.53 | -0.3134 | 0.02868 | -0.243 | 1.9977 | 35.6492 | 1.9977 | 35.6492 | 8.0142 | 34.8889 | [6 empty] | 2019-04-15 | 2019-06-03
LG Electronics Inc. | LG375Q1K-A6 | 369 W, 60 cell monocrystalline module, black backsheet, black colored frame, 1000V max system Vdc | UL 61730 | 375 | 351.7 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.84 | 43.4 | 10.12 | 37 | 46.26 | -0.3068 | 0.0301 | -0.2416 |  |  | 2.0132 | 35.0016 | 8.0931 | 34.408 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG380A1C-V5 | 380 W, monocrystalline ACPV module, white backsheet. DC Module: LG380Q1C-V5. Microinverter: LM320UE-A2. | UL 1741 | 380 | 358.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.84 | 42.9 | 10.17 | 37.4 | 44.53 | -0.3134 | 0.02868 | -0.243 |  |  | 2.0136 | 35.8408 | 8.0777 | 35.0765 | [6 empty] | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG380M1C-A6 | 380 W, monocrystalline ACPV module, white backsheet. DC Module: LG380N1C-A6. Microinverter: LM320UE-A2. | UL 1741 | 380 | 352.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.39 | 41.9 | 10.65 | 35.7 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.137 | 34.2235 | 8.518 | 32.5851 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG380M1K-A6 | 380 W, monocrystalline ACPV module, black backsheet. DC Module : LG380N1K-A6. Microinverter : LM320UE-A2. | UL 1741 | 380 | 350.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.04 | 42.1 | 10.47 | 36.3 | 48.71 | -0.3424 | 0.026 | -0.255 |  |  | 2.092 | 34.3991 | 8.3119 | 32.5689 | [6 empty] | 2021-09-13
LG Electronics Inc. | LG380N1C-A6 | 380 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 380 | 352.1 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.39 | 41.9 | 10.65 | 35.7 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.137 | 34.2235 | 8.518 | 32.5851 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG380N1C-E6 | 380 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 380 | 352.1 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.39 | 41.7 | 10.85 | 35.1 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.128 | 33.74 | 2.128 | 33.74 | 8.568 | 32.49 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG380N1K-A6 | 380 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 380 | 350.8 |  | 2021-04-12 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.04 | 42.1 | 10.47 | 36.3 | 48.71 | -0.3424 | 0.026 | -0.255 |  |  | 2.092 | 34.3991 | 8.3119 | 32.5689 | [6 empty] | 2021-07-01
LG Electronics Inc. | LG380N1K-E6 | 380 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 380 | 353.6 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.43 | 41.7 | 10.83 | 35.2 | 47.2 | -0.3309 | 0.0257 | -0.2581 | 2.1156 | 34.1611 | 2.1156 | 34.1611 | 8.4907 | 32.9811 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG380N1W-A6 | 380 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 380 | 352.1 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.39 | 41.9 | 10.65 | 35.7 | 47.43 | -0.3444 | 0.0239 | -0.2586 | 0.0239 |  | 2.137 | 34.2235 | 8.518 | 32.5851 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG380N1W-E6 | 380 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 380 | 352.1 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.39 | 41.7 | 10.85 | 35.1 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.128 | 33.74 | 2.128 | 33.74 | 8.568 | 32.49 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG380N2C-A5 | 380 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 380 | 349.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.31 | 48.9 | 9.75 | 39 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9263 | 38.146 | 7.7842 | 35.9635 | Rack | Flat Plate | 1 | 2 | 1 | 0.19337 |  | 2018-02-15
LG Electronics Inc. | LG380N2C-G4 | 380 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 380 | 351.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 10.1 | 48.6 | 9.55 | 39.8 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.908 | 38.9045 | 7.6116 | 36.7155 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19534 |  | 2018-02-15
LG Electronics Inc. | LG380N2K-A5 | 380 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 380 | 350.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.13 | 49 | 9.65 | 39.4 | 47.2 | -0.353 | 0.03 | -0.26 | -0.02 | -0.34 | 1.922 | 38.2552 | 7.728 | 36.4426 | Rack | Flat Plate | 1 | 2 | 1 | 0.19349 |  | 2018-02-15
LG Electronics Inc. | LG380N2K-G4 | 380 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 380 | 351.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 9.94 | 49.1 | 9.43 | 40.3 | 45.7 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.884 | 39.2925 | 7.5257 | 37.2775 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.1948 |  | 2018-02-15
LG Electronics Inc. | LG380N2T-A4 | 380 W Bifacial Monocrystalline Module, 1500V System Voltage | UL 1703 | 380 | 350.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9502 | 72 | 1 | N | 9.86 | 49.4 | 9.28 | 41 | 46.8 | -0.37 | 0.03 | -0.27 | -0.01 | -0.36 | 1.8804 | 39.6807 | 7.4199 | 37.854 | Rack | Flat Plate | 0.98 | 1.99 | 1 | 0.19636 |  | 2018-02-15
LG Electronics Inc. | LG380N2T-A5 | 380 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 380 | 349.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 1 | N | 10.07 | 49 | 9.37 | 40.6 | 47.8 | -0.355 | 0.03 | -0.26 | -0.02 | -0.34 | 1.8701 | 39.4175 | 7.4902 | 37.4466 | Rack | Flat Plate | 1 | 2.04 | 1 | 0.19399 |  | 2018-02-15
LG Electronics Inc. | LG380N2W-A5 | 380 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 380 | 349.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.31 | 48.9 | 9.75 | 39 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9263 | 38.146 | 7.7842 | 35.9635 | Rack | Flat Plate | 1 | 2 | 1 | 0.19337 |  | 2018-02-15
LG Electronics Inc. | LG380N2W-G4 | 380 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 380 | 351.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 10.1 | 48.6 | 9.55 | 39.8 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.908 | 38.9045 | 7.6116 | 36.7155 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19534 |  | 2018-02-15
LG Electronics Inc. | LG380N2W-V5 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 349 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.31 | 48.9 | 9.75 | 39 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.9412 | 37.9737 | 1.9412 | 37.9737 | 7.8402 | 35.5385 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG380Q1C-V5 | 380 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 380 | 358.7 |  | 2019-07-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6733 | 60 | 1 | N | 10.84 | 42.9 | 10.17 | 37.4 | 44.53 | -0.3134 | 0.02868 | -0.243 | 2.0136 | 35.8408 | 2.0136 | 35.8408 | 8.0777 | 35.0765 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG380Q1K-A6 | 376 W, 60 cell monocrystalline module, black backsheet, black colored frame, 1000V max system Vdc | UL 61730 | 380 | 356.5 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.85 | 43.5 | 10.21 | 37.2 | 46.26 | -0.3068 | 0.0301 | -0.2416 |  |  | 2.0311 | 35.1908 | 8.165 | 34.594 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG385M1C-A6 | 385 W, monocrystalline ACPV module, white backsheet. DC Module: LG385N1C-A6. Microinverter: LM320UE-A2. | UL 1741 | 385 | 356.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.43 | 42 | 10.67 | 36.1 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.141 | 34.6069 | 8.534 | 32.9502 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG385N1C-A6 | 385 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 385 | 356.9 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.43 | 42 | 10.67 | 36.1 | 47.43 | -0.3444 | 0.0239 | -0.2586 |  |  | 2.141 | 34.6069 | 8.534 | 32.9502 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG385N1C-E6 | 385 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 385 | 356.9 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.44 | 42 | 10.88 | 35.5 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1339 | 34.1245 | 2.1339 | 34.1245 | 8.5917 | 32.8603 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG385N1K-E6 | 385 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 385 | 358.4 |  | 2021-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.53 | 41.9 | 10.91 | 25.3 | 47.2 | -0.3309 | 0.0257 | -0.2581 |  |  | 2.1313 | 24.5533 | 8.5534 | 23.7052 | [6 empty] | 2021-09-21
LG Electronics Inc. | LG385N1W-A6 | 385 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 385 | 356.9 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.43 | 42 | 10.67 | 36.1 | 47.43 | -0.3444 | 0.0239 | -0.2586 | 0.0239 |  | 2.141 | 34.6069 | 8.534 | 32.9502 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG385N1W-E6 | 385 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 385 | 356.9 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.44 | 42 | 10.88 | 35.5 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1339 | 34.1245 | 2.1339 | 34.1245 | 8.5917 | 32.8603 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG385N2C-A5 | 385 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 385 | 354.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.35 | 49 | 9.78 | 39.4 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9322 | 38.5372 | 7.8081 | 36.3324 | Rack | Flat Plate | 1 | 2 | 1 | 0.19341 |  | 2018-02-15
LG Electronics Inc. | LG385N2C-G4 | 385 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 385 | 356.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 10.16 | 48.9 | 9.61 | 40.1 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.92 | 39.1977 | 7.6594 | 36.9922 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19548 |  | 2018-02-15
LG Electronics Inc. | LG385N2K-A5 | 385 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 385 | 355.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.17 | 49.1 | 9.68 | 39.8 | 47.2 | -0.353 | 0.03 | -0.26 | -0.02 | -0.34 | 1.928 | 38.6436 | 7.752 | 36.8126 | Rack | Flat Plate | 1 | 2 | 1 | 0.19352 |  | 2018-02-15
LG Electronics Inc. | LG385N2T-A5 | 385 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 385 | 354.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 1 | N | 10.11 | 49.1 | 9.4 | 41 | 47.8 | -0.355 | 0.03 | -0.26 | -0.02 | -0.34 | 1.8761 | 39.8058 | 7.5142 | 37.8155 | Rack | Flat Plate | 1 | 2.04 | 1 | 0.19397 |  | 2018-02-15
LG Electronics Inc. | LG385N2T-J5 | 385W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 385 | 351.8 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.1 | 49.4 | 9.56 | 40.3 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.913 | 39.2415 | 1.913 | 39.2415 | 7.6965 | 36.6487 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG385N2W-A5 | 385 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 385 | 354.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.35 | 49 | 9.78 | 39.4 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9322 | 38.5372 | 7.8081 | 36.3324 | Rack | Flat Plate | 1 | 2 | 1 | 0.19341 |  | 2018-02-15
LG Electronics Inc. | LG385N2W-G4 | 385 W Monocrystalline Module, 1000 V System Voltage | UL 1703 | 385 | 356.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9012 | 72 | 1 | N | 10.16 | 48.9 | 9.61 | 40.1 | 45.9 | -0.37 | 0.03 | -0.28 | -0.01 | -0.36 | 1.92 | 39.1977 | 7.6594 | 36.9922 | Rack | Flat Plate | 0.98 | 1.94 | 1 | 0.19548 |  | 2018-02-15
LG Electronics Inc. | LG385N2W-V5 | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 353.7 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.35 | 49 | 9.78 | 39.4 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.9471 | 38.3632 | 1.9471 | 38.3632 | 7.8643 | 35.903 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG385Q1K-A6 | 380 W, 60 cell monocrystalline module, black backsheet, black colored frame, 1000V max system Vdc | UL 61730 | 385 | 361.3 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.86 | 43.7 | 10.3 | 37.4 | 46.26 | -0.3068 | 0.0301 | -0.2416 |  |  | 2.049 | 35.38 | 8.237 | 34.78 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG410N2T-V5 | 385W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 385 | 351.8 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.1 | 49.4 | 9.56 | 40.3 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.913 | 39.2415 | 1.913 | 39.2415 | 7.6965 | 36.6487 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG390N1C-E6 | 390 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 390 | 361.7 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.49 | 42.4 | 10.92 | 35.8 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1417 | 34.4129 | 2.1417 | 34.4129 | 8.6233 | 33.1379 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG390N1K-E6 | 390 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 390 | 363.2 |  | 2021-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.63 | 42.1 | 10.99 | 35.5 | 47.2 | -0.3309 | 0.0257 | -0.2581 |  |  | 2.1469 | 34.4523 | 8.6162 | 33.2622 | [6 empty] | 2021-09-21
LG Electronics Inc. | LG390N1W-E6 | 390 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 390 | 361.7 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.49 | 42.4 | 10.92 | 35.8 | 47.8 | -0.3405 | 0.0244 | -0.2613 | 2.1417 | 34.4129 | 2.1417 | 34.4129 | 8.6233 | 33.1379 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG390N2C-A5 | 390 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 390 | 358.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.39 | 49.1 | 9.81 | 39.8 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9381 | 38.9285 | 7.8321 | 36.7012 | Rack | Flat Plate | 1 | 2 | 1 | 0.19346 |  | 2018-02-15
LG Electronics Inc. | LG390N2K-A5 | 390 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 390 | 360.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.21 | 49.2 | 9.71 | 40.2 | 47.2 | -0.353 | 0.03 | -0.26 | -0.02 | -0.34 | 1.934 | 39.032 | 7.776 | 37.1826 | Rack | Flat Plate | 1 | 2 | 1 | 0.19356 |  | 2018-02-15
LG Electronics Inc. | LG390N2T-A5 | 390 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 390 | 359 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 1 | N | 10.15 | 49.2 | 9.43 | 41.4 | 47.8 | -0.355 | 0.03 | -0.26 | -0.02 | -0.34 | 1.8821 | 40.1942 | 7.5381 | 38.1845 | Rack | Flat Plate | 1 | 2.04 | 1 | 0.19397 |  | 2018-02-15
LG Electronics Inc. | LG390N2T-J5 | 390W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 390 | 356.5 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.14 | 49.5 | 9.59 | 40.7 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.919 | 39.631 | 1.919 | 39.631 | 7.7207 | 37.0125 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG390N2W-A5 | 390 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 390 | 358.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.39 | 49.1 | 9.81 | 39.8 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9381 | 38.9285 | 7.8321 | 36.7012 | Rack | Flat Plate | 1 | 2 | 1 | 0.19346 |  | 2018-02-15
LG Electronics Inc. | LG390N2W-L5 | 390 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 390 | 362.1 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.39 | 49.1 | 9.81 | 39.8 | 46.17 | -0.3422 | 0.02508 | -0.258 |  |  | 1.9875 | 38.0488 | 7.9097 | 36.4568 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG390N2W-N5 | 390 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 390 | 362.3 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.36 | 49 | 10.02 | 39 | 46.17 | -0.3405 | 0.02309 | -0.2573 |  |  | 2.004 | 40.3099 | 7.9447 | 38.6924 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG390N2W-V5 | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 358.5 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.39 | 49.1 | 9.81 | 39.8 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.9531 | 38.7526 | 1.9531 | 38.7526 | 7.8885 | 36.2675 | [6 empty] | 2018-10-15 | 2019-08-15
LG Electronics Inc. | LG390N3K-V6 | 395 W, 66 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 390 | 362.3 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.08 | 45 | 10.72 | 36.4 | 46.23 | -0.3497 | 0.03365 | -0.266 |  |  | 2.0932 | 35.8618 | 8.3738 | 34.3745 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG390Q1C-A6 | 390 W, 60 cell monocrystalline module, white backsheet, black colored frame, 1000V max system Vdc | UL 61730 | 390 | 364.2 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 11.26 | 43.5 | 10.63 | 36.7 | 47.68 | -0.31 | 0.0269 | -0.2416 |  |  | 2.1001 | 35.1229 | 8.4513 | 34.3095 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG390Q1K-A6 | 390 W, 60 cell monocrystalline module, black backsheet, black colored frame, 1000V max system Vdc | UL 61730 | 390 | 366.1 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 10.87 | 43.9 | 10.39 | 37.5 | 46.26 | -0.3068 | 0.0301 | -0.2416 |  |  | 2.0669 | 35.4746 | 8.309 | 34.873 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG415N2T-V5 | 390W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 390 | 356.5 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.14 | 49.5 | 9.59 | 40.7 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.919 | 39.631 | 1.919 | 39.631 | 7.7207 | 37.0125 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG395A1C-A6 | 395 W, monocrystalline ACPV module, white backsheet. DC Module: LG395Q1C-A6. Microinverter: LM320UE-A2. | UL 1741 | 395 | 369 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.29 | 43.6 | 10.69 | 37 | 47.68 | -0.31 | 0.0269 | -0.2416 |  |  | 2.112 | 35.41 | 8.499 | 34.59 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG395N1C-E6 | 395 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 395 | 366.4 |  | 2021-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.53 | 42.7 | 10.96 | 36 | 47.8 | -0.3405 | 0.0244 | -0.2613 |  |  | 2.1496 | 34.6051 | 8.6549 | 33.3231 | [6 empty] | 2021-09-21
LG Electronics Inc. | LG395N1W-E6 | 395 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 395 | 366.4 |  | 2021-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.53 | 42.7 | 10.96 | 36 | 47.8 | -0.3405 | 0.0244 | -0.2613 |  |  | 2.1496 | 34.6051 | 8.6549 | 33.3231 | [6 empty] | 2021-09-21
LG Electronics Inc. | LG395N2C-A5 | 395 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 395 | 363.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.43 | 49.2 | 9.83 | 40.2 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9421 | 39.3197 | 7.8481 | 37.0701 | Rack | Flat Plate | 1 | 2 | 1 | 0.19332 |  | 2018-02-15
LG Electronics Inc. | LG395N2K-A5 | 395 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 395 | 365 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.25 | 49.3 | 9.74 | 40.6 | 47.2 | -0.353 | 0.03 | -0.26 | -0.02 | -0.34 | 1.94 | 39.4203 | 7.8 | 37.5525 | Rack | Flat Plate | 1 | 2 | 1 | 0.1936 |  | 2018-02-15
LG Electronics Inc. | LG395N2T-A5 | 395 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 395 | 363.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 1 | N | 10.19 | 49.3 | 9.46 | 41.8 | 47.8 | -0.355 | 0.03 | -0.26 | -0.02 | -0.34 | 1.8881 | 40.5825 | 7.5621 | 38.5534 | Rack | Flat Plate | 1 | 2.04 | 1 | 0.19398 |  | 2018-02-15
LG Electronics Inc. | LG395N2T-J5 | 395W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 395 | 361.2 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.18 | 49.6 | 9.62 | 41.1 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.925 | 40.0205 | 1.925 | 40.0205 | 7.7448 | 37.3762 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG395N2W-A5 | 395 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 395 | 363.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.43 | 49.2 | 9.83 | 40.2 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9421 | 39.3197 | 7.8481 | 37.0701 | Rack | Flat Plate | 1 | 2 | 1 | 0.19332 |  | 2018-02-15
LG Electronics Inc. | LG395N2W-L5 | 395 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 395 | 366.9 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.43 | 49.2 | 9.83 | 40.2 | 46.17 | -0.3422 | 0.02508 | -0.258 |  |  | 1.9915 | 38.4312 | 7.9259 | 36.8232 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG395N2W-N5 | 395 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 395 | 367 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.4 | 49.1 | 10.06 | 39.3 | 46.17 | -0.3405 | 0.02309 | -0.2573 |  |  | 2.012 | 40.62 | 7.9764 | 38.99 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG395N2W-V5 | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 363.2 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.43 | 49.2 | 9.83 | 40.2 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.9571 | 39.1421 | 1.9571 | 39.1421 | 7.9045 | 36.632 | [6 empty] | 2018-10-15 | 2019-08-15
LG Electronics Inc. | LG395N3C-V6 | 395 W, 66 cell bifacial monocrystalline module, black frame, 1000V max system Vdc | UL 61730 | 395 | 364.8 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.3 | 44.6 | 10.89 | 36.3 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.1193 | 35.5159 | 8.4731 | 33.7832 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG395N3K-V6 | 400 W, 66 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 395 | 367.1 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.12 | 45.1 | 10.74 | 36.8 | 46.23 | -0.3497 | 0.03365 | -0.266 |  |  | 2.0971 | 36.2559 | 8.3894 | 34.7523 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG395N3W-V6 | 395 W, 66 cell bifacial monocrystalline module, silver frame, 1000V max system Vdc | UL 61730 | 395 | 364.8 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.3 | 44.6 | 10.89 | 36.3 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.1193 | 35.5159 | 8.4731 | 33.7832 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG395Q1C-A6 | 395 W, 60 cell monocrystalline module, white backsheet, black colored frame, 1000V max system Vdc | UL 61730 | 395 | 369 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 11.29 | 43.6 | 10.69 | 37 | 47.68 | -0.31 | 0.0269 | -0.2416 |  |  | 2.112 | 35.41 | 8.499 | 34.59 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG420N2T-V5 | 395W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 395 | 361.2 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.18 | 49.6 | 9.62 | 41.1 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.925 | 40.0205 | 1.925 | 40.0205 | 7.7448 | 37.3762 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG400A1C-A6 | 400 W, monocrystalline ACPV module, white backsheet. DC Module: LG400Q1C-A6. Microinverter: LM320UE-A2. | UL 1741 | 400 | 373.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.32 | 43.8 | 10.76 | 37.2 | 47.68 | -0.31 | 0.0269 | -0.2416 |  |  | 2.1258 | 35.6014 | 8.5547 | 34.777 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG400N1C-E6 | 400 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 400 | 371.2 |  | 2021-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.58 | 43 | 10.99 | 36.4 | 47.8 | -0.3405 | 0.0244 | -0.2613 |  |  | 2.1555 | 34.9896 | 8.6786 | 33.6933 | [6 empty] | 2021-09-21
LG Electronics Inc. | LG400N1W-E6 | 400 W, 60 cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730 | 400 | 371.2 |  | 2021-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.58 | 43 | 10.99 | 36.4 | 47.8 | -0.3405 | 0.0244 | -0.2613 |  |  | 2.1555 | 34.9896 | 8.6786 | 33.6933 | [6 empty] | 2021-09-21
LG Electronics Inc. | LG400N2C-A5 | 400 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 400 | 368.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.47 | 49.3 | 9.86 | 40.6 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.948 | 39.7109 | 7.872 | 37.4389 | Rack | Flat Plate | 1 | 2 | 1 | 0.19339 |  | 2018-02-15
LG Electronics Inc. | LG400N2K-A5 | 400 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 400 | 369.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.29 | 49.4 | 9.76 | 41 | 47.2 | -0.353 | 0.03 | -0.26 | -0.02 | -0.34 | 1.9439 | 39.8087 | 7.8161 | 37.9225 | Rack | Flat Plate | 1 | 2 | 1 | 0.19346 |  | 2018-02-15
LG Electronics Inc. | LG400N2T-A5 | 400 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 400 | 368.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.04 | 72 | 1 | N | 10.23 | 49.4 | 9.49 | 42.2 | 47.8 | -0.355 | 0.03 | -0.26 | -0.02 | -0.34 | 1.8941 | 40.9709 | 7.5861 | 38.9223 | Rack | Flat Plate | 1 | 2.04 | 1 | 0.194 |  | 2018-02-15
LG Electronics Inc. | LG400N2T-J5 | 400W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 400 | 366 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.22 | 49.7 | 9.65 | 41.5 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.931 | 40.41 | 1.931 | 40.41 | 7.769 | 37.74 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG400N2T-L5 | 400 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 370.5 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0725 | 72 | 1 | N | 10.38 | 49.2 | 9.74 | 41.1 | 46 | -0.3587 | 0.0343 | -0.2702 |  |  | 1.9939 | 39.3074 | 7.8938 | 37.6139 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG400N2W-A5 | 400 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 400 | 368.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.47 | 49.3 | 9.86 | 40.6 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.948 | 39.7109 | 7.872 | 37.4389 | Rack | Flat Plate | 1 | 2 | 1 | 0.19339 |  | 2018-02-15
LG Electronics Inc. | LG400N2W-L5 | 400 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 400 | 371.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.47 | 49.3 | 9.86 | 40.6 | 46.17 | -0.3422 | 0.02508 | -0.258 |  |  | 1.9976 | 38.8136 | 7.9501 | 37.1896 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG400N2W-N5 | 400 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 400 | 371.8 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.44 | 49.2 | 10.09 | 39.7 | 46.17 | -0.3405 | 0.02309 | -0.2573 |  |  | 2.018 | 41.0334 | 8.0002 | 39.3868 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG400N2W-V5 | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 367.9 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.47 | 49.3 | 9.86 | 40.6 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.9631 | 39.5316 | 1.9631 | 39.5316 | 7.9287 | 36.9965 | [6 empty] | 2018-10-15 | 2019-08-15
LG Electronics Inc. | LG400N3C-V6 | 400 W, 66 cell bifacial monocrystalline module, black frame, 1000V max system Vdc | UL 61730 | 400 | 369.6 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.35 | 44.8 | 10.9 | 36.7 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.1212 | 35.9073 | 8.4809 | 34.1555 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG400N3K-V6 | 405 W, 66 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 400 | 371.9 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.16 | 45.2 | 10.76 | 37.2 | 46.23 | -0.3497 | 0.03365 | -0.266 |  |  | 2.101 | 36.65 | 8.405 | 35.13 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG400N3W-V6 | 400 W, 66 cell bifacial monocrystalline module, silver frame, 1000V max system Vdc | UL 61730 | 400 | 369.6 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.35 | 44.8 | 10.9 | 36.7 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.1212 | 35.9073 | 8.4809 | 34.1555 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG400Q1C-A6 | 400 W, 60 cell monocrystalline module, white backsheet, black colored frame, 1000V max system Vdc | UL 61730 | 400 | 373.8 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 11.32 | 43.8 | 10.76 | 37.2 | 47.68 | -0.31 | 0.0269 | -0.2416 |  |  | 2.1258 | 35.6014 | 8.5547 | 34.777 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG425N2T-B5 | 400 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 370.5 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0725 | 72 | 1 | N | 10.38 | 49.2 | 9.74 | 41.1 | 46 | -0.3587 | 0.0343 | -0.2702 |  |  | 1.9939 | 39.3074 | 7.8938 | 37.6139 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG425N2T-V5 | 400W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 400 | 366 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.22 | 49.7 | 9.65 | 41.5 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.931 | 40.41 | 1.931 | 40.41 | 7.769 | 37.74 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG405A1C-A6 | 405 W, monocrystalline ACPV module, white backsheet. DC Module: LG405Q1C-A6. Microinverter: LM320UE-A2. | UL 1741 | 405 | 378.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8131 | 60 | 1 | N | 11.35 | 43.9 | 10.82 | 37.5 | 47.68 | -0.31 | 0.0269 | -0.2416 |  |  | 2.1377 | 35.8885 | 8.6024 | 35.0574 | [6 empty] | 2021-05-11
LG Electronics Inc. | LG405N2C-A5 | 405 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 405 | 373.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.51 | 49.4 | 9.89 | 41 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.954 | 40.1022 | 7.896 | 37.8078 | Rack | Flat Plate | 1 | 2 | 1 | 0.19348 |  | 2018-02-15
LG Electronics Inc. | LG405N2K-A5 | 405 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 405 | 374.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.33 | 49.5 | 9.79 | 41.4 | 47.2 | -0.353 | 0.03 | -0.26 | -0.02 | -0.34 | 1.9499 | 40.1971 | 7.8401 | 38.2925 | Rack | Flat Plate | 1 | 2 | 1 | 0.19353 |  | 2018-02-15
LG Electronics Inc. | LG405N2T-J5 | 405W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 405 | 370.7 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.26 | 49.8 | 9.68 | 41.9 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.937 | 40.7995 | 1.937 | 40.7995 | 7.7932 | 38.1038 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG405N2T-L5 | 405 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 375.3 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0725 | 72 | 1 | N | 10.42 | 49.3 | 9.76 | 41.5 | 46 | -0.3587 | 0.0343 | -0.2702 |  |  | 1.998 | 39.69 | 7.91 | 37.98 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG405N2W-A5 | 405 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 405 | 373.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.51 | 49.4 | 9.89 | 41 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.954 | 40.1022 | 7.896 | 37.8078 | Rack | Flat Plate | 1 | 2 | 1 | 0.19348 |  | 2018-02-15
LG Electronics Inc. | LG405N2W-L5 | 405 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 405 | 376.4 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.51 | 49.4 | 9.89 | 41 | 46.17 | -0.3422 | 0.02508 | -0.258 |  |  | 2.0037 | 39.196 | 7.9742 | 37.556 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG405N2W-N5 | 405 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 405 | 376.6 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.48 | 49.3 | 10.12 | 40.1 | 46.17 | -0.3405 | 0.02309 | -0.2573 |  |  | 2.024 | 41.4469 | 8.024 | 39.7837 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG405N2W-V5 | 405 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 405 | 372.7 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.51 | 49.4 | 9.89 | 41 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.969 | 39.9211 | 1.969 | 39.9211 | 7.9528 | 37.361 | [6 empty] | 2018-10-15 | 2019-08-15
LG Electronics Inc. | LG405N3C-V6 | 405 W, 66 cell bifacial monocrystalline module, black frame, 1000V max system Vdc | UL 61730 | 405 | 374.4 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.4 | 45 | 10.92 | 37.1 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.1251 | 36.2986 | 8.4964 | 34.5277 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG405N3K-V6 | 410 W, 66 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 405 | 376.6 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.2 | 45.28 | 10.78 | 37.6 | 46.23 | -0.3497 | 0.03365 | -0.266 |  |  | 2.1049 | 37.0441 | 8.4206 | 35.5077 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG405N3W-V6 | 405 W, 66 cell bifacial monocrystalline module, silver frame, 1000V max system Vdc | UL 61730 | 405 | 374.4 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.4 | 45 | 10.92 | 37.1 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.1251 | 36.2986 | 8.4964 | 34.5277 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG405Q1C-A6 | 405 W, 60 cell monocrystalline module, white backsheet, black colored frame, 1000V max system Vdc | UL 61730 | 405 | 378.6 |  | 2020-11-30 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 1 | N | 11.35 | 43.9 | 10.82 | 37.5 | 47.68 | -0.31 | 0.0269 | -0.2416 |  |  | 2.1377 | 35.8885 | 8.6024 | 35.0574 | [6 empty] | 2021-02-01
LG Electronics Inc. | LG430N2T-B5 | 405 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 375.3 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0725 | 72 | 1 | N | 10.42 | 49.3 | 9.76 | 41.5 | 46 | -0.3587 | 0.0343 | -0.2702 |  |  | 1.998 | 39.69 | 7.91 | 37.98 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG430N2T-V5 | 405W, 72 cell monocrystalline module, transparent backsheet, silver frame, 1500V max system Vdc | UL 1703 | 405 | 370.7 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.26 | 49.8 | 9.68 | 41.9 | 50.66 | -0.343 | 0.02222 | -0.2574 | 1.937 | 40.7995 | 1.937 | 40.7995 | 7.7932 | 38.1038 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG410N2C-A5 | 410 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 410 | 377.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.55 | 49.5 | 9.91 | 41.4 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9579 | 40.4934 | 7.9119 | 38.1766 | Rack | Flat Plate | 1 | 2 | 1 | 0.19337 |  | 2018-02-15
LG Electronics Inc. | LG410N2T-L5 | 410 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 380.1 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0725 | 72 | 1 | N | 10.46 | 49.4 | 9.79 | 41.9 | 46 | -0.3587 | 0.0343 | -0.2702 |  |  | 2.0041 | 40.0726 | 7.9343 | 38.3461 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG410N2W-A5 | 410 W Monocrystalline Module, 1500V System Voltage | UL 1703 | 410 | 377.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.55 | 49.5 | 9.91 | 41.4 | 47.7 | -0.36 | 0.03 | -0.26 | -0.03 | -0.34 | 1.9579 | 40.4934 | 7.9119 | 38.1766 | Rack | Flat Plate | 1 | 2 | 1 | 0.19337 |  | 2018-02-15
LG Electronics Inc. | LG410N2W-L5 | 410 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 410 | 381.2 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.55 | 49.5 | 9.91 | 41.4 | 46.17 | -0.3422 | 0.02508 | -0.258 |  |  | 2.0077 | 39.5784 | 7.9904 | 37.9224 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG410N2W-N5 | 410 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 410 | 381.3 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.52 | 49.4 | 10.16 | 40.4 | 46.17 | -0.3405 | 0.02309 | -0.2573 |  |  | 2.032 | 41.7569 | 8.0557 | 40.0813 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG410N2W-V5 | 410 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 410 | 377.4 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.55 | 49.5 | 9.91 | 41.4 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.973 | 40.3105 | 1.973 | 40.3105 | 7.9689 | 37.7255 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG410N3C-V6 | 410 W, 66 cell bifacial monocrystalline module, black frame, 1000V max system Vdc | UL 61730 | 410 | 379.1 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.44 | 45.2 | 10.94 | 37.5 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.129 | 36.69 | 8.512 | 34.9 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG410N3K-V6 | 415 W, 66 cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 410 | 381.4 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.24 | 45.4 | 10.79 | 38 | 46.23 | -0.3497 | 0.03365 | -0.266 |  |  | 2.1069 | 37.4382 | 8.4284 | 35.8855 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG410N3W-V6 | 410 W, 66 cell bifacial monocrystalline module, silver frame, 1000V max system Vdc | UL 61730 | 410 | 379.1 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.44 | 45.2 | 10.94 | 37.5 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.129 | 36.69 | 8.512 | 34.9 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG435N2T-B5 | 410 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 380.1 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0725 | 72 | 1 | N | 10.46 | 49.4 | 9.79 | 41.9 | 46 | -0.3587 | 0.0343 | -0.2702 |  |  | 2.0041 | 40.0726 | 7.9343 | 38.3461 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG415N2T-L5 | 415 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 384.8 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0725 | 72 | 1 | N | 10.5 | 49.5 | 9.82 | 42.3 | 46 | -0.3587 | 0.0343 | -0.2702 |  |  | 2.0103 | 40.4551 | 7.9586 | 38.7121 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG415N2W-L5 | 415 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 415 | 386 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.59 | 49.6 | 9.94 | 41.8 | 46.17 | -0.3422 | 0.02508 | -0.258 |  |  | 2.0138 | 39.9608 | 8.0146 | 38.2888 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG415N2W-N5 | 415 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 415 | 386.1 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.56 | 49.5 | 10.21 | 40.7 | 46.17 | -0.3405 | 0.02309 | -0.2573 |  |  | 2.042 | 42.067 | 8.0954 | 40.379 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG415N2W-V5 | 415 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 415 | 382.2 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.59 | 49.6 | 9.94 | 41.8 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.979 | 40.7 | 1.979 | 40.7 | 7.993 | 38.09 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG415N3C-V6 | 415 W, 66 cell bifacial monocrystalline module, black frame, 1000V max system Vdc | UL 61730 | 415 | 383.9 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.49 | 45.4 | 10.95 | 37.9 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.1309 | 37.0814 | 8.5198 | 35.2723 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG415N3W-V6 | 415 W, 66 cell bifacial monocrystalline module, silver frame, 1000V max system Vdc | UL 61730 | 415 | 383.9 |  | 2021-05-28 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9 | 66 | 1 | N | 11.49 | 45.4 | 10.95 | 37.9 | 47.8 | -0.35145 | 0.0313 | -0.26595 |  |  | 2.1309 | 37.0814 | 8.5198 | 35.2723 | [6 empty] | 2021-08-02
LG Electronics Inc. | LG415QAK-A6 | 415 W, 66 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 415 | 386.5 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 66 | 1 | N | 10.82 | 47.9 | 10.08 | 41.2 | 49.31 | -0.297 | 0.0323 | -0.2386 |  |  | 1.9812 | 39.4941 | 7.974 | 38.2871 | [6 empty] | 2021-03-11
LG Electronics Inc. | LG440N2T-B5 | 415 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 384.8 |  | 2020-08-05 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0725 | 72 | 1 | N | 10.5 | 49.5 | 9.82 | 42.3 | 46 | -0.3587 | 0.0343 | -0.2702 |  |  | 2.0103 | 40.4551 | 7.9586 | 38.7121 | [6 empty] | 2020-10-01
LG Electronics Inc. | LG420N2T-E6 | 420 W, 144 half-cut cell monocrystalline module, transparent backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 420 | 387.5 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 10.82 | 48.5 | 10.37 | 40.5 | 47.37 | -0.3518 | 0.0321 | -0.2716 |  |  | 2.0652 | 38.7227 | 8.243 | 37.0424 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG420N2W-L5 | 420 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 420 | 390.8 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.63 | 49.7 | 9.98 | 42.1 | 46.17 | -0.3422 | 0.02508 | -0.258 |  |  | 2.0219 | 40.2476 | 8.0468 | 38.5636 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG420N2W-N5 | 420 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 420 | 390.9 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.6 | 49.6 | 10.23 | 41.1 | 46.17 | -0.3405 | 0.02309 | -0.2573 |  |  | 2.046 | 42.4805 | 8.1112 | 40.7758 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG420N2W-V5 | 420 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 420 | 386.9 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.63 | 49.7 | 9.98 | 42.1 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.987 | 40.9921 | 1.987 | 40.9921 | 8.0252 | 38.3634 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG420QAK-A6 | 420 W, 66 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 420 | 391.2 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 66 | 1 | N | 10.83 | 48 | 10.19 | 41.3 | 49.31 | -0.297 | 0.0323 | -0.2386 |  |  | 2.0028 | 39.59 | 8.0611 | 38.38 | [6 empty] | 2021-03-11
LG Electronics Inc. | LG425N2T-E6 | 425 W, 144 half-cut cell monocrystalline module, transparent backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 425 | 392.2 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 10.88 | 48.8 | 10.42 | 40.8 | 47.37 | -0.3518 | 0.0321 | -0.2716 |  |  | 2.0751 | 39.0095 | 8.2827 | 37.3168 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG425N2W-L5 | 425 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 425 | 395.5 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.67 | 49.8 | 10.01 | 42.5 | 46.17 | -0.3422 | 0.02508 | -0.258 |  |  | 2.028 | 40.63 | 8.071 | 38.93 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG425N2W-N5 | 425 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 425 | 395.7 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.64 | 49.7 | 10.26 | 41.5 | 46.17 | -0.3405 | 0.02309 | -0.2573 |  |  | 2.052 | 42.8939 | 8.135 | 41.1726 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG425N2W-V5 | 425 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 425 | 391.7 |  | 2019-06-27 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.67 | 49.8 | 10.01 | 42.5 | 48.88 | -0.3472 | 0.02232 | -0.257 | 1.9929 | 41.3816 | 1.9929 | 41.3816 | 8.0493 | 38.7279 | [6 empty] | 2019-08-15
LG Electronics Inc. | LG425QAK-A6 | 425 W, 66 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 425 | 396 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 66 | 1 | N | 10.84 | 48.1 | 10.31 | 41.3 | 49.31 | -0.297 | 0.0323 | -0.2386 |  |  | 2.0264 | 39.59 | 8.156 | 38.38 | [6 empty] | 2021-03-11
LG Electronics Inc. | LG430N2T-E6 | 430 W, 144 half-cut cell monocrystalline module, transparent backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 430 | 396.9 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 10.94 | 49.1 | 10.47 | 41.1 | 47.37 | -0.3518 | 0.0321 | -0.2716 |  |  | 2.0851 | 39.2963 | 8.3225 | 37.5912 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG430N2W-E6 | 430 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 430 | 400 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.08 | 48.6 | 10.6 | 40.6 | 45.63 | -0.3469 | 0.0338 | -0.2677 |  |  | 2.1279 | 38.8517 | 8.4839 | 37.3947 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG430N2W-L5 | 430 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 430 | 400.3 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.71 | 49.9 | 10.04 | 42.9 | 46.17 | -0.3422 | 0.02508 | -0.258 |  |  | 2.0341 | 41.0124 | 8.0952 | 39.2964 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG430N2W-N5 | 430 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 430 | 400.5 |  | 2020-06-08 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.0726 | 72 | 1 | N | 10.68 | 49.8 | 10.3 | 41.8 | 46.17 | -0.3405 | 0.02309 | -0.2573 |  |  | 2.06 | 43.204 | 8.1667 | 41.4703 | [6 empty] | 2020-08-11
LG Electronics Inc. | LG430QAC-A6 | 430 W, 66 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 430 | 402.1 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 66 | 1 | N | 11.19 | 47.9 | 10.54 | 40.8 | 47.96 | -0.301 | 0.0291 | -0.2392 |  |  | 2.0922 | 38.9374 | 8.4379 | 37.9026 | [6 empty] | 2021-03-11
LG Electronics Inc. | LG430QAK-A6 | 430 W, 66 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 430 | 400.8 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 66 | 1 | N | 10.85 | 48.2 | 10.42 | 41.3 | 49.31 | -0.297 | 0.0323 | -0.2386 |  |  | 2.048 | 39.59 | 8.243 | 38.38 | [6 empty] | 2021-03-11
LG Electronics Inc. | LG435N2T-E6 | 435 W, 144 half-cut cell monocrystalline module, transparent backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 435 | 401.7 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11 | 49.4 | 10.51 | 41.4 | 47.37 | -0.3518 | 0.0321 | -0.2716 |  |  | 2.093 | 39.5832 | 8.3543 | 37.8656 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG435N2W-E6 | 435 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 435 | 404.8 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.14 | 48.8 | 10.65 | 40.9 | 45.63 | -0.3469 | 0.0338 | -0.2677 |  |  | 2.1379 | 39.1388 | 8.5239 | 37.6711 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG435QAC-A6 | 435 W, 66 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 435 | 406.9 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 66 | 1 | N | 11.2 | 48 | 10.59 | 41.1 | 47.96 | -0.301 | 0.0291 | -0.2392 |  |  | 2.1021 | 39.2237 | 8.478 | 38.1813 | [6 empty] | 2021-03-11
LG Electronics Inc. | LG440N2T-E6 | 440 W, 144 half-cut cell monocrystalline module, transparent backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 440 | 406.4 |  | 2021-06-07 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11.06 | 49.7 | 10.56 | 41.7 | 47.37 | -0.3518 | 0.0321 | -0.2716 |  |  | 2.103 | 39.87 | 8.394 | 38.14 | [6 empty] | 2021-02-11 | 2021-08-23
LG Electronics Inc. | LG440N2W-E6 | 440 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 440 | 409.6 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.2 | 49.1 | 10.7 | 41.2 | 45.63 | -0.3469 | 0.0338 | -0.2677 |  |  | 2.1479 | 39.4258 | 8.564 | 37.9474 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG440QAC-A6 | 440 W, 66 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 440 | 411.7 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 66 | 1 | N | 11.2 | 48.2 | 10.64 | 41.4 | 47.96 | -0.301 | 0.0291 | -0.2392 |  |  | 2.112 | 39.51 | 8.518 | 38.46 | [6 empty] | 2021-03-11
LG Electronics Inc. | LG445N2T-E6 | 445 W, 144 half-cut cell monocrystalline module, transparent backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 445 | 411.2 |  | 2021-06-07 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11.11 | 50 | 10.61 | 42 | 47.37 | -0.3518 | 0.0321 | -0.2716 |  |  | 2.113 | 40.1568 | 8.4337 | 38.4144 | [6 empty] | 2021-08-23
LG Electronics Inc. | LG445N2W-E6 | 445 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 445 | 414.4 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.27 | 49.4 | 10.74 | 41.5 | 45.63 | -0.3469 | 0.0338 | -0.2677 |  |  | 2.156 | 39.7129 | 8.596 | 38.2237 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG445QAC-A6 | 445 W, 66 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 445 | 416.5 |  | 2021-01-15 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 66 | 1 | N | 11.21 | 48.3 | 10.7 | 41.6 | 47.96 | -0.301 | 0.0291 | -0.2392 |  |  | 2.1239 | 39.7009 | 8.566 | 38.6458 | [6 empty] | 2021-03-11
LG Electronics Inc. | LG450N2T-E6 | 450 W, 144 half-cut cell monocrystalline module, transparent backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 450 | 415.9 |  | 2021-06-07 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 72 | 2 | N | 11.15 | 50.3 | 10.67 | 42.2 | 47.37 | -0.3518 | 0.0321 | -0.2716 |  |  | 2.1249 | 40.3481 | 8.4814 | 38.5973 | [6 empty] | 2021-08-23
LG Electronics Inc. | LG450N2W-E6 | 450 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 450 | 419.2 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.34 | 49.7 | 10.79 | 41.8 | 45.63 | -0.3469 | 0.0338 | -0.2677 |  |  | 2.166 | 40 | 8.636 | 38.5 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG455N2W-E6 | 455 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 455 | 423.9 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.39 | 49.9 | 10.83 | 42.1 | 45.63 | -0.3469 | 0.0338 | -0.2677 |  |  | 2.174 | 40.2871 | 8.668 | 38.7763 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG460N2W-E6 | 460 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 460 | 428.7 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.45 | 50.2 | 10.86 | 42.4 | 45.63 | -0.3469 | 0.0338 | -0.2677 |  |  | 2.1801 | 40.5742 | 8.692 | 39.0526 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG465N2W-E6 | 465 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 465 | 431.8 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.51 | 50.5 | 10.89 | 42.7 | 48.07 | -0.3306 | 0.0272 | -0.2551 |  |  | 2.155 | 40.92 | 8.602 | 39.38 | [6 empty] | 2021-02-11 | 2021-10-11
LG Electronics Inc. | LG470N2W-E6 | 470 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 470 | 438.3 |  | 2020-12-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.2 | 72 | 2 | N | 11.57 | 50.7 | 10.93 | 43 | 45.63 | -0.3469 | 0.0338 | -0.2677 |  |  | 2.1941 | 41.1483 | 8.7481 | 39.6053 | [6 empty] | 2021-02-11
LG Electronics Inc. | LG475N2W-E6 | 475 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 475 | 441.3 |  | 2021-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.62 | 51 | 10.97 | 43.3 | 48.07 | -0.3306 | 0.0272 | -0.2551 |  |  | 2.1708 | 41.495 | 8.6652 | 39.9333 | [6 empty] | 2021-10-11
LG Electronics Inc. | LG480N2W-E6 | 480 W, 144 half-cut cell monocrystalline module, white backsheet, silver colored frame, 1500V max system Vdc | UL 61730 | 480 | 446.1 |  | 2021-08-03 | No Information Submitted | Monocrystalline | Mono-c-Si | 2.14 | 72 | 2 | N | 11.68 | 51.3 | 11.01 | 43.6 | 48.07 | -0.3306 | 0.0272 | -0.2551 |  |  | 2.1787 | 41.7825 | 8.6968 | 40.21 | [6 empty] | 2021-10-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-158M-395W | 395 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 370.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.016 | 48 | 3 | N | 10.37 | 48.7 | 9.86 | 40.1 | 43.21 | -0.3536 | 0.0492 | -0.2749 |  |  | 1.8594 | 38.8339 | 7.4542 | 37.7452 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-158M-400W | 400 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 375.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.016 | 48 | 3 | N | 10.45 | 49 | 9.92 | 40.3 | 43.21 | -0.3536 | 0.0492 | -0.2749 |  |  | 1.8707 | 39.0276 | 7.4996 | 37.9335 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-158M-405W | 405 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 379.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.016 | 48 | 3 | N | 10.52 | 49.2 | 10 | 40.5 | 43.21 | -0.3536 | 0.0492 | -0.2749 |  |  | 1.8858 | 39.2213 | 7.5601 | 38.1217 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-158M-410W | 410 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 410 | 384.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.016 | 48 | 3 | N | 10.59 | 49.4 | 10.07 | 40.7 | 43.21 | -0.3536 | 0.0492 | -0.2749 |  |  | 1.899 | 39.415 | 7.613 | 38.31 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-158M-415W | 415 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 389.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.016 | 48 | 3 | N | 10.66 | 49.6 | 10.15 | 40.9 | 43.21 | -0.3536 | 0.0492 | -0.2749 |  |  | 1.9141 | 39.6087 | 7.6735 | 38.4983 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-166M-425W | 425 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 399.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.154 | 48 | 3 | N | 11.23 | 48.3 | 10.5 | 40.5 | 43.12 | -0.3421 | 0.0376 | -0.2583 |  |  | 2.0795 | 38.9182 | 8.3357 | 37.7131 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-166M-430W | 430 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 404.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.154 | 48 | 3 | N | 11.31 | 48.5 | 10.57 | 40.7 | 43.12 | -0.3421 | 0.0376 | -0.2583 |  |  | 2.0934 | 39.1104 | 8.3913 | 37.8993 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-166M-435W | 435 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 409.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.154 | 48 | 3 | N | 11.39 | 48.7 | 10.64 | 40.9 | 43.12 | -0.3421 | 0.0376 | -0.2583 |  |  | 2.1073 | 39.3026 | 8.4469 | 38.0855 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-166M-440W | 440 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 413.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.154 | 48 | 3 | N | 11.46 | 48.9 | 10.71 | 41.1 | 43.12 | -0.3421 | 0.0376 | -0.2583 |  |  | 2.1211 | 39.4948 | 8.5024 | 38.2718 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-166M-445W | 445 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 418.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.154 | 48 | 3 | N | 11.53 | 49.1 | 10.78 | 41.3 | 43.12 | -0.3421 | 0.0376 | -0.2583 |  |  | 2.135 | 39.687 | 8.558 | 38.458 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-166M-450W | 450 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 423.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.154 | 48 | 3 | N | 11.6 | 49.3 | 10.85 | 41.5 | 43.12 | -0.3421 | 0.0376 | -0.2583 |  |  | 2.1489 | 39.8792 | 8.6136 | 38.6442 | [6 empty] | 2021-01-11
LIGHT&HOPE ENERGY CO.,LTD. | LHM72H-166M-455W | 455 W, 144 half-cut cell monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 428.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.154 | 48 | 3 | N | 11.66 | 49.5 | 10.92 | 41.7 | 43.12 | -0.3421 | 0.0376 | -0.2583 |  |  | 2.1627 | 40.0714 | 8.6691 | 38.8305 | [6 empty] | 2021-01-11
Lightway Green New Energy | LW165(23)P1310x990 | 165 W Polycrystalline Module | UL 1703 | 165 | 146.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 48 | 1 | N | 7.9 | 29 | 7.2 | 23 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.3664 | 22.5544 | 5.6592 | 21.1162 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.18677
Lightway Green New Energy | LW170(23)P1310x990 | 170 W Polycrystalline Module | UL 1703 | 170 | 151.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2835 | 48 | 1 | N | 8.1 | 29.5 | 7.4 | 23 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.4043 | 22.5544 | 5.8164 | 21.1162 | Rack | Flat Plate | 0.985 | 1.303 | 1 | 0.18631
Lightway Green New Energy | LW175(23)P1310x990 | 175 W Polycrystalline Module | UL 1703 | 175 | 156.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2835 | 48 | 1 | N | 8.2 | 29.5 | 7.6 | 23 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.4423 | 22.5544 | 5.9736 | 21.1162 | Rack | Flat Plate | 0.985 | 1.303 | 1 | 0.18588
Lightway Green New Energy | LW180(23)P1310x990 | 180 W Polycrystalline Module | UL 1703 | 180 | 161.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2835 | 48 | 1 | N | 8.32 | 29.5 | 7.7 | 23.5 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.5263 | 22.8266 | 6.203 | 21.5194 | Rack | Flat Plate | 0.985 | 1.303 | 1 | 0.19356
Lightway Green New Energy | LW185(23)P1310x990 | 185 W Polycrystalline Module | UL 1703 | 185 | 165.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2835 | 48 | 1 | N | 8.36 | 30 | 7.83 | 24 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.5521 | 23.3123 | 6.3078 | 21.9772 | Rack | Flat Plate | 0.985 | 1.303 | 1 | 0.19558
Lightway Green New Energy | LW190(23)P1310x990 | 190 W Polycrystalline Module | UL 1703 | 190 | 170.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.2835 | 48 | 1 | N | 8.56 | 30 | 7.92 | 24 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.5699 | 23.3123 | 6.3803 | 21.9772 | Rack | Flat Plate | 0.985 | 1.303 | 1 | 0.19262
Lightway Green New Energy | LW200(29)P1650x990 | 200 W Polycrystalline Module | UL 1703 | 200 | 178.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 7.6 | 36 | 6.9 | 29 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.3419 | 27.5756 | 5.5771 | 25.8603 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.18502
Lightway Green New Energy | LW205(29)P1650x990 | 205 W Polycrystalline Module | UL 1703 | 205 | 183 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 7.8 | 36 | 7.1 | 29 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.3808 | 27.5756 | 5.7388 | 25.8603 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.18574
Lightway Green New Energy | LW210(29)P1650x990 | 210 W Polycrystalline Module | UL 1703 | 210 | 187.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 7.95 | 36 | 7.24 | 29 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.4081 | 27.5756 | 5.8519 | 25.8603 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.18489
Lightway Green New Energy | LW215(29)P1650x990 | 215 W Polycrystalline Module | UL 1703 | 215 | 192.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.1 | 36.6 | 7.36 | 29.2 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.4314 | 27.7658 | 5.9489 | 26.0386 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.18485
Lightway Green New Energy | LW220(29)P1650x990 | 220 W Polycrystalline Module | UL 1703 | 220 | 196.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.18 | 36.6 | 7.53 | 29.2 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.4867 | 28.612 | 5.995 | 26.1704 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19335
Lightway Green New Energy | LW225(29)P1650x990 | 225 W Polycrystalline Module | UL 1703 | 225 | 201.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.28 | 36.6 | 7.7 | 29.2 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.5203 | 28.612 | 6.1304 | 26.1704 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19332
Lightway Green New Energy | LW230(29)P1650x990 | 230 W Polycrystalline Module | UL 1703 | 230 | 205.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.38 | 36.6 | 7.87 | 29.2 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.5538 | 28.612 | 6.2657 | 26.1704 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.1933
Lightway Green New Energy | LW235(29)P1650x990 | 235 W Polycrystalline Module | UL 1703 | 235 | 210.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.45 | 37.2 | 8 | 29.6 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.5795 | 29.004 | 6.3692 | 26.5289 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19494
Lightway Green New Energy | LW240(29)P1640x990 | 240 W Polycrystalline Module | UL 1703 | 240 | 214.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.56 | 37.4 | 8.11 | 29.65 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.5467 | 29.057 | 6.5534 | 26.5565 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18725
Lightway Green New Energy | LW240(29)P1650x990 | 240 W Polycrystalline Module | UL 1703 | 240 | 215.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6193 | 60 | 1 | N | 8.56 | 37.4 | 8.05 | 29.8 | 46.4 | -0.46 | 0.07 | -0.36 | -0.02 | -0.45 | 1.5894 | 29.1999 | 6.409 | 26.7081 | Rack | Flat Plate | 0.985 | 1.644 | 1 | 0.19337
Lightway Green New Energy | LW245(29)P1640x990 | 245 W Polycrystalline Module | UL 1703 | 245 | 219.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.69 | 37.5 | 8.24 | 29.8 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.5714 | 29.204 | 6.6585 | 26.6909 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.18732
Lightway Green New Energy | LW245(29)P1650x990 | 245 W Polycrystalline Module | UL 1703 | 245 | 219.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 72 | 1 | N | 8.69 | 37.5 | 8.24 | 29.8 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.5714 | 29.204 | 6.6585 | 26.6909 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.18732
Lightway Green New Energy | LW250(29)P1640x990 | 250 W Polycrystalline Module | UL 1703 | 250 | 223.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.78 | 37.8 | 8.36 | 29.95 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.5943 | 29.351 | 6.7555 | 26.8252 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.18718
Lightway Green New Energy | LW250(29)P1650x990 | 250 W Polycrystalline Module | UL 1703 | 250 | 223.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.78 | 37.8 | 8.36 | 29.95 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.5943 | 29.351 | 6.7555 | 26.8252 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.18718
Lightway Green New Energy | LW255(29)P1640x990 | 255 W Polycrystalline Module | UL 1703 | 255 | 228.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 8.9 | 37.88 | 8.48 | 30.1 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6065 | 30.4534 | 6.7921 | 27.3939 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19186
Lightway Green New Energy | LW255(29)P1650x990 | 255 W Polycrystalline Module | UL 1703 | 255 | 228.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 8.9 | 37.88 | 8.48 | 30.1 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6065 | 30.4534 | 6.7921 | 27.3939 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19186
Lightway Green New Energy | LW260(29)P1640x990 | 260 W Polycrystalline Module | UL 1703 | 260 | 233 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 9.06 | 37.95 | 8.61 | 30.25 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6312 | 30.6052 | 6.8963 | 27.5304 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19201
Lightway Green New Energy | LW260(29)P1650x990 | 260 W Polycrystalline Module | UL 1703 | 260 | 233 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 9.06 | 37.95 | 8.61 | 30.25 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6312 | 30.6052 | 6.8963 | 27.5304 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19201
Lightway Green New Energy | LW265(29)P1640x990 | 265 W Polycrystalline Module | UL 1703 | 265 | 237.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6236 | 60 | 1 | N | 9.1 | 38.22 | 8.73 | 30.4 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6539 | 30.7569 | 6.9924 | 27.667 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.19196
Lightway Green New Energy | LW265(29)P1650x990 | 265 W Polycrystalline Module | UL 1703 | 265 | 237.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6335 | 60 | 1 | N | 9.1 | 38.22 | 8.73 | 30.4 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6539 | 30.7569 | 6.9924 | 27.667 | Rack | Flat Plate | 0.99 | 1.65 | 1 | 0.19196
Lightway Green New Energy | LW280(35)P1970x990 | 280 W Polycrystalline Module | UL 1703 | 280 | 251 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.68 | 43.6 | 7.93 | 35.3 | 47.2 | -0.44 | 0.06 | -0.33 | 0.02 | -0.45 | 1.5314 | 34.8719 | 6.3487 | 32.1912 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19073
Lightway Green New Energy | LW285(35)P1970x990 | 285 W Polycrystalline Module | UL 1703 | 285 | 255.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.83 | 43.6 | 8.03 | 35.5 | 47.2 | -0.44 | 0.06 | -0.33 | 0.02 | -0.45 | 1.5507 | 35.0694 | 6.4288 | 32.3736 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19082
Lightway Green New Energy | LW290(35)P1960x990 | 290 W Polycrystalline Module | UL 1703 | 290 | 259.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.49 | 44.81 | 8.11 | 35.81 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.5943 | 34.9906 | 6.5157 | 32.0251 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19236
Lightway Green New Energy | LW290(35)P1970x990 | 290 W Polycrystalline Module | UL 1703 | 290 | 260.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.6 | 44.96 | 7.97 | 36.4 | 47.2 | -0.44 | 0.06 | -0.33 | 0.02 | -0.45 | 1.5392 | 35.9585 | 6.3807 | 33.1943 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19085
Lightway Green New Energy | LW295(35)P1960x990 | 295 W Polycrystalline Module | UL 1703 | 295 | 264 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.59 | 44.91 | 8.21 | 35.99 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6139 | 35.1665 | 6.5961 | 32.1861 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19239
Lightway Green New Energy | LW295(35)P1970x990 | 295 W Polycrystalline Module | UL 1703 | 295 | 263.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.59 | 44.91 | 8.21 | 35.99 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6139 | 35.1665 | 6.5961 | 32.1861 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19239
Lightway Green New Energy | LW300(35)P1960x990 | 300 W Polycrystalline Module | UL 1703 | 300 | 268.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 45.08 | 8.31 | 36.15 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6336 | 35.3228 | 6.6764 | 32.3292 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19234
Lightway Green New Energy | LW300(35)P1970x990 | 300 W Polycrystalline Module | UL 1703 | 300 | 268.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.68 | 45.08 | 8.31 | 36.15 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6336 | 35.3228 | 6.6764 | 32.3292 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19234
Lightway Green New Energy | LW305(35)P1960x990 | 305 W Polycrystalline Module | UL 1703 | 305 | 273.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.76 | 45.31 | 8.42 | 36.34 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6552 | 35.5085 | 6.7648 | 32.4991 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.1927
Lightway Green New Energy | LW305(35)P1970x990 | 305 W Polycrystalline Module | UL 1703 | 305 | 273.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.76 | 45.31 | 8.42 | 36.34 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6552 | 35.5085 | 6.7648 | 32.4991 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.1927
Lightway Green New Energy | LW310(35)P1960x990 | 310 W Polycrystalline Module | UL 1703 | 310 | 277.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.85 | 45.56 | 8.51 | 36.54 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6729 | 35.7039 | 6.8371 | 32.678 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19268
Lightway Green New Energy | LW310(35)P1970x990 | 310 W Polycrystalline Module | UL 1703 | 310 | 277.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.85 | 45.56 | 8.51 | 36.54 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6729 | 35.7039 | 6.8371 | 32.678 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19268
Lightway Green New Energy | LW315(35)P1960x990 | 315 W Polycrystalline Module | UL 1703 | 315 | 282.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.92 | 45.79 | 8.57 | 36.81 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6847 | 35.9677 | 6.8853 | 32.9194 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19236
Lightway Green New Energy | LW315(35)P1970x990 | 315 W Polycrystalline Module | UL 1703 | 315 | 282.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.92 | 45.79 | 8.57 | 36.81 | 45.9 | -0.48 | 0.06 | -0.37 | 0.04 | -0.49 | 1.6847 | 35.9677 | 6.8853 | 32.9194 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19236
LONGi Green Energy Technology Co., Ltd. | LR6-60-270M | 270 W 60 Cell Mono-Si PV Module | UL 1703 | 270 | 248.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.2 | 38.1 | 8.68 | 31.1 | 44.37 | -0.4 | 0 | -0.3 | 0.004 | -0.403 | 1.777 | 30.369 | 7.13 | 28.957 | [6 empty] | 2017-11-01
LONGi Green Energy Technology Co., Ltd. | LR6-60-275M | 275 W 60 Cell Mono-Si PV Module | UL 1703 | 275 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.32 | 38.3 | 8.79 | 31.3 | 44.37 | -0.4 | 0 | -0.3 | 0.004 | -0.403 | 1.777 | 30.369 | 7.13 | 28.957 | [6 empty] | 2017-11-01
LONGi Green Energy Technology Co., Ltd. | LR6-60-280M | 280 W 60 Cell Mono-Si PV Module | UL 1703 | 280 | 258.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.45 | 38.5 | 8.92 | 31.4 | 44.37 | -0.4 | 0 | -0.3 | 0.004 | -0.403 | 1.777 | 30.369 | 7.13 | 28.957 | [6 empty] | 2017-11-01
LONGi Green Energy Technology Co., Ltd. | LR6-60PB-280M | 280 W Monocrystalline Module | UL 1703 | 280 | 254.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.635 | 60 | 1 | N | 9.34 | 39.3 | 8.75 | 32 | 48.2 | -0.391 | 0.036 | -0.284 | -0.011 | -0.381 | 1.76 | 31.14 | 7.01 | 29.18 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.19574 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60PE-280M | 280 W Monocrystalline Module | UL 1703 | 280 | 258.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.635 | 60 | 1 | N | 9.34 | 39.3 | 8.75 | 32 | 45.2 | -0.379 | 0.037 | -0.281 | -0.002 | -0.377 | 1.76 | 31.17 | 7.08 | 29.46 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.19593 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60-285M | 285 W 60 Cell Mono-Si PV Module | UL 1703 | 285 | 262.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.59 | 38.6 | 9.05 | 31.5 | 44.37 | -0.4 | 0 | -0.3 | 0.004 | -0.403 | 1.777 | 30.369 | 7.13 | 28.957 | [6 empty] | 2017-11-01
LONGi Green Energy Technology Co., Ltd. | LR6-60PB-285M | 285 W Monocrystalline Module | UL 1703 | 285 | 258.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.635 | 60 | 1 | N | 9.46 | 39.5 | 8.88 | 32.1 | 48.2 | -0.391 | 0.036 | -0.284 | -0.011 | -0.381 | 1.78 | 31.24 | 7.11 | 29.28 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.19511 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60PE-285M | 285 W Monocrystalline Module | UL 1703 | 285 | 263 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.635 | 60 | 1 | N | 9.46 | 39.5 | 8.88 | 32.1 | 45.2 | -0.379 | 0.037 | -0.281 | -0.002 | -0.377 | 1.79 | 31.27 | 7.18 | 29.56 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.1964 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60-290M | 290 W 60 Cell Mono-Si PV Module | UL 1703 | 290 | 267.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.71 | 38.8 | 9.15 | 31.7 | 44.37 | -0.4 | 0 | -0.3 | 0.004 | -0.403 | 1.777 | 30.369 | 7.13 | 28.957 | [6 empty] | 2017-11-01
LONGi Green Energy Technology Co., Ltd. | LR6-60BP-290M | 290 W, 60 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 290 | 267.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.605 | 60 |  | N | 9.36 | 39.2 | 8.9 | 32.6 | 46.57 | -0.353 | 0.04 | -0.266 | 0.003 | -0.356 | 1.7288 | 32.0593 | 6.9935 | 30.4776 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-60PB-290M | 290 W Monocrystalline Module | UL 1703 | 290 | 263.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.635 | 60 | 1 | N | 9.58 | 39.7 | 8.98 | 32.3 | 48.2 | -0.391 | 0.036 | -0.284 | -0.011 | -0.381 | 1.8 | 31.43 | 7.19 | 29.46 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.19508 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60PE-290M | 290 W Monocrystalline Module | UL 1703 | 290 | 267.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.635 | 60 | 1 | N | 9.58 | 39.7 | 8.98 | 32.3 | 45.2 | -0.379 | 0.037 | -0.281 | -0.002 | -0.377 | 1.81 | 31.46 | 7.26 | 29.74 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.19635 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60-295M | 295 W 60 Cell Mono-Si PV Module | UL 1703 | 295 | 272.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.85 | 38.9 | 9.28 | 31.8 | 44.37 | -0.4 | 0 | -0.3 | 0.004 | -0.403 | 1.777 | 30.369 | 7.13 | 28.957 | [6 empty] | 2017-11-01
LONGi Green Energy Technology Co., Ltd. | LR6-60BP-295M | 295 W, 60 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 295 | 272.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.605 | 60 |  | N | 9.47 | 39.4 | 9.01 | 32.7 | 46.57 | -0.353 | 0.04 | -0.266 | 0.003 | -0.356 | 1.7502 | 32.1576 | 7.08 | 30.571 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HIB-295M | 295 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 295 | 274.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.59 | 39.6 | 9.03 | 32.7 | 46.2 | -0.335 | 0.044 | -0.269 |  |  | 1.7105 | 31.6821 | 6.9693 | 30.8874 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-60HPB-295M | 295 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 295 | 275 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 9.59 | 39.6 | 9.03 | 32.7 | 44.63 | -0.347 | 0.046 | -0.267 |  |  | 1.7225 | 31.7043 | 6.9803 | 30.6761 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60PB-295M | 295 W Monocrystalline Module | UL 1703 | 295 | 268.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.635 | 60 | 1 | N | 9.69 | 39.9 | 9.05 | 32.6 | 48.2 | -0.391 | 0.036 | -0.284 | -0.011 | -0.381 | 1.82 | 31.73 | 7.25 | 29.73 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.19576 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60PE-295M | 295 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 295 | 273.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 | 1 | N | 9.92 | 39.7 | 9.21 | 32 | 45.95 | -0.353 | 0.04 | -0.268 | -0.002 | -0.377 | 1.7898 | 31.3436 | 7.2499 | 29.9727 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.19017 | 2017-06-01 | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-60BP-300M | 300 W, 60 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 300 | 277.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.605 | 60 |  | N | 9.58 | 39.6 | 9.11 | 32.9 | 46.57 | -0.353 | 0.04 | -0.266 | 0.003 | -0.356 | 1.7696 | 32.3543 | 7.1586 | 30.758 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HBD-300M | 300 W, 120 half cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 300 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.44 | 40.3 | 9.01 | 33.3 | 43.93 | -0.334 | 0.038 | -0.263 |  |  | 1.7943 | 32.3542 | 7.2515 | 31.6281 | [6 empty] | 2019-10-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HIB-300M | 300 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 300 | 278.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.7 | 39.8 | 9.13 | 32.9 | 46.2 | -0.335 | 0.044 | -0.269 |  |  | 1.7294 | 31.8759 | 7.0465 | 31.0763 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-60HIBD-300M | 300 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 300 | 283.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.44 | 40.25 | 9.01 | 33.29 | 41.49 | -0.338 | 0.041 | -0.267 |  |  | 1.7306 | 31.8139 | 7.0879 | 31.486 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HIH-300M | 300 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 300 | 282.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.7 | 39.8 | 9.13 | 32.9 | 43.68 | -0.322 | 0.057 | -0.268 |  |  | 1.7385 | 31.5618 | 7.1456 | 31.0081 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HPB-300M | 300 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 300 | 279.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 9.7 | 39.8 | 9.13 | 32.9 | 44.63 | -0.347 | 0.046 | -0.267 |  |  | 1.7416 | 31.8982 | 7.0576 | 30.8638 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60HPH-300M | 300 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 300 | 278 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 9.7 | 39.8 | 9.13 | 32.9 | 46.48 | -0.344 | 0.041 | -0.263 |  |  | 1.7899 | 31.7929 | 7.2582 | 30.4359 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60PB-300M | 300 W Monocrystalline Module | UL 1703 | 300 | 272.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.635 | 60 | 1 | N | 9.81 | 40.1 | 9.15 | 32.8 | 48.2 | -0.391 | 0.036 | -0.284 | -0.011 | -0.381 | 1.84 | 31.92 | 7.33 | 29.91 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.19578 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60PE-300M | 300 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 300 | 278.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 | 1 | N | 9.96 | 39.9 | 9.28 | 32.3 | 45.95 | -0.353 | 0.04 | -0.268 | -0.002 | -0.377 | 1.8035 | 31.6374 | 7.305 | 30.2537 |  | Flat Plate | 0.991 | 1.65 | 1 | 0.19019 | 2017-06-01 | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-60BP-305M | 305 W, 60 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 305 | 282.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.605 | 60 |  | N | 9.69 | 39.8 | 9.22 | 33.1 | 46.57 | -0.353 | 0.04 | -0.266 | 0.003 | -0.356 | 1.791 | 32.551 | 7.245 | 30.945 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HBD-305M | 305 W, 120 half cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 305 | 285.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.55 | 40.5 | 9.12 | 33.5 | 43.93 | -0.334 | 0.038 | -0.263 |  |  | 1.8162 | 32.5485 | 7.34 | 31.8181 | [6 empty] | 2019-10-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HIB-305M | 305 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 305 | 283.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.78 | 40.1 | 9.21 | 33.1 | 46.2 | -0.335 | 0.044 | -0.269 |  |  | 1.7446 | 32.0697 | 7.1082 | 31.2653 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-60HIBD-305M | 305 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 305 | 288.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.55 | 40.46 | 9.12 | 33.46 | 41.49 | -0.338 | 0.041 | -0.267 |  |  | 1.7505 | 31.9764 | 7.1694 | 31.6468 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HIH-305M | 305 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 305 | 286.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.78 | 40.06 | 9.205 | 33.135 | 43.68 | -0.322 | 0.057 | -0.268 |  |  | 1.7528 | 31.7873 | 7.2043 | 31.2296 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HPB-305M | 305 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 305 | 284.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 9.78 | 40.1 | 9.21 | 33.1 | 44.63 | -0.347 | 0.046 | -0.267 |  |  | 1.7568 | 32.0921 | 7.1194 | 31.0514 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60HPH-305M | 305 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 305 | 282.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 9.78 | 40.1 | 9.21 | 33.1 | 46.48 | -0.344 | 0.041 | -0.263 |  |  | 1.8056 | 31.9862 | 7.3218 | 30.6209 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60PB-305M | 305 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 305 | 278.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.94 | 40.2 | 9.24 | 33 | 48.75 | -0.368 | 0.042 | -0.279 | 0 | -0.368 | 1.798 | 32.024 | 7.198 | 30.246 | [6 empty] | 2018-12-03
LONGi Green Energy Technology Co., Ltd. | LR6-60PE-305M | 305 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 305 | 282.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 | 1 | N | 9.99 | 40.2 | 9.33 | 32.7 | 45.95 | -0.353 | 0.04 | -0.268 | -0.002 | -0.377 | 1.8132 | 32.0292 | 7.3444 | 30.6283 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19041 | 2017-06-01 | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-60BP-310M | 310 W, 60 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 310 | 286.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.605 | 60 |  | N | 10.05 | 40.2 | 9.44 | 32.9 | 46.57 | -0.353 | 0.04 | -0.266 | 0.003 | -0.356 | 1.8337 | 32.3543 | 7.4179 | 30.758 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HBD-310M | 310 W, 120 half cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 310 | 290.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.66 | 40.7 | 9.23 | 33.6 | 43.93 | -0.334 | 0.038 | -0.263 |  |  | 1.8381 | 32.6457 | 7.4286 | 31.913 | [6 empty] | 2019-10-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HIB-310M | 310 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.86 | 40.3 | 9.3 | 33.3 | 46.2 | -0.335 | 0.044 | -0.269 |  |  | 1.7616 | 32.2635 | 7.1777 | 31.4542 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-60HIBD-310M | 310 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 310 | 293 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.66 | 40.67 | 9.23 | 33.63 | 41.49 | -0.338 | 0.041 | -0.267 |  |  | 1.7725 | 32.1388 | 7.2596 | 31.8076 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HIH-310M | 310 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 310 | 291.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.86 | 40.34 | 9.299 | 33.34 | 43.68 | -0.322 | 0.057 | -0.268 |  |  | 1.7707 | 31.9839 | 7.2779 | 31.4228 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HPB-310M | 310 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 289.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 9.86 | 40.3 | 9.3 | 33.3 | 44.63 | -0.347 | 0.046 | -0.267 |  |  | 1.774 | 32.286 | 7.189 | 31.239 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60HPH-310M | 310 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 310 | 287.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 9.86 | 40.3 | 9.3 | 33.3 | 46.48 | -0.344 | 0.041 | -0.263 |  |  | 1.8232 | 32.1795 | 7.3933 | 30.806 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60PB-310M | 310 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 283.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 9.98 | 40.3 | 9.35 | 33.2 | 48.75 | -0.368 | 0.042 | -0.279 | 0 | -0.368 | 1.8194 | 32.2181 | 7.2837 | 30.4293 | [6 empty] | 2018-12-03
LONGi Green Energy Technology Co., Ltd. | LR6-60PE-310M | 310 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 310 | 287.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 | 1 | N | 10.02 | 40.5 | 9.36 | 33.1 | 45.95 | -0.353 | 0.04 | -0.268 |  |  | 1.819 | 32.421 | 7.368 | 31.003 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-60BP-315M | 315 W, 60 cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 315 | 291.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.605 | 60 |  | N | 10.14 | 40.4 | 9.52 | 33.1 | 46.57 | -0.353 | 0.04 | -0.266 | 0.003 | -0.356 | 1.8493 | 32.551 | 7.4807 | 30.945 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HBD-315M | 315 W, 120 half cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 315 | 295.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.75 | 40.9 | 9.32 | 33.8 | 43.93 | -0.334 | 0.038 | -0.263 |  |  | 1.856 | 32.84 | 7.501 | 32.103 | [6 empty] | 2019-10-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HIB-315M | 315 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 315 | 293.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.94 | 40.6 | 9.36 | 33.7 | 46.2 | -0.335 | 0.044 | -0.269 |  |  | 1.773 | 32.651 | 7.224 | 31.832 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-60HIBD-315M | 315 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 315 | 297.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.75 | 40.91 | 9.32 | 33.83 | 41.49 | -0.338 | 0.041 | -0.267 |  |  | 1.7898 | 32.33 | 7.3303 | 31.9968 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HIH-315M | 315 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 315 | 296.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.94 | 40.63 | 9.357 | 33.666 | 43.68 | -0.322 | 0.057 | -0.268 |  |  | 1.7817 | 32.2967 | 7.3233 | 31.7301 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HPB-315M | 315 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 315 | 294.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 9.94 | 40.6 | 9.36 | 33.7 | 44.63 | -0.347 | 0.046 | -0.267 |  |  | 1.7854 | 32.6738 | 7.2354 | 31.6142 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60HPH-315M | 315 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 315 | 292.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 9.94 | 40.6 | 9.36 | 33.7 | 46.48 | -0.344 | 0.041 | -0.263 |  |  | 1.835 | 32.566 | 7.441 | 31.176 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60PB-315M | 315 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 315 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 10.1 | 40.5 | 9.43 | 33.4 | 48.75 | -0.368 | 0.042 | -0.279 | 0 | -0.368 | 1.835 | 32.4122 | 7.346 | 30.6126 | [6 empty] | 2018-12-03
LONGi Green Energy Technology Co., Ltd. | LR6-60PE-315M | 315 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 292.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 | 1 | N | 10.05 | 40.8 | 9.41 | 33.5 | 45.95 | -0.353 | 0.04 | -0.268 |  |  | 1.8287 | 32.8128 | 7.4074 | 31.3777 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-60HBD-320M | 320 W, 120 half cut cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 320 | 300.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.86 | 41.1 | 9.42 | 34 | 43.93 | -0.334 | 0.038 | -0.263 |  |  | 1.8759 | 33.0343 | 7.5815 | 32.293 | [6 empty] | 2019-10-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HIB-320M | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 298 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.02 | 40.9 | 9.43 | 33.9 | 46.2 | -0.335 | 0.044 | -0.269 |  |  | 1.7863 | 32.8448 | 7.278 | 32.0209 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-60HIBD-320M | 320 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 320 | 302.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 2 | N | 9.86 | 41.13 | 9.42 | 34.01 | 41.49 | -0.338 | 0.041 | -0.267 |  |  | 1.809 | 32.502 | 7.409 | 32.167 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HIH-320M | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 320 | 301.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.02 | 40.93 | 9.432 | 33.928 | 43.68 | -0.322 | 0.057 | -0.268 |  |  | 1.796 | 32.548 | 7.382 | 31.977 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-60HPB-320M | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 298.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 10.02 | 40.9 | 9.43 | 33.9 | 44.63 | -0.347 | 0.046 | -0.267 |  |  | 1.7988 | 32.8677 | 7.2895 | 31.8019 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60HPH-320M | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 320 | 297 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.623 | 60 | 2 | N | 10.02 | 40.9 | 9.43 | 33.9 | 46.48 | -0.344 | 0.041 | -0.263 |  |  | 1.8487 | 32.7593 | 7.4966 | 31.361 | [6 empty] | 2019-04-15
LONGi Green Energy Technology Co., Ltd. | LR6-60PB-320M | 320 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 293.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 |  | N | 10.19 | 40.8 | 9.52 | 33.6 | 48.75 | -0.368 | 0.042 | -0.279 | 0 | -0.368 | 1.8525 | 32.6063 | 7.4161 | 30.7959 | [6 empty] | 2018-12-03
LONGi Green Energy Technology Co., Ltd. | LR6-60PE-320M | 320 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 320 | 297.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.583 | 60 | 1 | N | 10.14 | 41 | 9.5 | 33.7 | 45.95 | -0.353 | 0.04 | -0.268 |  |  | 1.8462 | 33.0087 | 7.4782 | 31.565 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-72-320M | 320 W Monocrystalline Module | UL 1703 | 320 | 292.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.27 | 44.42 | 8.66 | 36.97 | 45.4 | -0.411 | 0.043 | -0.311 | -0.003 | -0.409 | 1.73 | 35.69 | 6.99 | 33.84 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19295 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HV-320M | 320 W Monocrystalline Module | UL 1703 | 320 | 292.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.07 | 45.8 | 8.58 | 37.3 | 45.8 | -0.408 | 0.041 | -0.309 | -0.002 | -0.408 | 1.72 | 35.98 | 6.89 | 34.06 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19339 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HIH-325M | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 325 | 306.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.12 | 41.13 | 9.52 | 34.128 | 43.68 | -0.322 | 0.057 | -0.268 |  |  | 1.8133 | 32.7399 | 7.4532 | 32.1655 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-72-325M | 325 W Monocrystalline Module | UL 1703 | 325 | 297.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.3 | 44.51 | 8.79 | 36.99 | 45.4 | -0.411 | 0.043 | -0.311 | -0.003 | -0.409 | 1.75 | 35.71 | 7.09 | 33.86 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19228 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HV-325M | 325 W Monocrystalline Module | UL 1703 | 325 | 296.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.18 | 46 | 8.67 | 37.5 | 45.8 | -0.408 | 0.041 | -0.309 | -0.002 | -0.408 | 1.73 | 36.17 | 6.96 | 34.24 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19254 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-60HIH-330M | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 330 | 311 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.19 | 41.4 | 9.61 | 34.4 | 43.68 | -0.322 | 0.057 | -0.268 |  |  | 1.8299 | 33.0008 | 7.5213 | 32.4219 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR6-72-330M | 330 W Monocrystalline Module | UL 1703 | 330 | 301.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.34 | 44.56 | 8.89 | 37.11 | 45.4 | -0.411 | 0.043 | -0.311 | -0.003 | -0.409 | 1.77 | 35.82 | 7.18 | 33.97 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19213 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HV-330M | 330 W Monocrystalline Module | UL 1703 | 330 | 301.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.3 | 46.1 | 8.78 | 37.59 | 45.8 | -0.408 | 0.041 | -0.309 | -0.002 | -0.408 | 1.76 | 36.26 | 7.05 | 34.33 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19339 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-60HPB-335M | 335 W, 120 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 335 | 312 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.812 | 60 | 2 | N | 10.76 | 39.9 | 10.25 | 32.7 | 45.55 | -0.337 | 0.044 | -0.269 | 1.9506 |  | 1.9506 | 31.9792 | 7.9184 | 30.9481 | [6 empty] | 2019-10-15
LONGi Green Energy Technology Co., Ltd. | LR6-72-335M | 335 W Monocrystalline Module | UL 1703 | 335 | 306.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.45 | 44.6 | 9 | 37.21 | 45.4 | -0.411 | 0.043 | -0.311 | -0.003 | -0.409 | 1.8 | 35.92 | 7.27 | 34.06 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.193 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HV-335M | 335 W Monocrystalline Module | UL 1703 | 335 | 306.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.4 | 46.3 | 8.89 | 37.7 | 45.8 | -0.408 | 0.041 | -0.309 | -0.002 | -0.408 | 1.78 | 36.37 | 7.14 | 34.43 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19325 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-60HPB-340M | 340 W, 120 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 340 | 316.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.812 | 60 | 2 | N | 10.84 | 40.1 | 10.34 | 32.9 | 45.55 | -0.337 | 0.044 | -0.269 | 1.9677 |  | 1.9677 | 32.1748 | 7.9879 | 31.1374 | [6 empty] | 2019-10-15
LONGi Green Energy Technology Co., Ltd. | LR6-72-340M | 340 W Monocrystalline Module | UL 1703 | 340 | 311.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.58 | 45.66 | 9.13 | 37.26 | 45.4 | -0.411 | 0.043 | -0.311 | -0.003 | -0.409 | 1.82 | 35.97 | 7.37 | 34.1 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19255 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HV-340M | 340 W Monocrystalline Module | UL 1703 | 340 | 310.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.49 | 46.5 | 8.97 | 37.9 | 45.8 | -0.408 | 0.041 | -0.309 | -0.002 | -0.408 | 1.79 | 36.56 | 7.2 | 34.61 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19248 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PE-340M | 340 W Monocrystalline Module | UL 1703 | 340 | 310.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.36 | 47.2 | 8.81 | 38.6 | 45.8 | -0.416 | 0.038 | -0.289 | -0.038 | -0.385 | 1.79 | 37.73 | 7.02 | 35.62 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19864 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PH-340M | 340 W Monocrystalline Module | UL 1703 | 340 | 313 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.36 | 47.2 | 8.81 | 38.6 | 45.8 | -0.379 | 0.038 | -0.283 | 0.001 | -0.38 | 1.76 | 37.72 | 7.09 | 35.64 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19526 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-60HBD-345M | 345 W, 120 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 345 | 321.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 10.88 | 40.7 | 10.24 | 33.7 | 46.49 | -0.326 | 0.042 | -0.268 |  |  | 1.9323 | 32.5711 | 7.9036 | 31.4078 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIBD-345M | 345 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 345 | 325.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 10.88 | 40.7 | 10.24 | 33.7 | 42.36 | -0.334 | 0.053 | -0.266 |  |  | 1.9771 | 32.0081 | 8.128 | 31.3636 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HPB-345M | 345 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 345 | 322 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.06 | 40.2 | 10.09 | 34.2 | 45.17 | -0.339 | 0.04 | -0.266 | 1.9849 |  | 1.9878 | 32.5411 | 8.0554 | 31.4611 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR6-72-345M | 345 W Monocrystalline Module | UL 1703 | 345 | 316 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.7 | 45.74 | 9.24 | 37.35 | 45.4 | -0.411 | 0.043 | -0.311 | -0.003 | -0.409 | 1.84 | 36.05 | 7.46 | 34.19 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19227 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HV-345M | 345 W Monocrystalline Module | UL 1703 | 345 | 315.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.58 | 46.7 | 9.05 | 38.1 | 45.8 | -0.408 | 0.041 | -0.309 | -0.002 | -0.408 | 1.81 | 36.75 | 7.27 | 34.79 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.1928 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PE-345M | 345 W Monocrystalline Module | UL 1703 | 345 | 315 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.46 | 47.4 | 8.92 | 38.7 | 45.8 | -0.416 | 0.038 | -0.289 | -0.038 | -0.385 | 1.81 | 37.83 | 7.11 | 35.71 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19847 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PH-345M | 345 W Monocrystalline Module | UL 1703 | 345 | 317.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.46 | 47.4 | 8.92 | 38.7 | 45.8 | -0.379 | 0.038 | -0.283 | 0.001 | -0.38 | 1.78 | 37.82 | 7.18 | 35.73 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19513 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-60HBD-350M | 350 W, 120 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 350 | 326 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 10.96 | 40.9 | 10.33 | 33.9 | 46.49 | -0.326 | 0.042 | -0.268 |  |  | 1.9497 | 32.7644 | 7.9751 | 31.5942 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIBD-350M | 350 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 350 | 330.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 10.96 | 40.9 | 10.33 | 33.9 | 42.36 | -0.334 | 0.053 | -0.266 |  |  | 1.995 | 32.1981 | 8.2015 | 31.5497 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIH-350M | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 350 | 326.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.02 | 40.5 | 10.52 | 33.3 | 44.74 | -0.344 | 0.039 | -0.271 |  |  | 2.0282 | 32.2486 | 8.2556 | 31.2753 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HPB-350M | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 350 | 326.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.16 | 40.4 | 10.18 | 34.4 | 45.17 | -0.339 | 0.04 | -0.266 | 2.002 |  | 2.0055 | 32.7314 | 8.1273 | 31.645 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-60HPH-350M | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 350 | 328 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.15 | 40.1 | 10.42 | 33.6 | 44.02 | -0.341 | 0.037 | -0.265 |  |  | 2.0401 | 32.5527 | 8.2765 | 31.5359 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR6-72BP-350M | 350 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 350 | 326.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 9.51 | 47.9 | 8.97 | 39 | 43.73 | -0.361 | 0.041 | -0.269 | 0.003 | -0.373 | 1.7678 | 38.454 | 7.1605 | 36.7331 | [6 empty] | 2018-09-04 | 2019-05-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HV-350M | 350 W Monocrystalline Module | UL 1703 | 350 | 320.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.68 | 46.9 | 9.16 | 38.2 | 45.8 | -0.408 | 0.041 | -0.309 | -0.002 | -0.408 | 1.83 | 36.85 | 7.36 | 34.88 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19267 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PE-350M | 350 W Monocrystalline Module | UL 1703 | 350 | 319.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.57 | 47.5 | 9.03 | 38.8 | 45.8 | -0.416 | 0.038 | -0.289 | -0.038 | -0.385 | 1.83 | 37.93 | 7.2 | 35.8 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19832 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PH-350M | 350 W Monocrystalline Module | UL 1703 | 350 | 322.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.57 | 47.5 | 9.03 | 38.8 | 45.8 | -0.379 | 0.038 | -0.283 | 0.001 | -0.38 | 1.81 | 37.92 | 7.27 | 35.82 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.1961 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-60HBD-355M | 355 W, 120 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 355 | 330.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.04 | 41.1 | 10.42 | 34.1 | 46.49 | -0.326 | 0.042 | -0.268 |  |  | 1.9667 | 32.9577 | 8.0446 | 31.7806 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIBD-355M | 355 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 355 | 334.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.04 | 41.1 | 10.42 | 34.1 | 42.36 | -0.334 | 0.053 | -0.266 |  |  | 2.0124 | 32.388 | 8.273 | 31.7359 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIH-355M | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 355 | 331.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.1 | 40.7 | 10.6 | 33.5 | 44.74 | -0.344 | 0.039 | -0.271 |  |  | 2.0431 | 32.4423 | 8.316 | 31.4632 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HPB-355M | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 355 | 331.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.25 | 40.6 | 10.27 | 34.6 | 45.17 | -0.339 | 0.04 | -0.266 | 2.0172 |  | 2.0232 | 32.9217 | 8.1991 | 31.829 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-60HPH-355M | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 355 | 332.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.25 | 40.3 | 10.51 | 33.8 | 44.02 | -0.341 | 0.037 | -0.265 |  |  | 2.0577 | 32.7465 | 8.348 | 31.7236 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR6-72BP-355M | 355 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 355 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 9.61 | 48.1 | 9.06 | 39.2 | 43.73 | -0.361 | 0.041 | -0.269 | 0.003 | -0.373 | 1.7856 | 38.6512 | 7.2323 | 36.9214 | [6 empty] | 2018-09-04 | 2019-05-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PE-355M | 355 W Monocrystalline Module | UL 1703 | 355 | 324.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.63 | 47.7 | 9.1 | 39.032 | 45.8 | -0.416 | 0.038 | -0.289 | -0.038 | -0.385 | 1.85 | 38.15 | 7.25 | 36.02 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19881 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PH-355M | 355 W Monocrystalline Module | UL 1703 | 355 | 327.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.63 | 47.7 | 9.1 | 39.032 | 45.8 | -0.379 | 0.038 | -0.283 | 0.001 | -0.38 | 1.82 | 38.15 | 7.32 | 36.03 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19559 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-60HBD-360M | 360 W, 120 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 360 | 335.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.11 | 41.3 | 10.5 | 34.3 | 46.49 | -0.326 | 0.042 | -0.268 |  |  | 1.981 | 33.151 | 8.103 | 31.967 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIBD-360M | 360 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 360 | 339.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.11 | 41.3 | 10.5 | 34.3 | 42.36 | -0.334 | 0.053 | -0.266 |  |  | 2.027 | 32.578 | 8.333 | 31.922 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIH-360M | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 360 | 336.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.2 | 40.9 | 10.69 | 33.7 | 44.74 | -0.344 | 0.039 | -0.271 |  |  | 2.061 | 32.636 | 8.389 | 31.651 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HPB-360M | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 360 | 336.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.33 | 40.8 | 10.35 | 34.8 | 45.17 | -0.339 | 0.04 | -0.266 | 2.0344 |  | 2.039 | 33.112 | 8.263 | 32.013 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-60HPH-360M | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 360 | 337.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.35 | 40.5 | 10.59 | 34 | 44.02 | -0.341 | 0.037 | -0.265 |  |  | 2.0734 | 32.9402 | 8.4115 | 31.9113 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR6-72BP-360M | 360 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 360 | 336 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 9.72 | 48.2 | 9.16 | 39.3 | 43.73 | -0.361 | 0.041 | -0.269 | 0.003 | -0.373 | 1.8053 | 38.7498 | 7.3122 | 37.0156 | [6 empty] | 2018-09-04 | 2019-05-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-360M | 360 W, 144 half cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 360 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.952 | 72 |  | N | 9.64 | 47.7 | 9.14 | 39.4 | 44.64 | -0.343 | 0.045 | -0.269 | 0.008 | -0.351 | 1.7676 | 38.4889 | 7.1668 | 37.2399 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-360MC | 360 W, 144 half cell bifacial monocrystalline module with DC optimizer junction box, 1500V max system Vdc | UL 1703 | 360 | 335.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.64 | 47.7 | 9.14 | 39.4 | 44.64 | -0.343 | 0.045 | -0.269 |  |  | 1.7676 | 38.4889 | 7.1668 | 37.2399 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIBD-360M | 360 W, 144 half-cell monocrystalline bifacial module, 1500V max system Vdc | UL 1703 | 360 | 335.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.64 | 47.7 | 9.14 | 39.4 | 45.69 | -0.33 | 0.049 | -0.268 |  |  | 1.7471 | 38.3559 | 7.1766 | 37.4024 | [6 empty] | 2020-01-21
LONGi Green Energy Technology Co., Ltd. | LR6-72PE-360M | 360 W Monocrystalline Module | UL 1703 | 360 | 329.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.7 | 47.9 | 9.18 | 39.196 | 45.8 | -0.416 | 0.038 | -0.289 | -0.038 | -0.385 | 1.86 | 38.31 | 7.32 | 36.17 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19794 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PH-360M | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 336 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 9.87 | 47.84 | 9.23 | 39.01 | 44.48 | -0.349 | 0.038 | -0.263 | 1.7961 | 38.2664 | 1.7961 | 38.2664 | 7.3029 | 36.5972 | [6 empty] | 2017-06-01 | 2020-02-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HBD-365M | 365 W, 120 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 340.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.18 | 41.5 | 10.58 | 34.5 | 46.49 | -0.326 | 0.042 | -0.268 |  |  | 1.9969 | 33.3443 | 8.1679 | 32.1534 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIBD-365M | 365 W, 120 half-cut cell, bifacial double glass monocrystalline module, 1500V max system Vdc | UL 61730 | 365 | 344.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.83 | 60 | 2 | N | 11.18 | 41.5 | 10.58 | 34.5 | 42.36 | -0.334 | 0.053 | -0.266 |  |  | 2.0432 | 32.768 | 8.3998 | 32.1081 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIH-365M | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 365 | 341.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.28 | 41.1 | 10.77 | 33.9 | 44.74 | -0.344 | 0.039 | -0.271 |  |  | 2.0758 | 32.8297 | 8.4494 | 31.8388 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HPB-365M | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 365 | 341.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.41 | 41 | 10.43 | 35 | 45.17 | -0.339 | 0.04 | -0.266 | 2.0496 |  | 2.0548 | 33.3023 | 8.3269 | 32.197 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-60HPH-365M | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 365 | 342.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.43 | 40.7 | 10.68 | 34.2 | 44.02 | -0.341 | 0.037 | -0.265 |  |  | 2.091 | 33.134 | 8.483 | 32.099 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR6-72BP-365M | 365 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 365 | 340.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 9.84 | 48.3 | 9.25 | 39.5 | 43.73 | -0.361 | 0.041 | -0.269 | 0.003 | -0.373 | 1.823 | 38.947 | 7.384 | 37.204 | [6 empty] | 2018-09-04 | 2019-05-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-365M | 365 W, 144 half cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 365 | 340.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.952 | 72 |  | N | 9.72 | 47.9 | 9.22 | 39.6 | 44.64 | -0.343 | 0.045 | -0.269 | 0.008 | -0.351 | 1.7831 | 38.6843 | 7.2295 | 37.4289 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-365MC | 365 W, 144 half cell bifacial monocrystalline module with DC optimizer junction box, 1500V max system Vdc | UL 1703 | 365 | 340.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.72 | 47.9 | 9.22 | 39.6 | 44.64 | -0.343 | 0.045 | -0.269 |  |  | 1.7831 | 38.6842 | 7.2295 | 37.4289 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIBD-365M | 365 W, 144 half-cell monocrystalline bifacial module, 1500V max system Vdc | UL 1703 | 365 | 340.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.72 | 47.9 | 9.22 | 39.6 | 45.69 | -0.33 | 0.049 | -0.268 |  |  | 1.7624 | 38.5506 | 7.2394 | 37.5923 | [6 empty] | 2020-01-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIH-365M | 365 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 339.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.71 | 48.4 | 9.13 | 40 | 46.89 | -0.324 | 0.055 | -0.267 |  |  | 1.7698 | 38.3461 | 7.2449 | 37.1235 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-365M | 365 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 343.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 9.71 | 48.4 | 9.13 | 40 | 42.59 | -0.343 | 0.041 | -0.267 | 1.785 | 38.1754 | 1.785 | 38.1754 | 7.2357 | 37.2207 | [6 empty] | 2019-05-15 | 2020-02-11
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-365MC | 365 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 343.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.71 | 48.4 | 9.13 | 40 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.785 | 38.1754 | 7.2357 | 37.2207 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72PE-365M | 365 W Monocrystalline Module | UL 1703 | 365 | 333.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.74 | 48 | 9.29 | 39.3 | 45.8 | -0.416 | 0.038 | -0.289 | -0.038 | -0.385 | 1.88 | 38.42 | 7.4 | 36.26 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19789 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PH-365M | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 340.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 9.9 | 48.13 | 9.28 | 39.34 | 44.48 | -0.349 | 0.038 | -0.263 | 1.8058 | 38.5901 | 1.8058 | 38.5901 | 7.3421 | 36.9068 | [6 empty] | 2017-06-01 | 2020-02-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HIH-370M | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 370 | 345.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.81 | 60 | 2 | N | 11.37 | 41.3 | 10.86 | 34.1 | 44.74 | -0.344 | 0.039 | -0.271 |  |  | 2.0938 | 33.0234 | 8.5224 | 32.0267 | [6 empty] | 2020-05-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HPB-370M | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V or 1500V max system Vdc | UL 61730 | 370 | 346 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.5 | 41.2 | 10.52 | 35.2 | 45.17 | -0.339 | 0.04 | -0.266 |  |  | 2.0725 | 33.4926 | 8.3987 | 32.381 | [6 empty] | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-60HPH-370M | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 370 | 347.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.52 | 40.9 | 10.76 | 34.4 | 44.02 | -0.341 | 0.037 | -0.265 |  |  | 2.1067 | 33.3278 | 8.5465 | 32.2867 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR6-72BP-370M | 370 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 370 | 345.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 9.95 | 48.4 | 9.35 | 39.6 | 43.73 | -0.361 | 0.041 | -0.269 | 0.003 | -0.373 | 1.8427 | 39.0456 | 7.4638 | 37.2982 | [6 empty] | 2018-09-04 | 2019-05-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-370M | 370 W, 144 half cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 370 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.952 | 72 |  | N | 9.8 | 48.1 | 9.3 | 39.8 | 44.64 | -0.343 | 0.045 | -0.269 | 0.008 | -0.351 | 1.7985 | 38.8796 | 7.2923 | 37.618 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-370MC | 370 W, 144 half cell bifacial monocrystalline module with DC optimizer junction box, 1500V max system Vdc | UL 1703 | 370 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.8 | 48.1 | 9.3 | 39.8 | 44.64 | -0.343 | 0.045 | -0.269 |  |  | 1.7985 | 38.8796 | 7.2923 | 37.618 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIBD-370M | 370 W, 144 half-cell monocrystalline bifacial module, 1500V max system Vdc | UL 1703 | 370 | 345.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.8 | 48.1 | 9.3 | 39.8 | 45.69 | -0.33 | 0.049 | -0.268 |  |  | 1.7777 | 38.7453 | 7.3022 | 37.7821 | [6 empty] | 2020-01-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIH-370M | 370 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 344.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.79 | 48.6 | 9.21 | 40.2 | 46.89 | -0.324 | 0.055 | -0.267 |  |  | 1.7854 | 38.5378 | 7.3084 | 37.3091 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-370M | 370 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 348.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 9.79 | 48.6 | 9.21 | 40.2 | 42.59 | -0.343 | 0.041 | -0.267 | 1.8007 | 38.3662 | 1.8007 | 38.3662 | 7.2991 | 37.4068 | [6 empty] | 2019-05-15 | 2020-02-11
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-370MC | 370 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 348.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.79 | 48.6 | 9.21 | 40.2 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.8007 | 38.3662 | 7.2991 | 37.4068 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72PE-370M | 370 W Monocrystalline Module | UL 1703 | 370 | 338.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.938 | 72 | 1 | N | 9.84 | 48.3 | 9.39 | 39.4 | 45.8 | -0.416 | 0.038 | -0.289 | -0.038 | -0.385 | 1.91 | 38.51 | 7.48 | 36.36 |  | Flat Plate | 0.991 | 1.956 | 1 | 0.19879 | 2017-06-01
LONGi Green Energy Technology Co., Ltd. | LR6-72PH-370M | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 345.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 9.93 | 48.4 | 9.32 | 39.69 | 44.48 | -0.349 | 0.038 | -0.263 | 1.8144 | 38.9334 | 1.8144 | 38.9334 | 7.3771 | 37.2351 | [6 empty] | 2017-06-01 | 2020-02-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HPH-375M | 375 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 375 | 352 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.6 | 41.1 | 10.84 | 34.6 | 44.02 | -0.341 | 0.037 | -0.265 |  |  | 2.1223 | 33.5215 | 8.6101 | 32.4744 | [6 empty] | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR6-72BP-375M | 375 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 375 | 350.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 10.03 | 48.6 | 9.43 | 39.8 | 43.73 | -0.361 | 0.041 | -0.269 |  |  | 1.8585 | 39.2428 | 7.5277 | 37.4866 | [6 empty] | 2019-05-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-375M | 370 W, 144 half cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 375 | 350.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.87 | 48.3 | 9.38 | 40 | 44.64 | -0.343 | 0.045 | -0.269 | 0.008 | -0.351 | 1.814 | 39.075 | 7.355 | 37.807 | [6 empty] | 2019-02-01 | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-375MC | 375 W, 144 half cell bifacial monocrystalline module with DC optimizer junction box, 1500V max system Vdc | UL 1703 | 375 | 350.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.87 | 48.3 | 9.38 | 40 | 44.64 | -0.343 | 0.045 | -0.269 |  |  | 1.814 | 39.075 | 7.355 | 37.807 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIBD-375M | 375 W, 144 half-cell monocrystalline bifacial module, 1500V max system Vdc | UL 1703 | 375 | 349.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.87 | 48.3 | 9.38 | 40 | 45.69 | -0.33 | 0.049 | -0.268 |  |  | 1.793 | 38.94 | 7.365 | 37.972 | [6 empty] | 2020-01-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIH-375M | 375 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 349 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.87 | 48.8 | 9.28 | 40.4 | 46.89 | -0.324 | 0.055 | -0.267 |  |  | 1.7989 | 38.7295 | 7.364 | 37.4948 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-375M | 375 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 352.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 9.87 | 48.8 | 9.28 | 40.4 | 42.59 | -0.343 | 0.041 | -0.267 | 1.8144 | 38.5571 | 1.8144 | 38.5571 | 7.3546 | 37.5929 | [6 empty] | 2019-05-15 | 2020-02-11
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-375MC | 375 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 352.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.87 | 48.8 | 9.28 | 40.4 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.8144 | 38.5571 | 7.3546 | 37.5929 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72PH-375M | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 350.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 9.96 | 48.71 | 9.36 | 40.08 | 44.48 | -0.349 | 0.038 | -0.263 | 1.821 | 39.316 | 1.821 | 39.316 | 7.404 | 37.601 | [6 empty] | 2017-06-01 | 2020-02-11
LONGi Green Energy Technology Co., Ltd. | LR4-60HPH-380M | 380 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 380 | 356.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.69 | 41.3 | 10.92 | 34.8 | 44.02 | -0.341 | 0.037 | -0.265 |  |  | 2.138 | 33.7153 | 8.6736 | 32.6621 | [6 empty] | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR6-72BP-380M | 380 W, 72 cell double glass bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 380 | 355.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 10.11 | 48.8 | 9.51 | 40 | 43.73 | -0.361 | 0.041 | -0.269 |  |  | 1.8742 | 39.44 | 7.5916 | 37.6749 | [6 empty] | 2019-05-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-380M | 380 W, 144 half cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 380 | 355.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.952 | 72 |  | N | 9.97 | 48.5 | 9.47 | 40.2 | 44.64 | -0.343 | 0.045 | -0.269 | 0.008 | -0.351 | 1.8314 | 39.2704 | 7.4256 | 37.996 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-380MC | 380 W, 144 half cell bifacial monocrystalline module with DC optimizer junction box, 1500V max system Vdc | UL 1703 | 380 | 355.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.97 | 48.5 | 9.47 | 40.2 | 44.64 | -0.343 | 0.045 | -0.269 |  |  | 1.8314 | 39.2704 | 7.4256 | 37.996 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIBD-380M | 380 W, 144 half-cell monocrystalline bifacial module, 1500V max system Vdc | UL 1703 | 380 | 354.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.97 | 48.5 | 9.47 | 40.2 | 45.69 | -0.33 | 0.049 | -0.268 |  |  | 1.8102 | 39.1347 | 7.4357 | 38.1619 | [6 empty] | 2020-01-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIH-380M | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 353.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.96 | 49 | 9.36 | 40.6 | 46.89 | -0.324 | 0.055 | -0.267 |  |  | 1.8144 | 38.9213 | 7.4275 | 37.6804 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-380M | 380 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 357.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.96 | 49 | 9.36 | 40.6 | 42.59 | -0.343 | 0.041 | -0.267 | 1.83 | 38.748 | 1.83 | 38.748 | 7.418 | 37.779 | [6 empty] | 2019-05-15 | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-380MC | 380 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 357.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 9.96 | 49 | 9.36 | 40.6 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.83 | 38.748 | 7.418 | 37.779 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72PH-380M | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 355.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.88 | 72 | 1 | N | 10 | 49.03 | 9.4 | 40.41 | 44.48 | -0.349 | 0.038 | -0.263 | 1.8293 | 39.6397 | 1.8293 | 39.6397 | 7.4378 | 37.9106 | [6 empty] | 2019-06-03 | 2020-02-11
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-385M | 385 W, 144 half cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 385 | 359.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.952 | 72 |  | N | 10.03 | 48.7 | 9.53 | 40.4 | 44.64 | -0.343 | 0.045 | -0.269 | 0.008 | -0.351 | 1.843 | 39.4657 | 7.4726 | 38.1851 | [6 empty] | 2019-02-01
LONGi Green Energy Technology Co., Ltd. | LR6-72HBD-385MC | 385 W, 144 half cell bifacial monocrystalline module with DC optimizer junction box, 1500V max system Vdc | UL 1703 | 385 | 359.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.03 | 48.7 | 9.53 | 40.4 | 44.64 | -0.343 | 0.045 | -0.269 |  |  | 1.843 | 39.4657 | 7.4726 | 38.1851 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIBD-385M | 385 W, 144 half-cell monocrystalline bifacial module, 1500V max system Vdc | UL 1703 | 385 | 359.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.03 | 48.7 | 9.53 | 40.4 | 45.69 | -0.33 | 0.049 | -0.268 |  |  | 1.8217 | 39.3294 | 7.4828 | 38.3517 | [6 empty] | 2020-01-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIH-385M | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 358.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 10.03 | 49.2 | 9.43 | 40.8 | 46.89 | -0.324 | 0.055 | -0.267 |  |  | 1.828 | 39.113 | 7.483 | 37.866 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-385M | 385 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 362.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 10.03 | 49.2 | 9.43 | 40.8 | 42.59 | -0.343 | 0.041 | -0.267 | 1.8437 | 38.9389 | 1.8437 | 38.9389 | 7.4735 | 37.9651 | [6 empty] | 2019-05-15 | 2020-02-11
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-385MC | 385 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 362.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 10.03 | 49.2 | 9.43 | 40.8 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.8437 | 38.9389 | 7.4735 | 37.9651 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-72HIH-390M | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 363.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 10.12 | 49.5 | 9.52 | 41 | 46.89 | -0.324 | 0.055 | -0.267 |  |  | 1.8454 | 39.3047 | 7.5544 | 38.0516 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-390M | 390 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 367.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 10.12 | 49.5 | 9.52 | 41 | 42.59 | -0.343 | 0.041 | -0.267 | 1.8613 | 39.1298 | 1.8613 | 39.1298 | 7.5448 | 38.1512 | [6 empty] | 2019-05-15
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-390MC | 390 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 367.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 10.12 | 49.5 | 9.52 | 41 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.8613 | 39.1298 | 7.5448 | 38.1512 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-78HBD-390M | 390W, 156 half cell Bifacial Mono-Si PV Module, 1500V max system dc | UL 1703 | 390 | 364.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.108 | 78 | 2 | N | 9.744 | 51.935 | 8.99 | 43.435 | 44.81 | -0.337 | 0.047 | -0.268 |  |  | 1.7455 | 41.623 | 7.0954 | 40.3834 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-72HIH-395M | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 368.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 10.18 | 49.7 | 9.57 | 41.3 | 46.89 | -0.324 | 0.055 | -0.267 |  |  | 1.8551 | 39.5923 | 7.5941 | 38.33 | [6 empty] | 2020-02-03
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-395M | 395 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 372.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.936 | 72 | 2 | N | 10.18 | 49.7 | 9.57 | 41.3 | 42.59 | -0.343 | 0.041 | -0.267 | 1.8711 | 39.4161 | 1.8711 | 39.4161 | 7.5844 | 38.4304 | [6 empty] | 2019-05-15
LONGi Green Energy Technology Co., Ltd. | LR6-72HPH-395MC | 395 W, 144 half cut cell monocrystalline module with DC optimizer junction box, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 372.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 2 | N | 10.18 | 49.7 | 9.57 | 41.3 | 42.59 | -0.343 | 0.041 | -0.267 |  |  | 1.8711 | 39.4161 | 7.5844 | 38.4304 | [6 empty] | 2020-02-21
LONGi Green Energy Technology Co., Ltd. | LR6-78HBD-395M | 395W, 156 half cell Bifacial Mono-Si PV Module, 1500V max system dc | UL 1703 | 395 | 369 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.108 | 78 | 2 | N | 9.815 | 52.145 | 9.06 | 43.6495 | 44.81 | -0.337 | 0.047 | -0.268 |  |  | 1.7591 | 41.8285 | 7.1506 | 40.5829 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-78HBD-400M | 400W, 156 half cell Bifacial Mono-Si PV Module, 1500V max system dc | UL 1703 | 400 | 373.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.108 | 78 | 2 | N | 9.8793 | 52.376 | 9.14 | 43.832 | 44.81 | -0.337 | 0.047 | -0.268 |  |  | 1.7747 | 42.0034 | 7.2138 | 40.7526 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-78HBD-405M | 405W, 156 half cell Bifacial Mono-Si PV Module, 1500V max system dc | UL 1703 | 405 | 378.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.108 | 78 | 2 | N | 9.953 | 52.5896 | 9.208 | 43.985 | 44.81 | -0.337 | 0.047 | -0.268 |  |  | 1.7879 | 42.15 | 7.2674 | 40.8948 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR6-78HBD-410M | 410W, 156 half cell Bifacial Mono-Si PV Module, 1500V max system dc | UL 1703 | 410 | 383.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.108 | 78 | 2 | N | 10.022 | 52.812 | 9.286 | 44.153 | 44.81 | -0.337 | 0.047 | -0.268 |  |  | 1.803 | 42.311 | 7.329 | 41.051 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR4-72HBD-415M | 415 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 388.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 10.89 | 49 | 10.23 | 40.6 | 44.84 | -0.331 | 0.041 | -0.259 |  |  | 2.0031 | 39.4582 | 8.122 | 38.1373 | [6 empty] | 2020-03-11 | 2020-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-72HIBD-415M | 415 W, 144 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 415 | 390.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 10.89 | 49 | 10.23 | 40.6 | 43.11 | -0.329 | 0.049 | -0.266 |  |  | 1.9797 | 38.569 | 8.1843 | 37.9105 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR6-78HBD-415M | 415W, 156 half cell Bifacial Mono-Si PV Module, 1500V max system dc | UL 1703 | 415 | 388.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.108 | 78 | 2 | N | 10.102 | 53.032 | 9.353 | 44.373 | 44.81 | -0.337 | 0.047 | -0.268 |  |  | 1.816 | 42.5218 | 7.3819 | 41.2555 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR4-72HBD-420M | 420 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 420 | 393.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 10.96 | 49.2 | 10.3 | 40.8 | 44.84 | -0.331 | 0.041 | -0.259 |  |  | 2.0168 | 39.6526 | 8.1776 | 38.3251 | [6 empty] | 2020-03-11 | 2020-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-72HIBD-420M | 420 W, 144 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 420 | 395.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 10.96 | 49.2 | 10.3 | 40.8 | 43.11 | -0.329 | 0.049 | -0.266 |  |  | 1.9933 | 38.759 | 8.2403 | 38.0972 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR4-72HIH-420M | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 420 | 391.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.0368 | 48.8 | 10.4478 | 40.2 | 45.62 | -0.34 | 0.04 | -0.269 |  |  | 2.0206 | 38.7564 | 8.2478 | 37.5464 | [6 empty] | 2020-03-23
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-420M | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 420 | 392.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.16 | 48.1 | 10.43 | 40.3 | 45.1 | -0.334 | 0.041 | -0.265 | 2.0604 |  | 2.0299 | 38.8266 | 8.2385 | 37.4907 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR6-78HBD-420M | 420W, 156 half cell Bifacial Mono-Si PV Module, 1500V max system dc | UL 1703 | 420 | 392.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.108 | 78 | 2 | N | 10.182 | 53.249 | 9.419 | 44.593 | 44.81 | -0.337 | 0.047 | -0.268 |  |  | 1.8288 | 42.7326 | 7.434 | 41.4601 | [6 empty] | 2019-03-15
LONGi Green Energy Technology Co., Ltd. | LR4-72HBD-425M | 425 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 398.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.22 | 48.7 | 10.52 | 40.4 | 44.84 | -0.331 | 0.041 | -0.259 |  |  | 2.0599 | 39.2639 | 8.3523 | 37.9494 | [6 empty] | 2020-03-11 | 2020-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-72HIBD-425M | 425 W, 144 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 425 | 400.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.02 | 49.4 | 10.37 | 41 | 43.11 | -0.329 | 0.049 | -0.266 |  |  | 2.006 | 38.949 | 8.293 | 38.284 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR4-72HIH-425M | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 425 | 396 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.1084 | 49 | 10.5198 | 40.4 | 45.62 | -0.34 | 0.04 | -0.269 |  |  | 2.0345 | 38.9492 | 8.3047 | 37.7332 | [6 empty] | 2020-03-23
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-425M | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 425 | 397.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.23 | 48.3 | 10.5 | 40.5 | 45.1 | -0.334 | 0.041 | -0.265 | 2.0742 |  | 2.0435 | 39.0192 | 8.2938 | 37.6768 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-72HBD-430M | 430 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 402.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.3 | 48.9 | 10.6 | 40.6 | 44.84 | -0.331 | 0.041 | -0.259 |  |  | 2.0755 | 39.4582 | 8.4158 | 38.1373 | [6 empty] | 2020-03-11 | 2020-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-72HIBD-430M | 430 W, 144 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 405.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.09 | 49.6 | 10.44 | 41.2 | 43.11 | -0.329 | 0.049 | -0.266 |  |  | 2.0197 | 39.139 | 8.3498 | 38.4708 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR4-72HIH-430M | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 430 | 400.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.19 | 49.2 | 10.6 | 40.6 | 45.62 | -0.34 | 0.04 | -0.269 |  |  | 2.05 | 39.142 | 8.368 | 37.92 | [6 empty] | 2020-03-23
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-430M | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 430 | 402.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.31 | 48.5 | 10.57 | 40.7 | 45.1 | -0.334 | 0.041 | -0.265 | 2.09 |  | 2.0571 | 39.2119 | 8.3491 | 37.8628 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-72HBD-435M | 435 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 407.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.36 | 49.1 | 10.66 | 40.8 | 44.84 | -0.331 | 0.041 | -0.259 |  |  | 2.0873 | 39.6526 | 8.4634 | 38.3251 | [6 empty] | 2020-03-11 | 2020-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-72HIBD-435M | 435 W, 144 half-cut cell, bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 410 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.16 | 49.8 | 10.51 | 41.4 | 43.11 | -0.329 | 0.049 | -0.266 |  |  | 2.0334 | 39.329 | 8.4061 | 38.6575 | [6 empty] | 2020-03-11
LONGi Green Energy Technology Co., Ltd. | LR4-72HIH-435M | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 435 | 405.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.26 | 49.4 | 10.67 | 40.8 | 45.62 | -0.34 | 0.04 | -0.269 |  |  | 2.0635 | 39.3348 | 8.4233 | 38.1068 | [6 empty] | 2020-03-23
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-435M | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 435 | 407.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.39 | 48.7 | 10.64 | 40.9 | 45.1 | -0.334 | 0.041 | -0.265 | 2.1038 |  | 2.0708 | 39.4046 | 8.4044 | 38.0489 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-72HBD-440M | 440 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 412.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.45 | 49.2 | 10.73 | 41 | 44.84 | -0.331 | 0.041 | -0.259 |  |  | 2.101 | 39.847 | 8.519 | 38.513 | [6 empty] | 2020-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-72HIH-440M | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 440 | 410.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.33 | 49.6 | 10.74 | 41 | 45.62 | -0.34 | 0.04 | -0.269 |  |  | 2.0771 | 39.5276 | 8.4785 | 38.2936 | [6 empty] | 2020-03-23
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-440M | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 440 | 411.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.46 | 48.9 | 10.71 | 41.1 | 45.1 | -0.334 | 0.041 | -0.265 | 2.1176 |  | 2.0844 | 39.5973 | 8.4597 | 38.2349 | [6 empty] | 2019-10-15 | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-72HBD-445M | 445 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 417.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.52 | 49.4 | 10.8 | 41.2 | 44.84 | -0.331 | 0.041 | -0.259 |  |  | 2.1147 | 40.0414 | 8.5746 | 38.7009 | [6 empty] | 2020-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-72HIH-445M | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 445 | 415.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.4 | 49.8 | 10.8 | 41.2 | 45.62 | -0.34 | 0.04 | -0.269 |  |  | 2.0887 | 39.7205 | 8.5259 | 38.4804 | [6 empty] | 2020-03-23
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-445M | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 445 | 416.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.53 | 49.1 | 10.78 | 41.3 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.098 | 39.79 | 8.515 | 38.421 | [6 empty] | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-72HBD-450M | 450 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 422.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.58 | 49.6 | 10.87 | 41.4 | 44.84 | -0.331 | 0.041 | -0.259 |  |  | 2.1284 | 40.2358 | 8.6302 | 38.8887 | [6 empty] | 2020-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-72HIH-450M | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 450 | 419.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.17 | 72 | 2 | N | 11.5 | 50 | 10.9 | 41.4 | 45.62 | -0.34 | 0.04 | -0.269 |  |  | 2.108 | 39.9133 | 8.6048 | 38.6672 | [6 empty] | 2020-03-23
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-450M | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 450 | 421.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.6 | 49.3 | 10.85 | 41.5 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.1116 | 39.9827 | 8.5703 | 38.6071 | [6 empty] | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-72HBD-455M | 455 W, 144 half-cut cell bifacial dual-glass monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 427 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.11 | 72 | 2 | N | 11.65 | 49.8 | 10.93 | 41.6 | 44.84 | -0.331 | 0.041 | -0.259 |  |  | 2.1402 | 40.4301 | 8.6778 | 39.0766 | [6 empty] | 2020-06-01
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-455M | 455 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 455 | 426.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.66 | 49.5 | 10.92 | 41.7 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.1252 | 40.1754 | 8.6256 | 38.7931 | [6 empty] | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-460M | 460 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 460 | 431.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.73 | 49.7 | 10.98 | 41.9 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.1369 | 40.3681 | 8.673 | 38.9792 | [6 empty] | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR4-72HPH-465M | 465 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V or 1500V max system Vdc | UL 61730 | 465 | 435.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.12 | 72 | 2 | N | 11.79 | 49.9 | 11.05 | 42.1 | 45.1 | -0.334 | 0.041 | -0.265 |  |  | 2.1505 | 40.5608 | 8.7283 | 39.1652 | [6 empty] | 2020-05-21
LONGi Green Energy Technology Co., Ltd. | LR5-66HBD-475M | 475 W, 132 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 475 | 442 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 66 | 2 | N | 13.5087 | 44.8 | 12.6259 | 37.63 | 47.67 | -0.321 | 0.042 | -0.255 |  |  | 2.4972 | 36.4244 | 10.1232 | 35.0054 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-66HBD-480M | 480 W, 132 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 480 | 446.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 66 | 2 | N | 13.588 | 44.95 | 12.7051 | 37.78 | 47.67 | -0.321 | 0.042 | -0.255 |  |  | 2.5129 | 36.5696 | 10.1867 | 35.1449 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-66HBD-485M | 485 W, 132 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 485 | 451.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 66 | 2 | N | 13.67 | 45.1 | 12.79 | 37.93 | 47.67 | -0.321 | 0.042 | -0.255 |  |  | 2.5296 | 36.7148 | 10.2547 | 35.2845 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-66HBD-490M | 490 W, 132 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 490 | 456.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 66 | 2 | N | 13.7441 | 45.25 | 12.8676 | 38.08 | 47.67 | -0.321 | 0.042 | -0.255 |  |  | 2.545 | 36.86 | 10.317 | 35.424 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-66HBD-495M | 495 W, 132 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 495 | 461.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.29 | 66 | 2 | N | 13.821 | 45.4 | 12.9479 | 38.23 | 47.67 | -0.321 | 0.042 | -0.255 |  |  | 2.5609 | 37.0052 | 10.3814 | 35.5635 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-72HBD-520M | 520 W, 144 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 520 | 484.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.571 | 48.9 | 12.6675 | 41.05 | 47.34 | -0.323 | 0.041 | -0.259 |  |  | 2.4941 | 39.7166 | 10.1276 | 38.0934 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-72HBD-525M | 525 W, 144 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 525 | 489.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.65 | 49.05 | 12.75 | 41.2 | 47.34 | -0.323 | 0.041 | -0.259 |  |  | 2.5103 | 39.8617 | 10.1936 | 38.2326 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-72HBD-530M | 530 W, 144 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 530 | 493.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.7127 | 49.2 | 12.8174 | 41.35 | 47.34 | -0.323 | 0.041 | -0.259 |  |  | 2.5236 | 40.0069 | 10.2475 | 38.3718 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-72HBD-535M | 535 W, 144 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 535 | 498.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.7824 | 49.35 | 12.8956 | 41.5 | 47.34 | -0.323 | 0.041 | -0.259 |  |  | 2.539 | 40.152 | 10.31 | 38.511 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-72HBD-540M | 540 W, 144 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 540 | 503.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.8472 | 49.5 | 12.9652 | 41.65 | 47.34 | -0.323 | 0.041 | -0.259 |  |  | 2.5527 | 40.2971 | 10.3657 | 38.6502 | [6 empty] | 2021-05-03
LONGi Green Energy Technology Co., Ltd. | LR5-72HBD-545M | 545 W, 144 half-cut cell bifacial dual glass monocrystalline module, 1500V max system Vdc | UL 61730 | 545 | 508.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.49 | 72 | 2 | N | 13.9155 | 49.65 | 13.0383 | 41.8 | 47.34 | -0.323 | 0.041 | -0.259 |  |  | 2.5671 | 40.4423 | 10.4241 | 38.7894 | [6 empty] | 2021-05-03
LUMA Resources | LRSS | 60 W Polycrystalline Shingle | UL 1703 | 60 | 47.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 0.44762 | 16 | 1 | Y | 8.11 | 9.8 | 7.55 | 8.08 | 58.3 | -0.5777 | 0.0404 | -0.3658 | -0.0503 | -0.5142 | 1.5452 | 8.3139 | 6.5525 | 6.8999 | BIPV | Flat Plate | 0.33885 | 1.321 | 1 | 0.21411
Lumos | GSX 72/48 | 240 W, 48 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 240 | 221.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 12 | 4 | N | 9.99 | 31.71 | 9.32 | 25.75 | 43.38 | -0.382 | 0.036 | -0.281 |  |  | 1.79 | 25.47 | 7.23 | 24.37 | [6 empty] | 2020-02-03
Lumos | GSX260-60M | 260 W Monocrystalline Module | UL 1703 | 260 | 232.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6378 | 60 | 1 | N | 8.8 | 37.8 | 8.5 | 30.6 | 46 | -0.4796 | 0.05373 | -0.3564 | -0.01732 | -0.4685 | 1.777 | 30.4187 | 6.7777 | 28.0284 | Rack | Flat Plate | 0.995 | 1.646 | 1 | 0.2079
Lumos | GSX270-60M | 270 W Monocrystalline Module | UL 1703 | 270 | 247.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.07 | 38.45 | 8.69 | 31.06 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7301 | 29.8164 | 6.9599 | 28.0735 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19106
Lumos | GSX275-60M | 275 W Monocrystalline Module | UL 1703 | 275 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.2 | 38.77 | 8.79 | 31.29 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.75 | 30.0372 | 7.04 | 28.2813 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19115
Lumos | GSX280-60M | 280 W Monocrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.34 | 39.1 | 8.88 | 31.53 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.768 | 30.2676 | 7.112 | 28.4983 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19111
Lumos | LSX280-60M-C | 280 W Monocrystalline Module | UL 1703 | 280 | 256.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.34 | 39.1 | 8.88 | 31.53 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.768 | 30.2676 | 7.112 | 28.4983 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19111
Lumos | GSX285-60M | 285 W Monocrystalline Module | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.48 | 39.43 | 8.97 | 31.76 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7859 | 30.4884 | 7.1841 | 28.7062 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19105
Lumos | LSX285-60M-C | 285 W Monocrystalline Module | UL 1703 | 285 | 261.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.48 | 39.43 | 8.97 | 31.76 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7859 | 30.4884 | 7.1841 | 28.7062 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19105
Lumos | GSX290-60M | 290 W Monocrystalline Module | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.62 | 39.77 | 9.06 | 32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8038 | 30.7188 | 7.2562 | 28.9231 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19107
Lumos | LSX290-60M-C | 290 W Monocrystalline Module | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.62 | 39.77 | 9.06 | 32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8038 | 30.7188 | 7.2562 | 28.9231 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19107
Lumos | GSX295-60M | 295 W Monocrystalline Module | UL 1703 | 295 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.814 | 31.2838 | 7.323 | 29.5803 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
Lumos | LSX295-60M-C | 295 W Monocrystalline Module | UL 1703 | 295 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.814 | 31.2838 | 7.323 | 29.5803 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
Lumos | GSX300-60M | 300 W Monocrystalline Module | UL 1703 | 300 | 275.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8319 | 31.5167 | 7.395 | 29.8005 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19245
Lumos | LSX300-60M-C | 300 W Monocrystalline Module | UL 1703 | 300 | 275.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8319 | 31.5167 | 7.395 | 29.8005 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19245
Lumos | GSX305-60M | 305 W Monocrystalline Module | UL 1703 | 305 | 279.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 10.0618 | 40.792 | 9.3191 | 32.7286 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8475 | 31.7578 | 7.4583 | 30.0285 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
Lumos | LSX305-60M-C | 305 W Monocrystalline Module | UL 1703 | 305 | 279.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 10.0618 | 40.792 | 9.3191 | 32.7286 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8475 | 31.7578 | 7.4583 | 30.0285 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19237
Lumos | GSX340-72M | 340 W Monocrystalline Module | UL 1703 | 340 | 311.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.64 | 47.18 | 8.96 | 38.32 | 44.58 | -0.42 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7738 | 36.8198 | 7.1761 | 34.6753 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19209
Lumos | GSX345-72M | 345 W Monocrystalline Module | UL 1703 | 345 | 315.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.72 | 47.28 | 8.98 | 38.4 | 44.6 | -0.43 | 0.04 | -0.3 | -0.02 | -0.41 | 1.7777 | 36.8967 | 7.1921 | 34.7477 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19012
Lumos | GSX350-72M | 350 W Monocrystalline Module | UL 1703 | 350 | 320.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.81 | 47.37 | 9.1 | 38.48 | 44.6 | -0.43 | 0.04 | -0.3 | -0.02 | -0.41 | 1.8015 | 36.9736 | 7.2882 | 34.8201 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19031
Lumos | GSX355-72M | 355 W Monocrystalline Module | UL 1703 | 355 | 325.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.8985 | 47.4657 | 9.2082 | 38.5524 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8182 | 37.5082 | 7.381 | 35.3921 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
Lumos | GSX 72/72 | 360 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 360 | 334.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 12 | 6 | N | 9.99 | 47.6 | 9.32 | 38.6 | 43.8 | -0.37 | 0.045 | -0.279 |  |  | 1.74 | 38.08 | 7.15 | 36.5 | [6 empty] | 2020-02-03
Lumos | GSX360-72M | 360 W Monocrystalline Module | UL 1703 | 360 | 330.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.9876 | 47.5606 | 9.3193 | 38.6295 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.8401 | 37.5832 | 7.47 | 35.4629 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
Lumos | GSX365-72M | 365 W Monocrystalline Module | UL 1703 | 365 | 334.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 10.0775 | 47.6557 | 9.4299 | 38.7068 | 46.67 | -0.386 | 0.042 | -0.282 | -0.005 | -0.381 | 1.862 | 37.6584 | 7.5586 | 35.5338 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19211
Luxco | LXP-3J240W | 240 W Polycrystalline Module | UL 1703 | 240 | 217.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.43 | 37.5 | 8 | 30 | 45.4 | -0.43 | 0.05 | -0.32 | -0.005 | -0.42 | 1.5805 | 28.2896 | 6.4 | 27.3952 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.1863
Luxco | LXP-3J245W | 245 W Polycrystalline Module | UL 1741 | 245 | 222.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.58 | 37.6 | 8.14 | 30.1 | 45.4 | -0.43 | 0.05 | -0.32 | -0.005 | -0.42 | 1.6081 | 28.3839 | 6.512 | 27.4865 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18631
Luxco | LXP-3J250W | 250 W Polycrystalline Module | UL 1703 | 250 | 227.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.73 | 37.7 | 8.28 | 30.2 | 45.4 | -0.43 | 0.05 | -0.32 | -0.005 | -0.42 | 1.6358 | 28.4782 | 6.624 | 27.5778 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18634
Luxco | LXP-3J255W | 255 W Polycrystalline Module | UL 1703 | 255 | 231.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 8.89 | 37.8 | 8.42 | 30.3 | 45.4 | -0.43 | 0.05 | -0.32 | -0.005 | -0.42 | 1.6635 | 28.5725 | 6.736 | 27.6691 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18639
Luxco | LXP-3J260W | 260 W Polycrystalline Module | UL 1703 | 260 | 236.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.617 | 60 | 1 | N | 9.03 | 37.9 | 8.56 | 30.4 | 45.4 | -0.43 | 0.05 | -0.32 | -0.005 | -0.42 | 1.6911 | 28.6668 | 6.848 | 27.7604 | Rack | Flat Plate | 0.983 | 1.645 | 1 | 0.18646
Luxco | LXP-3L285W | 285 W Polycrystalline Module | UL 1703 | 285 | 259.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.38 | 44.8 | 7.92 | 36 | 44.7 | -0.43 | 0.05 | -0.32 | -0.002 | -0.42 | 1.5628 | 33.8968 | 6.3283 | 32.8256 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.18587
Luxco | LXP-3L290W | 290 W Polycrystalline Module | UL 1741 | 290 | 264.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.49 | 44.9 | 8.03 | 36.1 | 44.7 | -0.43 | 0.05 | -0.32 | -0.002 | -0.42 | 1.5845 | 33.991 | 6.4162 | 32.9167 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.18572
Luxco | LXP-3L295W | 295 W Polycrystalline Module | UL 1703 | 295 | 268.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.63 | 45 | 8.15 | 36.2 | 44.7 | -0.43 | 0.05 | -0.32 | -0.002 | -0.42 | 1.6082 | 34.0851 | 6.5121 | 33.0079 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.18581
Luxco | LXP-3L300W | 300 W Polycrystalline Module | UL 1703 | 300 | 273.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.75 | 45.1 | 8.27 | 36.3 | 44.7 | -0.43 | 0.05 | -0.32 | -0.002 | -0.42 | 1.6318 | 34.1793 | 6.6079 | 33.0991 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.18592
Luxor Solar | LX-265M/156-60+ | 265 W Monocrystalline Module | UL 1703 | 265 | 236.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.83 | 38.1 | 8.59 | 30.9 | 47.1 | -0.4718 | 0.0519 | -0.3374 | -0.0053 | -0.4565 | 1.73 | 30.86 | 6.85 | 27.56 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20146
Luxor Solar | LX-270M/156-60+ | 270 W Monocrystalline Module | UL 1703 | 270 | 241.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.89 | 38.2 | 8.71 | 31 | 47.1 | -0.4718 | 0.0519 | -0.3374 | -0.0053 | -0.4565 | 1.75 | 30.96 | 6.95 | 27.65 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20067
Luxor Solar | LX-275M/156-60+ | 275 W Monocrystalline Module | UL 1703 | 275 | 245.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 8.95 | 38.3 | 8.85 | 31.1 | 47.1 | -0.4718 | 0.0519 | -0.3374 | -0.0053 | -0.4565 | 1.78 | 31.06 | 7.06 | 27.74 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20104
Luxor Solar | LX-280M/156-60+ | 280 W Monocrystalline Module | UL 1703 | 280 | 250.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 9.23 | 38.4 | 8.96 | 31.2 | 47.1 | -0.4718 | 0.0519 | -0.3374 | -0.0053 | -0.4565 | 1.8 | 31.16 | 7.15 | 27.83 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20031
Luxor Solar | LX-280P/156-72+ | 280 W Polycrystalline Module | UL 1741 | 280 | 250.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.56 | 44 | 7.83 | 35.8 | 46.3 | -0.4609 | 0.0586 | -0.3262 | -0.0474 | -0.4215 | 1.5278 | 36.3656 | 6.2258 | 32.9825 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19843
Luxor Solar | LX-285M/156-60+ | 285 W Monocrystalline Module | UL 1703 | 285 | 255.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6236 | 60 | 1 | N | 9.37 | 38.5 | 9.12 | 31.3 | 47.1 | -0.4718 | 0.0519 | -0.3374 | -0.0053 | -0.4565 | 1.84 | 31.26 | 7.27 | 27.92 | Rack | Flat Plate | 0.99 | 1.64 | 1 | 0.20182
Luxor Solar | LX-320M/156-72+ | 320 W Monocrystalline Module | UL 1703 | 320 | 290.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.9 | 46.2 | 8.58 | 37.3 | 45.2 | -0.4432 | 0.064 | -0.3324 | -0.0012 | -0.4424 | 1.7055 | 35.7782 | 6.6718 | 32.795 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.19068
Luxor Solar | LX-325M/156-72+ | 325 W Monocrystalline Module | UL 1703 | 325 | 291.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.15 | 46 | 8.76 | 37.1 | 46.2 | -0.4781 | 0.0543 | -0.365 | -0.0139 | -0.4769 | 1.77 | 37.17 | 6.96 | 33.71 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.20243
Luxor Solar | LX-330M/156-72+ | 330 W Monocrystalline Module | UL 1703 | 330 | 296 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.19 | 46.1 | 8.85 | 37.3 | 46.2 | -0.4781 | 0.0543 | -0.365 | -0.0139 | -0.4769 | 1.79 | 37.37 | 7.04 | 33.89 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.2027
Luxor Solar | LX-335M/156-72+ | 335 W Monocrystalline Module | UL 1703 | 335 | 300.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.23 | 46.15 | 8.96 | 37.4 | 46.2 | -0.4781 | 0.0543 | -0.365 | -0.0139 | -0.4769 | 1.81 | 37.47 | 7.12 | 33.98 | Rack | Flat Plate | 0.99 | 1.96 | 1 | 0.20245
Mage Solar | POWERTEC Plus 240 / 6 PL US AC | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 216.8 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.48 | 37.26 | 7.87 | 30.54 | 45.3 | -0.451 | 0.083 | -0.353 | 0.034 | -0.485 | 1.5982 | 29.8262 | 6.3047 | 27.3846 | Rack | Flat Plate | 0.989 | 1.655 | 1 | 0.19861
Mage Solar | POWERTEC Plus 245 / 6 PL US AC | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 221.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.69 | 37.8 | 8.14 | 30.67 | 45.3 | -0.451 | 0.083 | -0.353 | 0.034 | -0.485 | 1.653 | 29.9531 | 6.521 | 27.5012 | Rack | Flat Plate | 0.989 | 1.655 | 1 | 0.20209
Mage Solar USA | Powertec Plus 250/6 PL US AC | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 226 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 72 | 1 | N | 8.66 | 37.66 | 8.01 | 31.28 | 45.3 | -0.451 | 0.083 | -0.353 | 0.034 | -0.485 | 1.6266 | 30.5489 | 6.4169 | 28.0482 | Rack | Flat Plate | 0.989 | 1.655 | 1 | 0.19876
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS605PUL-260 | 260 W, 60 cell polycrystalline module, white backsheet, silver frame | UL 1703 | 260 | 235.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.72 | 38.53 | 8.39 | 31.05 | 45.8 | -0.4369 | 0.0962 | -0.4137 | 0.0134 | -0.4484 | 1.7033 | 30.6659 | 6.8969 | 28.9426 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS605PUL-265 | 265 W, 60 cell polycrystalline module, white backsheet, silver frame | UL 1703 | 265 | 240.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.75 | 38.72 | 8.46 | 31.43 | 45.8 | -0.4369 | 0.0962 | -0.4137 | 0.0134 | -0.4484 | 1.7175 | 31.0412 | 6.9545 | 29.2968 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS605PUL-270 | 270 W, 60 cell polycrystalline module, white backsheet, silver frame | UL 1703 | 270 | 242.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.13 | 38.21 | 8.63 | 31.32 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.8001 | 30.4452 | 7.0033 | 28.1135 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS605PUL-275 | 275 W, 60 cell polycrystalline module, white backsheet, silver frame | UL 1703 | 275 | 247.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.22 | 38.45 | 8.73 | 31.54 | 47.4 | -0.4387 | 0.0549 | -0.331 | -0.023 | -0.4178 | 1.821 | 30.6591 | 7.0845 | 28.3109 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS605MUL-290 | 290 W, 60 cell monocrystalline module, white backsheet, silver frame | UL 1703 | 290 | 264 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.54 | 39.45 | 9.03 | 32.15 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.9047 | 32.1858 | 7.2041 | 29.6133 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS605MUL-295 | 295 W, 60 cell monocrystalline module, white backsheet, silver frame | UL 1703 | 295 | 268.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.59 | 39.81 | 9.12 | 32.38 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8262 | 32.4161 | 7.2762 | 29.825 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS725PUL-310 | 310 W, 72 cell polycrystalline module, white backsheet, silver frame | UL 1703 | 310 | 280.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.56 | 45.42 | 8.68 | 35.8 | 46.3 | -0.4348 | 0.0899 | -0.4136 | 0.0211 | -0.4529 | 1.7669 | 35.4123 | 7.1976 | 32.6584 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS725PUL-315 | 315 W, 72 cell polycrystalline module, white backsheet, silver frame | UL 1703 | 315 | 286.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.02 | 45.55 | 8.8 | 35.83 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.71 | 35.57 | 6.81 | 32.88 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS725PUL-320 | 320 W, 72 cell polycrystalline module, white backsheet, silver frame | UL 1703 | 320 | 290.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.06 | 45.68 | 8.93 | 35.86 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.74 | 35.6 | 6.91 | 32.9 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS725PUL-325 | 325 W, 72 cell polycrystalline module, white backsheet, silver frame | UL 1703 | 325 | 295.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.1 | 45.82 | 8.95 | 36.31 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.74 | 36.05 | 6.93 | 33.32 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS725PUL-330 | 330 W, 72 cell polycrystalline module, white backsheet, silver frame | UL 1703 | 330 | 300.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 72 |  | N | 9.13 | 45.95 | 8.97 | 36.79 | 46.7 | -0.4097 | 0.0511 | -0.3113 | -0.0069 | -0.4035 | 1.74 | 36.53 | 6.94 | 33.76 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS725MUL-350 | 350 W, 72 cell monocrystalline module, white backsheet, silver frame | UL 1703 | 350 | 318.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.53 | 47.01 | 9.08 | 38.58 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8107 | 36.7868 | 7.244 | 35.6253 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS725MUL-355 | 355 W, 72 cell monocrystalline module, white backsheet, silver frame | UL 1703 | 355 | 323.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.6 | 47.31 | 9.15 | 38.82 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.825 | 37.0157 | 7.3011 | 35.8469 | [6 empty] | 2019-01-15
MAR SOLAR PANEL IMALATI VE ELEKTRIK URT. DAG. PRJ. HİZ. SAN. VE TİC. A.S. | MS725MUL-360 | 360 W, 72 cell monocrystalline module, white backsheet, silver frame | UL 1703 | 360 | 328.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 72 |  | N | 9.66 | 47.62 | 9.2 | 39.14 | 46.1 | -0.4234 | 0.0489 | -0.3211 | -0.0022 | -0.4218 | 1.8422 | 40.471 | 7.3401 | 36.009 | [6 empty] | 2019-01-15
Merlin Solar Technologies, Inc. | FXS 95-B | 95 W, 24 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 95 | 83.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.75 | 24 | 1 | N | 8.46 | 15.08 | 8.1 | 11.84 | 51.28 | -0.413 | 0.051 | -0.31 |  |  | 1.5883 | 11.6927 | 6.4265 | 10.8245 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 100-B | 100 W, 24 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 100 | 88.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.75 | 24 | 1 | N | 8.55 | 15.33 | 8.18 | 12.3 | 51.28 | -0.413 | 0.051 | -0.31 |  |  | 1.604 | 12.147 | 6.49 | 11.245 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 100-W | 100 W, 24 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 100 | 91.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.75 | 24 | 1 | N | 8.65 | 15.21 | 8.31 | 12.06 | 44.65 | -0.399 | 0.032 | -0.307 |  |  | 1.634 | 11.994 | 6.633 | 11.392 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FX105 | 105 W, 24 Cell monocrystalline module, white backsheet, 600V max system Vdc | UL 1703 | 105 | 96 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.757 | 24 | 1 | N | 8.85 | 15.4 | 8.6 | 12.5 | 45.28 | -0.395 | 0.045 | -0.31 |  |  | 1.6444 | 11.8809 | 6.713 | 11.3711 | [6 empty] | 2019-12-23
Merlin Solar Technologies, Inc. | FXS 105-W | 105 W, 24 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 105 | 96.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.75 | 24 | 1 | N | 8.81 | 15.5 | 8.5 | 12.36 | 44.65 | -0.399 | 0.032 | -0.307 |  |  | 1.6714 | 12.2924 | 6.7847 | 11.6754 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FX110 | 110 W, 24 Cell monocrystalline module, white backsheet, 600V max system Vdc | UL 1703 | 110 | 100.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.757 | 24 | 1 | N | 8.98 | 15.6 | 8.65 | 12.7 | 45.28 | -0.395 | 0.045 | -0.31 |  |  | 1.654 | 12.071 | 6.752 | 11.553 | [6 empty] | 2019-12-23
Merlin Solar Technologies, Inc. | FXS 145L-B | 145 W, 36 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 145 | 128 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.11 | 36 | 1 | N | 8.35 | 22.67 | 8.1 | 18.02 | 51.28 | -0.413 | 0.051 | -0.31 |  |  | 1.618 | 17.804 | 6.3774 | 16.38 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 145S-B | 145 W, 36 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 145 | 128.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.05 | 36 | 1 | N | 8.35 | 22.67 | 8.1 | 18.02 | 51.28 | -0.413 | 0.051 | -0.31 |  |  | 1.618 | 17.804 | 6.3774 | 16.38 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FX 150L-B | 150 W, 36 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 150 | 134.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.11 | 36 | 1 | N | 8.35 | 22.67 | 8.1 | 18.58 | 49 | -0.41 | 0.031 | -0.313 |  |  | 1.5628 | 17.6255 | 6.3656 | 16.613 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 150L-B | 150 W, 36 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 150 | 132.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.11 | 36 | 1 | N | 8.46 | 23.01 | 8.21 | 18.35 | 51.28 | -0.413 | 0.051 | -0.31 |  |  | 1.64 | 18.13 | 6.464 | 16.68 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 150L-W | 150 W, 36 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 150 | 137.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.11 | 36 | 1 | N | 8.61 | 22.67 | 8.35 | 18.02 | 44.65 | -0.399 | 0.032 | -0.307 |  |  | 1.6137 | 18.0004 | 6.5408 | 17.2079 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 150S-B | 150 W, 36 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 150 | 132.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.05 | 36 | 1 | N | 8.46 | 23.01 | 8.21 | 18.35 | 51.28 | -0.413 | 0.051 | -0.31 |  |  | 1.64 | 18.13 | 6.464 | 16.68 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 150S-W | 150 W, 36 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 150 | 137.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.05 | 36 | 1 | N | 8.61 | 22.67 | 8.35 | 18.02 | 44.65 | -0.399 | 0.032 | -0.307 |  |  | 1.6137 | 18.0004 | 6.5408 | 17.2079 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FX 155L-B | 155 W, 36 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 155 | 138.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.11 | 36 | 1 | N | 8.46 | 23.01 | 8.21 | 18.92 | 49 | -0.41 | 0.031 | -0.313 |  |  | 1.584 | 17.948 | 6.452 | 16.917 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FX155L | 155 W Monocrystalline Module | UL 1703 | 155 | 141.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.113 | 36 |  | N | 8.84 | 22.94 | 8.45 | 18.8 | 45.28 | -0.396 | 0.044 | -0.31 | 0.008 | -0.405 | 1.626 | 18.031 | 6.566 | 17.039 | [6 empty] | 2017-09-01
Merlin Solar Technologies, Inc. | FX155S | 155 W Monocrystalline Module | UL 1703 | 155 | 141.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.054 | 36 |  | N | 8.84 | 22.94 | 8.45 | 18.8 | 45.28 | -0.396 | 0.044 | -0.31 | 0.008 | -0.405 | 1.626 | 18.031 | 6.566 | 17.039 | [6 empty] | 2017-09-01
Merlin Solar Technologies, Inc. | FXS 155L-B | 155 W, 36 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 155 | 137.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.11 | 36 | 1 | N | 8.55 | 23.25 | 8.28 | 18.75 | 51.28 | -0.413 | 0.051 | -0.31 |  |  | 1.654 | 18.5252 | 6.5191 | 17.0436 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 155L-W | 155 W, 36 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 155 | 142 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.11 | 36 | 1 | N | 8.72 | 23.01 | 8.46 | 18.35 | 44.65 | -0.399 | 0.032 | -0.307 |  |  | 1.635 | 18.33 | 6.627 | 17.523 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 155S-B | 155 W, 36 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 155 | 137.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.05 | 36 | 1 | N | 8.55 | 23.25 | 8.28 | 18.75 | 51.28 | -0.413 | 0.051 | -0.31 |  |  | 1.654 | 18.5252 | 6.5191 | 17.0436 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 155S-W | 155 W, 36 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 155 | 142.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.05 | 36 | 1 | N | 8.72 | 23.01 | 8.46 | 18.35 | 44.65 | -0.399 | 0.032 | -0.307 |  |  | 1.635 | 18.33 | 6.627 | 17.523 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FX 160L-B | 160 W, 36 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 160 | 143.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.11 | 36 | 1 | N | 8.55 | 23.25 | 8.28 | 19.34 | 49 | -0.41 | 0.031 | -0.313 |  |  | 1.5975 | 18.3464 | 6.507 | 17.2925 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FX160L | 160 W Monocrystalline Module | UL 1703 | 160 | 146.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.113 | 36 |  | N | 8.88 | 23.12 | 8.55 | 18.89 | 45.28 | -0.396 | 0.044 | -0.31 | 0.008 | -0.405 | 1.626 | 18.031 | 6.566 | 17.039 | [6 empty] | 2017-09-01
Merlin Solar Technologies, Inc. | FX160S | 160 W Monocrystalline Module | UL 1703 | 160 | 146.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.054 | 36 |  | N | 8.88 | 23.12 | 8.55 | 18.89 | 45.28 | -0.396 | 0.044 | -0.31 | 0.008 | -0.405 | 1.626 | 18.031 | 6.566 | 17.039 | [6 empty] | 2017-09-01
Merlin Solar Technologies, Inc. | FXS 160L-W | 160 W, 36 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 160 | 146.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.11 | 36 | 1 | N | 8.81 | 23.25 | 8.54 | 18.75 | 44.65 | -0.399 | 0.032 | -0.307 |  |  | 1.6505 | 18.7296 | 6.6897 | 17.905 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | FXS 160S-W | 160 W, 36 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 160 | 146.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.05 | 36 | 1 | N | 8.81 | 23.25 | 8.54 | 18.75 | 44.65 | -0.399 | 0.032 | -0.307 |  |  | 1.6505 | 18.7296 | 6.6897 | 17.905 | [6 empty] | 2020-03-11
Merlin Solar Technologies, Inc. | GX160 | 160 W Monocrystalline Module | UL 1703 | 160 | 141.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.011 | 36 |  | N | 8.95 | 22.85 | 8.6 | 18.7 | 51.86 | -0.421 | 0.046 | -0.332 | 0.005 | -0.426 | 1.681 | 18.031 | 6.764 | 16.842 | [6 empty] | 2017-09-01
Merlin Solar Technologies, Inc. | FX165L | 165 W Monocrystalline Module | UL 1703 | 165 | 151 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.113 | 36 |  | N | 8.95 | 23.28 | 8.65 | 18.98 | 45.28 | -0.396 | 0.044 | -0.31 | 0.008 | -0.405 | 1.626 | 18.031 | 6.566 | 17.039 | [6 empty] | 2017-09-01
Merlin Solar Technologies, Inc. | FX165S | 165 W Monocrystalline Module | UL 1703 | 165 | 151.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.054 | 36 |  | N | 8.95 | 23.28 | 8.65 | 18.98 | 45.28 | -0.396 | 0.044 | -0.31 | 0.008 | -0.405 | 1.626 | 18.031 | 6.566 | 17.039 | [6 empty] | 2017-09-01
Merlin Solar Technologies, Inc. | GX165 | 165 W Monocrystalline Module | UL 1703 | 165 | 145.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.011 | 36 |  | N | 9.05 | 23.1 | 8.74 | 18.95 | 51.86 | -0.421 | 0.046 | -0.332 | 0.005 | -0.426 | 1.681 | 18.031 | 6.764 | 16.842 | [6 empty] | 2017-09-01
Merlin Solar Technologies, Inc. | GX170 | 170 W Monocrystalline Module | UL 1703 | 170 | 150.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.011 | 36 |  | N | 9.15 | 23.4 | 8.9 | 19.15 | 51.86 | -0.421 | 0.046 | -0.332 | 0.005 | -0.426 | 1.681 | 18.031 | 6.764 | 16.842 | [6 empty] | 2017-09-01
Merlin Solar Technologies, Inc. | BR320 | 320W Monocrystalline Module | UL 1703 | 320 | 291.7 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 |  | N | 8.95 | 45.75 | 8.77 | 36.5 | 46.21 | -0.406 | 0.048 | -0.311 | -0.001 | -0.405 | 1.724 | 36.201 | 6.905 | 34.321 | [6 empty] | 2018-02-15
Merlin Solar Technologies, Inc. | BR325 | 325W Monocrystalline Module | UL 1703 | 325 | 296.4 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 |  | N | 9.05 | 45.8 | 8.87 | 36.7 | 46.21 | -0.406 | 0.048 | -0.311 | -0.001 | -0.405 | 1.724 | 36.201 | 6.905 | 34.321 | [6 empty] | 2018-02-15
Merlin Solar Technologies, Inc. | BR330 | 330W Monocrystalline Module | UL 1703 | 330 | 301.1 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 |  | N | 9.12 | 46 | 8.94 | 37 | 46.21 | -0.406 | 0.048 | -0.311 | -0.001 | -0.405 | 1.724 | 36.201 | 6.905 | 34.321 | [6 empty] | 2018-02-15
Merlin Solar Technologies, Inc. | BR335 | 335W Monocrystalline Module | UL 1703 | 335 | 305.7 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 |  | N | 9.15 | 46.25 | 8.94 | 37.71 | 46.21 | -0.406 | 0.048 | -0.311 | -0.001 | -0.405 | 1.724 | 36.201 | 6.905 | 34.321 | [6 empty] | 2018-02-15
Merlin Solar Technologies, Inc. | BR340 | 340W Monocrystalline Module | UL 1703 | 340 | 310.4 | N/A | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 |  | N | 9.18 | 46.5 | 8.95 | 38.41 | 46.21 | -0.406 | 0.048 | -0.311 | -0.001 | -0.405 | 1.724 | 36.201 | 6.905 | 34.321 | [6 empty] | 2018-02-15
Miasole | FLEX-02 70N | 70 W Thin Film CIGS Module | UL 1703 | 70 | 60.9 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.6097 | 60 | 1 | Y | 4.33 | 24.5 | 3.77 | 19.5 | 45.8 | -0.5065 | 0.0047 | -0.3466 | -0.05 | -0.459 | 0.76 | 18.42 | 2.93 | 18.1 | BIPV | Flat Plate | 0.99 | 1.626 | 1 | 0.19999 |  | 2018-12-17
Miasole | MR-107 | 111W Thin Film CIGS Module | UL 1703 | 111 | 97.1 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.0787 | 44 | 2 | N | 6.79 | 24.9 | 5.69 | 19.4 | 49.9 | -0.446 | -0.003 | -0.358 | -0.004 | -0.0041 | 0.97978 | 17.845 | 4.3306 | 17.6832 | Rack | Flat Plate | 0.67 | 1.61 | 1 | 0.15751
Miasole | FLEX-03 120N | 120 W, 56 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 115.1 | 104.6 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 0.898 | 56 | 1 | N | 4.58 | 37.8 | 3.97 | 30.3 | 48.2 | -0.3605 | -0.0011 | -0.2412 |  |  | 0.765 | 27.983 | 3.132 | 27.948 | [6 empty] | 2021-10-21
Miasole | FLEX-02 220W | 220 W CIGS Flexible Module | UL 1703 | 220 | 194.4 |  | No Information Submitted | No Information Submitted | Thin Film | Thin Film | 1.6097 | 60 | 1 | Y | 12.91 | 25.16 | 11.41 | 19.99 | 45 | -0.5418 | -0.0451 | -0.3402 | -0.1045 | -0.4328 | 2.3 | 18.88 | 9.07 | 17.91 | BIPV | Flat Plate | 0.99 | 1.626 | 1 | 0.19738 |  | 2018-12-17
Miasole | FLEX-02-275N C132 | 275 W CIGS Flexible Module | UL 1703 | 275 | 253.6 |  | No Information Submitted | No Information Submitted | CIGS Thin Film | Thin Film | 2.1915 | 132 | 1 | Y | 4.52 | 89 | 3.89 | 70.7 | 43.21 | -0.3893 | -0.0097 | -0.2634 | -0.0589 | -0.3423 | 0.50829 | 60.7409 | 2.9875 | 65.6514 | BIPV | Flat Plate | 0.37 | 5.923 | 1 | 0.11227 |  | 2018-12-17
Miasole | FLEX-03 280NL | 280 W, 132 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 280 | 258.8 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 2.057 | 132 | 1 | N | 4.59 | 88.7 | 3.96 | 70.8 | 45.35 | -0.3464 | 0.0063 | -0.2266 |  |  | 0.53 | 60.14 | 3.04 | 63.36 | [6 empty] | 2021-10-21
Miasole | FLEX-03 290W | 290 W, 144 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 290 | 250.8 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 2.211 | 72 | 2 | Y | 9.27 | 47.2 | 7.83 | 37.2 | 49.1 | -0.5188 | -0.0072 | -0.3551 |  |  | 1.6034 | 32.3258 | 6.2561 | 33.3083 | [6 empty] | 2021-10-21
Miasole | FLEX-03 300W | 300 W, 144 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 300 | 259.7 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 2.211 | 72 | 2 | Y | 9.21 | 48 | 7.89 | 38.1 | 49.1 | -0.5188 | -0.0072 | -0.3551 |  |  | 1.6157 | 33.1079 | 6.3041 | 34.1142 | [6 empty] | 2021-10-21
Miasole | FLEX-03 310W | 310 W, 144 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 310 | 268.6 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 2.211 | 72 | 2 | Y | 9.14 | 48.7 | 7.96 | 39 | 49.1 | -0.5188 | -0.0072 | -0.3551 |  |  | 1.63 | 33.89 | 6.36 | 34.92 | [6 empty] | 2021-10-21
Miasole | FLEX-03 320W | 320 W, 144 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 320 | 277.6 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 2.211 | 72 | 2 | Y | 9.08 | 49.5 | 8.02 | 40 | 49.1 | -0.5188 | -0.0072 | -0.3551 |  |  | 1.6423 | 34.759 | 6.4079 | 35.8154 | [6 empty] | 2021-10-21
Miasole | FLEX-02 340W | 340 W, 168 cell CIGS thin film module, 600V max system Vdc | UL 1703 | 340 | 287 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 2.57 | 168 |  | Y | 13.54 | 37.5 | 11.61 | 29.3 | 61.1 | -0.4015 | -0.0108 | -0.2832 | -0.0645 | -0.3451 | 2.219 | 29.447 | 8.6778 | 25.782 | [6 empty] | 2018-12-17
Miasole | FLEX-02 350W | 350 W, 168 cell CIGS thin film module, 600V max system Vdc | UL 1703 | 350 | 295.8 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 2.57 | 168 | 1 | Y | 13.55 | 37.9 | 11.72 | 29.9 | 61.1 | -0.4015 | -0.0108 | -0.2832 | -0.0645 | -0.3451 | 2.24 | 30.05 | 8.76 | 26.31 | BIPV | Flat Plate | 0.99 | 2.598 | 1 | 0.19232 |  | 2018-12-17
Miasole | FLEX-02 360W | 360 W, 168 cell CIGS thin film module, 600V max system Vdc | UL 1703 | 360 | 304.5 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 2.57 | 168 |  | Y | 13.56 | 38.3 | 11.83 | 30.4 | 61.1 | -0.4015 | -0.0108 | -0.2832 | -0.0645 | -0.3451 | 2.261 | 30.5525 | 8.8422 | 26.75 | [6 empty] | 2018-12-17
Miasole | FLEX-03 470W | 470 W, 224 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 470 | 412.4 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 3 | 112 | 2 | N | 9.19 | 74.8 | 7.91 | 59.6 | 62.9 | -0.31195 | 0.0102 | -0.2475 |  |  | 0.85567 | 51.9751 | 6.0395 | 53.1622 | [6 empty] | 2021-10-21
Miasole | FLEX-03 480W | 480 W, 224 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 480 | 421.5 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 3 | 112 | 2 | N | 9.15 | 75.6 | 7.95 | 60.5 | 62.9 | -0.31195 | 0.0102 | -0.2475 |  |  | 0.86 | 52.76 | 6.07 | 53.965 | [6 empty] | 2021-10-21
Miasole | FLEX-03 490W | 490 W, 224 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 490 | 430.5 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 3 | 112 | 2 | N | 9.11 | 76.4 | 7.99 | 61.4 | 62.9 | -0.31195 | 0.0102 | -0.2475 |  |  | 0.86433 | 53.5449 | 6.1005 | 54.7678 | [6 empty] | 2021-10-21
Miasole | FLEX-03 500W | 500 W, 224 cell CIGS thin film module, 1000V max system Vdc | UL 61730 | 500 | 439.6 |  | No Information Submitted | No Information Submitted | Thin Film | CIGS | 3 | 112 | 2 | Y | 9.07 | 77.2 | 8.03 | 62.4 | 62.9 | -0.31195 | 0.0102 | -0.2475 |  |  | 0.86865 | 54.4169 | 6.1311 | 55.6598 | [6 empty] | 2021-10-21
Mission Solar Energy LLC | MSE260SO5T | 260 W P-Monocrystalline Module | UL 1703 | 260 | 234.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 8.9 | 37.89 | 8.44 | 30.82 | 47.49 | -0.416 | 0.043 | -0.312 | -0.001 | -0.414 | 1.6778 | 29.8193 | 6.7495 | 27.9806 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19243
Mission Solar Energy LLC | MSE265SO5T | 265 W P-Monocrystalline Module | UL 1703 | 265 | 239.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 8.99 | 38.07 | 8.53 | 31.14 | 47.49 | -0.416 | 0.043 | -0.312 | -0.001 | -0.414 | 1.6957 | 30.1289 | 6.8214 | 28.2712 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19279
Mission Solar Energy LLC | MSE270SO5K | 270 W Monocrystalline Module White | UL 1703 | 270 | 243.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.28 | 37.64 | 8.78 | 30.79 | 48.26 | -0.418 | 0.046 | -0.312 | 0.001 | -0.418 | 1.753 | 29.8916 | 7.0479 | 27.7736 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19408
Mission Solar Energy LLC | MSE270SO5T | 270 W P-Monocrystalline Module | UL 1703 | 270 | 244.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.09 | 38.21 | 8.64 | 31.28 | 47.49 | -0.416 | 0.043 | -0.312 | -0.001 | -0.414 | 1.7176 | 30.2643 | 6.9094 | 28.3983 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19252
Mission Solar Energy LLC | MSE275SO5K | 275 W Monocrystalline Module White | UL 1703 | 275 | 247.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.34 | 37.82 | 8.89 | 30.95 | 48.26 | -0.418 | 0.046 | -0.312 | 0.001 | -0.418 | 1.775 | 30.0469 | 7.1362 | 27.918 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19394
Mission Solar Energy LLC | MSE275SO5T | 275 W P-Monocrystalline Module | UL 1703 | 275 | 248.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.17 | 38.45 | 8.72 | 31.55 | 47.49 | -0.416 | 0.043 | -0.312 | -0.001 | -0.414 | 1.7335 | 30.5256 | 6.9734 | 28.6434 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19242
Mission Solar Energy LLC | MSE280SO5K | 280 W Monocrystalline Module White | UL 1703 | 280 | 252.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.37 | 38.22 | 8.93 | 31.37 | 48.26 | -0.418 | 0.046 | -0.312 | 0.001 | -0.418 | 1.783 | 30.4547 | 7.1683 | 28.2968 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19393
Mission Solar Energy LLC | MSE280SO5T | 280 W P-Monocrystalline Module | UL 1703 | 280 | 253.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.27 | 38.6 | 8.79 | 31.87 | 47.49 | -0.416 | 0.043 | -0.312 | -0.001 | -0.414 | 1.7474 | 30.8352 | 7.0293 | 28.9339 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19243
Mission Solar Energy LLC | MSE285SO5K | 285 W Monocrystalline Module White | UL 1703 | 285 | 257.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.42 | 38.62 | 8.98 | 31.77 | 48.26 | -0.418 | 0.046 | -0.312 | 0.001 | -0.418 | 1.7929 | 30.843 | 7.2084 | 28.6576 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19403
Mission Solar Energy LLC | MSE285SQ5K | 285 W PERC Module White | UL 1703 | 285 | 262.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.67 | 38.05 | 9.05 | 31.66 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8257 | 30.9227 | 7.2763 | 29.1801 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19809
Mission Solar Energy LLC | MSE285SQ5T | 285 W P-Monocrystalline Module | UL 1703 | 285 | 262.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.599 | 60 | 1 | N | 9.37 | 39.56 | 8.87 | 32.36 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.7681 | 31.2597 | 7.1019 | 29.7349 | Rack | Flat Plate | 0.975 | 1.64 | 1 | 0.19393
Mission Solar Energy LLC | MSE285SQ8T | 285 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 285 | 262.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.367 | 39.69 | 8.72 | 32.68 | 46.09 | -0.379 | 0.036 | -0.281 | 0 | -0.378 | 1.6962 | 31.5598 | 6.929 | 29.8735 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE290SB1A | 290 W Monocrystalline Module | UL 1703 | 290 | 258.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 8.72 | 44.5 | 8.12 | 36 | 47 | -0.4647 | 0.0185 | -0.3319 | -0.0359 | -0.4396 | 1.64 | 35.59 | 6.23 | 31.82 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.20127
Mission Solar Energy LLC | MSE290SQ5K | 290 W PERC Module White | UL 1703 | 290 | 267.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.7 | 39.08 | 9.12 | 31.89 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8398 | 31.1473 | 7.3325 | 29.392 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.1976
Mission Solar Energy LLC | MSE290SQ5T | 290 W P-Monocrystalline Module | UL 1703 | 290 | 267.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.599 | 60 | 1 | N | 9.44 | 39.81 | 8.95 | 32.54 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.784 | 31.4336 | 7.166 | 29.9003 | Rack | Flat Plate | 0.975 | 1.64 | 1 | 0.19337
Mission Solar Energy LLC | MSE290SQ8K | 290 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 290 | 266.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.561 | 39 | 8.982 | 32.3 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.7663 | 31.0874 | 7.1294 | 29.4046 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE290SQ8T | 290 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 290 | 266.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.42 | 39.91 | 8.811 | 32.91 | 46.09 | -0.379 | 0.036 | -0.281 | 0 | -0.378 | 1.7139 | 31.7819 | 7.0013 | 30.0838 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE60A290 | 290 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 290 | 266.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 9.62 | 39.77 | 9.06 | 32 | 44.58 | -0.42 | 0.04 | -0.3 |  |  | 1.8038 | 30.7188 | 7.2562 | 28.9231 | [6 empty] | 2019-08-15
Mission Solar Energy LLC | MSE295SB1A | 295 W Monocrystalline Module | UL 1703 | 295 | 263.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 8.79 | 44.8 | 8.19 | 36.3 | 47 | -0.4647 | 0.0185 | -0.3319 | -0.0359 | -0.4396 | 1.65 | 35.89 | 6.29 | 32.09 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.20074
Mission Solar Energy LLC | MSE295SQ5K | 295 W PERC Module White | UL 1703 | 295 | 272.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.73 | 39.38 | 9.2 | 32.19 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8559 | 31.4404 | 7.3969 | 29.6685 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.1978
Mission Solar Energy LLC | MSE295SQ5T | 295 W P-Monocrystalline Module | UL 1703 | 295 | 272.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.599 | 60 | 1 | N | 9.52 | 40.11 | 9.03 | 32.72 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8 | 31.6075 | 7.23 | 30.0657 | Rack | Flat Plate | 0.975 | 1.64 | 1 | 0.19286
Mission Solar Energy LLC | MSE295SQ8K | 295 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 295 | 271.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.578 | 39.24 | 9.027 | 32.68 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.7751 | 31.4531 | 7.1651 | 29.7505 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE295SQ8T | 295 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.48 | 40.07 | 8.912 | 33.1 | 46.09 | -0.379 | 0.036 | -0.281 | 0 | -0.378 | 1.7336 | 31.9654 | 7.0816 | 30.2574 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE60A295 | 295 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 295 | 270.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 46.67 | -0.386 | 0.042 | -0.282 |  |  | 1.814 | 31.2838 | 7.323 | 29.5803 | [6 empty] | 2019-08-15
Mission Solar Energy LLC | MSE300MC1A | 300 W Polycrystalline Module | UL 1703 | 300 | 264.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.78 | 44.5 | 8.31 | 36 | 48.2 | -0.4936 | 0.04553 | -0.3792 | -0.0217 | -0.4911 | 1.6825 | 34.9524 | 6.7198 | 31.8095 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19603
Mission Solar Energy LLC | MSE300SB1A | 300 W Monocrystalline Module | UL 1703 | 300 | 268 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 8.86 | 45.2 | 8.26 | 36.6 | 47 | -0.4647 | 0.0185 | -0.3319 | -0.0359 | -0.4396 | 1.66 | 36.18 | 6.34 | 32.35 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.2002
Mission Solar Energy LLC | MSE300SQ5K | 300 W PERC Module White | UL 1703 | 300 | 276.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.77 | 39.72 | 9.27 | 32.38 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8701 | 31.6259 | 7.4531 | 29.8437 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19714
Mission Solar Energy LLC | MSE300SQ5T | 300 W P-Monocrystalline Module | UL 1703 | 300 | 276.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.599 | 60 | 1 | N | 9.61 | 40.18 | 9.17 | 32.8 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8279 | 31.6847 | 7.3421 | 30.1392 | Rack | Flat Plate | 0.975 | 1.64 | 1 | 0.19305
Mission Solar Energy LLC | MSE300SQ8K | 300 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 300 | 276.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.652 | 39.66 | 9.104 | 32.95 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.7903 | 31.713 | 7.2262 | 29.9963 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE300SQ8T | 300 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.571 | 40.08 | 9.058 | 33.12 | 46.09 | -0.379 | 0.036 | -0.281 | 0 | -0.378 | 1.762 | 31.9847 | 7.1976 | 30.2757 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE300TS60 | 300 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 300 | 271.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.83 | 40 | 9.31 | 32.6 | 48.9 | -0.403 | 0.032 | -0.288 |  |  | 1.8103 | 31.0203 | 7.1846 | 29.1891 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE60A300 | 300 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 300 | 275.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 46.67 | -0.386 | 0.042 | -0.282 |  |  | 1.8319 | 31.5167 | 7.395 | 29.8005 | [6 empty] | 2019-08-15
Mission Solar Energy LLC | MSE305MC1A | 305 W Polycrystalline Module | UL 1703 | 305 | 268.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.94 | 44.7 | 8.42 | 36.2 | 48.2 | -0.4936 | 0.04553 | -0.3792 | -0.0217 | -0.4911 | 1.7048 | 35.1466 | 6.8088 | 31.9862 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19645
Mission Solar Energy LLC | MSE305SB1A | 305 W Monocrystalline Module | UL 1703 | 305 | 272.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 8.94 | 45.6 | 8.32 | 36.9 | 47 | -0.4647 | 0.0185 | -0.3319 | -0.0359 | -0.4396 | 1.68 | 36.48 | 6.39 | 32.62 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.20094
Mission Solar Energy LLC | MSE305SE1A | 305 W P-Monocrystalline Module | UL 1703 | 305 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 8.93 | 45.6 | 8.32 | 36.9 | 47.25 | -0.41 | 0.04 | -0.31 | -0.01 | -0.41 | 1.6541 | 35.6108 | 6.6184 | 33.5411 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19313
Mission Solar Energy LLC | MSE305SE1J | 305 W P-Monocrystalline Module | UL 1703 | 305 | 276.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 8.93 | 45.6 | 8.32 | 36.9 | 47.25 | -0.414 | 0.039 | -0.307 | -0.008 | -0.406 | 1.6541 | 35.6108 | 6.6184 | 33.5411 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19313
Mission Solar Energy LLC | MSE305SQ5K | 305 W PERC Module White | UL 1703 | 305 | 281.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6095 | 60 | 1 | N | 9.81 | 39.95 | 9.36 | 32.61 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8882 | 31.8506 | 7.5255 | 30.0556 | Rack | Flat Plate | 0.979 | 1.644 | 1 | 0.19718
Mission Solar Energy LLC | MSE305SQ8K | 305 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 305 | 280.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.723 | 39.96 | 9.238 | 33.02 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8166 | 31.7804 | 7.3326 | 30.0601 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE305SQ8T | 305 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 305 | 281.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.664 | 40.1 | 9.202 | 33.14 | 46.09 | -0.379 | 0.036 | -0.281 | 0 | -0.378 | 1.79 | 32.004 | 7.312 | 30.294 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE305TS60 | 305 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 305 | 276 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.9 | 40.1 | 9.38 | 32.8 | 48.9 | -0.403 | 0.032 | -0.288 |  |  | 1.8298 | 31.2106 | 7.2618 | 29.3681 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE60A305 | 305 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 305 | 279.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 10.06 | 40.79 | 9.32 | 32.73 | 46.67 | -0.386 | 0.042 | -0.282 |  |  | 1.8475 | 31.7578 | 7.4583 | 30.0285 | [6 empty] | 2019-08-15
Mission Solar Energy LLC | MSE310MC1A | 310 W Polycrystalline Module | UL 1703 | 310 | 273.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 9.08 | 44.9 | 8.52 | 36.4 | 48.2 | -0.4936 | 0.04553 | -0.3792 | -0.0217 | -0.4911 | 1.725 | 35.3407 | 6.8896 | 32.163 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19666
Mission Solar Energy LLC | MSE310SB1A | 310 W Monocrystalline Module | UL 1703 | 310 | 277.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.01 | 45.9 | 8.39 | 37.2 | 47 | -0.4647 | 0.0185 | -0.3319 | -0.0359 | -0.4396 | 1.71 | 37.09 | 6.47 | 33.24 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.20459
Mission Solar Energy LLC | MSE310SE1A | 310 W P-Monocrystalline Module | UL 1703 | 310 | 281 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 8.96 | 45.6 | 8.38 | 37 | 47.25 | -0.41 | 0.04 | -0.31 | -0.01 | -0.41 | 1.6661 | 35.7073 | 6.6662 | 33.632 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.1919
Mission Solar Energy LLC | MSE310SE1J | 310 W P-Monocrystalline Module | UL 1703 | 310 | 280.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 8.96 | 45.6 | 8.38 | 37 | 47.25 | -0.414 | 0.039 | -0.307 | -0.008 | -0.406 | 1.6661 | 35.7073 | 6.6662 | 33.632 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.1919
Mission Solar Energy LLC | MSE310SQ8K | 310 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 310 | 285.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.819 | 40.09 | 9.362 | 33.11 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.841 | 31.867 | 7.431 | 30.142 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE310SQ8T | 310 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.76 | 40.12 | 9.345 | 33.17 | 46.09 | -0.379 | 0.036 | -0.281 | 0 | -0.378 | 1.8178 | 32.033 | 7.4256 | 30.3214 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE310SR8T | 310 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 284.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.967 | 40.14 | 9.202 | 33.69 | 47.15 | -0.373 | 0.046 | -0.276 |  |  | 1.864 | 31.823 | 7.574 | 29.936 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE310TS60 | 310 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 310 | 280.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.94 | 40.3 | 9.45 | 33.1 | 48.9 | -0.403 | 0.032 | -0.288 |  |  | 1.8473 | 31.4009 | 7.3312 | 29.5472 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE60A310 | 310 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 310 | 284.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 10.21 | 41.14 | 9.4 | 32.97 | 46.67 | -0.386 | 0.042 | -0.282 |  |  | 1.8638 | 31.996 | 7.5242 | 30.2538 | [6 empty] | 2019-08-15
Mission Solar Energy LLC | MSE315MC1A | 315 W Polycrystalline Module | UL 1703 | 315 | 277.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 9.18 | 45.1 | 8.61 | 36.6 | 48.2 | -0.4936 | 0.04553 | -0.3792 | -0.0217 | -0.4911 | 1.7433 | 35.5349 | 6.9624 | 32.3397 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19666
Mission Solar Energy LLC | MSE315SB1A | 315 W Monocrystalline Module | UL 1703 | 315 | 281.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.08 | 46.3 | 8.45 | 37.5 | 47 | -0.4647 | 0.0185 | -0.3319 | -0.0359 | -0.4396 | 1.72 | 37.39 | 6.51 | 33.51 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.20416
Mission Solar Energy LLC | MSE315SE1A | 315 W P-Monocrystalline Module | UL 1703 | 315 | 285.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 8.99 | 45.8 | 8.47 | 37.2 | 47.25 | -0.41 | 0.04 | -0.31 | -0.01 | -0.41 | 1.6839 | 35.9003 | 6.7378 | 33.8138 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19192
Mission Solar Energy LLC | MSE315SE1J | 315 W P-Monocrystalline Module | UL 1703 | 315 | 285.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 8.99 | 45.8 | 8.47 | 37.2 | 47.25 | -0.414 | 0.039 | -0.307 | -0.008 | -0.406 | 1.6839 | 35.9003 | 6.7378 | 33.8138 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19192
Mission Solar Energy LLC | MSE315SQ8K | 315 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 290.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6 | 60 |  | N | 9.917 | 40.13 | 9.465 | 33.28 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8613 | 32.0306 | 7.5128 | 30.2968 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE315SR8K | 315 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 290.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.963 | 40.14 | 9.352 | 33.68 | 45.98 | -0.374 | 0.041 | -0.275 |  |  | 1.896 | 31.972 | 7.673 | 30.241 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE315SR8T | 315 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 315 | 289.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.997 | 40.44 | 9.253 | 34.04 | 47.15 | -0.373 | 0.046 | -0.276 |  |  | 1.8743 | 32.1536 | 7.616 | 30.247 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE60A315 | 315 W, 60 cell monocrystalline module, 1000V max system Vdc | UL 1703 | 315 | 289.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.627 | 60 | 1 | N | 10.37 | 41.49 | 9.48 | 33.22 | 46.67 | -0.386 | 0.042 | -0.282 |  |  | 1.8798 | 32.236 | 7.5886 | 30.4807 | [6 empty] | 2019-08-15
Mission Solar Energy LLC | MSE320MC1A | 320 W Polycrystalline Module | UL 1703 | 320 | 282.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 9.26 | 45.3 | 8.69 | 36.8 | 48.2 | -0.4936 | 0.04553 | -0.3792 | -0.0217 | -0.4911 | 1.7595 | 35.7291 | 7.0271 | 32.5164 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19645
Mission Solar Energy LLC | MSE320MM4J | 330 W P-Type Multicrystalline modules, 1.5kV | UL 1703 | 320 | 295 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.926 | 72 |  | N | 9.24 | 45.18 | 8.69 | 36.88 | 44.57 | -0.39 | 0.053 | -0.303 | 0.009 | -0.399 | 1.729 | 35.8 | 7.019 | 34.213 | [6 empty] | 2017-09-01
Mission Solar Energy LLC | MSE320MM6J | 330 W P-Type Multicrystalline modules, 1.5kV | UL 1703 | 320 | 295 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.926 | 72 |  | N | 9.24 | 45.18 | 8.69 | 36.88 | 44.57 | -0.39 | 0.053 | -0.303 | 0.009 | -0.399 | 1.729 | 35.8 | 7.019 | 34.213 | [6 empty] | 2017-09-01
Mission Solar Energy LLC | MSE320SB1A | 320 W Monocrystalline Module | UL 1703 | 320 | 286.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.15 | 46.7 | 8.52 | 37.8 | 47 | -0.4647 | 0.0185 | -0.3319 | -0.0359 | -0.4396 | 1.73 | 37.69 | 6.57 | 33.78 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.20376
Mission Solar Energy LLC | MSE320SE1A | 320 W P-Monocrystalline Module | UL 1703 | 320 | 290.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 9.12 | 45.9 | 8.56 | 37.4 | 47.25 | -0.41 | 0.04 | -0.31 | -0.01 | -0.41 | 1.7018 | 36.0933 | 6.8094 | 33.9956 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19195
Mission Solar Energy LLC | MSE320SE1J | 320 W P-Monocrystalline Module | UL 1703 | 320 | 290 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 9.12 | 45.9 | 8.56 | 37.4 | 47.25 | -0.414 | 0.039 | -0.307 | -0.008 | -0.406 | 1.7018 | 36.0933 | 6.8094 | 33.9956 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19195
Mission Solar Energy LLC | MSE320SO4J | 320 W P-Monocrystalline Module | UL 1703 | 320 | 288.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 8.97 | 45.68 | 8.51 | 37.65 | 48.26 | -0.418 | 0.049 | -0.315 | 0.003 | -0.421 | 1.7006 | 36.2795 | 6.8308 | 33.8258 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19281
Mission Solar Energy LLC | MSE320SO6J | 320 W Monocrystalline Module, 1kv | UL 1703 | 320 | 287.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 8.97 | 45.68 | 8.51 | 37.65 | 48.26 | -0.421 | 0.049 | -0.315 | 0.004 | -0.425 | 1.7006 | 36.2795 | 6.8308 | 33.8258 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19281
Mission Solar Energy LLC | MSE320SO6W | 320 W Monocrystalline Module Black | UL 1703 | 320 | 290.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.985 | 72 | 1 | N | 8.92 | 46.13 | 8.49 | 37.71 | 46.38 | -0.412 | 0.045 | -0.311 | 0.004 | -0.415 | 1.6909 | 36.6403 | 6.8197 | 34.3559 | Rack | Flat Plate | 0.999 | 1.987 | 1 | 0.19361
Mission Solar Energy LLC | MSE320SR8K | 320 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 320 | 295.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 9.988 | 40.38 | 9.435 | 33.92 | 45.98 | -0.374 | 0.041 | -0.275 |  |  | 1.9128 | 32.1998 | 7.7411 | 30.4565 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE320SR8T | 320 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 294.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 10.028 | 40.8 | 9.351 | 34.22 | 47.15 | -0.373 | 0.046 | -0.276 |  |  | 1.8942 | 32.3236 | 7.6966 | 30.4069 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE325MC1A | 325 W Polycrystalline Module | UL 1703 | 325 | 286.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 9.32 | 45.7 | 8.76 | 37 | 48.2 | -0.4936 | 0.04553 | -0.3792 | -0.0217 | -0.4911 | 1.7736 | 35.9233 | 7.0837 | 32.6931 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.19604
Mission Solar Energy LLC | MSE325MM4J | 325 W P-Type Multicrystalline modules, 1.5kV | UL 1703 | 325 | 299.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.926 | 72 |  | N | 9.26 | 45.8 | 8.72 | 37.3 | 44.57 | -0.39 | 0.053 | -0.303 | 0.009 | -0.399 | 1.729 | 35.8 | 7.019 | 34.213 | [6 empty] | 2017-09-01
Mission Solar Energy LLC | MSE325MM6J | 325 W P-Type Multicrystalline modules, 1.5kV | UL 1703 | 325 | 299.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.926 | 72 |  | N | 9.26 | 45.8 | 8.72 | 37.3 | 44.57 | -0.39 | 0.053 | -0.303 | 0.009 | -0.399 | 1.729 | 35.8 | 7.019 | 34.213 | [6 empty] | 2017-09-01
Mission Solar Energy LLC | MSE325SB1A | 325 W Monocrystalline Module | UL 1703 | 325 | 291 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.23 | 47 | 8.59 | 38.1 | 47 | -0.4647 | 0.0185 | -0.3319 | -0.0359 | -0.4396 | 1.75 | 37.99 | 6.62 | 34.05 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.20456
Mission Solar Energy LLC | MSE325SE1A | 325 W P-Monocrystalline Module | UL 1703 | 325 | 295 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 9.13 | 46.1 | 8.6 | 37.8 | 47.25 | -0.41 | 0.04 | -0.31 | -0.01 | -0.41 | 1.7098 | 36.4793 | 6.8412 | 34.3592 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19191
Mission Solar Energy LLC | MSE325SE1J | 325 W P-Monocrystalline Module | UL 1703 | 325 | 294.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 9.13 | 46.1 | 8.6 | 37.8 | 47.25 | -0.414 | 0.039 | -0.307 | -0.008 | -0.406 | 1.7098 | 36.4793 | 6.8412 | 34.3592 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19191
Mission Solar Energy LLC | MSE325SO4J | 325 W P-Monocrystalline Module | UL 1703 | 325 | 292.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.08 | 45.79 | 8.62 | 37.72 | 48.26 | -0.418 | 0.049 | -0.315 | 0.003 | -0.421 | 1.7226 | 36.3469 | 6.9191 | 33.8887 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19265
Mission Solar Energy LLC | MSE325SO6J | 325 W Monocrystalline Module, 1k | UL 1703 | 325 | 292.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.08 | 45.79 | 8.62 | 37.72 | 48.26 | -0.421 | 0.049 | -0.315 | 0.004 | -0.425 | 1.7226 | 36.3469 | 6.9191 | 33.8887 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19265
Mission Solar Energy LLC | MSE325SO6W | 325 W Monocrystalline Module Black | UL 1703 | 325 | 295.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.985 | 72 | 1 | N | 9.06 | 46.39 | 8.6 | 37.84 | 46.38 | -0.412 | 0.045 | -0.311 | 0.004 | -0.415 | 1.7128 | 36.7667 | 6.908 | 34.4743 | Rack | Flat Plate | 0.999 | 1.987 | 1 | 0.19377
Mission Solar Energy LLC | MSE325SR8K | 325 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 325 | 300.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 10.024 | 40.8 | 9.499 | 34.21 | 45.98 | -0.374 | 0.041 | -0.275 |  |  | 1.9258 | 32.4751 | 7.7936 | 30.7169 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE325SR8T | 325 W, 60 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 325 | 299 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 10.06 | 41.14 | 9.387 | 34.62 | 47.15 | -0.373 | 0.046 | -0.276 |  |  | 1.9015 | 32.7015 | 7.7263 | 30.7624 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE330MM4J | 320 W P-Type Multicrystalline modules, 1.5kV | UL 1703 | 330 | 304.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.926 | 72 |  | N | 9.33 | 46.01 | 8.81 | 37.5 | 44.57 | -0.39 | 0.053 | -0.303 | 0.009 | -0.399 | 1.729 | 35.8 | 7.019 | 34.213 | [6 empty] | 2017-09-01
Mission Solar Energy LLC | MSE330MM6J | 320 W P-Type Multicrystalline modules, 1.5kV | UL 1703 | 330 | 304.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.926 | 72 |  | N | 9.33 | 46.01 | 8.81 | 37.5 | 44.57 | -0.39 | 0.053 | -0.303 | 0.009 | -0.399 | 1.729 | 35.8 | 7.019 | 34.213 | [6 empty] | 2017-09-01
Mission Solar Energy LLC | MSE330SB1A | 330 W Monocrystalline Module | UL 1703 | 330 | 295.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.3 | 47.4 | 8.65 | 38.4 | 47 | -0.4647 | 0.0185 | -0.3319 | -0.0359 | -0.4396 | 1.76 | 38.29 | 6.67 | 34.32 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.20421
Mission Solar Energy LLC | MSE330SE1A | 330 W P-Monocrystalline Module | UL 1703 | 330 | 299.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 9.14 | 46.11 | 8.62 | 37.5 | 47.25 | -0.41 | 0.04 | -0.31 | -0.01 | -0.41 | 1.7138 | 36.1898 | 6.8571 | 34.0865 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.18794
Mission Solar Energy LLC | MSE330SE1J | 330 W P-Monocrystalline Module | UL 1703 | 330 | 299.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 9.14 | 46.11 | 8.62 | 37.5 | 47.25 | -0.414 | 0.039 | -0.307 | -0.008 | -0.406 | 1.7138 | 36.1898 | 6.8571 | 34.0865 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.18794
Mission Solar Energy LLC | MSE330SO4J | 330 W P-Monocrystalline Module | UL 1703 | 330 | 297.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.23 | 46.12 | 8.72 | 37.85 | 48.26 | -0.418 | 0.049 | -0.315 | 0.003 | -0.421 | 1.7426 | 36.4722 | 6.9994 | 34.0055 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.1926
Mission Solar Energy LLC | MSE330SO6J | 330 W Monocrystalline Module, 1kv | UL 1703 | 330 | 297.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.23 | 46.12 | 8.72 | 37.85 | 48.26 | -0.421 | 0.049 | -0.315 | 0.004 | -0.425 | 1.7426 | 36.4722 | 6.9994 | 34.0055 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.1926
Mission Solar Energy LLC | MSE330SO6W | 330 W Monocrystalline Module Black | UL 1703 | 330 | 300.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.985 | 72 | 1 | N | 9.12 | 46.62 | 8.64 | 38.38 | 46.38 | -0.412 | 0.045 | -0.311 | 0.004 | -0.415 | 1.7208 | 37.2913 | 6.9402 | 34.9663 | Rack | Flat Plate | 0.999 | 1.987 | 1 | 0.19446
Mission Solar Energy LLC | MSE330SO7J | 330 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 330 | 302.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.325 | 45.85 | 8.816 | 37.43 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.7638 | 36.1853 | 7.0385 | 34.351 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE330SO9J | 330 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 330 | 302.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.325 | 45.85 | 8.816 | 37.43 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.7638 | 36.1853 | 7.0385 | 34.351 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE330SR8K | 330 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 330 | 305 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.64 | 60 | 1 | N | 10.045 | 41.06 | 9.556 | 34.53 | 45.98 | -0.374 | 0.041 | -0.275 |  |  | 1.9374 | 32.7789 | 7.8404 | 31.0042 | [6 empty] | 2020-01-13
Mission Solar Energy LLC | MSE330SX5T | 330 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 330 | 307 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.787 | 60 | 1 | N | 10.72 | 40.4 | 10.05 | 32.85 | 44.43 | -0.361 | 0.039 | -0.262 |  |  | 2.0437 | 32.7068 | 8.2699 | 30.8321 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE335SB1A | 335 W Monocrystalline Module | UL 1703 | 335 | 294.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9503 | 72 | 1 | N | 9.32 | 47.6 | 8.71 | 38.7 | 48.1 | -0.5198 | 0.0129 | -0.3638 | -0.0509 | -0.4812 | 1.7837 | 38.4919 | 6.968 | 34.5387 | Rack | Flat Plate | 0.99 | 1.97 | 1 | 0.20495
Mission Solar Energy LLC | MSE335SE1A | 335 W P-Monocrystalline Module | UL 1703 | 335 | 304.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 9.15 | 46.4 | 8.68 | 38.9 | 47.25 | -0.41 | 0.04 | -0.31 | -0.01 | -0.41 | 1.7257 | 37.5409 | 6.9048 | 35.359 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19339
Mission Solar Energy LLC | MSE335SE1J | 335 W P-Monocrystalline Module | UL 1703 | 335 | 304 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8798 | 72 | 1 | N | 9.15 | 46.4 | 8.68 | 38.9 | 47.25 | -0.414 | 0.039 | -0.307 | -0.008 | -0.406 | 1.7257 | 37.5409 | 6.9048 | 35.359 | Rack | Flat Plate | 0.966 | 1.946 | 1 | 0.19339
Mission Solar Energy LLC | MSE335SO4J | 335 W P-Monocrystalline Module | UL 1703 | 335 | 302.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.38 | 46.14 | 8.87 | 37.89 | 48.26 | -0.418 | 0.049 | -0.315 | 0.003 | -0.421 | 1.7726 | 36.5107 | 7.1198 | 34.0414 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19319
Mission Solar Energy LLC | MSE335SO6J | 335 W Monocrystalline Module, 1kv | UL 1703 | 335 | 301.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.38 | 46.14 | 8.87 | 37.89 | 48.26 | -0.421 | 0.049 | -0.315 | 0.004 | -0.425 | 1.7726 | 36.5107 | 7.1198 | 34.0414 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19319
Mission Solar Energy LLC | MSE335SO7J | 335 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 335 | 306.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.41 | 46.05 | 8.904 | 37.62 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.7814 | 36.369 | 7.1088 | 34.5253 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE335SO9J | 335 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 335 | 306.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.41 | 46.05 | 8.904 | 37.62 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.7814 | 36.369 | 7.1088 | 34.5253 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE335SQ6W | 335 W PERC Module Black | UL 1703 | 335 | 306.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.985 | 72 | 1 | N | 9.35 | 47.88 | 8.68 | 38.82 | 46.13 | -0.398 | 0.039 | -0.288 | -0.005 | -0.392 | 1.7329 | 37.783 | 6.9413 | 35.6846 | Rack | Flat Plate | 0.999 | 1.987 | 1 | 0.19545
Mission Solar Energy LLC | MSE335SX5K | 335 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 335 | 310.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.787 | 60 | 1 | N | 10.85 | 40.35 | 10.19 | 32.89 | 45.86 | -0.361 | 0.049 | -0.262 |  |  | 2.0826 | 32.697 | 8.3978 | 30.6138 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE335SX5T | 335 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 335 | 311.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.787 | 60 | 1 | N | 10.78 | 40.58 | 10.14 | 33.03 | 44.43 | -0.361 | 0.039 | -0.262 |  |  | 2.062 | 32.886 | 8.344 | 31.001 | [6 empty] | 2021-02-11 | 2021-06-11
Mission Solar Energy LLC | MSE340SO4J | 340 W P-Monocrystalline Module | UL 1703 | 340 | 306.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.49 | 46.35 | 8.95 | 38.02 | 48.26 | -0.418 | 0.049 | -0.315 | 0.003 | -0.421 | 1.7886 | 36.636 | 7.184 | 34.1582 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19272
Mission Solar Energy LLC | MSE340SO6J | 340 W Monocrystalline Module, 1kv | UL 1703 | 340 | 306.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.49 | 46.35 | 8.95 | 38.02 | 48.26 | -0.421 | 0.049 | -0.315 | 0.004 | -0.425 | 1.7886 | 36.636 | 7.184 | 34.1582 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19272
Mission Solar Energy LLC | MSE340SO7J | 340 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 340 | 311.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.505 | 46.21 | 9.002 | 37.77 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.801 | 36.514 | 7.187 | 34.663 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE340SO9J | 340 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 340 | 311.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.505 | 46.21 | 9.002 | 37.77 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.801 | 36.514 | 7.187 | 34.663 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE340SQ6S | 340 W PERC Module, 1kv | UL 1703 | 340 | 313.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.67 | 46.57 | 8.93 | 38.25 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.777 | 37.365 | 7.1403 | 35.4778 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19529
Mission Solar Energy LLC | MSE340SQ6W | 340 W PERC Module Black | UL 1703 | 340 | 311 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.985 | 72 | 1 | N | 9.39 | 47.96 | 8.79 | 38.96 | 46.13 | -0.398 | 0.039 | -0.288 | -0.005 | -0.392 | 1.7549 | 37.9192 | 7.0293 | 35.8133 | Rack | Flat Plate | 0.999 | 1.987 | 1 | 0.19572
Mission Solar Energy LLC | MSE340SX5K | 340 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 340 | 314.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.787 | 60 | 1 | N | 10.91 | 40.53 | 10.28 | 33.06 | 45.86 | -0.361 | 0.049 | -0.262 |  |  | 2.101 | 32.866 | 8.472 | 30.772 | [6 empty] | 2021-02-11 | 2021-06-11
Mission Solar Energy LLC | MSE340SX5T | 340 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 340 | 316.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.787 | 60 | 1 | N | 10.86 | 40.82 | 10.24 | 33.2 | 44.43 | -0.361 | 0.039 | -0.262 |  |  | 2.0823 | 33.0553 | 8.4263 | 31.1606 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE345SO4J | 345 W P-Monocrystalline Module | UL 1703 | 345 | 311.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.52 | 46.52 | 9.05 | 38.14 | 48.26 | -0.418 | 0.049 | -0.315 | 0.003 | -0.421 | 1.8085 | 36.7516 | 7.2643 | 34.266 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19266
Mission Solar Energy LLC | MSE345SO6J | 345 W Monocrystalline Module, 1kv | UL 1703 | 345 | 311.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.52 | 46.52 | 9.05 | 38.14 | 48.26 | -0.421 | 0.049 | -0.315 | 0.004 | -0.425 | 1.8085 | 36.7516 | 7.2643 | 34.266 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19266
Mission Solar Energy LLC | MSE345SO7J | 345 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 345 | 316.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.583 | 46.47 | 9.082 | 37.99 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.817 | 36.7267 | 7.2509 | 34.8649 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE345SO9J | 345 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 345 | 316.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.583 | 46.47 | 9.082 | 37.99 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.817 | 36.7267 | 7.2509 | 34.8649 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE345SQ4S | 345 W P-Monocrystalline Module | UL 1703 | 345 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9139 | 72 | 1 | N | 9.7 | 46.98 | 9.04 | 38.43 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.7989 | 37.5408 | 7.2283 | 35.6448 | Rack | Flat Plate | 0.975 | 1.963 | 1 | 0.19575 |  | 2018-03-15
Mission Solar Energy LLC | MSE345SQ6S | 345 W PERC Module, 1kv | UL 1703 | 345 | 318.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.7 | 46.98 | 9.04 | 38.43 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.7989 | 37.5408 | 7.2283 | 35.6448 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19575
Mission Solar Energy LLC | MSE345SQ6W | 345 W PERC Module Black | UL 1703 | 345 | 315.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Multi-c-Si | 1.985 | 72 | 1 | N | 9.42 | 48.06 | 8.87 | 39 | 46.13 | -0.398 | 0.039 | -0.288 | -0.005 | -0.392 | 1.7708 | 37.9582 | 7.0932 | 35.8501 | Rack | Flat Plate | 0.999 | 1.987 | 1 | 0.19483
Mission Solar Energy LLC | MSE345SX5K | 345 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 345 | 319.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.787 | 60 | 1 | N | 10.97 | 40.71 | 10.38 | 33.24 | 45.86 | -0.361 | 0.049 | -0.262 |  |  | 2.1214 | 33.0449 | 8.5544 | 30.9395 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE345SX5T | 345 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 345 | 321.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.787 | 60 | 1 | N | 10.92 | 41 | 10.34 | 33.37 | 44.43 | -0.361 | 0.039 | -0.262 |  |  | 2.1027 | 33.2245 | 8.5086 | 31.3201 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE350SO7J | 350 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 350 | 321 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.681 | 46.69 | 9.183 | 38.14 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.8372 | 36.8717 | 7.3315 | 35.0026 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE350SO9J | 350 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 350 | 321 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.681 | 46.69 | 9.183 | 38.14 | 45.79 | -0.401 | 0.043 | -0.299 | 0.001 | -0.402 | 1.8372 | 36.8717 | 7.3315 | 35.0026 | [6 empty] | 2019-01-02
Mission Solar Energy LLC | MSE350SQ4S | 350 W P-Monocrystalline Module | UL 1703 | 350 | 322.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9139 | 72 | 1 | N | 9.73 | 47.38 | 9.11 | 38.68 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8129 | 37.785 | 7.2842 | 35.8767 | Rack | Flat Plate | 0.975 | 1.963 | 1 | 0.19571 |  | 2018-03-15
Mission Solar Energy LLC | MSE350SQ6S | 350 W PERC Module, 1kv | UL 1703 | 350 | 322.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.73 | 47.38 | 9.11 | 38.68 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8129 | 37.785 | 7.2842 | 35.8767 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19571
Mission Solar Energy LLC | MSE350SX5K | 350 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 350 | 324.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.787 | 60 | 1 | N | 11.05 | 40.95 | 10.48 | 33.41 | 45.86 | -0.361 | 0.049 | -0.262 |  |  | 2.1419 | 33.2139 | 8.6368 | 31.0978 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE350SX5T | 350 W, 60 cell monocrystalline module, black backsheet, black frame, 1000V max system Vdc | UL 61730 | 350 | 326.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 10.97 | 41.18 | 10.44 | 33.52 | 44.43 | -0.361 | 0.039 | -0.262 |  |  | 2.123 | 33.3739 | 8.5909 | 31.4609 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-350120BB | 350 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 350 | 326.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8 | 60 | 2 | N | 11.04 | 40.2 | 10.48 | 33.4 | 45.6 | -0.3335 | 0.0476 | -0.2627 |  |  | 2.0075 | 32.3693 | 8.2277 | 31.5877 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | MSE355SQ4S | 355 W P-Monocrystalline Module | UL 1703 | 355 | 327.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9139 | 72 | 1 | N | 9.76 | 47.68 | 9.19 | 38.98 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8288 | 38.0781 | 7.3482 | 36.1549 | Rack | Flat Plate | 0.975 | 1.963 | 1 | 0.19616 |  | 2018-03-15
Mission Solar Energy LLC | MSE355SQ6S | 355 W PERC Module, 1kv | UL 1703 | 355 | 327.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.76 | 47.68 | 9.19 | 38.98 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8288 | 38.0781 | 7.3482 | 36.1549 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19616
Mission Solar Energy LLC | MSE355SQ7S | 355 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 355 | 326.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.62 | 47.44 | 9.058 | 39.2 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.7994 | 37.6909 | 7.1974 | 35.6148 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE355SQ9S | 355 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 326.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.62 | 47.44 | 9.058 | 39.2 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.7994 | 37.6909 | 7.1974 | 35.6148 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE355SX5K | 355 W, 60 cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 355 | 329.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.79 | 60 | 1 | N | 11.1 | 40.99 | 10.59 | 33.51 | 45.86 | -0.361 | 0.049 | -0.262 |  |  | 2.1644 | 33.4283 | 8.7275 | 31.3624 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-355120BB | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 355 | 331.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8 | 60 | 2 | N | 11.14 | 40.4 | 10.57 | 33.6 | 45.6 | -0.3335 | 0.0476 | -0.2627 |  |  | 2.0248 | 32.5632 | 8.2983 | 31.7769 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | MSE360SQ4S | 360 W P-Monocrystalline Module | UL 1703 | 360 | 332.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9139 | 72 | 1 | N | 9.79 | 48.08 | 9.28 | 39.28 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8467 | 38.3712 | 7.4202 | 36.4332 | Rack | Flat Plate | 0.975 | 1.963 | 1 | 0.19683 |  | 2018-03-15
Mission Solar Energy LLC | MSE360SQ6S | 360 W PERC Module, 1kv | UL 1703 | 360 | 332.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.79 | 48.08 | 9.28 | 39.28 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8467 | 38.3712 | 7.4202 | 36.4332 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19683
Mission Solar Energy LLC | MSE360SQ7S | 360 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 360 | 331.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.661 | 47.83 | 9.143 | 39.38 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8162 | 37.8639 | 7.265 | 35.7784 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE360SQ9S | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 331.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.661 | 47.83 | 9.143 | 39.38 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8162 | 37.8639 | 7.265 | 35.7784 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | TXS6-360120BB | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 360 | 336.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8 | 60 | 2 | N | 11.24 | 40.6 | 10.66 | 33.8 | 45.6 | -0.3335 | 0.0476 | -0.2627 |  |  | 2.042 | 32.757 | 8.369 | 31.966 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | MSE365SQ4S | 365 W P-Monocrystalline Module | UL 1703 | 365 | 337.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9139 | 72 | 1 | N | 9.81 | 48.12 | 9.32 | 39.32 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8546 | 38.4102 | 7.4521 | 36.4703 | Rack | Flat Plate | 0.975 | 1.963 | 1 | 0.19517 |  | 2018-03-15
Mission Solar Energy LLC | MSE365SQ6S | 365 W PERC Module, 1kv | UL 1703 | 365 | 337 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9257 | 72 | 1 | N | 9.81 | 48.12 | 9.32 | 39.32 | 45.51 | -0.38 | 0.046 | -0.28 | -0.002 | -0.377 | 1.8546 | 38.4102 | 7.4521 | 36.4703 | Rack | Flat Plate | 0.979 | 1.967 | 1 | 0.19517
Mission Solar Energy LLC | MSE365SQ7S | 365 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 365 | 336.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.705 | 48.05 | 9.236 | 39.52 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8347 | 37.9985 | 7.3389 | 35.9055 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE365SQ9S | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 336.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.705 | 48.05 | 9.236 | 39.52 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8347 | 37.9985 | 7.3389 | 35.9055 | [6 empty] | 2018-12-17 | 2020-01-13
Mission Solar Energy LLC | TXS6-365120BB | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 365 | 340.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8 | 60 | 2 | N | 11.33 | 40.8 | 10.74 | 34 | 45.6 | -0.3335 | 0.0476 | -0.2627 |  |  | 2.0573 | 32.9508 | 8.4318 | 32.1551 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | MSE370SQ7S | 370 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 370 | 341 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.767 | 48.08 | 9.323 | 39.69 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.852 | 38.162 | 7.408 | 36.06 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE370SQ9S | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 341 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.767 | 48.08 | 9.323 | 39.69 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.852 | 38.162 | 7.408 | 36.06 | [6 empty] | 2018-12-17 | 2020-01-13
Mission Solar Energy LLC | TXS6-370120BB | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 370 | 345.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8 | 60 | 2 | N | 11.42 | 41 | 10.82 | 34.2 | 45.6 | -0.3335 | 0.0476 | -0.2627 |  |  | 2.0726 | 33.1447 | 8.4946 | 32.3443 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | MSE375SQ7S | 375 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 375 | 345.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.826 | 48.16 | 9.432 | 39.76 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8737 | 38.2293 | 7.4946 | 36.1236 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE375SQ9S | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 345.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.826 | 48.16 | 9.432 | 39.76 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8737 | 38.2293 | 7.4946 | 36.1236 | [6 empty] | 2018-12-17 | 2020-01-13
Mission Solar Energy LLC | MSE375SR9S | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 346.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 9.939 | 48.02 | 9.36 | 40.06 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9009 | 38.0763 | 7.7084 | 36.0768 | [6 empty] | 2020-01-13 | 2020-02-03
Mission Solar Energy LLC | MSE375SX5R | 375 W, 66 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 375 | 349.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 66 | 1 | N | 10.8524 | 44.6393 | 10.2575 | 36.5585 | 43.75 | -0.367 | 0.033 | -0.259 |  |  | 2.0691 | 36.1798 | 8.3173 | 34.1453 | [6 empty] | 2021-05-21
Mission Solar Energy LLC | TXS6-375120BB | 375 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 375 | 350.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.8 | 60 | 2 | N | 11.51 | 41.2 | 10.91 | 34.4 | 45.6 | -0.3335 | 0.0476 | -0.2627 |  |  | 2.0899 | 33.3385 | 8.5653 | 32.5334 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | MSE380SQ7S | 380 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 380 | 350.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.904 | 48.17 | 9.552 | 39.78 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8975 | 38.2485 | 7.59 | 36.1418 | [6 empty] | 2018-12-17
Mission Solar Energy LLC | MSE380SQ9S | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 350.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 |  | N | 9.904 | 48.17 | 9.552 | 39.78 | 46.43 | -0.375 | 0.045 | -0.28 | 0.003 | -0.379 | 1.8975 | 38.2485 | 7.59 | 36.1418 | [6 empty] | 2018-12-17 | 2020-01-13
Mission Solar Energy LLC | MSE380SR9S | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 351.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 9.966 | 48.31 | 9.385 | 40.49 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.906 | 38.485 | 7.729 | 36.464 | [6 empty] | 2020-01-13 | 2020-02-03
Mission Solar Energy LLC | MSE380SX5R | 380 W, 66 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 380 | 354.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 66 | 1 | N | 10.9128 | 44.8365 | 10.3411 | 36.7466 | 43.75 | -0.367 | 0.033 | -0.259 |  |  | 2.086 | 36.366 | 8.385 | 34.321 | [6 empty] | 2021-05-21
Mission Solar Energy LLC | MSE385SR9S | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 356 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 9.993 | 48.53 | 9.426 | 40.84 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9143 | 38.8177 | 7.7628 | 36.7792 | [6 empty] | 2020-01-13 | 2020-02-03
Mission Solar Energy LLC | MSE385SX5R | 385 W, 66 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 385 | 359.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 66 | 1 | N | 10.9741 | 45.0337 | 10.4238 | 36.9347 | 43.75 | -0.367 | 0.033 | -0.259 |  |  | 2.1027 | 36.5522 | 8.4521 | 34.4967 | [6 empty] | 2021-05-21
Mission Solar Energy LLC | MSE390SR9S | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 360.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 10.024 | 48.96 | 9.499 | 41.05 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9292 | 39.0173 | 7.8229 | 36.9683 | [6 empty] | 2020-01-13 | 2020-02-03
Mission Solar Energy LLC | MSE390SX5R | 390 W, 66 cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 390 | 364.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.93 | 66 | 1 | N | 11.0144 | 45.1652 | 10.5234 | 37.0601 | 43.75 | -0.367 | 0.033 | -0.259 |  |  | 2.1228 | 36.6763 | 8.5329 | 34.6138 | [6 empty] | 2021-05-21
Mission Solar Energy LLC | MSE395SR9S | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 365.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 10.045 | 49.28 | 9.532 | 41.44 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9359 | 39.388 | 7.8501 | 37.3195 | [6 empty] | 2020-01-13 | 2020-02-03
Mission Solar Energy LLC | MSE400SR9S | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 370.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 10.067 | 49.46 | 9.61 | 41.62 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9517 | 39.559 | 7.9143 | 37.4816 | [6 empty] | 2020-01-13 | 2020-02-03
Mission Solar Energy LLC | MSE405SX6S | 405 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 405 | 376.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 10.89 | 48.56 | 10.23 | 39.59 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.0421 | 39.1022 | 8.2657 | 36.8366 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE405SX6W | 405 W, 72 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 405 | 376.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 10.89 | 48.56 | 10.23 | 39.59 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.0421 | 39.1022 | 8.2657 | 36.8366 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE405SX6Z | 405 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 405 | 375.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.124 | 72 | 1 | N | 10.8112 | 48.554 | 10.1899 | 39.7451 | 46.08 | -0.347 | 0.043 | -0.261 |  |  | 2.0227 | 39.0192 | 8.1923 | 37.07 | [6 empty] | 2021-05-21
Mission Solar Energy LLC | MSE410SX6S | 410 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 410 | 381.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 10.93 | 48.71 | 10.32 | 39.73 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.06 | 39.2405 | 8.3384 | 36.9669 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE410SX6W | 410 W, 72 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 410 | 381.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 10.93 | 48.71 | 10.32 | 39.73 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.06 | 39.2405 | 8.3384 | 36.9669 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE410SX6Z | 410 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 410 | 380.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.124 | 72 | 1 | N | 10.8524 | 48.6974 | 10.2803 | 39.882 | 46.08 | -0.347 | 0.043 | -0.261 |  |  | 2.0407 | 39.1535 | 8.265 | 37.1976 | [6 empty] | 2021-05-21
Mission Solar Energy LLC | MSE415SX6S | 415 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 415 | 386.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 10.99 | 48.92 | 10.39 | 39.93 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.074 | 39.438 | 8.395 | 37.153 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE415SX6W | 415 W, 72 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 415 | 386.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 10.99 | 48.92 | 10.39 | 39.93 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.074 | 39.438 | 8.395 | 37.153 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE415SX6Z | 415 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 415 | 385.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.124 | 72 | 1 | N | 10.9128 | 48.9126 | 10.3524 | 40.0872 | 46.08 | -0.347 | 0.043 | -0.261 |  |  | 2.055 | 39.355 | 8.323 | 37.389 | [6 empty] | 2021-05-21
Mission Solar Energy LLC | MSE420SX6S | 420 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 420 | 391.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 11.05 | 49.14 | 10.46 | 40.14 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.088 | 39.6454 | 8.4516 | 37.3484 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE420SX6W | 420 W, 72 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 420 | 391.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 11.05 | 49.14 | 10.46 | 40.14 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.088 | 39.6454 | 8.4516 | 37.3484 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE420SX6Z | 420 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 420 | 390.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.124 | 72 | 1 | N | 10.9741 | 49.1277 | 10.4238 | 40.2924 | 46.08 | -0.347 | 0.043 | -0.261 |  |  | 2.0692 | 39.5565 | 8.3804 | 37.5804 | [6 empty] | 2021-05-21
Mission Solar Energy LLC | TXS6-420144BB | 420 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 420 | 390.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.04 | 49.1 | 10.45 | 40.2 | 46.8 | -0.3265 | 0.0598 | -0.2619 |  |  | 1.9875 | 38.8455 | 8.2249 | 37.5593 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-420144BW | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 391.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.04 | 49.1 | 10.45 | 40.2 | 45.7 | -0.3317 | 0.0439 | -0.2591 |  |  | 2.1134 | 38.7724 | 8.36 | 37.6321 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | MSE425SX6S | 425 W, 72 cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 425 | 395.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 11.09 | 49.28 | 10.55 | 40.27 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.1059 | 39.7738 | 8.5243 | 37.4694 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE425SX6W | 425 W, 72 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 425 | 395.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.136 | 72 | 1 | N | 11.09 | 49.28 | 10.55 | 40.27 | 44.69 | -0.359 | 0.044 | -0.261 |  |  | 2.1059 | 39.7738 | 8.5243 | 37.4694 | [6 empty] | 2021-02-11
Mission Solar Energy LLC | MSE425SX6Z | 425 W, 72 cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 425 | 395 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.124 | 72 | 1 | N | 11.0144 | 49.2712 | 10.5122 | 40.4292 | 46.08 | -0.347 | 0.043 | -0.261 |  |  | 2.0867 | 39.6908 | 8.4514 | 37.708 | [6 empty] | 2021-05-21
Mission Solar Energy LLC | TXS6-425144BB | 425 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 425 | 395.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.11 | 49.3 | 10.52 | 40.4 | 46.8 | -0.3265 | 0.0598 | -0.2619 |  |  | 2.0008 | 39.0387 | 8.28 | 37.7461 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-425144BW | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 396.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.11 | 49.3 | 10.52 | 40.4 | 45.7 | -0.3317 | 0.0439 | -0.2591 |  |  | 2.1275 | 38.9653 | 8.416 | 37.8193 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-430144BB | 430 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 430 | 400.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.19 | 49.5 | 10.6 | 40.6 | 46.8 | -0.3265 | 0.0598 | -0.2619 |  |  | 2.016 | 39.232 | 8.343 | 37.933 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-430144BW | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 401.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.19 | 49.5 | 10.6 | 40.6 | 45.7 | -0.3317 | 0.0439 | -0.2591 |  |  | 2.1437 | 39.1582 | 8.48 | 38.0066 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-435144BB | 435 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 435 | 405.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.26 | 49.7 | 10.67 | 40.8 | 46.8 | -0.3265 | 0.0598 | -0.2619 |  |  | 2.0293 | 39.4253 | 8.3981 | 38.1199 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-435144BW | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 406.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.26 | 49.7 | 10.67 | 40.8 | 45.7 | -0.3317 | 0.0439 | -0.2591 |  |  | 2.1578 | 39.3511 | 8.536 | 38.1938 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-440144BB | 440 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 440 | 410 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.33 | 49.9 | 10.74 | 41 | 46.8 | -0.3265 | 0.0598 | -0.2619 |  |  | 2.0426 | 39.6185 | 8.4532 | 38.3067 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-440144BW | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 411.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.33 | 49.9 | 10.74 | 41 | 45.7 | -0.3317 | 0.0439 | -0.2591 |  |  | 2.172 | 39.544 | 8.592 | 38.381 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-445144BB | 445 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 445 | 414.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.4 | 50.1 | 10.81 | 41.2 | 46.8 | -0.3265 | 0.0598 | -0.2619 |  |  | 2.0559 | 39.8118 | 8.5083 | 38.4936 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-445144BW | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 415.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.4 | 50.1 | 10.81 | 41.2 | 45.7 | -0.3317 | 0.0439 | -0.2591 |  |  | 2.1862 | 39.7369 | 8.648 | 38.5682 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-450144BB | 450 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 450 | 419.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.46 | 50.3 | 10.87 | 41.4 | 46.8 | -0.3265 | 0.0598 | -0.2619 |  |  | 2.0674 | 40.005 | 8.5555 | 38.6804 | [6 empty] | 2021-06-11
Mission Solar Energy LLC | TXS6-450144BW | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 420.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.15 | 72 | 2 | N | 11.46 | 50.3 | 10.87 | 41.4 | 45.7 | -0.3317 | 0.0439 | -0.2591 |  |  | 2.1983 | 39.9298 | 8.696 | 38.7554 | [6 empty] | 2021-06-11
Mitsubishi Electric | PV-EE120MF5F | 120 W Polycrystalline Module, Lead-Free Solder | UL 1703 | 120 | 108.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.0076 | 36 | 1 | N | 7.75 | 21.6 | 6.99 | 17.2 | 43 | -0.4741 | 0.0639 | -0.3451 | 3.7e-05 | -0.473 | 1.3903 | 16.8929 | 5.6577 | 16.0738 | Rack | Flat Plate | 0.674 | 1.495 | 1 | 0.19571
Mitsubishi Electric | PV-EE125MF5F | 125 W Polycrystalline Module, Lead-Free Solder | UL 1703 | 125 | 112.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.0076 | 36 | 1 | N | 7.9 | 21.8 | 7.23 | 17.3 | 43 | -0.5098 | 0.0427 | -0.3637 | -0.0268 | -0.4808 | 1.438 | 16.9911 | 5.8519 | 16.1673 | Rack | Flat Plate | 0.674 | 1.495 | 1 | 0.19547
Mitsubishi Electric | PV-EE130MF5F | 130 W Polycrystalline Module, Lead-Free Solder | UL 1703 | 130 | 117 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.0076 | 36 | 1 | N | 8.05 | 21.9 | 7.47 | 17.4 | 43 | -0.5098 | 0.0427 | -0.3637 | -0.0268 | -0.4808 | 1.4857 | 17.0893 | 6.0462 | 16.2607 | Rack | Flat Plate | 0.674 | 1.495 | 1 | 0.19531
Mitsubishi Electric | PV-MF170UD4 | 170 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 170 | 151.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3844 | 50 | 1 | N | 7.83 | 29.9 | 7.19 | 23.7 | 47.3 | -0.4429 | 0.0732 | -0.3409 | 0.0145 | -0.4563 | 1.2839 | 23.1602 | 5.6197 | 21.2858 | Rack | Flat Plate | 0.835 | 1.658 | 1 | 0.17492
Mitsubishi Electric | PV-UD170MF5 | 170 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 170 | 150.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3828 | 50 | 1 | N | 7.83 | 29.9 | 7.19 | 23.7 | 45 | -0.5098 | 0.0427 | -0.3637 | -0.0268 | -0.4808 | 1.4481 | 23.2966 | 5.8128 | 21.5821 | Rack | Flat Plate | 0.834 | 1.658 | 1 | 0.19845
Mitsubishi Electric | PV-MF175UD4 | 175 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 175 | 156.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3844 | 50 | 1 | N | 7.93 | 30.2 | 7.32 | 23.9 | 47.3 | -0.4429 | 0.0732 | -0.3409 | 0.0145 | -0.4563 | 1.3071 | 23.3557 | 5.7116 | 21.3925 | Rack | Flat Plate | 0.835 | 1.658 | 1 | 0.17445
Mitsubishi Electric | PV-UD175MF5 | 175 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 175 | 157 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3828 | 50 | 1 | N | 7.93 | 30.2 | 7.32 | 23.9 | 46.4 | -0.4396 | 0.0754 | -0.3427 | 0.0358 | -0.4713 | 1.4883 | 23.0338 | 5.7406 | 21.449 | Rack | Flat Plate | 0.834 | 1.658 | 1 | 0.19589
Mitsubishi Electric | PV-MF180UD4 | 180 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 180 | 160.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3844 | 50 | 1 | N | 8.03 | 30.4 | 7.45 | 24.2 | 47.3 | -0.4429 | 0.0732 | -0.3409 | 0.0145 | -0.4563 | 1.3304 | 23.6489 | 5.8229 | 21.7349 | Rack | Flat Plate | 0.835 | 1.658 | 1 | 0.17479
Mitsubishi Electric | PV-UD180MF5 | 180 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 180 | 161.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3828 | 50 | 1 | N | 8.03 | 30.4 | 7.45 | 24.2 | 46.4 | -0.4396 | 0.0754 | -0.3427 | 0.0358 | -0.4713 | 1.5147 | 23.3229 | 5.8425 | 21.7182 | Rack | Flat Plate | 0.834 | 1.658 | 1 | 0.19627
Mitsubishi Electric | PV-UD185HA6 | 185 W Polycrystalline Module | UL 1703 | 185 | 169.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3828 | 50 | 1 | N | 8.24 | 30.3 | 7.44 | 24.9 | 45.2 | -0.381 | 0.124 | -0.338 | 0.121 | -0.482 | 1.4976 | 24.109 | 6.2242 | 22.7574 | Rack | Flat Plate | 0.834 | 1.658 | 1 | 0.19516
Mitsubishi Electric | PV-UD185MF5 | 185 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 185 | 166.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3828 | 50 | 1 | N | 8.13 | 30.6 | 7.58 | 24.4 | 46.4 | -0.4396 | 0.0754 | -0.3427 | 0.0358 | -0.4713 | 1.5412 | 23.5157 | 5.9445 | 21.8977 | Rack | Flat Plate | 0.834 | 1.658 | 1 | 0.1959
Mitsubishi Electric | PV-UD190HA6 | 190 W Polycrystalline Module | UL 1703 | 190 | 174.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3828 | 50 | 1 | N | 8.36 | 30.5 | 7.56 | 25.1 | 45.2 | -0.381 | 0.124 | -0.338 | 0.121 | -0.482 | 1.5217 | 24.3027 | 6.3246 | 22.9402 | Rack | Flat Plate | 0.834 | 1.658 | 1 | 0.19464
Mitsubishi Electric | PV-UD190MF5 | 190 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 190 | 169.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3844 | 50 | 1 | N | 8.23 | 30.8 | 7.71 | 24.7 | 47.4 | -0.4427 | 0.0382 | -0.3257 | -0.0238 | -0.4215 | 1.4726 | 23.8207 | 5.9639 | 22.3719 | Rack | Flat Plate | 0.835 | 1.658 | 1 | 0.18462
Mitsubishi Electric | PV-UD195HA6 | 195 W Polycrystalline Module | UL 1703 | 195 | 179 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.3828 | 50 | 1 | N | 8.48 | 30.6 | 7.69 | 25.4 | 45.2 | -0.381 | 0.124 | -0.338 | 0.121 | -0.482 | 1.5479 | 24.5932 | 6.4334 | 23.2144 | Rack | Flat Plate | 0.834 | 1.658 | 1 | 0.19522
Mitsubishi Electric | PV-UJ212G6 | 212W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 212 | 194.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.13 | 36.1 | 7.31 | 29 | 45.5 | -0.37 | 0.13 | -0.3 | 0.06 | -0.51 | 1.5279 | 29.1948 | 5.9219 | 26.8575 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.21041
Mitsubishi Electric | PV-UJ218G6 | 218W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 218 | 200.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.25 | 36.3 | 7.44 | 29.3 | 45.5 | -0.37 | 0.13 | -0.3 | 0.06 | -0.51 | 1.5551 | 29.4968 | 6.0272 | 27.1354 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.21041
Mitsubishi Electric | PV-UJ220GA6 | 220 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 220 | 198.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.2 | 36.2 | 7.39 | 29.7 | 47 | -0.41 | 0.15 | -0.32 | 0.05 | -0.44 | 1.5685 | 28.7601 | 6.103 | 26.5836 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.20505
Mitsubishi Electric | PV-UJ220GA6-D | 220 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 220 | 198.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.2 | 36.2 | 7.39 | 29.7 | 47 | -0.41 | 0.15 | -0.32 | 0.05 | -0.44 | 1.5685 | 28.7601 | 6.103 | 26.5836 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.20505
Mitsubishi Electric | PV-UJ224G6 | 224W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 224 | 205.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.37 | 36.6 | 7.56 | 29.6 | 45.5 | -0.37 | 0.13 | -0.3 | 0.06 | -0.51 | 1.5802 | 29.7988 | 6.1244 | 27.4132 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.21021
Mitsubishi Electric | PV-UJ225GA6 | 225 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 225 | 203.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.3 | 36.4 | 7.5 | 30 | 47 | -0.41 | 0.15 | -0.32 | 0.05 | -0.44 | 1.5918 | 29.0506 | 6.1939 | 26.8521 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.20553
Mitsubishi Electric | PV-UJ225GA6-D | 225 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 225 | 203.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.3 | 36.4 | 7.5 | 30 | 47 | -0.41 | 0.15 | -0.32 | 0.05 | -0.44 | 1.5918 | 29.0506 | 6.1939 | 26.8521 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.20553
Mitsubishi Electric | PV-UJ230GA6 | 230 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 230 | 207.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.39 | 36.6 | 7.62 | 30.2 | 47 | -0.41 | 0.15 | -0.32 | 0.05 | -0.44 | 1.6173 | 29.2443 | 6.293 | 27.0311 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.20564
Mitsubishi Electric | PV-UJ230GA6-D | 230 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 230 | 207.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.39 | 36.6 | 7.62 | 30.2 | 47 | -0.41 | 0.15 | -0.32 | 0.05 | -0.44 | 1.6173 | 29.2443 | 6.293 | 27.0311 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.20564
Mitsubishi Electric | PV-MJU235GB | 235 W Monocrystalline Module | UL 1703 | 235 | 212.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5258 | 60 | 1 | N | 8.49 | 36.8 | 7.95 | 29.6 | 45 | -0.456 | 0.06 | -0.34 | 0.012 | -0.466 | 1.6825 | 28.6602 | 6.4896 | 26.577 | Rack | Flat Plate | 0.956 | 1.596 | 1 | 0.20519
Mitsubishi Electric | PV-UJ235GA6 | 235 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 235 | 212.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.49 | 36.8 | 7.71 | 30.5 | 47 | -0.41 | 0.15 | -0.32 | 0.05 | -0.44 | 1.6364 | 29.5348 | 6.3673 | 27.2996 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.20566
Mitsubishi Electric | PV-UJ235GA6-D | 235 W Polycrystalline Module, Lead-Free Solder, MC Connectors | UL 1703 | 235 | 212.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6481 | 60 | 1 | N | 8.49 | 36.8 | 7.71 | 30.5 | 47 | -0.41 | 0.15 | -0.32 | 0.05 | -0.44 | 1.6364 | 29.5348 | 6.3673 | 27.2996 | Rack | Flat Plate | 0.994 | 1.658 | 1 | 0.20566
Mitsubishi Electric | PV-MJU240GB | 240 W Monocrystalline Module | UL 1703 | 240 | 217.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5258 | 60 | 1 | N | 8.6 | 37 | 8.07 | 29.8 | 45 | -0.456 | 0.06 | -0.34 | 0.012 | -0.466 | 1.7079 | 28.8538 | 6.5876 | 26.7566 | Rack | Flat Plate | 0.956 | 1.596 | 1 | 0.20533
Mitsubishi Electric | PV-MJU245GB | 245 W Monocrystalline Module | UL 1703 | 245 | 221.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5258 | 60 | 1 | N | 8.72 | 37.2 | 8.18 | 30 | 45 | -0.456 | 0.06 | -0.34 | 0.012 | -0.466 | 1.7311 | 29.0475 | 6.6774 | 26.9362 | Rack | Flat Plate | 0.956 | 1.596 | 1 | 0.20525
Mitsubishi Electric | PV-MLU250HC | 250 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 250 | 225.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5283 | 60 | 1 | N | 8.79 | 37.6 | 8.08 | 31 | 45.7 | -0.454 | 0.104 | -0.387 | 0.033 | -0.485 | 1.6053 | 34.0143 | 6.5164 | 26.843 | Rack | Flat Plate | 0.963 | 1.587 | 1 | 0.21841
Mitsubishi Electric | PV-MLE255HD | 255 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 255 | 230.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5283 | 60 | 1 | N | 8.89 | 37.8 | 8.18 | 31.2 | 45.7 | -0.454 | 0.104 | -0.387 | 0.033 | -0.485 | 1.6251 | 34.2337 | 6.5971 | 27.0162 | Rack | Flat Plate | 0.963 | 1.587 | 1 | 0.21817
Mitsubishi Electric | PV-MLU255HC | 255 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 255 | 230.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5283 | 60 | 1 | N | 8.89 | 37.8 | 8.18 | 31.2 | 45.7 | -0.454 | 0.104 | -0.387 | 0.033 | -0.485 | 1.6251 | 34.2337 | 6.5971 | 27.0162 | Rack | Flat Plate | 0.963 | 1.587 | 1 | 0.21817
Mitsubishi Electric | PV-MLE260HD | 260 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 260 | 235.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5283 | 60 | 1 | N | 8.98 | 38 | 8.29 | 31.4 | 45.7 | -0.454 | 0.104 | -0.387 | 0.033 | -0.485 | 1.647 | 34.4532 | 6.6858 | 27.1894 | Rack | Flat Plate | 0.963 | 1.587 | 1 | 0.21825
Mitsubishi Electric | PV-MLU260HC | 260 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 260 | 235.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.5283 | 60 | 1 | N | 8.98 | 38 | 8.29 | 31.4 | 45.7 | -0.454 | 0.104 | -0.387 | 0.033 | -0.485 | 1.647 | 34.4532 | 6.6858 | 27.1894 | Rack | Flat Plate | 0.963 | 1.587 | 1 | 0.21825
Mitsubishi Electric | PV-MJE265FB | 265 W Monocrystalline Module | UL 1703 | 265 | 239.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4339 | 60 | 1 | N | 9.1 | 38 | 8.59 | 30.9 | 46 | -0.465 | 0.059 | -0.347 | -0.006 | -0.459 | 1.69 | 29.85 | 6.92 | 27.78 | Rack | Flat Plate | 0.911 | 1.574 | 1 | 0.19036
Mitsubishi Electric | PV-MLE265HD | 265 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 265 | 239.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4602 | 60 | 1 | N | 9.08 | 38.2 | 8.38 | 31.7 | 45.9 | -0.466 | 0.081 | -0.373 | 0.029 | -0.492 | 1.754 | 30.9005 | 6.6619 | 28.4587 | Rack | Flat Plate | 0.936 | 1.56 | 1 | 0.20452
Mitsubishi Electric | PV-MLE265HD2 | 265 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 265 | 238.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4602 | 60 | 1 | N | 9.08 | 38.2 | 8.38 | 31.7 | 48.5 | -0.433 | 0.051 | -0.337 | -0.003 | -0.431 | 1.63 | 30.57 | 6.64 | 28.99 | Rack | Flat Plate | 0.936 | 1.56 | 1 | 0.18803
Mitsubishi Electric | PV-MJE270FB | 270 W Monocrystalline Module | UL 1703 | 270 | 244 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4339 | 60 | 1 | N | 9.23 | 38.2 | 8.69 | 31.1 | 46 | -0.465 | 0.059 | -0.347 | -0.006 | -0.459 | 1.71 | 30.05 | 7 | 27.96 | Rack | Flat Plate | 0.911 | 1.574 | 1 | 0.19032
Mitsubishi Electric | PV-MLE270HD | 270 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 270 | 242.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4602 | 60 | 1 | N | 9.18 | 38.4 | 8.48 | 31.9 | 46.5 | -0.4806 | 0.0455 | -0.4285 | -0.0227 | -0.4606 | 2.52 | 31.67 | 6.78 | 28.51 | Rack | Flat Plate | 0.936 | 1.56 | 1 | 0.29559
Mitsubishi Electric | PV-MLE270HD2 | 270 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 270 | 242.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4602 | 60 | 1 | N | 9.18 | 38.4 | 8.48 | 31.9 | 48.5 | -0.433 | 0.051 | -0.337 | -0.003 | -0.431 | 1.65 | 30.76 | 6.71 | 29.17 | Rack | Flat Plate | 0.936 | 1.56 | 1 | 0.18798
Mitsubishi Electric | PV-MJE275FB | 275 W Monocrystalline Module | UL 1703 | 275 | 247.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.36 | 38.3 | 8.79 | 31.3 | 46 | -0.465 | 0.059 | -0.347 | -0.006 | -0.459 | 1.7292 | 30.2383 | 7.0814 | 28.1349 | Rack | Flat Plate | 0.986 | 1.65 | 1 | 0.19014
Mitsubishi Electric | PV-MJE275FB-B | 275 W Monocrystalline Module | UL 1703 | 275 | 247.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6471 | 60 | 1 | N | 9.36 | 38.3 | 8.79 | 31.3 | 46 | -0.465 | 0.059 | -0.347 | -0.006 | -0.459 | 1.68 | 29.9678 | 6.88 | 27.8833 | Rack | Flat Plate | 0.994 | 1.657 | 1 | 0.18308
Mitsubishi Electric | PV-MLE275HD2 | 275 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 275 | 247.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4602 | 60 | 1 | N | 9.28 | 38.5 | 8.58 | 32.1 | 48.5 | -0.433 | 0.051 | -0.337 | -0.003 | -0.431 | 1.65 | 30.76 | 6.71 | 29.17 | Rack | Flat Plate | 0.936 | 1.56 | 1 | 0.18456
Mitsubishi Electric | PV-MJE280FB | 280 W Monocrystalline Module | UL 1703 | 280 | 252.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6471 | 60 | 1 | N | 9.5 | 38.4 | 8.9 | 31.5 | 46 | -0.465 | 0.059 | -0.347 | -0.006 | -0.459 | 1.6407 | 29.5524 | 6.7189 | 27.4967 | Rack | Flat Plate | 0.994 | 1.657 | 1 | 0.17316
Mitsubishi Electric | PV-MJE280FB-B | 280 W Monocrystalline Module | UL 1703 | 280 | 252.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6471 | 60 | 1 | N | 9.5 | 38.4 | 8.9 | 31.5 | 46 | -0.465 | 0.059 | -0.347 | -0.006 | -0.459 | 1.6603 | 29.7649 | 6.7994 | 27.6945 | Rack | Flat Plate | 0.994 | 1.657 | 1 | 0.1765
Mitsubishi Electric | PV-MLE280HD2 | 280 W Monocrystalline Module, Half-Cut Cells | UL 1703 | 280 | 252.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.4602 | 60 | 1 | N | 9.37 | 38.6 | 8.68 | 32.4 | 48.5 | -0.433 | 0.051 | -0.337 | -0.003 | -0.431 | 1.6682 | 36.9854 | 6.7926 | 35.0806 | Rack | Flat Plate | 0.936 | 1.56 | 1 | 0.22036
MSquare Energy Pty Ltd | MSE-345W-m60H | 345 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 345 | 322.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.84 | 60 | 2 | N | 10.53 | 41.25 | 10.03 | 34.39 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.0423 | 32.2244 | 7.8416 | 32.6984 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-350W-m60H | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 327.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.84 | 60 | 2 | N | 10.59 | 41.4 | 10.06 | 34.79 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.0484 | 32.5992 | 7.8651 | 33.0787 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-355W-m60H | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 331.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.84 | 60 | 2 | N | 10.63 | 41.6 | 10.1 | 35.14 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.0565 | 32.9271 | 7.8964 | 33.4115 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-360W-m60H | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 336.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.84 | 60 | 2 | N | 11.24 | 41.8 | 10.23 | 35.19 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.083 | 32.974 | 7.998 | 33.459 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-365W-m60H | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 341.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.84 | 60 | 2 | N | 11.3 | 42 | 10.33 | 35.33 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.1034 | 33.1052 | 8.0762 | 33.5921 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-370W-m60H | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 346.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.84 | 60 | 2 | N | 11.36 | 42.2 | 10.45 | 35.4 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.1278 | 33.1708 | 8.17 | 33.6587 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-415W-m72H | 415 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 415 | 387.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.23 | 49.6 | 10.08 | 41.15 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.0306 | 38.9691 | 8.5106 | 36.7376 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-420W-m72H | 420 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 420 | 392.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.27 | 49.8 | 10.19 | 41.2 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.0528 | 39.0164 | 8.6035 | 36.7822 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-425W-m72H | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 397.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.29 | 50 | 10.3 | 41.26 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.0749 | 39.0732 | 8.6963 | 36.8358 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-430W-m72H | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 402 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.3 | 50.2 | 10.36 | 41.51 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.087 | 39.31 | 8.747 | 37.059 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-435W-m72H | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 406.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.31 | 50.35 | 10.44 | 41.66 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.1031 | 39.4521 | 8.8145 | 37.1929 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-440W-m72H | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 411.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.34 | 50.5 | 10.52 | 41.81 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.1192 | 39.5941 | 8.8821 | 37.3268 | [6 empty] | 2021-09-21
MSquare Energy Pty Ltd | MSE-445W-m72H | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 416.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.21 | 72 | 2 | N | 11.37 | 50.58 | 10.61 | 41.96 | 43.8 | -0.3551 | 0.0569 | -0.2761 |  |  | 2.1374 | 39.7362 | 8.9581 | 37.4607 | [6 empty] | 2021-09-21
New East Solar Energy (Cambodia) Co.,Ltd. | NESE295-60MV | 295 W, 60 cell monocrystalline module, white or black backsheet, silver or black frame, 1500V max system Vdc | UL 61730 | 295 | 271.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 9.66 | 40.1 | 9.16 | 32.3 | 46.9 | -0.3675 | 0.0506 | -0.2792 |  |  | 1.8557 | 31.5275 | 7.2302 | 29.9894 | [6 empty] | 2020-05-01 | 2020-11-23
New East Solar Energy (Cambodia) Co.,Ltd. | NESE300-60MV | 300 W, 60 cell monocrystalline module, white or black backsheet, silver or black frame, 1500V max system Vdc | UL 61730 | 300 | 275.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 9.75 | 40.2 | 9.26 | 32.4 | 46.9 | -0.3675 | 0.0506 | -0.2792 |  |  | 1.876 | 31.6251 | 7.3092 | 30.0822 | [6 empty] | 2020-05-01 | 2020-11-23
New East Solar Energy (Cambodia) Co.,Ltd. | NESE305-60MV | 305 W, 60 cell monocrystalline module, white or black backsheet, silver or black frame, 1500V max system Vdc | UL 61730 | 305 | 280.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 9.86 | 40.3 | 9.36 | 32.6 | 46.9 | -0.3675 | 0.0506 | -0.2792 |  |  | 1.8962 | 31.8203 | 7.3881 | 30.2679 | [6 empty] | 2020-05-01 | 2020-11-23
New East Solar Energy (Cambodia) Co.,Ltd. | NESE310-60MV | 310 W, 60 cell monocrystalline module, white or black backsheet, silver or black frame, 1500V max system Vdc | UL 61730 | 310 | 285.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 9.95 | 40.5 | 9.45 | 32.8 | 46.9 | -0.3675 | 0.0506 | -0.2792 |  |  | 1.9145 | 32.0156 | 7.4591 | 30.4536 | [6 empty] | 2020-05-01 | 2020-11-23
New East Solar Energy (Cambodia) Co.,Ltd. | NESE315-60MV | 315 W, 60 cell monocrystalline module, white or black backsheet, silver or black frame, 1500V max system Vdc | UL 61730 | 315 | 290 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.07 | 40.6 | 9.55 | 33 | 46.9 | -0.3675 | 0.0506 | -0.2792 |  |  | 1.9347 | 32.2108 | 7.5381 | 30.6393 | [6 empty] | 2020-05-01 | 2020-11-23
New East Solar Energy (Cambodia) Co.,Ltd. | NESE315-72PV | 315 W, 72 cell polycrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 315 | 290.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 24 | 3 | N | 8.79 | 46.7 | 8.43 | 37.6 | 46 | -0.3665 | 0.0603 | -0.2849 | 36.0055 | 6.7782 | 1.6717 | 36.4908 | 6.7536 | 34.8809 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE320-60MV | 320 W, 60 cell monocrystalline module, white or black backsheet, silver or black frame, 1500V max system Vdc | UL 61730 | 320 | 294.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.18 | 40.7 | 9.65 | 33.2 | 46.9 | -0.3675 | 0.0506 | -0.2792 |  |  | 1.955 | 32.406 | 7.617 | 30.825 | [6 empty] | 2020-05-01 | 2020-11-23
New East Solar Energy (Cambodia) Co.,Ltd. | NESE320-72PV | 320W, 72 cell polycrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 320 | 294.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 24 | 3 | N | 8.89 | 46.8 | 8.54 | 37.7 | 46 | -0.3665 | 0.0603 | -0.2849 | 36.1996 | 6.8502 | 1.6935 | 36.5879 | 6.8417 | 34.9737 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE325-60MV | 325 W, 60 cell monocrystalline module, white or black backsheet, silver or black frame, 1500V max system Vdc | UL 61730 | 325 | 299.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.27 | 40.8 | 9.75 | 33.3 | 46.9 | -0.3675 | 0.0506 | -0.2792 |  |  | 1.9753 | 32.5036 | 7.6959 | 30.9178 | [6 empty] | 2020-05-01 | 2020-11-23
New East Solar Energy (Cambodia) Co.,Ltd. | NESE325-72PV | 325 W, 72 cell polycrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 325 | 299.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 24 | 3 | N | 8.99 | 46.9 | 8.64 | 37.8 | 46 | -0.3665 | 0.0603 | -0.2849 | 36.4908 | 6.9221 | 1.7133 | 36.6849 | 6.9218 | 35.0665 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE330-60MV | 330 W, 60 cell monocrystalline module, white or black backsheet, silver or black frame, 1500V max system Vdc | UL 61730 | 330 | 304.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 1 | N | 10.37 | 41 | 9.86 | 33.5 | 46.9 | -0.3675 | 0.0506 | -0.2792 |  |  | 1.9975 | 32.6988 | 7.7828 | 31.1035 | [6 empty] | 2020-11-23
New East Solar Energy (Cambodia) Co.,Ltd. | NESE330-72PV | 330 W, 72 cell polycrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 330 | 304.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 24 | 3 | N | 9.08 | 47 | 8.74 | 37.9 | 46 | -0.3665 | 0.0603 | -0.2849 | 36.6849 | 6.9941 | 1.7331 | 36.7819 | 7.0019 | 35.1592 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE335-72PV | 335 W, 72 cell polycrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 335 | 309 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 24 | 3 | N | 9.18 | 47.1 | 8.82 | 38 | 46 | -0.3665 | 0.0603 | -0.2849 | 36.879 | 7.066 | 1.749 | 36.879 | 7.066 | 35.252 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE340-72PV | 340 W, 72 cell polycrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 340 | 313.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 24 | 3 | N | 9.27 | 47.2 | 8.93 | 38.1 | 46 | -0.3665 | 0.0603 | -0.2849 | 36.9761 | 7.1459 | 1.7708 | 36.9761 | 7.1541 | 35.3448 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE345-72PV | 345 W, 72 cell polycrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 345 | 318.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.92 | 24 | 3 | N | 9.38 | 47.3 | 9.04 | 38.2 | 46 | -0.3665 | 0.0603 | -0.2849 | 37.0731 | 7.2259 | 1.7926 | 37.0731 | 7.2422 | 35.4375 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE355-72MV | 355 W, 72 cell monocrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 355 | 331.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 24 | 3 | N | 9.59 | 48.1 | 9.04 | 39.3 | 44.3 | -0.3432 | 0.0412 | -0.2615 |  |  | 1.7616 | 39.0186 | 7.0891 | 37.3459 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE360-72MV | 360 W, 72 cell monocrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 360 | 336.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 24 | 3 | N | 9.69 | 48.2 | 9.15 | 39.4 | 44.3 | -0.3432 | 0.0412 | -0.2615 |  |  | 1.7831 | 39.1179 | 7.1753 | 37.4409 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE365-72MV | 365 W, 72 cell monocrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 365 | 341.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 24 | 3 | N | 9.78 | 48.3 | 9.24 | 39.5 | 44.3 | -0.3432 | 0.0412 | -0.2615 |  |  | 1.8006 | 39.2171 | 7.2459 | 37.5359 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE370-72MV | 370 W, 72 cell monocrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 370 | 346 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 24 | 3 | N | 9.87 | 48.4 | 9.34 | 39.6 | 44.3 | -0.3432 | 0.0412 | -0.2615 |  |  | 1.8201 | 39.3164 | 7.3243 | 37.6309 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE375-72MV | 375 W, 72 cell monocrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 375 | 350.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 24 | 3 | N | 9.99 | 48.6 | 9.45 | 39.7 | 44.3 | -0.3432 | 0.0412 | -0.2615 |  |  | 1.8415 | 39.4157 | 7.4106 | 37.726 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE380-72MV | 380 W, 72 cell monocrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 380 | 355.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 24 | 3 | N | 10.08 | 48.7 | 9.55 | 39.8 | 44.3 | -0.3432 | 0.0412 | -0.2615 |  |  | 1.861 | 39.515 | 7.489 | 37.821 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE385-72MV | 385 W, 72 cell monocrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 385 | 360.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 24 | 3 | N | 10.18 | 48.8 | 9.65 | 39.9 | 44.3 | -0.3432 | 0.0412 | -0.2615 |  |  | 1.8805 | 39.6143 | 7.5674 | 37.916 | [6 empty] | 2020-05-01
New East Solar Energy (Cambodia) Co.,Ltd. | NESE390-72MV | 390 W, 72 cell monocrystalline module, white frame and substrate, 1500V max system Vdc | UL 61730 | 390 | 365.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.92 | 24 | 3 | N | 10.28 | 48.9 | 9.75 | 40 | 44.3 | -0.3432 | 0.0412 | -0.2615 |  |  | 1.9 | 39.7136 | 7.6458 | 38.0111 | [6 empty] | 2020-05-01
Next Energy Alliance LLC | NEA265M-60 | 265 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 265 | 238.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.05 | 38.26 | 8.52 | 31.11 | 46.6 | -0.4567 | 0.0634 | -0.3541 |  |  | 1.5432 | 30.4901 | 6.6044 | 27.901 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA270M-60 | 270 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 270 | 242.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.17 | 38.46 | 8.62 | 31.33 | 46.6 | -0.4567 | 0.0634 | -0.3541 |  |  | 1.5613 | 30.7057 | 6.6819 | 28.0983 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA275M-60 | 275 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 275 | 247.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.25 | 38.86 | 8.73 | 31.51 | 46.6 | -0.4567 | 0.0634 | -0.3541 |  |  | 1.5812 | 30.8822 | 6.7672 | 28.2598 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA280M-60 | 280 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 280 | 252 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.37 | 39.05 | 8.84 | 31.68 | 46.6 | -0.4567 | 0.0634 | -0.3541 |  |  | 1.6012 | 31.0488 | 6.8525 | 28.4122 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA285M-60 | 285 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 285 | 256.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.49 | 39.25 | 8.95 | 31.85 | 46.6 | -0.4567 | 0.0634 | -0.3541 |  |  | 1.6211 | 31.2154 | 6.9377 | 28.5647 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA290M-60 | 290 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 290 | 261.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.6 | 39.46 | 9.06 | 32.07 | 46.6 | -0.4567 | 0.0634 | -0.3541 |  |  | 1.641 | 31.431 | 7.023 | 28.762 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA295M-60 | 295 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 295 | 265.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.72 | 39.64 | 9.14 | 32.29 | 46.6 | -0.4567 | 0.0634 | -0.3541 |  |  | 1.6555 | 31.6466 | 7.085 | 28.9593 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA300M-60 | 300 W, 60 cell monocrystalline module, white backsheet | UL 1703 | 300 | 270.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.84 | 39.82 | 9.23 | 32.51 | 46.6 | -0.4567 | 0.0634 | -0.3541 |  |  | 1.6718 | 31.8622 | 7.1548 | 29.1566 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA305M-60 | 305 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 305 | 280.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.96 | 40 | 9.32 | 32.73 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.837 | 32.101 | 7.383 | 30.727 | [6 empty] | 2019-05-15 | 2019-06-17
Next Energy Alliance LLC | NEA310M-60 | 310 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 310 | 285 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.08 | 40.18 | 9.41 | 32.95 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.8547 | 32.3168 | 7.4543 | 30.9335 | [6 empty] | 2019-06-17
Next Energy Alliance LLC | NEA315M-60 | 315 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 315 | 289.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.04 | 40.7 | 9.49 | 33.2 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.8705 | 32.562 | 7.5177 | 31.1682 | [6 empty] | 2019-06-17
Next Energy Alliance LLC | NEA320M-60 | 320 W, 60 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 320 | 294.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.15 | 40.9 | 9.59 | 33.4 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.8902 | 32.7581 | 7.5969 | 31.356 | [6 empty] | 2019-06-17
Next Energy Alliance LLC | NEA365M-72 | 365 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 365 | 335.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.93 | 48.01 | 9.29 | 39.29 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.7628 | 39.4272 | 7.2466 | 36.8546 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA370M-72 | 370 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 370 | 340.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.03 | 48.23 | 9.37 | 39.51 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.778 | 39.648 | 7.309 | 37.061 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA375M-72 | 375 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 375 | 344.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.12 | 48.45 | 9.44 | 39.73 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.7913 | 39.8688 | 7.3636 | 37.2674 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA380M-72 | 380 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 380 | 349.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.22 | 48.67 | 9.52 | 39.95 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.8065 | 40.0895 | 7.426 | 37.4737 | [6 empty] | 2019-05-15
Next Energy Alliance LLC | NEA385M-72 | 385 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 385 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.31 | 48.89 | 9.59 | 40.17 | 44.9 | -0.4131 | 0.0654 | -0.3339 |  |  | 1.8197 | 40.3103 | 7.4806 | 37.6801 | [6 empty] | 2019-05-15
ONYX SOLAR ENERGY S.L. | ONYX G/G M06666 | 291 W, 66 cell double glass monocrystalline module, 1000V max system rating | UL 1703 | 291 | 256.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.99 | 66 |  | Y | 8.93 | 42 | 8.39 | 35 | 49.3 | -0.46 | 0.02 | -0.33 | -0.02 | -0.44 | 1.186 | 31.981 | 7.337 | 31.238 | [6 empty] | 2019-01-02
Orb Energy Private Limited | Orb295M60-15 | 295 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 295 | 272.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 | 1 | N | 9.56 | 41 | 8.85 | 33.34 | 45.87 | -0.3643 | 0.0555 | -0.2757 |  |  | 1.7797 | 32.8086 | 7.1477 | 30.8306 | [6 empty] | 2020-02-03
Orb Energy Private Limited | Orb300M60-15 | 300 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 300 | 277.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 | 1 | N | 9.64 | 41.1 | 8.95 | 33.52 | 45.87 | -0.3643 | 0.0555 | -0.2757 |  |  | 1.7998 | 32.9857 | 7.2285 | 30.9971 | [6 empty] | 2020-02-03
Orb Energy Private Limited | Orb305M60-15 | 305 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 305 | 282.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 | 1 | N | 9.72 | 41.2 | 9.05 | 33.71 | 45.87 | -0.3643 | 0.0555 | -0.2757 |  |  | 1.8199 | 33.1727 | 7.3092 | 31.1728 | [6 empty] | 2020-02-03
Orb Energy Private Limited | Orb310M60-15 | 310 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 310 | 287.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 | 1 | N | 9.8 | 41.3 | 9.15 | 33.88 | 45.87 | -0.3643 | 0.0555 | -0.2757 |  |  | 1.84 | 33.34 | 7.39 | 31.33 | [6 empty] | 2020-02-03
Orb Energy Private Limited | Orb315M60-15 | 315 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 315 | 291.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 | 1 | N | 9.88 | 41.4 | 9.25 | 34.06 | 45.87 | -0.3643 | 0.0555 | -0.2757 |  |  | 1.8601 | 33.5171 | 7.4708 | 31.4965 | [6 empty] | 2020-02-03
Orb Energy Private Limited | Orb320M60-15 | 320 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 320 | 296.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 | 1 | N | 9.96 | 41.5 | 9.35 | 34.23 | 45.87 | -0.3643 | 0.0555 | -0.2757 |  |  | 1.8802 | 33.6844 | 7.5515 | 31.6537 | [6 empty] | 2020-02-03
Orb Energy Private Limited | Orb325M60-15 | 325 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 325 | 301.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.58 | 60 | 1 | N | 10.04 | 41.6 | 9.45 | 34.4 | 45.87 | -0.3643 | 0.0555 | -0.2757 |  |  | 1.9003 | 33.8517 | 7.6323 | 31.8109 | [6 empty] | 2020-02-03
Orb Energy Private Limited | Orb345M72-15 | 345 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 345 | 316.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.89 | 72 | 1 | N | 9.42 | 48.9 | 8.64 | 39.94 | 45.87 | -0.3968 | 0.0597 | -0.2994 |  |  | 1.7187 | 37.6445 | 6.8373 | 36.4819 | [6 empty] | 2019-12-23
Orb Energy Private Limited | Orb350M72-15 | 350 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 350 | 321.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.89 | 72 | 1 | N | 9.5 | 49 | 8.74 | 39.84 | 45.87 | -0.3968 | 0.0597 | -0.2994 |  |  | 1.7386 | 37.5502 | 6.9164 | 36.3906 | [6 empty] | 2019-12-23
Orb Energy Private Limited | Orb355M72-15 | 355 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 326 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.89 | 72 | 1 | N | 9.58 | 49.1 | 8.84 | 40.14 | 45.87 | -0.3968 | 0.0597 | -0.2994 |  |  | 1.7584 | 37.833 | 6.9955 | 36.6646 | [6 empty] | 2019-12-23
Orb Energy Private Limited | Orb360M72-15 | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 330.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.89 | 72 | 1 | N | 9.66 | 49.2 | 8.95 | 40.24 | 45.87 | -0.3968 | 0.0597 | -0.2994 |  |  | 1.7803 | 37.9272 | 7.0826 | 36.756 | [6 empty] | 2019-12-23
Orb Energy Private Limited | Orb365M72-15 | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 335.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.89 | 72 | 1 | N | 9.74 | 49.3 | 9.05 | 40.34 | 45.87 | -0.3968 | 0.0597 | -0.2994 |  |  | 1.8002 | 38.0215 | 7.1617 | 36.8473 | [6 empty] | 2019-12-23
Orb Energy Private Limited | Orb370M72-15 | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 340.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.89 | 72 | 1 | N | 9.82 | 49.4 | 9.15 | 40.44 | 45.87 | -0.3968 | 0.0597 | -0.2994 |  |  | 1.8201 | 38.1157 | 7.2409 | 36.9387 | [6 empty] | 2019-12-23
Orb Energy Private Limited | Orb375M72-15 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 344.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.89 | 72 | 1 | N | 9.9 | 49.5 | 9.25 | 40.54 | 45.87 | -0.3968 | 0.0597 | -0.2994 |  |  | 1.84 | 38.21 | 7.32 | 37.03 | [6 empty] | 2019-12-23
Orb Energy Private Limited | Orb380M72-15 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 349.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.89 | 72 | 1 | N | 9.98 | 49.6 | 9.35 | 40.64 | 45.87 | -0.3968 | 0.0597 | -0.2994 |  |  | 1.8599 | 38.3043 | 7.3991 | 37.1213 | [6 empty] | 2019-12-23
Panasonic Corporation of North America | EVPV350K | 350 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 350 | 331.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.44 | 43.2 | 9.73 | 36 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.8057 | 34.6483 | 7.3523 | 34.2359 | [6 empty] | 2020-12-21
Panasonic Corporation of North America | EVPV360 | 360 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730 | 360 | 342 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.49 | 43.9 | 9.82 | 36.7 | 44.01 | -0.279 | 0.037 | -0.241 |  |  | 1.8959 | 35.2656 | 7.5857 | 35.057 | [6 empty] | 2020-12-21
Panasonic Corporation of North America | EVPV360K | 360 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 341 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.49 | 43.9 | 9.82 | 36.7 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.8224 | 35.322 | 7.4203 | 34.9016 | [6 empty] | 2020-12-21
Panasonic Corporation of North America | EVPV370 | 370 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730 | 370 | 351.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.55 | 44.1 | 9.9 | 37.4 | 45.45 | -0.258 | 0.034 | -0.236 |  |  | 1.888 | 35.65 | 7.667 | 35.28 | [6 empty] | 2020-12-21
Panasonic Corporation of North America | EVPV370K | 370 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 370 | 350.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.55 | 44.1 | 9.9 | 37.4 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.8373 | 35.9957 | 7.4808 | 35.5673 | [6 empty] | 2021-05-03
Panasonic Corporation of North America | EVPV380 | 380 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730 | 380 | 361.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.61 | 44.3 | 9.98 | 38.1 | 45.45 | -0.258 | 0.034 | -0.236 |  |  | 1.9033 | 36.3172 | 7.729 | 35.9403 | [6 empty] | 2021-05-21
PEIMAR | SG160M | 160 W Monocrystalline Module | UL 1703 | 160 | 141.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.12 | 42.42 | 4.57 | 35.01 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.87 | 34.05 | 3.76 | 30.76 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18515
PEIMAR | SG165M | 165 W Monocrystalline Module | UL 1703 | 165 | 146 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.22 | 42.5 | 4.66 | 35.4 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.89 | 34.43 | 3.83 | 31.1 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18571
PEIMAR | SG170M | 170 W Monocrystalline Module | UL 1703 | 170 | 150.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.35 | 42.7 | 4.78 | 35.6 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.91 | 34.62 | 3.93 | 31.28 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18532
PEIMAR | SG175M | 175 W Monocrystalline Module | UL 1703 | 175 | 155.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.45 | 43.1 | 4.87 | 35.9 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.91 | 35.44 | 3.89 | 32.21 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18429
PEIMAR | SG180M | 180 W Monocrystalline Module | UL 1703 | 180 | 159.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.59 | 43.3 | 4.99 | 36.1 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.93 | 35.64 | 3.98 | 32.39 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18414
PEIMAR | SG185M | 185 W Monocrystalline Module | UL 1703 | 185 | 164.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.72 | 43.4 | 5.11 | 36.2 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.95 | 35.74 | 4.08 | 32.48 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18353
PEIMAR | SG190M | 190 W Monocrystalline Module | UL 1703 | 190 | 168.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.86 | 43.5 | 5.23 | 36.3 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 0.97 | 35.23 | 4.11 | 32.57 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.17986
PEIMAR | SG195M | 195 W Monocrystalline Module | UL 1703 | 195 | 173.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 6.01 | 43.6 | 5.37 | 36.3 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 1 | 35.23 | 4.22 | 32.57 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18067
PEIMAR | SG200M | 200 W Monocrystalline Module | UL 1703 | 200 | 178 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.95 | 45.7 | 5.54 | 36.12 | 46.9 | -0.484 | 0.054 | -0.367 | 0.028 | -0.508 | 1.03 | 35.05 | 4.35 | 32.41 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18051
PEIMAR | SG205P | 205 W Polycrystalline Module | UL 1703 | 205 | 182.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 7.84 | 35.1 | 7 | 29.3 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.35 | 27.66 | 5.58 | 26.79 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18215
PEIMAR | SG210P | 210 W Polycrystalline Module | UL 1703 | 210 | 186.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.01 | 35.2 | 7.14 | 29.4 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.38 | 27.75 | 5.7 | 26.88 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18236
PEIMAR | SG215P | 215 W Polycrystalline Module | UL 1703 | 215 | 191.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.16 | 35.4 | 7.29 | 29.5 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.41 | 27.85 | 5.82 | 26.97 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18264
PEIMAR | SG220M | 220 W Monocrystalline Module | UL 1703 | 220 | 197.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 7.98 | 36.29 | 7.46 | 29.5 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.4619 | 28.9804 | 5.8261 | 26.9399 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19257
PEIMAR | SG220P | 220 W Polycrystalline Module | UL 1703 | 220 | 196 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.32 | 35.4 | 7.46 | 29.5 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.44 | 27.85 | 5.95 | 26.97 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18229
PEIMAR | SG225M | 225 W Monocrystalline Module | UL 1703 | 225 | 202.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.13 | 36.41 | 7.6 | 29.6 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.4899 | 29.0787 | 5.9378 | 27.0312 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19255
PEIMAR | SG225P | 225 W Polycrystalline Module | UL 1703 | 225 | 200.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.46 | 35.8 | 7.6 | 29.6 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.47 | 27.94 | 6.06 | 27.06 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18254
PEIMAR | SG230M | 230 W Monocrystalline Module | UL 1703 | 230 | 206.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.29 | 36.53 | 7.74 | 29.7 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.5179 | 29.1769 | 6.0496 | 27.1225 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19256
PEIMAR | SG230P | 230 W Polycrystalline Module | UL 1703 | 230 | 205.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.6 | 36 | 7.72 | 29.8 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.55 | 28.21 | 6.16 | 27.26 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19011
PEIMAR | SG235M | 235 W Monocrystalline Module | UL 1703 | 235 | 211.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.44 | 36.65 | 7.89 | 29.8 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.5458 | 29.2752 | 6.1605 | 27.2138 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19256
PEIMAR | SG235P | 235 W Polycrystalline Module | UL 1703 | 235 | 209.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.75 | 36.1 | 7.83 | 30 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.57 | 28.4 | 6.25 | 27.44 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18974
PEIMAR | SG240M | 240 W Monocrystalline Module | UL 1703 | 240 | 216 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.59 | 36.78 | 8.03 | 29.9 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.5734 | 29.3734 | 6.2706 | 27.3052 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19257
PEIMAR | SG240P | 240 W Polycrystalline Module | UL 1703 | 240 | 214.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.9 | 36.2 | 7.95 | 30.2 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.6 | 28.59 | 6.34 | 27.63 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1906
PEIMAR | SG245M | 245 W Monocrystalline Module | UL 1703 | 245 | 220.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.71 | 37.02 | 8.14 | 30.1 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.5854 | 29.4112 | 6.5249 | 27.4744 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19032
PEIMAR | SG245P | 245 W Polycrystalline Module | UL 1703 | 245 | 219 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.06 | 36.4 | 8.09 | 30.3 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.62 | 28.69 | 6.45 | 27.72 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18971
PEIMAR | SG250M | 250 W Monocrystalline Module | UL 1703 | 250 | 225.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.86 | 37.15 | 8.28 | 30.2 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.6122 | 29.5089 | 6.6355 | 27.5656 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1903
PEIMAR | SG250P | 250 W Polycrystalline Module | UL 1703 | 250 | 223.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.21 | 36.5 | 8.22 | 30.4 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.65 | 28.78 | 6.56 | 27.81 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18995
PEIMAR | SG255M | 255 W Monocrystalline Module | UL 1703 | 255 | 229.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.92 | 37.64 | 8.33 | 30.6 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.6158 | 30.7005 | 6.5965 | 28.6078 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19453
PEIMAR | SG255P | 255 W Polycrystalline Module | UL 1703 | 255 | 231 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.95 | 37.52 | 8.36 | 30.5 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6063 | 29.8981 | 6.6289 | 27.9636 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18834
PEIMAR | SG260M | 260 W Monocrystalline Module | UL 1703 | 260 | 234.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.15 | 37.39 | 8.55 | 30.4 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.6591 | 30.4998 | 6.7731 | 28.4208 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19462
PEIMAR | SG260P | 260 W, 60 cell Polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 260 | 235.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 8.98 | 37.81 | 8.4 | 30.98 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6324 | 29.9961 | 6.7367 | 28.0553 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18833 |  | 2021-01-11
PEIMAR | SG265M | 265 W Monocrystalline Module | UL 1703 | 265 | 239.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.3 | 37.52 | 8.69 | 30.5 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.6854 | 30.6002 | 6.8808 | 28.5143 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19462
PEIMAR | SG265P | 265 W, 60 cell Polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 265 | 240.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 9.09 | 38.04 | 8.5 | 31.18 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6584 | 30.0941 | 6.8438 | 28.1469 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18833 |  | 2021-01-11
PEIMAR | SG270M | 270 W Monocrystalline Module | UL 1703 | 270 | 243.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.44 | 37.64 | 8.82 | 30.6 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.7116 | 30.7005 | 6.9877 | 28.6078 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19462
PEIMAR | SG270P | 270 W, 60 cell Polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 270 | 245 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 9.22 | 38.29 | 8.61 | 31.38 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6841 | 30.1921 | 6.95 | 28.2386 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18832 |  | 2021-01-11
PEIMAR | SG275M | 275 W Monocrystalline Module | UL 1703 | 275 | 248.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.55 | 37.88 | 8.93 | 30.8 | 45.2 | -0.46817 | 0.033267 | -0.32704 | -0.02859 | -0.44374 | 1.732 | 30.9012 | 7.0709 | 28.7948 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19462
PEIMAR | SG275P | 275 W, 60 cell Polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 275 | 249.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 9.32 | 38.53 | 8.71 | 31.58 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.7099 | 30.2902 | 7.0562 | 28.3303 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18833 |  | 2021-01-11
PEIMAR | SG280M | 280 W Monocrystalline Module | UL 1703 | 280 | 251.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.39 | 43.91 | 7.84 | 35.7 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5008 | 34.7851 | 6.1722 | 32.5512 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18645
PEIMAR | SG280P | 280 W, 60 cell Polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 280 | 251.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 9.43 | 38.78 | 8.82 | 31.78 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.47 | 34.21 | 6.23 | 31.48 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1796 |  | 2021-01-11
PEIMAR | SG285M | 285 W Monocrystalline Module | UL 1703 | 285 | 255.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.52 | 44.03 | 7.96 | 35.8 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5234 | 34.8825 | 6.2651 | 32.6424 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18645
PEIMAR | SG285P | 285 W, 60 cell Polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 285 | 255.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 9.55 | 39.02 | 8.92 | 31.98 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.5 | 34.63 | 6.22 | 32.11 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18226 |  | 2021-01-11
PEIMAR | SG290M | 290 W Monocrystalline Module | UL 1703 | 290 | 260.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.64 | 44.16 | 8.08 | 35.9 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5458 | 34.98 | 6.3571 | 32.7336 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18645
PEIMAR | SG290P | 290 W, 60 cell Polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 290 | 260.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 | 1 | N | 9.64 | 39.28 | 9.01 | 32.2 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.53 | 34.72 | 6.31 | 32.2 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18318 |  | 2021-01-11
PEIMAR | SG295M | 295 W Monocrystalline Module | UL 1703 | 295 | 265.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.77 | 44.28 | 8.19 | 36 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.568 | 35.0774 | 6.4484 | 32.8247 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18644
PEIMAR | SG295P | 295 W Polycrystalline Module | UL 1703 | 295 | 263.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.15 | 43.3 | 8.17 | 36.1 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.55 | 34.82 | 6.4 | 32.28 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18295
PEIMAR | SM295M (BF) | 295 W, 60 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 295 | 272.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.5 | 40.21 | 8.98 | 32.95 | 45.5 | -0.3722 | 0.0542 | -0.2817 |  |  | 1.7595 | 31.7492 | 7.0475 | 30.2457 | [6 empty] | 2021-06-21
PEIMAR | SM295M (FB) | 295 W, 60 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 61730 | 295 | 271.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.5 | 40.21 | 8.98 | 32.95 | 46.2 | -0.375 | 0.057 | -0.2827 |  |  | 1.7378 | 31.7911 | 7.0093 | 30.3179 | [6 empty] | 2021-06-21
PEIMAR | SG300M | 300 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 300 | 271.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.72 | 40.33 | 9.08 | 33.05 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.5902 | 35.1749 | 6.5397 | 32.9159 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18644 |  | 2021-01-11
PEIMAR | SG300P | 300 W Polycrystalline Module | UL 1703 | 300 | 268.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.27 | 43.4 | 8.28 | 36.2 | 46.9 | -0.462 | 0.073 | -0.361 | 0.016 | -0.475 | 1.57 | 34.92 | 6.49 | 32.37 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18275
PEIMAR | SM300M (BF) | 300 W, 60 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 300 | 277.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.59 | 40.45 | 9.07 | 33.15 | 45.5 | -0.3722 | 0.0542 | -0.2817 |  |  | 1.7771 | 31.9419 | 7.1181 | 30.4292 | [6 empty] | 2021-06-21
PEIMAR | SM300M (FB) | 300 W, 60 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 61730 | 300 | 276.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.59 | 40.45 | 9.07 | 33.15 | 46.2 | -0.375 | 0.057 | -0.2827 |  |  | 1.7552 | 31.9841 | 7.0795 | 30.502 | [6 empty] | 2021-06-21
PEIMAR | SG305M | 305 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 305 | 275.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.83 | 40.57 | 9.18 | 33.25 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.6232 | 35.4283 | 6.6483 | 33.2047 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18855 |  | 2021-01-11
PEIMAR | SG305P | 305 W Polycrystalline Module | UL 1703 | 305 | 276.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.02 | 44.53 | 8.43 | 36.2 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6207 | 35.4946 | 6.7544 | 33.3727 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18861
PEIMAR | SM305M (BF) | 305 W, 60 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 305 | 282 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.69 | 40.7 | 9.16 | 33.35 | 45.5 | -0.3722 | 0.0542 | -0.2817 |  |  | 1.7947 | 32.1346 | 7.1887 | 30.6128 | [6 empty] | 2021-06-21
PEIMAR | SM305M (FB) | 305 W, 60 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 61730 | 305 | 281 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.69 | 40.7 | 9.16 | 33.35 | 46.2 | -0.375 | 0.057 | -0.2827 |  |  | 1.7726 | 32.177 | 7.1498 | 30.686 | [6 empty] | 2021-06-21
PEIMAR | SG310M | 310 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 310 | 280.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.92 | 40.81 | 9.27 | 33.45 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.6454 | 35.5262 | 6.7391 | 33.2964 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18856 |  | 2021-01-11
PEIMAR | SG310P | 310 W Polycrystalline Module | UL 1703 | 310 | 281 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.14 | 44.65 | 8.54 | 36.3 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6429 | 35.5927 | 6.8466 | 33.4649 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18863
PEIMAR | SM310M (BF) | 310 W, 60 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 310 | 286.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.79 | 40.94 | 9.25 | 33.55 | 45.5 | -0.3722 | 0.0542 | -0.2817 |  |  | 1.8124 | 32.3273 | 7.2594 | 30.7964 | [6 empty] | 2021-06-21
PEIMAR | SM310M (FB) | 310 W, 60 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 61730 | 310 | 285.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.79 | 40.94 | 9.25 | 33.55 | 46.2 | -0.375 | 0.057 | -0.2827 |  |  | 1.79 | 32.37 | 7.22 | 30.87 | [6 empty] | 2021-06-21
PEIMAR | SG315M | 315 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 315 | 285.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.99 | 41.18 | 9.34 | 33.75 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.6673 | 35.624 | 6.829 | 33.3881 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18856 |  | 2021-01-11
PEIMAR | SG315P | 315 W Polycrystalline Module | UL 1703 | 315 | 285.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.26 | 44.77 | 8.65 | 36.4 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6648 | 35.6907 | 6.938 | 33.557 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18863
PEIMAR | SM315M (BF) | 315 W, 60 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 315 | 291.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.89 | 41.18 | 9.34 | 33.75 | 45.5 | -0.3722 | 0.0542 | -0.2817 |  |  | 1.83 | 32.52 | 7.33 | 30.98 | [6 empty] | 2021-06-21
PEIMAR | SM315M (FB) | 315 W, 60 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 61730 | 315 | 290.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.89 | 41.18 | 9.34 | 33.75 | 46.2 | -0.375 | 0.057 | -0.2827 |  |  | 1.8074 | 32.563 | 7.2902 | 31.054 | [6 empty] | 2021-06-21
PEIMAR | SG320M | 320 W Monocrystalline Module | UL 1703 | 320 | 288.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.38 | 44.9 | 8.77 | 36.5 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.6891 | 35.7219 | 6.9182 | 33.4798 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18856
PEIMAR | SG320P | 320 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 290.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.14 | 45.75 | 8.54 | 37.5 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.6865 | 35.7888 | 7.0286 | 33.6492 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18862 |  | 2021-01-11
PEIMAR | SM320M (BF) | 320 W, 60 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 320 | 296.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.98 | 41.42 | 9.43 | 33.95 | 45.5 | -0.3722 | 0.0542 | -0.2817 |  |  | 1.8476 | 32.7127 | 7.4006 | 31.1636 | [6 empty] | 2021-06-21
PEIMAR | SM320M (FB) | 320 W, 60 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 61730 | 320 | 295.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.98 | 41.42 | 9.43 | 33.95 | 46.2 | -0.375 | 0.057 | -0.2827 |  |  | 1.8248 | 32.7559 | 7.3605 | 31.238 | [6 empty] | 2021-06-21
PEIMAR | SG325M | 325 W Monocrystalline Module | UL 1703 | 325 | 292.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.48 | 45.14 | 8.86 | 36.7 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.7062 | 35.9177 | 6.9884 | 33.6633 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18857
PEIMAR | SG325P | 325 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 325 | 295 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.24 | 45.99 | 8.63 | 37.7 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.7083 | 35.8868 | 7.1192 | 33.7414 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18863 |  | 2021-01-11
PEIMAR | SM325M (BF) | 325 W, 60 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 325 | 301 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.08 | 41.67 | 9.52 | 34.15 | 45.5 | -0.3722 | 0.0542 | -0.2817 |  |  | 1.8653 | 32.9054 | 7.4713 | 31.3472 | [6 empty] | 2021-06-21
PEIMAR | SM325M (FB) | 325 W, 60 cell monocrystalline module, black backsheet and frame, 1500V max system Vdc | UL 61730 | 325 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.08 | 41.67 | 9.52 | 34.15 | 46.2 | -0.375 | 0.057 | -0.2827 |  |  | 1.8422 | 32.9489 | 7.4307 | 31.4221 | [6 empty] | 2021-06-21
PEIMAR | SG330M | 330 W Monocrystalline Module | UL 1703 | 330 | 297.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.6 | 45.26 | 8.97 | 36.8 | 45.7 | -0.46757 | 0.042146 | -0.33887 | -0.02374 | -0.47055 | 1.7276 | 36.0155 | 7.076 | 33.755 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18855
PEIMAR | SG330P | 330 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 330 | 299.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 | 1 | N | 9.32 | 46.24 | 8.71 | 37.9 | 45.4 | -0.44277 | 0.056061 | -0.3302 | 0.005526 | -0.44703 | 1.7298 | 35.9849 | 7.209 | 33.8336 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18863 |  | 2021-01-11
PEIMAR | SM330M (BF) | 330 W, 60 cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 330 | 305.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.18 | 41.91 | 9.61 | 34.35 | 45.5 | -0.3722 | 0.0542 | -0.2817 |  |  | 1.8829 | 33.0981 | 7.5419 | 31.5308 | [6 empty] | 2021-06-21
PEIMAR | SG335M | 335 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 335 | 304.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.335 | 46.848 | 8.724 | 38.4 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.6496 | 37.8557 | 6.98 | 35.3616 | [6 empty] | 2018-08-15
PEIMAR | SG340M | 340 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 340 | 309.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.449 | 46.97 | 8.831 | 38.5 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.6699 | 37.9543 | 7.0656 | 35.4537 | [6 empty] | 2018-08-15
PEIMAR | SG345M | 345 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 345 | 314 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.563 | 47.092 | 8.938 | 38.6 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.6901 | 38.0528 | 7.1512 | 35.5458 | [6 empty] | 2018-08-15
PEIMAR | SG350M | 350 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 350 | 318.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.677 | 47.214 | 9.044 | 38.7 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.7101 | 38.1514 | 7.236 | 35.6379 | [6 empty] | 2018-08-15
PEIMAR | SG355M | 355 W, 72 cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 1703 | 355 | 323.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 |  | N | 9.79 | 47.336 | 9.149 | 38.8 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.73 | 38.25 | 7.32 | 35.73 | [6 empty] | 2018-08-15
PEIMAR | SM355M | 355 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 328.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.54 | 48.19 | 9.01 | 39.5 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.7334 | 37.8307 | 6.9337 | 36.1711 | [6 empty] | 2021-06-21
PEIMAR | SG360M | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 328.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.71 | 48.44 | 9.07 | 39.7 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.7499 | 38.3486 | 7.404 | 35.8221 | [6 empty] | 2018-08-15 | 2021-01-11
PEIMAR | SM360M | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 333.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.62 | 48.44 | 9.09 | 39.7 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.7488 | 38.0223 | 6.9953 | 36.3543 | [6 empty] | 2021-06-21
PEIMAR | SG365M | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 332.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.79 | 48.68 | 9.15 | 39.9 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.7697 | 38.4472 | 7.488 | 35.9142 | [6 empty] | 2018-08-15 | 2021-01-11
PEIMAR | SM365M | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 338.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.7 | 48.68 | 9.16 | 39.9 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.7623 | 38.2138 | 7.0491 | 36.5374 | [6 empty] | 2021-06-21
PEIMAR | SG370M | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 337.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.81 | 48.93 | 9.23 | 40.1 | 45.8 | -0.43052 | 0.053292 | -0.34042 | -0.00321 | -0.42818 | 1.7894 | 38.5457 | 7.5712 | 36.0063 | [6 empty] | 2018-08-15 | 2021-01-11
PEIMAR | SM370M | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 342.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.78 | 48.92 | 9.24 | 40.1 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.7777 | 38.4054 | 7.1107 | 36.7206 | [6 empty] | 2021-06-21
PEIMAR | SM375M | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 347.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.86 | 49.17 | 9.31 | 40.3 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.7911 | 38.5969 | 7.1646 | 36.9037 | [6 empty] | 2021-06-21
PEIMAR | SM380M | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 352.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.94 | 49.41 | 9.39 | 40.5 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.8065 | 38.7885 | 7.2261 | 37.0869 | [6 empty] | 2021-06-21
PEIMAR | SM385M | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 357.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.02 | 49.66 | 9.46 | 40.7 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.82 | 38.98 | 7.28 | 37.27 | [6 empty] | 2021-06-21
PEIMAR | SM390M | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 362 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.1 | 49.9 | 9.54 | 40.9 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.8354 | 39.1715 | 7.3416 | 37.4531 | [6 empty] | 2021-06-21
PEIMAR | SM395M | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.18 | 50.14 | 9.61 | 41.1 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.8489 | 39.3631 | 7.3954 | 37.6363 | [6 empty] | 2021-06-21
PEIMAR | SM400M | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 371.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.26 | 50.39 | 9.69 | 41.3 | 45.9 | -0.3568 | 0.0529 | -0.2708 |  |  | 1.8642 | 39.5546 | 7.457 | 37.8194 | [6 empty] | 2021-06-21
Perfect Source Technology | PST 176 3GP48 | 176W Polycrystalline Module | UL 1703 | 176 | 156.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.341 | 48 | 1 | N | 8 | 29.33 | 7.33 | 24 | 46.4 | -0.47 | 0.09 | -0.34 | 0.02 | -0.49 | 1.6108 | 30.1237 | 6.6279 | 28.0789 | Rack | Flat Plate | 0.997 | 1.345 | 1 | 0.2757
Perfect Source Technology | PST 188 3GP48 | 188W Polycrystalline Module | UL 1703 | 188 | 167.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.341 | 48 | 1 | N | 8.21 | 30 | 7.65 | 24.58 | 46.4 | -0.47 | 0.09 | -0.34 | 0.02 | -0.49 | 1.6108 | 30.1237 | 6.6279 | 28.0789 | Rack | Flat Plate | 0.997 | 1.345 | 1 | 0.2581
Perlight Solar | PLM-215P-60 | 215 W Polycrystalline Module | UL 1741 | 215 | 187.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 7.93 | 36.6 | 7.29 | 29.5 | 47.3 | -0.534 | 0.072 | -0.404 | -0.014 | -0.56 | 1.498 | 28.86 | 6.175 | 25.4 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20108
Perlight Solar | PLM-235P-60 | 235 W Polycrystalline Module | UL 1741 | 235 | 210.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6368 | 60 | 1 | N | 8.28 | 37.25 | 7.75 | 30.3 | 46.9 | -0.441 | 0.062 | -0.41 | -0.009 | -0.562 | 1.672 | 28.12 | 6.348 | 25.61 | Rack | Flat Plate | 0.992 | 1.65 | 1 | 0.20007
Perlight Solar | PLM-270P-72 | 270 W Polycrystalline Module | UL 1741 | 270 | 240.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.58 | 44.76 | 7.94 | 35.29 | 48.5 | -0.44 | 0.05 | -0.32 | -0.06 | -0.51 | 1.5098 | 36.3898 | 6.1364 | 31.5072 | Rack | Flat Plate | 0.992 | 1.966 | 1 | 0.20349
Perlight Solar | PLM-290P-72 | 290 W Polycrystalline Module | UL 1741 | 290 | 258.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.69 | 45.14 | 8.23 | 35.27 | 48.5 | -0.44 | 0.05 | -0.32 | -0.06 | -0.51 | 1.5644 | 36.3692 | 6.3581 | 31.4893 | Rack | Flat Plate | 0.992 | 1.966 | 1 | 0.19619
Philadelphia Solar | PS-M36S-95 | 95 W Monocrystalline Module | UL 1741 | 95 | 84 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.66218 | 36 | 1 | N | 5.37 | 22.4 | 5.05 | 18.8 | 48.5 | -0.4621 | 0.0446 | -0.3281 | -0.0277 | -0.4405 | 1.012 | 18.1726 | 4.0675 | 16.4181 | Rack | Flat Plate | 0.545 | 1.215 | 1 | 0.19358
Philadelphia Solar | PS-M72S-185 | 185 W Monocrystalline Module | UL 1741 | 185 | 163.7 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.28 | 72 | 1 | N | 5.76 | 43.8 | 5.14 | 36 | 48.5 | -0.4621 | 0.0446 | -0.3281 | -0.0277 | -0.4405 | 0.99716 | 34.6329 | 4.184 | 31.4232 | Rack | Flat Plate | 0.8 | 1.6 | 1 | 0.18667
Philadelphia Solar | PS-P54-220 | 220 W Polycrystalline Module | UL 1741 | 220 | 195.1 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.4801 | 54 | 1 | N | 8.39 | 33.64 | 7.87 | 27.97 | 47.4 | -0.4791 | 0.0507 | -0.3361 | -0.0412 | -0.4469 | 1.57 | 27.8679 | 6.1267 | 24.7851 | Rack | Flat Plate | 0.99 | 1.495 | 1 | 0.19887
Philadelphia Solar | PS-P60-270 | 270 W, 60 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 270 | 243.4 |  | 2020-03-16 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 1 | N | 9.185 | 38.12 | 8.74 | 30.94 | 47.7 | -0.424 | 0.0607 | -0.322 |  |  | 2.1701 | 30.6127 | 6.8771 | 28.0443 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-P60-275 | 275 W, 60 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 275 | 248.1 |  | 2020-03-16 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 1 | N | 9.23 | 38.2 | 8.82 | 31.2 | 47.7 | -0.424 | 0.0607 | -0.322 |  |  | 2.19 | 30.87 | 6.94 | 28.28 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-P60-280 | 280 W, 60 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 280 | 252.7 |  | 2020-03-16 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 1 | N | 9.31 | 38.37 | 8.91 | 31.42 | 47.7 | -0.424 | 0.0607 | -0.322 |  |  | 2.2123 | 31.0877 | 7.0108 | 28.4794 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-P60-285 | 285 W, 60 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 285 | 257.4 |  | 2020-03-16 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 1 | N | 9.36 | 38.67 | 8.98 | 31.75 | 47.7 | -0.424 | 0.0607 | -0.322 |  |  | 2.2297 | 31.4142 | 7.0659 | 28.7785 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60(BF)-295 | 295 W, 60 cell monocrystalline bifacial module, 1500V max system Vdc | UL 61730 | 295 | 270.7 |  | 2020-02-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.83 | 39.6 | 9.3 | 31.74 | 46.1 | -0.3925 | 0.0477 | -0.2704 |  |  | 2.2519 | 31.9322 | 7.1456 | 29.0582 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60-295 | 295 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 295 | 268.7 |  | 2020-03-16 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.844 | 39.59 | 9.31 | 31.7 | 46.9 | -0.4091 | 0.0504 | -0.2769 |  |  | 2.3202 | 31.9098 | 7.2121 | 28.591 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60(BF)-300 | 300 W, 60 cell monocrystalline bifacial module, 1500V max system Vdc | UL 61730 | 300 | 275.4 |  | 2020-02-21 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.87 | 39.9 | 9.36 | 32.07 | 46.1 | -0.3925 | 0.0477 | -0.2704 |  |  | 2.2664 | 32.2642 | 7.1917 | 29.3603 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60-300 | 300 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 300 | 273.4 |  | 2020-03-16 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.893 | 39.89 | 9.37 | 32.06 | 46.9 | -0.4091 | 0.0504 | -0.2769 |  |  | 2.3352 | 32.2722 | 7.2586 | 28.9157 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60(BF)-305 | 305 W, 60 cell monocrystalline bifacial module, 1500V max system Vdc | UL 61730 | 305 | 280.1 |  | 2020-02-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.93 | 40.21 | 9.42 | 32.39 | 46.1 | -0.3925 | 0.0477 | -0.2704 |  |  | 2.2809 | 32.5862 | 7.2378 | 29.6532 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60-305 | 305 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 305 | 278.1 |  | 2020-03-16 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.942 | 40.19 | 9.43 | 32.35 | 46.9 | -0.4091 | 0.0504 | -0.2769 |  |  | 2.3502 | 32.5641 | 7.3051 | 29.1773 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60(BF)-310 | 310 W, 60 cell monocrystalline bifacial module, 1500V max system Vdc | UL 61730 | 310 | 284.8 |  | 2020-02-19 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.98 | 40.5 | 9.48 | 32.72 | 46.1 | -0.3925 | 0.0477 | -0.2704 |  |  | 2.2955 | 32.9182 | 7.2839 | 29.9553 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60-310 | 310 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 310 | 282.8 |  | 2020-03-16 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 9.991 | 40.49 | 9.51 | 32.65 | 46.9 | -0.4091 | 0.0504 | -0.2769 |  |  | 2.3701 | 32.8661 | 7.367 | 29.4479 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60(BF)-315 | 315 W, 60 cell monocrystalline bifacial module, 1500V max system Vdc | UL 61730 | 315 | 289.6 |  | 2020-02-18 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.03 | 40.8 | 9.54 | 33.02 | 46.1 | -0.3925 | 0.0477 | -0.2704 |  |  | 2.31 | 33.22 | 7.33 | 30.23 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60-315 | 315 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 315 | 287.5 |  | 2020-03-16 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.04 | 40.8 | 9.56 | 32.95 | 46.9 | -0.4091 | 0.0504 | -0.2769 |  |  | 2.3826 | 33.1681 | 7.4058 | 29.7184 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-M60-320 | 320 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 292.2 |  | 2020-03-16 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 1 | N | 10.09 | 41.1 | 9.63 | 33.24 | 46.9 | -0.4091 | 0.0504 | -0.2769 |  |  | 2.4 | 33.46 | 7.46 | 29.98 | [6 empty] | 2020-05-11
Philadelphia Solar | PS-P72-335 | 335 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 335 | 302.5 |  | 2020-02-19 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.97 | 72 | 1 | N | 9.29 | 46 | 8.94 | 37.52 | 47.4 | -0.4256 | 0.059 | -0.3286 |  |  | 2.19 | 36.81 | 6.93 | 34.28 | [6 empty] | 2020-03-23
Philadelphia Solar | PS-P72-340 | 340 W, 72 cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 340 | 307.2 |  | 2020-02-19 | No Information Submitted | Polycrystalline | Multi-c-Si | 1.97 | 72 | 1 | N | 9.38 | 46.2 | 9.03 | 37.72 | 47.4 | -0.4256 | 0.059 | -0.3286 |  |  | 2.212 | 37.0062 | 6.9998 | 34.4627 | [6 empty] | 2020-03-23
Philadelphia Solar | PS-M72(BF)-370 | 370 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 370 | 341.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 72 | 1 | N | 9.7 | 48.36 | 9.12 | 40.6 | 46.1 | -0.3646 | 0.052 | -0.2771 |  |  | 2.2949 | 39.0495 | 7.3516 | 36.3462 | [6 empty] | 2020-02-21
Philadelphia Solar | PS-M72-370 | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 338.3 |  | 2020-02-19 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 9.78 | 48.14 | 9.25 | 40 | 45.7 | -0.4174 | 0.0499 | -0.3028 |  |  | 2.3769 | 38.113 | 7.4772 | 35.3219 | [6 empty] | 2020-03-23
Philadelphia Solar | PS-M72(BF)-375 | 375 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 375 | 346.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 72 | 1 | N | 9.78 | 48.63 | 9.18 | 40.85 | 46.1 | -0.3646 | 0.052 | -0.2771 |  |  | 2.31 | 39.29 | 7.4 | 36.57 | [6 empty] | 2020-02-21
Philadelphia Solar | PS-M72-375 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 343 |  | 2020-02-19 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 9.83 | 48.44 | 9.29 | 40.39 | 45.7 | -0.4174 | 0.0499 | -0.3028 |  |  | 2.3872 | 38.4846 | 7.5096 | 35.6663 | [6 empty] | 2020-03-23
Philadelphia Solar | PS-M72(BF)-380 | 380 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 380 | 351.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.97 | 72 | 1 | N | 9.87 | 48.9 | 9.26 | 41.05 | 46.1 | -0.3646 | 0.052 | -0.2771 |  |  | 2.3301 | 39.4824 | 7.4645 | 36.749 | [6 empty] | 2020-02-21
Philadelphia Solar | PS-M72-380 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 347.7 |  | 2020-02-19 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 9.88 | 48.74 | 9.34 | 40.7 | 45.7 | -0.4174 | 0.0499 | -0.3028 |  |  | 2.4 | 38.78 | 7.55 | 35.94 | [6 empty] | 2020-03-23
Philadelphia Solar | PS-M72(BF)-385 | 385 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 385 | 358.7 |  | 2021-01-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 9.87 | 49.58 | 9.42 | 40.88 | 43.6 | -0.3757 | 0.0485 | -0.2674 |  |  | 1.9194 | 36.1759 | 7.6876 | 36.5964 | [6 empty] | 2021-04-01
Philadelphia Solar | PS-M72-385 | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 352.4 |  | 2020-02-19 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 9.925 | 49.04 | 9.4 | 40.96 | 45.7 | -0.4174 | 0.0499 | -0.3028 |  |  | 2.4154 | 39.0277 | 7.5985 | 36.1696 | [6 empty] | 2020-03-23
Philadelphia Solar | PS-M72(BF)-390 | 390 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 390 | 363.5 |  | 2021-01-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 9.92 | 49.88 | 9.47 | 41.19 | 43.6 | -0.3757 | 0.0485 | -0.2674 |  |  | 1.9296 | 36.4502 | 7.7284 | 36.8739 | [6 empty] | 2021-04-01
Philadelphia Solar | PS-M72-390 | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 357.2 |  | 2020-02-19 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 9.975 | 49.34 | 9.45 | 41.27 | 45.7 | -0.4174 | 0.0499 | -0.3028 |  |  | 2.4283 | 39.3231 | 7.6389 | 36.4433 | [6 empty] | 2020-03-23
Philadelphia Solar | PS-M72(BF)-395 | 395 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 395 | 368.2 |  | 2021-01-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 9.97 | 50.18 | 9.52 | 41.5 | 43.6 | -0.3757 | 0.0485 | -0.2674 |  |  | 1.9398 | 36.7245 | 7.7692 | 37.1514 | [6 empty] | 2021-04-01
Philadelphia Solar | PS-M72-395 | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 361.9 |  | 2020-02-19 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.025 | 49.64 | 9.505 | 41.57 | 45.7 | -0.4174 | 0.0499 | -0.3028 |  |  | 2.4424 | 39.609 | 7.6834 | 36.7083 | [6 empty] | 2020-03-23
Philadelphia Solar | PS-M72(BF)-400 | 400 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 400 | 373 |  | 2021-01-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.03 | 50.52 | 9.57 | 41.8 | 43.6 | -0.3757 | 0.0485 | -0.2674 |  |  | 1.95 | 36.99 | 7.81 | 37.42 | [6 empty] | 2021-04-01
Philadelphia Solar | PS-M72-400 | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 371.8 |  | 2021-01-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.3 | 50 | 9.67 | 41.38 | 45 | -0.3647 | 0.0493 | -0.2751 |  |  | 1.92 | 37.23 | 7.68 | 37.45 | [6 empty] | 2021-04-01
Philadelphia Solar | PS-M72(BF)-405 | 405 W, 72 cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 405 | 377.8 |  | 2021-01-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.08 | 50.8 | 9.62 | 42.1 | 43.6 | -0.3757 | 0.0485 | -0.2674 |  |  | 1.9602 | 37.2555 | 7.8508 | 37.6886 | [6 empty] | 2021-04-01
Philadelphia Solar | PS-M72-405 | 405 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 376.6 |  | 2021-01-22 | No Information Submitted | Monocrystalline | Mono-c-Si | 2 | 72 | 1 | N | 10.35 | 50.32 | 9.72 | 41.7 | 45 | -0.3647 | 0.0493 | -0.2751 |  |  | 1.9299 | 37.5179 | 7.7197 | 37.7396 | [6 empty] | 2021-04-01
Phono Solar Technology Co.,Ltd. | PS160M-24/F | 160 W Monocrystalline Module | UL 1703 | 160 | 145.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.05 | 43.8 | 4.63 | 34.6 | 45.3 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 0.95047 | 33.0591 | 3.6962 | 31.9304 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19639 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS165M-24/F | 165 W Monocrystalline Module | UL 1703 | 165 | 149.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.1 | 44 | 4.71 | 35 | 45.3 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 0.96689 | 33.4413 | 3.76 | 32.2995 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19596 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS170M-24/F | 170 W Monocrystalline Module | UL 1703 | 170 | 154.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.15 | 44.2 | 4.8 | 35.4 | 45.3 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 0.98537 | 33.8235 | 3.8319 | 32.6687 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19605 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS180M-24/F | 180 W Monocrystalline Module | UL 1703 | 180 | 163.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.25 | 44.6 | 4.98 | 36.2 | 45.3 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.0601 | 33.5487 | 3.9868 | 31.3764 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19759 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS185M-24/F | 185 W Monocrystalline Module | UL 1703 | 185 | 168.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.3 | 44.8 | 5.06 | 36.6 | 45.3 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.0771 | 33.9194 | 4.0508 | 31.7232 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19749 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS190M-24/F | 190 W Monocrystalline Module | UL 1703 | 190 | 173 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.35 | 45 | 5.14 | 37 | 45.3 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.0942 | 34.2901 | 4.1148 | 32.0699 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.19747 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS195M-24/F | 195 W Monocrystalline Module | UL 1703 | 195 | 176.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.4 | 45.2 | 5.22 | 37.4 | 45.3 | -0.452 | 0.052 | -0.353 | 0.002 | 0.453 | 1.0046 | 35.3931 | 4.1268 | 32.1998 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18234 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS200M-24/F | 200 W Monocrystalline Module | UL 1703 | 200 | 180.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.2766 | 72 | 1 | N | 5.45 | 45.4 | 5.3 | 37.8 | 45.3 | -0.452 | 0.052 | -0.353 | 0.002 | 0.453 | 1.02 | 35.7716 | 4.19 | 32.5442 | Rack | Flat Plate | 0.808 | 1.58 | 1 | 0.18244 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS210M-20/U | 210 W Monocrystalline Module | UL 1703 | 210 | 189.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 7.85 | 36.7 | 7.3 | 28.8 | 46.2 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.5747 | 28.4568 | 5.8947 | 26.128 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21338 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS210P-20/U | 210 W Polycrystalline Module | UL 1703 | 210 | 190.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 7.9 | 36.5 | 7.35 | 28.6 | 46.1 | -0.413 | 0.081 | -0.31 | -0.019 | -0.413 | 1.6151 | 28.4725 | 5.8646 | 26.6573 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21898 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS215M-20/U | 215 W Monocrystalline Module | UL 1703 | 215 | 194.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 7.95 | 36.9 | 7.42 | 29 | 46.2 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.6006 | 28.6544 | 5.9916 | 26.3094 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21332 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS215P-20/U | 215 W Polycrystalline Module | UL 1703 | 215 | 194.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8 | 36.7 | 7.47 | 28.8 | 46.1 | -0.413 | 0.081 | -0.31 | -0.019 | -0.413 | 1.6415 | 28.6716 | 5.9603 | 26.8437 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.2189 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS220M-20/U | 220 W Monocrystalline Module | UL 1703 | 220 | 199 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.05 | 37 | 7.54 | 29.2 | 46.2 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.6264 | 28.852 | 6.0885 | 26.4908 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.2133 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS220P-20/U | 220 W Polycrystalline Module | UL 1703 | 220 | 199.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.1 | 36.9 | 7.59 | 29 | 46.1 | -0.413 | 0.081 | -0.31 | -0.019 | -0.413 | 1.6679 | 28.8707 | 6.0561 | 27.0302 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21887 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS225M-20/U | 225 W Monocrystalline Module | UL 1703 | 225 | 203.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.15 | 37.1 | 7.66 | 29.4 | 46.2 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.647 | 27.4923 | 6.1811 | 25.8128 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20125 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS225P-20/U | 225 W Polycrystalline Module | UL 1703 | 225 | 204 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.2 | 37 | 7.71 | 29.2 | 46.1 | -0.413 | 0.081 | -0.31 | -0.019 | -0.413 | 1.6942 | 29.0698 | 6.1518 | 27.2166 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.21889 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS230M-20/U | 230 W Monocrystalline Module | UL 1703 | 230 | 208.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.25 | 37.3 | 7.78 | 29.6 | 46.2 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.6728 | 27.6793 | 6.2779 | 25.9884 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20132 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS230MB-20/U | 230 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 230 | 207.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.37 | 36.8 | 7.83 | 29.4 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.5161 | 28.8611 | 6.254 | 26.3263 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19025 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS230P-20/U | 230 W Polycrystalline Module | UL 1703 | 230 | 208.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 37.1 | 7.83 | 29.4 | 46.1 | -0.413 | 0.081 | -0.31 | -0.019 | -0.413 | 1.6869 | 27.6171 | 6.2638 | 27.1389 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20255 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS230PB-20/U | 230 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 230 | 207.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.3 | 37.1 | 7.83 | 29.4 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.592 | 28.3745 | 6.298 | 26.1245 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19641 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS235M-20/U | 235 W Monocrystalline Module | UL 1703 | 235 | 212.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.35 | 37.5 | 7.9 | 29.8 | 46.2 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.6987 | 27.8664 | 6.3748 | 26.164 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20143 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS235MB-20/U | 235 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 235 | 212.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.43 | 36.9 | 7.9 | 29.8 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.5297 | 29.2538 | 6.3099 | 26.6845 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19042 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS235P-20/U | 235 W Polycrystalline Module | UL 1703 | 235 | 213.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.4 | 37.3 | 7.94 | 29.6 | 46.1 | -0.413 | 0.081 | -0.31 | -0.019 | -0.413 | 1.7106 | 27.805 | 6.3518 | 27.3235 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.2024 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS235PB-20/U | 235 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 235 | 211.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.4 | 37.3 | 7.94 | 29.6 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.6144 | 28.5676 | 6.3865 | 26.3022 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19625 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS240M-20/U | 240 W Monocrystalline Module | UL 1703 | 240 | 217.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.45 | 37.6 | 8 | 30 | 46.2 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.7202 | 28.0534 | 6.4555 | 26.3396 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20107 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS240M-20/U-AC | 240 W DC, Monocrystalline ACPV Module | UL 1741 | 240 | 217.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.45 | 37.6 | 8 | 30 | 46.2 | -0.419 | 0.063 | -0.301 | 0.062 | -0.469 | 1.7202 | 28.0534 | 6.4555 | 26.3396 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20107 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS240MB-20/U | 240 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 240 | 216.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.49 | 37.1 | 7.95 | 30.2 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.5394 | 29.6464 | 6.3499 | 27.0426 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19015 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS240P-20/U | 240 W Polycrystalline Module | UL 1703 | 240 | 217.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.5 | 37.5 | 8.06 | 29.8 | 46.1 | -0.413 | 0.081 | -0.31 | -0.019 | -0.413 | 1.7365 | 27.9928 | 6.4478 | 27.5081 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20254 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS240P-20/U-AC | 240 W DC, Polycrystalline ACPV Module | UL 1741 | 240 | 217.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.5 | 37.5 | 8.06 | 29.8 | 46.1 | -0.413 | 0.081 | -0.31 | -0.019 | -0.413 | 1.7365 | 27.9928 | 6.4478 | 27.5081 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.20254 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS240PB-20/U | 240 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 240 | 216.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.5 | 37.5 | 8.06 | 29.8 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.6388 | 28.7606 | 6.483 | 26.4799 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19639 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS245M | 245 W Monocrystalline Module | UL 1703 | 245 | 218.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.55 | 37.8 | 8.13 | 30.2 | 46.2 | -0.48 | 0.05 | -0.35 | 0.02 | -0.49 | 1.5689 | 28.9731 | 6.4694 | 28.0378 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18554 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS245M-20/U | 245 W Monocrystalline Module | UL 1703 | 245 | 221.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.55 | 37.8 | 8.13 | 30.2 | 45.4 | -0.45 | 0.02 | -0.33 | 0.02 | -0.47 | 1.6199 | 28.7652 | 6.5203 | 27.9626 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19019 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS245M-20/U-AC | 245 W DC, Monocrystalline ACPV Module | UL 1741 | 245 | 221.4 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.55 | 37.8 | 8.13 | 30.2 | 45.4 | -0.45 | 0.02 | -0.33 | 0.02 | -0.47 | 1.6199 | 28.7652 | 6.5203 | 27.9626 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19019 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS245MB-20/U | 245 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 245 | 221.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.55 | 37.8 | 8.13 | 30.2 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.5945 | 28.9976 | 6.4075 | 26.6126 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18872 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS245P-20/U | 245 W Polycrystalline Module | UL 1703 | 245 | 221.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.6 | 37.7 | 8.18 | 30 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.5481 | 29.6911 | 6.2975 | 26.6622 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18761 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS245P-20/U-AC | 245 W DC, Polycrystalline ACPV Module | UL 1741 | 245 | 221.3 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.6 | 37.7 | 8.18 | 30 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.5481 | 29.6911 | 6.2975 | 26.6622 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18761 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS245PB-20/U | 245 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 245 | 221.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.6 | 37.7 | 8.18 | 30 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.6124 | 28.7381 | 6.4693 | 25.9382 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18913 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 250P-20/UV | 250 W Polycrystalline Module | UL 1703 | 250 | 223.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.85 | 37.5 | 8.31 | 30.1 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.55 | 29.41 | 6.68 | 26.95 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18234 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS250M | 250 W Monocrystalline Module | UL 1703 | 250 | 223.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.65 | 37.9 | 8.24 | 30.4 | 46.2 | -0.48 | 0.05 | -0.35 | 0.02 | -0.49 | 1.5902 | 29.165 | 6.5569 | 28.2235 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18551 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS250M-20/U | 250 W Monocrystalline Module | UL 1703 | 250 | 226 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.65 | 37.9 | 8.24 | 30.4 | 45.4 | -0.45 | 0.02 | -0.33 | 0.02 | -0.47 | 1.6418 | 28.9557 | 6.6085 | 28.1478 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19016 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS250M-20/U-AC | 250 W DC, Monocrystalline ACPV Module | UL 1741 | 250 | 226 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.65 | 37.9 | 8.24 | 30.4 | 45.4 | -0.45 | 0.02 | -0.33 | 0.02 | -0.47 | 1.6418 | 28.9557 | 6.6085 | 28.1478 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.19016 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS250MB-20/U | 250 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 250 | 226 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.65 | 37.9 | 8.24 | 30.4 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.6161 | 29.1896 | 6.4942 | 26.7888 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18869 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS250P-20/U | 250 W Polycrystalline | UL 1703 | 250 | 223.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.7 | 37.8 | 8.3 | 30.2 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 6.97 | 28.33 | [7 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS250P-20/U-AC | 250 W DC, Polycrystalline ACPV Module | UL 1741 | 250 | 225.9 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.7 | 37.8 | 8.3 | 30.2 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.5708 | 29.8891 | 6.3898 | 26.84 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.1878 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS250PB-20/U | 250 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 250 | 225.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.7 | 37.8 | 8.3 | 30.2 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.6361 | 28.9297 | 6.5642 | 26.1111 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18932 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 255P-20/UV | 255 W Polycrystalline Module | UL 1703 | 255 | 228.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.95 | 37.8 | 8.39 | 30.5 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.57 | 29.8 | 6.74 | 27.31 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18347 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS255M-20/U | 255 W Monocrystalline Module | UL 1703 | 255 | 230.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.75 | 38 | 8.35 | 30.6 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.455 | 1.5835 | 30.0225 | 6.3928 | 27.4488 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18643 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS255M-20/U-AC | 255 W DC, Monocrystalline ACPV Module | UL 1741 | 255 | 230.6 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.75 | 38 | 8.35 | 30.6 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.455 | 1.5835 | 30.0225 | 6.3928 | 27.4488 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18643 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS255MB-20/U | 255 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 255 | 230.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.75 | 38 | 8.35 | 30.6 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.6377 | 29.3816 | 6.5809 | 26.9651 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18869 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS255P-20/U | 255 W Polycrystalline | UL 1703 | 255 | 228.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.8 | 37.9 | 8.42 | 30.4 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 6.97 | 28.33 | [7 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS255P-20/U-AC | 255 W DC, Polycrystalline ACPV Module | UL 1741 | 255 | 230.5 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.8 | 37.9 | 8.42 | 30.4 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.5935 | 30.087 | 6.4822 | 27.0177 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18801 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS255PB-20/U | 255 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 255 | 230.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.8 | 37.9 | 8.42 | 30.4 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.6597 | 29.1213 | 6.6591 | 26.2841 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18954 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 260M-20/UV | 260 W Monocrystalline Module | UL 1703 | 260 | 232.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.14 | 38.1 | 8.47 | 30.7 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.62 | 29.92 | 6.75 | 27.56 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18642 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 260P-20/UV | 260 W Polycrystalline Module | UL 1703 | 260 | 233.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.01 | 38 | 8.42 | 30.7 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.57 | 30 | 6.77 | 27.49 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18115 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS260M-20/U | 260 W Monocrystalline | UL 1703 | 260 | 234.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.37 | 39.1 | 8.44 | 30.92 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [7 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS260M-20/U-AC | 260 W DC, Monocrystalline ACPV Module | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.85 | 38.1 | 8.46 | 30.8 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.455 | 1.6043 | 30.2187 | 6.477 | 27.6282 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18646 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS260M-24/T | 260 W Monocrystalline Module | UL 1703 | 260 | 234.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.05 | 44.3 | 7.32 | 35.5 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.455 | 1.367 | 34.6758 | 5.759 | 31.6635 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18232 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS260MB-20/U | 260 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 260 | 235.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 8.85 | 38.1 | 8.46 | 30.8 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.6592 | 29.5737 | 6.6676 | 27.1413 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18873 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS260P-20/U | 260 W Polycrystalline | UL 1703 | 260 | 233 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 8.9 | 38 | 8.54 | 30.6 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 6.97 | 28.33 | [7 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS260P-20/U-AC | 260 W DC, Polycrystalline ACPV Module | UL 1741 | 260 | 235.2 | This component is specific to ACPV modules and is not available individually. | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.9 | 38 | 8.54 | 30.6 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.6162 | 30.285 | 6.5746 | 27.1955 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18826 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS260P-24/T | 260 W Polycrystalline Module | UL 1703 | 260 | 234.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.1 | 44 | 7.38 | 35.2 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.3638 | 34.8351 | 5.755 | 31.6987 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18272 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS260PB-20/U | 260 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 260 | 235.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.9 | 38 | 8.54 | 30.6 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.6834 | 29.3128 | 6.754 | 26.457 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18979 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 265M-20/UV | 265 W Monocrystalline Module | UL 1703 | 265 | 236.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.16 | 38.3 | 8.56 | 30.95 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.64 | 30.16 | 6.82 | 27.79 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18665 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 265P-20/UV | 265 W Polycrystalline Module | UL 1703 | 265 | 237.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.2 | 38.3 | 8.47 | 30.89 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.58 | 30.18 | 6.81 | 27.66 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.17994 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS265M-20/U | 265 W Monocrystalline | UL 1703 | 265 | 239.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.43 | 39.2 | 8.55 | 31.08 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS265P-20/U | 265 W Polycrystalline | UL 1703 | 265 | 237.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9 | 38.1 | 8.59 | 30.8 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 6.97 | 28.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 270M-20/UV | 270 W Monocrystalline Module | UL 1703 | 270 | 241.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.2 | 38.6 | 8.68 | 31.09 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.66 | 30.3 | 6.91 | 27.91 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18629 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 270P-20/UV | 270 W Polycrystalline Module | UL 1703 | 270 | 242.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.31 | 38.5 | 8.57 | 31.11 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.6 | 30.4 | 6.89 | 27.86 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18015 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS270M-20/U | 270 W Monocrystalline | UL 1703 | 270 | 243.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.48 | 39.3 | 8.66 | 31.24 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS270M-24/T | 270 W Monocrystalline Module | UL 1703 | 270 | 243.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.15 | 44.7 | 7.54 | 35.8 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.455 | 1.4081 | 34.9688 | 5.9321 | 31.9311 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18237 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS270P-20/U | 270 W Polycrystalline | UL 1703 | 270 | 242.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.09 | 38.39 | 8.61 | 31.44 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 6.97 | 28.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS270P-24/T | 270 W Polycrystalline Module | UL 1703 | 270 | 243.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.2 | 44.4 | 7.61 | 35.5 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.4063 | 35.132 | 5.9344 | 31.9689 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18299 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 275M-20/UV | 275 W Monocrystalline Module | UL 1703 | 275 | 246.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.23 | 38.9 | 8.81 | 31.22 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.69 | 30.42 | 7.02 | 28.03 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18694 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS275M-20/U | 275 W Monocrystalline | UL 1703 | 275 | 248.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.54 | 39.4 | 8.77 | 31.4 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS275P-20/U | 275 W Polycrystalline | UL 1703 | 275 | 246.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.17 | 38.68 | 8.66 | 31.79 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 6.97 | 28.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 280M-20/UV | 280 W Monocrystalline Module | UL 1703 | 280 | 250.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6269 | 60 | 1 | N | 9.28 | 39.1 | 8.91 | 31.43 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.71 | 30.63 | 7.1 | 28.22 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18706 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS280M-20/U | 280 W Monocrystalline | UL 1703 | 280 | 253.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.59 | 39.5 | 8.88 | 31.56 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS280M-24/T | 280 W Monocrystalline Module | UL 1703 | 280 | 252.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.3 | 45.1 | 7.75 | 36.1 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.455 | 1.4474 | 35.2619 | 6.0974 | 32.1986 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18227 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS280MB-24/T | 280 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 280 | 252.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.3 | 45.1 | 7.75 | 36.1 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.5722 | 33.6233 | 6.46 | 31.5925 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18879 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS280P-20/U | 280 W Polycrystalline | UL 1703 | 280 | 251.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.25 | 39.02 | 8.73 | 32.1 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 6.97 | 28.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS280P-24/T | 280 W Polycrystalline Module | UL 1703 | 280 | 252.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.35 | 44.8 | 7.82 | 35.8 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.4451 | 35.4289 | 6.0982 | 32.2391 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18285 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS280PB-24/T | 280 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 280 | 252.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.35 | 44.8 | 7.82 | 35.8 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.554 | 33.8832 | 6.3855 | 31.8366 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18806 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS285M-20/U | 285 W Monocrystalline | UL 1703 | 285 | 257.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.65 | 39.6 | 8.99 | 31.72 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS285M-24/T | 285 W Monocrystalline Module | UL 1703 | 285 | 257.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.38 | 45.3 | 7.86 | 36.25 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.455 | 1.5417 | 35.2331 | 6.271 | 32.3419 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1906 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS285MB-24/T | 285 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 285 | 257.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.38 | 45.3 | 7.86 | 36.25 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.5945 | 33.763 | 6.5517 | 31.7237 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18889 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS285MH-20/U | 285 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 285 | 261.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.65 | 39.6 | 8.99 | 31.71 | 45.2 | -0.4083 | 0.0518 | -0.3058 |  |  | 1.6245 | 32.3116 | 6.9337 | 29.9828 | [6 empty] | 2019-05-15
Phono Solar Technology Co.,Ltd. | PS285P-20/U | 285 W Polycrystalline | UL 1703 | 285 | 256.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.63 | 60 |  | N | 9.32 | 39.35 | 8.81 | 32.42 | 48.1 | -0.435 | 0.068 | -0.358 | 0.005 | -0.432 | 1.63 | 30.59 | 6.97 | 28.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS285P-24/T | 285 W Polycrystalline Module | UL 1703 | 285 | 257.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.43 | 45 | 7.93 | 35.95 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.5689 | 34.9429 | 6.3136 | 32.0499 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19236 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS285PB-24/T | 285 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 285 | 257.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.43 | 45 | 7.93 | 35.95 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.5759 | 34.0252 | 6.4753 | 31.97 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18814 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS290M-20/U | 290 W Monocrystalline | UL 1703 | 290 | 262.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.71 | 39.7 | 9.1 | 31.87 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS290M-24/T | 290 W Monocrystalline Module | UL 1703 | 290 | 261.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.45 | 45.5 | 7.97 | 36.4 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.4553 | 1.5633 | 35.3789 | 6.3587 | 32.4757 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19072 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS290MB-24/T | 290 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 290 | 262 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.45 | 45.5 | 7.97 | 36.4 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.6168 | 33.9027 | 6.6434 | 31.855 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18901 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS290MH-20/U | 290 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 290 | 266 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.71 | 39.7 | 9.1 | 31.87 | 45.2 | -0.4083 | 0.0518 | -0.3058 |  |  | 1.6444 | 32.4746 | 7.0185 | 30.1341 | [6 empty] | 2019-05-15
Phono Solar Technology Co.,Ltd. | PS290P-24/T | 290 W Polycrystalline Module | UL 1703 | 290 | 261.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.5 | 45.2 | 8.03 | 36.1 | 45.4 | -0.452 | 0.057 | -0.346 | 0.006 | -0.458 | 1.5887 | 35.0887 | 6.3932 | 32.1836 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19222 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS290PB-24/T | 290 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 290 | 261.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.5 | 45.2 | 8.03 | 36.1 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.5958 | 34.1672 | 6.557 | 32.1034 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18801 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS295M-20/U | 295 W Monocrystalline | UL 1703 | 295 | 267.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 |  | N | 9.74 | 39.8 | 9.2 | 32.07 | 48.4 | -0.404 | 0.06 | -0.311 | 0 | -0.406 | 1.74 | 32.52 | 7.36 | 30.46 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS295M-24/T | 295 W Monocrystalline Module | UL 1703 | 295 | 266.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.53 | 45.7 | 8.07 | 36.55 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.455 | 1.5829 | 35.5247 | 6.4385 | 32.6095 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19062 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS295MB-24/T | 295 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 295 | 266.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.53 | 45.7 | 8.07 | 36.55 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.6258 | 34.7487 | 6.5618 | 32.5516 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1915 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS295MH-20/U | 295 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 295 | 270.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.74 | 39.8 | 9.2 | 32.07 | 45.2 | -0.4083 | 0.0518 | -0.3058 |  |  | 1.6625 | 32.6784 | 7.0956 | 30.3232 | [6 empty] | 2019-05-15
Phono Solar Technology Co.,Ltd. | PS295P-24/T | 295 W Polycrystalline | UL 1703 | 295 | 262.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.8 | 44.12 | 8.29 | 35.62 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20398 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS295PB-24/T | 295 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 295 | 266.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.58 | 45.4 | 8.12 | 36.3 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.6337 | 34.6731 | 6.5349 | 32.647 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19202 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 300P-24/TV | 300 W Polycrystalline Module | UL 1703 | 300 | 268.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.79 | 45.3 | 8.12 | 36.5 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.41 | 35.7 | 6.5 | 32.52 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.16779 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS300M-24/T | 300 W Monocrystalline Module | UL 1703 | 300 | 271.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.6 | 45.9 | 8.17 | 36.7 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.4553 | 1.6025 | 35.6705 | 6.5183 | 32.7433 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19054 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS300MB-24/T | 300 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 300 | 271.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.6 | 45.9 | 8.17 | 36.7 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.6459 | 34.8913 | 6.6431 | 32.6852 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19143 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS300MH-20/U | 300 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 300 | 275.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.82 | 39.9 | 9.32 | 32.19 | 45.2 | -0.4083 | 0.0518 | -0.3058 |  |  | 1.6842 | 32.8007 | 7.1882 | 30.4367 | [6 empty] | 2019-05-15
Phono Solar Technology Co.,Ltd. | PS300P-24/T | 300 W Polycrystalline | UL 1703 | 300 | 266.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.85 | 44.49 | 8.33 | 36.04 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.20058 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS300PB-24/T | 300 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 300 | 271 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.65 | 45.6 | 8.24 | 36.4 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.6579 | 34.7687 | 6.6315 | 32.737 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19214 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 305P-24/TV | 305 W Polycrystalline Module | UL 1703 | 305 | 273.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 45.6 | 8.16 | 37.4 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.42 | 36.58 | 6.53 | 33.32 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.17031 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS305M-24/T | 305 W Monocrystalline Module | UL 1703 | 305 | 275.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 46.1 | 8.26 | 36.9 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.455 | 1.6202 | 35.8649 | 6.5901 | 32.9218 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19052 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS305MB-24/T | 305 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 305 | 275.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.68 | 46.1 | 8.26 | 36.9 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.664 | 35.0815 | 6.7163 | 32.8633 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1914 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS305MH-20/U | 305 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 305 | 280.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.87 | 40 | 9.43 | 32.36 | 45.2 | -0.4083 | 0.0518 | -0.3058 |  |  | 1.7041 | 32.9739 | 7.273 | 30.5974 | [6 empty] | 2019-05-15
Phono Solar Technology Co.,Ltd. | PS305P-24/T | 305 W Polycrystalline | UL 1703 | 305 | 271.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.9 | 44.87 | 8.37 | 36.45 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1973 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS305PB-24/T | 305 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 305 | 275.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.73 | 45.7 | 8.36 | 36.5 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.682 | 34.8642 | 6.728 | 32.8269 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19227 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 310M-24/TV | 310 W Monocrystalline Module | UL 1703 | 310 | 276.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9 | 46.1 | 8.33 | 37.2 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.62 | 36.3 | 6.63 | 33.62 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.1897 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 310P-24/TV | 310 W Polycrystalline Module | UL 1703 | 310 | 277.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.08 | 45.8 | 8.22 | 37.7 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.43 | 36.88 | 6.58 | 33.59 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.17012 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS310M-24/T | 310 W Monocrystalline Module | UL 1703 | 310 | 280.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.75 | 46.3 | 8.36 | 37.1 | 45.4 | -0.451 | 0.041 | -0.443 | 0.006 | -0.4553 | 1.6398 | 36.0592 | 6.6699 | 33.1002 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19074 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS310MB-24/T | 310 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 310 | 280.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.75 | 46.3 | 8.36 | 37.1 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.6842 | 35.2716 | 6.7976 | 33.0414 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19162 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS310MH-20/U | 310 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 310 | 284.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.92 | 40.1 | 9.54 | 32.5 | 45.2 | -0.4083 | 0.0518 | -0.3058 |  |  | 1.7239 | 33.1166 | 7.3579 | 30.7298 | [6 empty] | 2019-05-15
Phono Solar Technology Co.,Ltd. | PS310MH-20/UH | 310 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 310 | 288 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.661 | 60 | 2 | N | 9.67 | 39.9 | 9.22 | 33.63 | 44.28 | -0.373 | 0.045 | -0.282 |  |  | 1.8187 | 32.1118 | 7.2836 | 31.0869 | [6 empty] | 2020-08-11
Phono Solar Technology Co.,Ltd. | PS310P-24/T | 310 W Polycrystalline | UL 1703 | 310 | 276 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.95 | 45.24 | 8.41 | 36.87 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19411 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS310PB-24/T | 310 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 310 | 280.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.8 | 46 | 8.45 | 36.7 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.7001 | 35.0552 | 6.8005 | 33.0068 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19225 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 315M-24/TV | 315 W Monocrystalline Module | UL 1703 | 315 | 281.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.05 | 46.1 | 8.38 | 37.6 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.63 | 36.7 | 6.67 | 33.98 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18991 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 315P-24/TV | 315 W Polycrystalline Module | UL 1703 | 315 | 282.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.17 | 45.9 | 8.31 | 37.9 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.44 | 37.07 | 6.65 | 33.77 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.16946 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS315M-24/T | 315 W Monocrystalline | UL 1703 | 315 | 283.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.32 | 46.8 | 8.55 | 36.99 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [7 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS315MB-24/T | 315 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 315 | 285.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.83 | 46.5 | 8.45 | 37.25 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.7023 | 35.4142 | 6.8708 | 33.175 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19138 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS315MH-20/U | 315 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 315 | 289.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 9.98 | 40.2 | 9.64 | 32.68 | 45.2 | -0.4083 | 0.0518 | -0.3058 |  |  | 1.742 | 33.3 | 7.435 | 30.9 | [6 empty] | 2019-05-15
Phono Solar Technology Co.,Ltd. | PS315MH-20/UH | 315 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 315 | 292.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.661 | 60 | 2 | N | 9.76 | 40.11 | 9.31 | 33.84 | 44.28 | -0.373 | 0.045 | -0.282 |  |  | 1.8365 | 32.3123 | 7.3547 | 31.281 | [6 empty] | 2020-08-11
Phono Solar Technology Co.,Ltd. | PS315P-24/T | 315 W Polycrystalline | UL 1703 | 315 | 280.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.01 | 45.59 | 8.45 | 37.28 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19103 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS315PB-24/T | 315 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 315 | 284.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.88 | 46.2 | 8.55 | 36.85 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.7202 | 35.1985 | 6.881 | 33.1417 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19222 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 320M-24/TV | 320 W Monocrystalline Module | UL 1703 | 320 | 286.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.08 | 46.3 | 8.46 | 37.8 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.65 | 36.89 | 6.73 | 34.16 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19021 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 320P-24/TV | 320 W Polycrystalline Module | UL 1703 | 320 | 287.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.2 | 46.2 | 8.33 | 38.4 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.45 | 37.56 | 6.66 | 34.21 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.17019 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS320M-24/T | 320 W Monocrystalline | UL 1703 | 320 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.37 | 46.92 | 8.64 | 37.18 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS320MB-24/T | 320 W Monocrystalline Module, Black Frame, Black Backsheet | UL 1703 | 320 | 289.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 8.9 | 46.7 | 8.55 | 37.4 | 45.3 | -0.452 | 0.049 | -0.443 | 0.003 | -0.455 | 1.7225 | 35.5568 | 6.9521 | 33.3086 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19139 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS320MH-20/U | 320 W, 60 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 320 | 294.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.63 | 60 | 1 | N | 10.06 | 40.3 | 9.75 | 32.83 | 45.2 | -0.4083 | 0.0518 | -0.3058 |  |  | 1.7619 | 33.4528 | 7.5198 | 31.0418 | [6 empty] | 2019-05-15
Phono Solar Technology Co.,Ltd. | PS320MH-20/UH | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 297.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.661 | 60 | 2 | N | 9.85 | 40.35 | 9.39 | 34.08 | 44.28 | -0.373 | 0.045 | -0.282 |  |  | 1.8522 | 32.5415 | 7.4179 | 31.5029 | [6 empty] | 2020-08-11
Phono Solar Technology Co.,Ltd. | PS320P-24/T | 320 W Polycrystalline | UL 1703 | 320 | 285.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.03 | 46.04 | 8.49 | 37.7 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS320PB-24/T | 320 W Polycrystalline Module, Black Frame, Black Backsheet | UL 1703 | 320 | 289.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 8.95 | 46.4 | 8.64 | 37 | 45.4 | -0.454 | 0.057 | -0.353 | 0.001 | -0.455 | 1.7383 | 35.3418 | 6.9534 | 33.2766 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19199 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 325M-24/TV | 325 W Monocrystalline Module | UL 1703 | 325 | 290.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.11 | 46.55 | 8.55 | 37.98 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.66 | 37.07 | 6.81 | 34.32 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18934 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 325P-24/TV | 325 W Polycrystalline Module | UL 1703 | 325 | 291.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9404 | 72 | 1 | N | 9.25 | 46.4 | 8.37 | 38.8 | 46.3 | -0.47 | 0.05 | -0.34 | 0.02 | -0.47 | 1.45 | 37.95 | 6.7 | 34.57 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.16932 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS325M-24/T | 325 W Monocrystalline | UL 1703 | 325 | 293 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.43 | 47.04 | 8.72 | 37.36 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS325MH-20/UH | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 325 | 302.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.661 | 60 | 2 | N | 9.94 | 40.57 | 9.48 | 34.29 | 44.28 | -0.373 | 0.045 | -0.282 |  |  | 1.87 | 32.742 | 7.489 | 31.697 | [6 empty] | 2020-08-11
Phono Solar Technology Co.,Ltd. | PS325P-24/T | 325 W Polycrystalline | UL 1703 | 325 | 289.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.11 | 46.34 | 8.53 | 38.11 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 330M-24/TV | 330 W Monocrystalline Module | UL 1703 | 330 | 295.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.15 | 46.84 | 8.61 | 38.31 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.68 | 37.39 | 6.85 | 34.62 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.19035 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS330M-24/T | 330 W Monocrystalline | UL 1703 | 330 | 297.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.48 | 47.16 | 8.81 | 37.55 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS330P-24/T | 330 W Polycrystalline | UL 1703 | 330 | 294.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.15 | 46.74 | 8.57 | 38.53 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS 335M-24/TV | 335 W Monocrystalline Module | UL 1703 | 335 | 300 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.9404 | 72 | 1 | N | 9.18 | 46.99 | 8.7 | 38.49 | 46.5 | -0.48 | 0.04 | -0.35 | 0.03 | -0.46 | 1.69 | 37.56 | 6.93 | 34.79 | Rack | Flat Plate | 0.992 | 1.956 | 1 | 0.18948 |  | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS335M-24/T | 335 W Monocrystalline | UL 1703 | 335 | 302.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.54 | 47.28 | 8.89 | 37.73 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS335P-24/T | 335 W Polycrystalline | UL 1703 | 335 | 299 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.2 | 47.12 | 8.61 | 38.94 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS340M-24/T | 340 W Monocrystalline | UL 1703 | 340 | 307 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.59 | 47.4 | 8.98 | 37.91 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS340P-24/T | 340 W Polycrystalline | UL 1703 | 340 | 303.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.94 | 72 |  | N | 9.25 | 47.49 | 8.65 | 39.36 | 48.7 | -0.448 | 0.063 | -0.361 | 0.017 | -0.46 | 1.65 | 36.47 | 6.88 | 34.33 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS345M-24/T | 345 W Monocrystalline | UL 1703 | 345 | 311.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.65 | 47.52 | 9.06 | 38.1 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS345MH-24/T | 345 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 345 | 316.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.65 | 47.52 | 9.06 | 38.1 | 45.3 | -0.4087 | 0.0619 | -0.3283 | 0.0314 | -0.4355 | 1.6889 | 38.2069 | 7.0511 | 35.8737 | [6 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS350M-24/T | 350 W Monocrystalline | UL 1703 | 350 | 316.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.71 | 47.64 | 9.15 | 38.26 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS350MH-24/T | 350 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 350 | 321 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.71 | 47.64 | 9.15 | 38.26 | 45.3 | -0.4087 | 0.0619 | -0.3283 | 0.0314 | -0.4355 | 1.7057 | 38.3674 | 7.1211 | 36.0243 | [6 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS350MH-24/TH | 350 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 350 | 320.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 9.4 | 46.4 | 9.03 | 38.77 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.6565 | 37.5747 | 7.0735 | 35.1438 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS355M-24/T | 355 W Monocrystalline | UL 1703 | 355 | 321 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.74 | 47.76 | 9.22 | 38.51 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS355M4-20/UHB | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 355 | 331.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.06 | 40.48 | 10.61 | 33.71 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.0356 | 34.1576 | 8.1661 | 33.0203 | [6 empty] | 2021-06-11
Phono Solar Technology Co.,Ltd. | PS355M4H-20/UHB | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 355 | 331.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.06 | 40.48 | 10.61 | 33.71 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.0356 | 34.1576 | 8.1661 | 33.0203 | [6 empty] | 2021-06-11
Phono Solar Technology Co.,Ltd. | PS355MH-24/T | 355 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 325.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.74 | 47.76 | 9.22 | 38.51 | 45.3 | -0.4087 | 0.0619 | -0.3283 | 0.0314 | -0.4355 | 1.7188 | 38.6181 | 7.1756 | 36.2597 | [6 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS355MH-24/TH | 355 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 355 | 325.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 9.47 | 46.66 | 9.1 | 39.02 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.6693 | 37.817 | 7.1283 | 35.3704 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS360M-24/T | 360 W Monocrystalline | UL 1703 | 360 | 325.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 |  | N | 9.82 | 47.88 | 9.32 | 38.63 | 48.8 | -0.405 | 0.044 | -0.32 | -0.014 | -0.397 | 1.71 | 38.98 | 7.47 | 36.23 | [6 empty] | 2017-11-01 | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS360M4-20/UHB | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 336.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.15 | 40.69 | 10.68 | 32.99 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.049 | 33.428 | 8.22 | 32.315 | [6 empty] | 2021-06-11
Phono Solar Technology Co.,Ltd. | PS360M4H-20/UHB | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 360 | 336.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.15 | 40.69 | 10.68 | 32.99 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.049 | 33.428 | 8.22 | 32.315 | [6 empty] | 2021-06-11
Phono Solar Technology Co.,Ltd. | PS360MH-24/T | 360 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 330.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.82 | 47.88 | 9.32 | 38.63 | 45.3 | -0.4087 | 0.0619 | -0.3283 | 0.0314 | -0.4355 | 1.7374 | 38.7384 | 7.2534 | 36.3727 | [6 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS360MH-24/TH | 360 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 360 | 329.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 9.55 | 46.92 | 9.16 | 39.31 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.6803 | 38.0981 | 7.1753 | 35.6333 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS365M4-20/UHB | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 340.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.23 | 40.81 | 10.75 | 33.96 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.0624 | 34.4109 | 8.2739 | 33.2652 | [6 empty] | 2021-06-11
Phono Solar Technology Co.,Ltd. | PS365M4H-20/UHB | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 365 | 340.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.23 | 40.81 | 10.75 | 33.96 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.0624 | 34.4109 | 8.2739 | 33.2652 | [6 empty] | 2021-06-11
Phono Solar Technology Co.,Ltd. | PS365MH-24/T | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 335.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.87 | 48 | 9.4 | 38.83 | 45.3 | -0.4087 | 0.0619 | -0.3283 | 0.0314 | -0.4355 | 1.7523 | 38.939 | 7.3157 | 36.561 | [6 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS365MH-24/TH | 365 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 334.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 9.63 | 47.19 | 9.22 | 39.59 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.6913 | 38.3694 | 7.2223 | 35.8871 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS370MH-24/T | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 339.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.92 | 48.12 | 9.49 | 39.02 | 45.3 | -0.4087 | 0.0619 | -0.3283 | 0.0314 | -0.4355 | 1.7691 | 39.1295 | 7.3857 | 36.7399 | [6 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS370MH-24/TH | 370 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 339.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 9.71 | 47.44 | 9.29 | 39.83 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.7042 | 38.602 | 7.2772 | 36.1046 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS375MH-24/T | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 344.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 9.98 | 48.24 | 9.57 | 39.19 | 45.3 | -0.4087 | 0.0619 | -0.3283 | 0.0314 | -0.4355 | 1.784 | 39.3 | 7.448 | 36.9 | [6 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS375MH-24/TH | 375 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 344.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 9.79 | 47.69 | 9.35 | 40.11 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.7152 | 38.8734 | 7.3242 | 36.3584 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS380M1-24/TH | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 380 | 354.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.05 | 48.57 | 9.52 | 39.92 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.8992 | 37.9469 | 7.6296 | 36.7597 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS380M1-24/THB | 380 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 380 | 355.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.05 | 48.57 | 9.52 | 39.92 | 43.2 | -0.359 | 0.0515 | -0.2776 |  |  | 1.8614 | 39.098 | 7.4963 | 38.0692 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS380M1H-24/TH | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 354.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.05 | 48.57 | 9.52 | 39.92 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.8992 | 37.9469 | 7.6296 | 36.7597 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS380M1H-24/THB | 380 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 380 | 355.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.05 | 48.57 | 9.52 | 39.92 | 43.2 | -0.359 | 0.0515 | -0.2776 |  |  | 1.8614 | 39.098 | 7.4963 | 38.0692 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS380MH-24/T | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 349.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.94 | 72 | 1 | N | 10.03 | 48.36 | 9.66 | 39.39 | 45.3 | -0.4087 | 0.0619 | -0.3283 | 0.0314 | -0.4355 | 1.8008 | 39.5006 | 7.518 | 37.0883 | [6 empty] | 2019-02-01
Phono Solar Technology Co.,Ltd. | PS380MH-24/TH | 380 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 348.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 9.87 | 47.94 | 9.42 | 40.35 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.728 | 39.106 | 7.379 | 36.576 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS385M1-24/TH | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 385 | 359.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.13 | 48.85 | 9.57 | 40.24 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.9091 | 38.2511 | 7.6696 | 37.0543 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS385M1-24/THB | 385 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 385 | 360.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.13 | 48.85 | 9.57 | 40.24 | 43.2 | -0.359 | 0.0515 | -0.2776 |  |  | 1.8712 | 39.4114 | 7.5356 | 38.3744 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS385M1H-24/TH | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 359.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.13 | 48.85 | 9.57 | 40.24 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.9091 | 38.2511 | 7.6696 | 37.0543 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS385M1H-24/THB | 385 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 385 | 360.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.13 | 48.85 | 9.57 | 40.24 | 43.2 | -0.359 | 0.0515 | -0.2776 |  |  | 1.8712 | 39.4114 | 7.5356 | 38.3744 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS385MH-24/TH | 385 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 353.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 9.95 | 48.19 | 9.48 | 40.62 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.739 | 39.3677 | 7.426 | 36.8207 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS390M1-24/TH | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 390 | 364.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.21 | 49.13 | 9.62 | 40.55 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.9191 | 38.5458 | 7.7097 | 37.3398 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS390M1-24/THB | 390 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 390 | 365.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.2 | 49.12 | 9.62 | 40.55 | 43.2 | -0.359 | 0.0515 | -0.2776 |  |  | 1.881 | 39.715 | 7.575 | 38.67 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS390M1H-24/TH | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 364.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.21 | 49.13 | 9.62 | 40.55 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.9191 | 38.5458 | 7.7097 | 37.3398 | [6 empty] | 2020-02-21 | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS390M1H-24/THB | 390 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 390 | 365.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.2 | 49.12 | 9.62 | 40.55 | 43.2 | -0.359 | 0.0515 | -0.2776 |  |  | 1.881 | 39.715 | 7.575 | 38.67 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS390MH-24/TH | 390 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 358.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 10.02 | 48.5 | 9.53 | 40.93 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.7482 | 39.6681 | 7.4652 | 37.1018 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS395M1-24/TH | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 395 | 369 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.29 | 49.41 | 9.67 | 40.85 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.9291 | 38.831 | 7.7498 | 37.616 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS395M1H-24/TH | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 369 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.29 | 49.41 | 9.67 | 40.85 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.9291 | 38.831 | 7.7498 | 37.616 | [6 empty] | 2020-02-21 | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS395MH-24/TH | 395 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 363 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.98 | 144 | 1 | N | 10.1 | 48.73 | 9.6 | 41.15 | 44.8 | -0.4235 | 0.0494 | -0.3408 |  |  | 1.761 | 39.8813 | 7.52 | 37.3012 | [6 empty] | 2019-06-03
Phono Solar Technology Co.,Ltd. | PS400M1-24/TH | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 400 | 373.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.37 | 49.69 | 9.72 | 41.16 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.9391 | 39.1257 | 7.7899 | 37.9015 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS400M1H-24/TH | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 373.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.37 | 49.69 | 9.72 | 41.16 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.9391 | 39.1257 | 7.7899 | 37.9015 | [6 empty] | 2020-02-21 | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS405M1-24/TH | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 405 | 378.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.45 | 49.97 | 9.77 | 41.46 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.949 | 39.4108 | 7.8299 | 38.1778 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS405M1H-24/TH | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 378.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.45 | 49.97 | 9.77 | 41.46 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.949 | 39.4108 | 7.8299 | 38.1778 | [6 empty] | 2020-02-21 | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS410M1-24/TH | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 410 | 383.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.53 | 50.25 | 9.82 | 41.76 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.959 | 39.696 | 7.87 | 38.454 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS410M1H-24/TH | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 410 | 383.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 48 | 3 | N | 10.53 | 50.25 | 9.82 | 41.76 | 43.5 | -0.3658 | 0.0457 | -0.2774 |  |  | 1.959 | 39.696 | 7.87 | 38.454 | [6 empty] | 2020-02-21 | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS425M4-24/THB | 425 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 425 | 396.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 10.95 | 48.59 | 10.52 | 40.4 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.0596 | 39.4457 | 8.2798 | 38.2736 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS425M4H-24/THB | 425 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 425 | 396.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 10.95 | 48.59 | 10.52 | 40.4 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.0596 | 39.4457 | 8.2798 | 38.2736 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS430M4-24/TH | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 430 | 400.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.04 | 48.72 | 10.59 | 40.61 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.1151 | 39.3979 | 8.4995 | 38.0065 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS430M4-24/THB | 430 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 430 | 401.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.04 | 48.72 | 10.59 | 40.61 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.0733 | 39.6507 | 8.3349 | 38.4725 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS430M4H-24/TH | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 400.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.04 | 48.72 | 10.59 | 40.61 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.1151 | 39.3979 | 8.4995 | 38.0065 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS430M4H-24/THB | 430 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 430 | 401.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.04 | 48.72 | 10.59 | 40.61 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.0733 | 39.6507 | 8.3349 | 38.4725 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS430M5GF-24/TH | 430 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 430 | 402.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.12 | 49.39 | 10.4 | 41.35 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.0588 | 39.8288 | 8.1881 | 38.7184 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS430M5GFH-24/TH | 430 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 430 | 402.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.12 | 49.39 | 10.4 | 41.35 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.0588 | 39.8288 | 8.1881 | 38.7184 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS435M4-24/TH | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 435 | 405.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.13 | 48.85 | 10.66 | 40.81 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.129 | 39.5919 | 8.5556 | 38.1936 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS435M4-24/THB | 435 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 435 | 406.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.13 | 48.85 | 10.66 | 40.81 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.087 | 39.846 | 8.39 | 38.662 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS435M4H-24/TH | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 405.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.13 | 48.85 | 10.66 | 40.81 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.129 | 39.5919 | 8.5556 | 38.1936 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS435M4H-24/THB | 435 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 435 | 406.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.13 | 48.85 | 10.66 | 40.81 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.087 | 39.846 | 8.39 | 38.662 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS435M5GF-24/TH | 435 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 435 | 406.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.18 | 49.45 | 10.5 | 41.43 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.0786 | 39.9058 | 8.2668 | 38.7933 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS435M5GFH-24/TH | 435 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 435 | 406.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.18 | 49.45 | 10.5 | 41.43 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.0786 | 39.9058 | 8.2668 | 38.7933 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS440M4-24/TH | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 440 | 409.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.21 | 48.98 | 10.73 | 41.01 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.143 | 39.786 | 8.6118 | 38.3808 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS440M4-24/THB | 440 W, 144 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 440 | 410.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.21 | 48.98 | 10.73 | 41.01 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.1007 | 40.0413 | 8.4451 | 38.8515 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS440M4H-24/TH | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 409.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.21 | 48.98 | 10.73 | 41.01 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.143 | 39.786 | 8.6118 | 38.3808 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS440M4H-24/THB | 440 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 440 | 410.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.21 | 48.98 | 10.73 | 41.01 | 44.8 | -0.3453 | 0.049 | -0.2663 |  |  | 2.1007 | 40.0413 | 8.4451 | 38.8515 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS440M5GF-24/TH | 440 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 440 | 411.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.24 | 49.51 | 10.6 | 41.51 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.0984 | 39.9829 | 8.3455 | 38.8682 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS440M5GFH-24/TH | 440 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 440 | 411.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.24 | 49.51 | 10.6 | 41.51 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.0984 | 39.9829 | 8.3455 | 38.8682 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS445M4-24/TH | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 445 | 414.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.29 | 49.11 | 10.8 | 41.21 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.157 | 39.98 | 8.668 | 38.568 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS445M4H-24/TH | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 414.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.29 | 49.11 | 10.8 | 41.21 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.157 | 39.98 | 8.668 | 38.568 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS445M5GF-24/TH | 445 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 445 | 416.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.3 | 49.57 | 10.7 | 41.59 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.1182 | 40.0599 | 8.4243 | 38.9431 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS445M5GFH-24/TH | 445 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 445 | 416.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.3 | 49.57 | 10.7 | 41.59 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.1182 | 40.0599 | 8.4243 | 38.9431 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS450M4-24/TH | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 450 | 419.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.38 | 49.24 | 10.87 | 41.4 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.171 | 40.1643 | 8.7242 | 38.7458 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS450M4H-24/TH | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 419.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.38 | 49.24 | 10.87 | 41.4 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.171 | 40.1643 | 8.7242 | 38.7458 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS450M5GF-24/TH | 450 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 450 | 421.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.36 | 49.63 | 10.8 | 41.67 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.138 | 40.137 | 8.503 | 39.018 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS450M5GFH-24/TH | 450 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 450 | 421.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.36 | 49.63 | 10.8 | 41.67 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.138 | 40.137 | 8.503 | 39.018 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS455M4-24/TH | 455 W, 144 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 455 | 424.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.47 | 49.37 | 10.94 | 41.6 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.185 | 40.3584 | 8.7804 | 38.933 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS455M4H-24/TH | 455 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 455 | 424.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.22 | 48 | 3 | N | 11.47 | 49.37 | 10.94 | 41.6 | 45 | -0.3528 | 0.0472 | -0.2724 |  |  | 2.185 | 40.3584 | 8.7804 | 38.933 | [6 empty] | 2021-01-21
Phono Solar Technology Co.,Ltd. | PS455M5GF-24/TH | 455 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 455 | 426.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.42 | 49.69 | 10.9 | 41.75 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.1578 | 40.2141 | 8.5817 | 39.0929 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS455M5GFH-24/TH | 455 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 455 | 426.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.42 | 49.69 | 10.9 | 41.75 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.1578 | 40.2141 | 8.5817 | 39.0929 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS460M5GF-24/TH | 460 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 460 | 430.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.48 | 49.75 | 11 | 41.82 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.1776 | 40.2815 | 8.6605 | 39.1585 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS460M5GFH-24/TH | 460 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 460 | 430.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.48 | 49.75 | 11 | 41.82 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.1776 | 40.2815 | 8.6605 | 39.1585 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS465M5GF-24/TH | 465 W, 144 half-cut cell bifacial monocrystalline module, 1000V max system Vdc | UL 61730 | 465 | 435.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.54 | 49.81 | 11.1 | 41.9 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.1974 | 40.3585 | 8.7392 | 39.2334 | [6 empty] | 2021-08-02
Phono Solar Technology Co.,Ltd. | PS465M5GFH-24/TH | 465 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 61730 | 465 | 435.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.16 | 72 | 2 | Y | 11.54 | 49.81 | 11.1 | 41.9 | 44.2 | -0.3498 | 0.0458 | -0.2662 |  |  | 2.1974 | 40.3585 | 8.7392 | 39.2334 | [6 empty] | 2021-08-02
Prism Solar Technologies, Inc. | BN60-295 | 295 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 295 | 274.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7328 | 31.3781 | 7.0058 | 30.0178 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN60-333BSTC | 295 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 295 | 274.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.77 | 40.11 | 9.15 | 32.24 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7328 | 31.3781 | 7.0058 | 30.0178 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN60-300 | 300 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 300 | 278.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7498 | 31.6117 | 7.0747 | 30.2412 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN60-338BSTC | 300 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 300 | 278.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 9.91 | 40.45 | 9.24 | 32.48 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7498 | 31.6117 | 7.0747 | 30.2412 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN60-305 | 305 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 305 | 283.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 10.06 | 40.79 | 9.32 | 32.73 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.765 | 31.855 | 7.136 | 30.474 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN60-344BSTC | 305 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 305 | 283.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 10.06 | 40.79 | 9.32 | 32.73 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.765 | 31.855 | 7.136 | 30.474 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN60-310 | 310 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 310 | 288.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 10.21 | 41.14 | 9.4 | 32.97 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7802 | 32.0886 | 7.1973 | 30.6975 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN60-315 | 315 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 315 | 293.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 10.37 | 41.49 | 9.48 | 33.22 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7953 | 32.3319 | 7.2585 | 30.9302 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BHC60-320 | 320 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 320 | 298.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.644 | 60 | 2 | N | 10.06 | 40.21 | 9.73 | 32.96 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.8648 | 31.6974 | 7.5502 | 30.594 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BN60-320 | 320 W, 60 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 320 | 297.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.653 | 60 | 1 | N | 10.52 | 41.84 | 9.56 | 33.47 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.8105 | 32.5752 | 7.3198 | 31.163 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BHC60-325 | 325 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 325 | 302.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.644 | 60 | 2 | N | 10.15 | 40.3 | 9.82 | 33.1 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.882 | 31.832 | 7.62 | 30.724 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BHC60-330 | 330 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 330 | 307.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.644 | 60 | 2 | N | 10.25 | 40.39 | 9.93 | 33.24 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9031 | 31.9666 | 7.7054 | 30.854 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BHC60-335 | 335 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 335 | 312.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.644 | 60 | 2 | N | 10.34 | 40.46 | 10.03 | 33.4 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9222 | 32.1205 | 7.783 | 31.0025 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BHC60-340 | 340 W, 120 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 340 | 317.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.644 | 60 | 2 | N | 10.43 | 40.6 | 10.11 | 33.62 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9376 | 32.3321 | 7.845 | 31.2067 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BN72-360 | 360 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 360 | 334.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 9.99 | 47.56 | 9.32 | 38.63 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7622 | 38.0841 | 7.1298 | 36.0444 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN72-429BSTC | 360 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 360 | 334.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 9.99 | 47.56 | 9.32 | 38.63 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.7622 | 38.0841 | 7.1298 | 36.0444 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN72-365 | 365 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 365 | 339.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.08 | 47.66 | 9.43 | 38.71 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.783 | 38.163 | 7.214 | 36.119 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN72-435BSTC | 365 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 365 | 339.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.08 | 47.66 | 9.43 | 38.71 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.783 | 38.163 | 7.214 | 36.119 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | P72-365 | 365 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 365 | 336.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 9.705 | 48.05 | 9.236 | 39.52 | 46.43 | -0.375 | 0.045 | -0.28 |  |  | 1.8347 | 37.9985 | 7.3389 | 35.9055 | [6 empty] | 2020-01-13
Prism Solar Technologies, Inc. | BN72-370 | 370 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 370 | 344.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.17 | 47.75 | 9.54 | 38.78 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.8038 | 38.232 | 7.2982 | 36.1843 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | BN72-441BSTC | 370 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 370 | 344.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.17 | 47.75 | 9.54 | 38.78 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.8038 | 38.232 | 7.2982 | 36.1843 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | P72-370 | 370 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 370 | 341 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 9.767 | 48.08 | 9.323 | 39.69 | 46.43 | -0.375 | 0.045 | -0.28 |  |  | 1.852 | 38.162 | 7.408 | 36.06 | [6 empty] | 2020-01-13
Prism Solar Technologies, Inc. | BN72-375 | 375 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 375 | 349 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.26 | 47.85 | 9.65 | 38.86 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.8246 | 38.3109 | 7.3823 | 36.259 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | P72-375 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 345.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 9.826 | 48.16 | 9.432 | 39.76 | 46.43 | -0.375 | 0.045 | -0.28 |  |  | 1.8737 | 38.2293 | 7.4946 | 36.1236 | [6 empty] | 2020-01-13
Prism Solar Technologies, Inc. | P72X-375 | 375 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 375 | 346.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 9.939 | 48.02 | 9.36 | 40.06 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9009 | 38.0763 | 7.7084 | 36.0768 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BN72-380 | 380 W, 72 cell double glass bifacial monocrystalline module, 1000V max system Vdc | UL 1703 | 380 | 353.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.969 | 72 | 1 | N | 10.35 | 47.94 | 9.76 | 38.94 | 43.78 | -0.376 | 0.044 | -0.277 |  |  | 1.8454 | 38.3897 | 7.4665 | 36.3336 | [6 empty] | 2019-07-15
Prism Solar Technologies, Inc. | P72-380 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 350.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.91 | 72 | 1 | N | 9.904 | 48.17 | 9.552 | 39.78 | 46.43 | -0.375 | 0.045 | -0.28 |  |  | 1.8975 | 38.2485 | 7.59 | 36.1418 | [6 empty] | 2020-01-13
Prism Solar Technologies, Inc. | P72X-380 | 380 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 380 | 351.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 9.966 | 48.31 | 9.385 | 40.49 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.906 | 38.485 | 7.729 | 36.464 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | P72X-385 | 385 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 385 | 356 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 9.993 | 48.53 | 9.426 | 40.84 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9143 | 38.8177 | 7.7628 | 36.7792 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BHC72-390 | 390 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 390 | 363.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.14 | 48.17 | 9.84 | 39.65 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.8738 | 38.3778 | 7.624 | 36.8487 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | P72X-390 | 390 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 390 | 360.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 10.024 | 48.96 | 9.499 | 41.05 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9292 | 39.0173 | 7.8229 | 36.9683 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BHC72-395 | 395 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 395 | 368.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.23 | 48.26 | 9.92 | 39.83 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.889 | 38.552 | 7.686 | 37.016 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | P72X-395 | 395 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 395 | 365.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 10.045 | 49.28 | 9.532 | 41.44 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9359 | 39.388 | 7.8501 | 37.3195 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BHC72-400 | 400 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 400 | 373.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.32 | 48.35 | 10 | 40.01 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9042 | 38.7262 | 7.748 | 37.1833 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | P72X-400 | 400 W, 72 cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 400 | 370.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.96 | 72 | 1 | N | 10.067 | 49.46 | 9.61 | 41.62 | 45.98 | -0.37 | 0.043 | -0.274 |  |  | 1.9517 | 39.559 | 7.9143 | 37.4816 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BHC72-405 | 405 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 405 | 378 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.42 | 48.45 | 10.08 | 40.19 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9195 | 38.9004 | 7.81 | 37.3506 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BHC72-410 | 410 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 410 | 382.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.51 | 48.56 | 10.16 | 40.38 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9347 | 39.0844 | 7.872 | 37.5271 | [6 empty] | 2020-02-03
Prism Solar Technologies, Inc. | BHC72-415 | 415 W, 144 half-cut cell bifacial monocrystalline module, 1500V max system Vdc | UL 1703 | 415 | 387.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.61 | 48.64 | 10.25 | 40.5 | 44.45 | -0.36 | 0.038 | -0.277 |  |  | 1.9518 | 39.2005 | 7.9417 | 37.6387 | [6 empty] | 2020-02-03
PT IDN SOLAR TECH | NUSA120H-310M | 310 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 310 | 288.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 9.87 | 39.8 | 9.37 | 33.1 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.8506 | 31.6569 | 7.5019 | 31.2273 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-310MB | 310 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 310 | 288.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 9.87 | 39.8 | 9.37 | 33.1 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.8506 | 31.6569 | 7.5019 | 31.2273 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-315M | 315 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 315 | 293.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 9.95 | 40.1 | 9.44 | 33.4 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.8644 | 31.9438 | 7.5579 | 31.5103 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-315MB | 315 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 315 | 293.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 9.95 | 40.1 | 9.44 | 33.4 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.8644 | 31.9438 | 7.5579 | 31.5103 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-320M | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 320 | 298.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.01 | 40.4 | 9.52 | 33.6 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.8802 | 32.1351 | 7.622 | 31.699 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-320MB | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 320 | 298.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.01 | 40.4 | 9.52 | 33.6 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.8802 | 32.1351 | 7.622 | 31.699 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-325M | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 325 | 303.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.08 | 40.7 | 9.59 | 33.9 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.894 | 32.422 | 7.678 | 31.982 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-325MB | 325 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 325 | 303.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.08 | 40.7 | 9.59 | 33.9 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.894 | 32.422 | 7.678 | 31.982 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-330M | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 330 | 308 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.16 | 41 | 9.66 | 34.2 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.9078 | 32.7089 | 7.734 | 32.265 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-330MB | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 330 | 308 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.16 | 41 | 9.66 | 34.2 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.9078 | 32.7089 | 7.734 | 32.265 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-335M | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 335 | 312.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.35 | 41.2 | 9.75 | 34.4 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.9256 | 32.9002 | 7.8061 | 32.4537 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-335MB | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 335 | 312.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.35 | 41.2 | 9.75 | 34.4 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.9256 | 32.9002 | 7.8061 | 32.4537 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-340M | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 340 | 317.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.44 | 41.4 | 9.82 | 34.6 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.9394 | 33.0915 | 7.8621 | 32.6424 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-340MB | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 340 | 317.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.44 | 41.4 | 9.82 | 34.6 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.9394 | 33.0915 | 7.8621 | 32.6424 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-350M | 350 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 350 | 326.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.01 | 41.1 | 10.42 | 33.6 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.0722 | 32.5633 | 8.3212 | 31.8815 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA120H-355M | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 355 | 331.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.08 | 41.3 | 10.51 | 33.8 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.0901 | 32.7572 | 8.3931 | 32.0712 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA120H-355MB | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 355 | 331.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.08 | 41.3 | 10.51 | 33.8 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.0901 | 32.7572 | 8.3931 | 32.0712 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA120H-360M | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 360 | 336.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.15 | 41.5 | 10.59 | 34 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.106 | 32.951 | 8.457 | 32.261 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA120H-360MB | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 360 | 336.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.15 | 41.5 | 10.59 | 34 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.106 | 32.951 | 8.457 | 32.261 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA120H-365M | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 341 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.22 | 41.7 | 10.68 | 34.2 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.1239 | 33.1448 | 8.5289 | 32.4508 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA120H-365MB | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 365 | 341 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.22 | 41.7 | 10.68 | 34.2 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.1239 | 33.1448 | 8.5289 | 32.4508 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA120H-370M | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 345.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.29 | 41.9 | 10.76 | 34.4 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.1398 | 33.3387 | 8.5928 | 32.6405 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-370M | 370 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 344.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.91 | 48.1 | 9.31 | 39.7 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.861 | 8.9917 | 7.1906 | 8.6811 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-370MB | 370 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 370 | 344.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.91 | 48.1 | 9.31 | 39.7 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.861 | 8.9917 | 7.1906 | 8.6811 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA120H-375M | 375 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 350.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.82 | 60 | 2 | N | 11.36 | 42.1 | 10.84 | 34.6 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.1557 | 33.5325 | 8.6566 | 32.8303 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-375M | 375 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 349.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.95 | 48.3 | 9.37 | 40 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.873 | 9.0496 | 7.237 | 8.7371 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-375MB | 375 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 375 | 349.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 9.95 | 48.3 | 9.37 | 40 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.873 | 9.0496 | 7.237 | 8.7371 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-380M | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10 | 48.5 | 9.42 | 40.3 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.883 | 38.9221 | 7.2756 | 37.5778 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-380MB | 380 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 380 | 354.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10 | 48.5 | 9.42 | 40.3 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.883 | 38.9221 | 7.2756 | 37.5778 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-385M | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 359.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.06 | 48.7 | 9.49 | 40.6 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.897 | 39.2118 | 7.3297 | 37.8575 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-385MB | 385 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 385 | 359.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.06 | 48.7 | 9.49 | 40.6 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.897 | 39.2118 | 7.3297 | 37.8575 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-390M | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 363.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.12 | 49 | 9.55 | 40.8 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.909 | 39.405 | 7.376 | 38.044 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-390MB | 390 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 390 | 363.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.12 | 49 | 9.55 | 40.8 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.909 | 39.405 | 7.376 | 38.044 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-395M | 395 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 395 | 368.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.19 | 49.2 | 9.62 | 41.1 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.923 | 39.6947 | 7.4301 | 38.3237 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-395MB | 395 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 395 | 368.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.19 | 49.2 | 9.62 | 41.1 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.923 | 39.6947 | 7.4301 | 38.3237 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-400M | 400 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 400 | 373.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.26 | 49.5 | 9.69 | 41.3 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.937 | 39.8879 | 7.4841 | 38.5102 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-400MB | 400 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 400 | 373.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.26 | 49.5 | 9.69 | 41.3 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.937 | 39.8879 | 7.4841 | 38.5102 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-405M | 405 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 405 | 378.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.32 | 49.8 | 9.75 | 41.5 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.949 | 40.0811 | 7.5305 | 38.6967 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-405MB | 405 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 405 | 378.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.32 | 49.8 | 9.75 | 41.5 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.949 | 40.0811 | 7.5305 | 38.6967 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-410M | 410 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 410 | 383.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.38 | 50.1 | 9.82 | 41.8 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.963 | 40.3708 | 7.5845 | 38.9765 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-410MB | 410 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 410 | 383.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.01 | 72 | 2 | N | 10.38 | 50.1 | 9.82 | 41.8 | 43.1 | -0.3788 | 0.0454 | -0.3193 |  |  | 1.963 | 40.3708 | 7.5845 | 38.9765 | [6 empty] | 2021-03-11
PT IDN SOLAR TECH | NUSA144H-425M | 425 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 425 | 396.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.03 | 49.3 | 10.48 | 40.6 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.0703 | 39.3612 | 8.2803 | 39.0176 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-430M | 430 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 430 | 401.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.09 | 49.5 | 10.55 | 40.8 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.0841 | 39.5551 | 8.3356 | 39.2098 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-430MB | 430 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 430 | 401.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.09 | 49.5 | 10.55 | 40.8 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.0841 | 39.5551 | 8.3356 | 39.2098 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-435M | 435 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 435 | 406.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.16 | 49.7 | 10.61 | 41 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.096 | 39.749 | 8.383 | 39.402 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-435MB | 435 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 435 | 406.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.16 | 49.7 | 10.61 | 41 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.096 | 39.749 | 8.383 | 39.402 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-440M | 440 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 440 | 411.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.23 | 49.9 | 10.68 | 41.2 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.1098 | 39.9429 | 8.4383 | 39.5942 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-440MB | 440 W, 144 half-cut cell monocrystalline module, black backsheet, 1500V max system Vdc | UL 61730 | 440 | 411.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.23 | 49.9 | 10.68 | 41.2 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.1098 | 39.9429 | 8.4383 | 39.5942 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-445M | 445 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 445 | 415.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.29 | 50.1 | 10.75 | 41.4 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.1237 | 40.1368 | 8.4936 | 39.7864 | [6 empty] | 2021-05-03
PT IDN SOLAR TECH | NUSA144H-450M | 450 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 450 | 420.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.18 | 72 | 2 | N | 11.36 | 50.3 | 10.82 | 41.6 | 43.2 | -0.3754 | 0.0674 | -0.2815 |  |  | 2.1375 | 40.3307 | 8.5489 | 39.9786 | [6 empty] | 2021-05-03
Rare Manufacturing | IW-40-B12345YZZ | 40 W Mono c-Si BIPV roof panel | UL 1703 | 40 | 25.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 0.34064 | 16 | 1 | Y | 5.54 | 9.26 | 5 | 8 | 61.3 | -0.89834 | 0.18808 | -0.59911 | 0.19849 | -0.75377 | 0.99345 | 7.9215 | 4.6397 | 5.811 | BIPV | Flat Plate | 0.3048 | 1.1176 | 1 | 0.19674
REC Solar | REC205PE Q2 | 205 W Polycrystalline Module | UL 1703 | 205 | 181.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.1 | 35.5 | 7.45 | 27.55 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.3975 | 26.5854 | 5.8458 | 23.6523 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.18123
REC Solar | REC205PE Q3 | 205 W Polycrystalline Module | UL 1703 | 205 | 181.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.1 | 35.5 | 7.45 | 27.55 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.3975 | 26.5854 | 5.8458 | 23.6523 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.18123
REC Solar | REC210PE Q2 | 210 W Polycrystalline Module | UL 1703 | 210 | 186.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 35.9 | 7.55 | 27.85 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.4162 | 26.8749 | 5.9243 | 23.9098 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.18125
REC Solar | REC210PE Q3 | 210 W Polycrystalline Module | UL 1703 | 210 | 186.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 35.9 | 7.55 | 27.85 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.4162 | 26.8749 | 5.9243 | 23.9098 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.18125
REC Solar | REC215AE-US | 215 W Polycrystalline Module, High Performance | UL 1703 | 215 | 187.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.1 | 36.3 | 7.6 | 28.27 | 49 | -0.4975 | 0.127 | -0.363 | 0.0255 | -0.489 | 1.3818 | 32.6026 | 6.3169 | 25.4538 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.20954
REC Solar | REC215PE | 215 W Polycrystalline Module | UL 1703 | 215 | 190.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.1 | 36.3 | 7.6 | 28.3 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.524 | 27.6036 | 6.0266 | 25.3597 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19566
REC Solar | REC215PE-US | 215 W Polycrystalline Module | UL 1703 | 215 | 190.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.1 | 36.3 | 7.6 | 28.3 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.524 | 27.6036 | 6.0266 | 25.3597 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19566
REC Solar | REC215PE-US (BLK) | 215 W Polycrystalline Module | UL 1703 | 215 | 190.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.1 | 36.3 | 7.6 | 28.3 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.524 | 27.6036 | 6.0266 | 25.3597 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19566
REC Solar | REC220AE-US | 220 W Polycrystalline Module, High Performance | UL 1703 | 220 | 191.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 49 | -0.4975 | 0.127 | -0.363 | 0.0255 | -0.489 | 1.4 | 33.0985 | 6.4 | 25.841 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.21063
REC Solar | REC220AE-US (BLK) | 220 W Polycrystalline Module, High Performance | UL 1703 | 220 | 191.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 49 | -0.4975 | 0.127 | -0.363 | 0.0255 | -0.489 | 1.4 | 33.0985 | 6.4 | 25.841 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.21063
REC Solar | REC220PE | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC220PE (BLK) | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC220PE2 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC220PE2 BLK | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC220PE2 BLK Q2 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC220PE2 BLK Q3 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC220PE2 Q2 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC220PE2 Q3 | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC220PE-US | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC220PE-US (BLK) | 220 W Polycrystalline Module | UL 1703 | 220 | 195.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.6 | 7.7 | 28.7 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 27.9938 | 6.1059 | 25.7182 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19647
REC Solar | REC225AE-US | 225 W Polycrystalline Module, High Performance | UL 1703 | 225 | 196.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 49 | -0.4975 | 0.127 | -0.363 | 0.0255 | -0.489 | 1.4438 | 31.1179 | 6.3525 | 25.5953 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19967
REC Solar | REC225AE-US (BLK) | 225 W Polycrystalline Module, High Performance | UL 1703 | 225 | 196.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 49 | -0.4975 | 0.127 | -0.363 | 0.0255 | -0.489 | 1.4438 | 31.1179 | 6.3525 | 25.5953 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19967
REC Solar | REC225PE | 225 W Polycrystalline Module | UL 1703 | 225 | 199.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 28.3839 | 6.1059 | 26.0766 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19478
REC Solar | REC225PE (BLK) | 225 W Polycrystalline Module | UL 1703 | 225 | 199.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 28.3839 | 6.1059 | 26.0766 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19478
REC Solar | REC225PE2 | 225 W Polycrystalline Module | UL 1703 | 225 | 199.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 28.3839 | 6.1059 | 26.0766 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19478
REC Solar | REC225PE2 BLK | 225 W Polycrystalline Module | UL 1703 | 225 | 199.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 28.3839 | 6.1059 | 26.0766 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19478
REC Solar | REC225PE2 BLK Q2 | 225 W Polycrystalline Module | UL 1703 | 225 | 199.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 28.3839 | 6.1059 | 26.0766 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19478
REC Solar | REC225PE2 BLK Q3 | 225 W Polycrystalline Module | UL 1703 | 225 | 199.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 28.3839 | 6.1059 | 26.0766 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19478
REC Solar | REC225PE2 Q2 | 225 W Polycrystalline Module | UL 1703 | 225 | 199.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 28.3839 | 6.1059 | 26.0766 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19478
REC Solar | REC225PE-US | 225 W Polycrystalline Module | UL 1703 | 225 | 199.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.2 | 36.8 | 7.7 | 29.1 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.544 | 28.3839 | 6.1059 | 26.0766 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19478
REC Solar | REC230AE-US | 230 W Polycrystalline Module, High Performance | UL 1703 | 230 | 200.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.3 | 37.1 | 7.8 | 29.4 | 49 | -0.4975 | 0.127 | -0.363 | 0.0255 | -0.489 | 1.4625 | 31.4387 | 6.435 | 25.8591 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19991
REC Solar | REC230PE | 230 W Polycrystalline Module | UL 1703 | 230 | 204.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.3 | 37.1 | 7.8 | 29.4 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.5478 | 29.0399 | 6.1504 | 25.8988 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19542
REC Solar | REC230PE-US | 230 W Polycrystalline Module | UL 1703 | 230 | 204.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.3 | 37.1 | 7.8 | 29.4 | 47.9 | -0.457 | 0.011 | -0.318 | -0.0422 | -0.414 | 1.5478 | 29.0399 | 6.1504 | 25.8988 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.19542
REC Solar | REC235PE | 235 W Polycrystalline Module | UL 1703 | 235 | 213.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.51 | 36.7 | 7.96 | 29.6 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6308 | 28.7142 | 6.3777 | 26.1348 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19927
REC Solar | REC235PE ECO | 235 W Polycrystalline Module | UL 1703 | 235 | 210.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.66 | 36.6 | 8.06 | 29.5 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.6159 | 29.1847 | 6.4637 | 26.485 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20068
REC Solar | REC235PE Q2 | 235 W Polycrystalline Module | UL 1703 | 235 | 213.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.51 | 36.7 | 7.96 | 29.6 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6308 | 28.7142 | 6.3777 | 26.1348 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19927
REC Solar | REC235PE Q2 ECO | 235 W Polycrystalline Module | UL 1703 | 235 | 210.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.66 | 36.6 | 8.06 | 29.5 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.6159 | 29.1847 | 6.4637 | 26.485 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20068
REC Solar | REC235PE Q3 | 235 W Polycrystalline Module | UL 1703 | 235 | 213.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.51 | 36.7 | 7.96 | 29.6 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6308 | 28.7142 | 6.3777 | 26.1348 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19927
REC Solar | REC235PE Q3 ECO | 235 W Polycrystalline Module | UL 1703 | 235 | 210.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.66 | 36.6 | 8.06 | 29.5 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.6159 | 29.1847 | 6.4637 | 26.485 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20068
REC Solar | REC235PE(BLK) ECO | 235 W Polycrystalline Module | UL 1703 | 235 | 210.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.66 | 36.6 | 8.06 | 29.5 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.6159 | 29.1847 | 6.4637 | 26.485 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20068
REC Solar | REC235PE-US | 235 W Polycrystalline Module | UL 1703 | 235 | 213.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.51 | 36.7 | 7.96 | 29.6 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6308 | 28.7142 | 6.3777 | 26.1348 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19927
REC Solar | REC235PE-US ECO | 235 W Polycrystalline Module | UL 1703 | 235 | 210.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.66 | 36.6 | 8.06 | 29.5 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.6159 | 29.1847 | 6.4637 | 26.485 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20068
REC Solar | REC235PE-US(BLK) ECO | 235 W Polycrystalline Module | UL 1703 | 235 | 210.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.66 | 36.6 | 8.06 | 29.5 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.6159 | 29.1847 | 6.4637 | 26.485 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20068
REC Solar | REC240PE | 240 W Polycrystalline Module | UL 1703 | 240 | 218 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.6 | 37 | 8.04 | 29.9 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6472 | 29.0053 | 6.4418 | 26.3997 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19908
REC Solar | REC240PE ECO | 240 W Polycrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.75 | 36.8 | 8.17 | 29.7 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.638 | 29.3826 | 6.5519 | 26.6645 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20053
REC Solar | REC240PE Q2 | 240 W Polycrystalline Module | UL 1703 | 240 | 218 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.6 | 37 | 8.04 | 29.9 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6472 | 29.0053 | 6.4418 | 26.3997 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19908
REC Solar | REC240PE Q2 ECO | 240 W Polycrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.75 | 36.8 | 8.17 | 29.7 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.638 | 29.3826 | 6.5519 | 26.6645 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20053
REC Solar | REC240PE Q3 | 240 W Polycrystalline Module | UL 1703 | 240 | 218 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.6 | 37 | 8.04 | 29.9 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6472 | 29.0053 | 6.4418 | 26.3997 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19908
REC Solar | REC240PE Q3 ECO | 240 W Polycrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.75 | 36.8 | 8.17 | 29.7 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.638 | 29.3826 | 6.5519 | 26.6645 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20053
REC Solar | REC240PE(BLK) ECO | 240 W Polycrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.75 | 36.8 | 8.17 | 29.7 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.638 | 29.3826 | 6.5519 | 26.6645 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20053
REC Solar | REC240PE-US | 240 W Polycrystalline Module | UL 1703 | 240 | 218 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.6 | 37 | 8.04 | 29.9 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6472 | 29.0053 | 6.4418 | 26.3997 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19908
REC Solar | REC240PE-US ECO | 240 W Polycrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.75 | 36.8 | 8.17 | 29.7 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.638 | 29.3826 | 6.5519 | 26.6645 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20053
REC Solar | REC240PE-US(BLK) ECO | 240 W Polycrystalline Module | UL 1703 | 240 | 215.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.75 | 36.8 | 8.17 | 29.7 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.638 | 29.3826 | 6.5519 | 26.6645 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20053
REC Solar | REC245PE | 245 W Polycrystalline Module | UL 1703 | 245 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.68 | 37.2 | 8.12 | 30.2 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6636 | 29.2963 | 6.5059 | 26.6646 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19893
REC Solar | REC245PE ECO | 245 W Polycrystalline Module | UL 1703 | 245 | 220 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.8 | 37.1 | 8.23 | 30.1 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.65 | 29.7783 | 6.6 | 27.0236 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20055
REC Solar | REC245PE Q2 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.68 | 37.2 | 8.12 | 30.2 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6636 | 29.2963 | 6.5059 | 26.6646 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19893
REC Solar | REC245PE Q2 ECO | 245 W Polycrystalline Module | UL 1703 | 245 | 220 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.8 | 37.1 | 8.23 | 30.1 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.65 | 29.7783 | 6.6 | 27.0236 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20055
REC Solar | REC245PE Q3 | 245 W Polycrystalline Module | UL 1703 | 245 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.68 | 37.2 | 8.12 | 30.2 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6636 | 29.2963 | 6.5059 | 26.6646 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19893
REC Solar | REC245PE Q3 ECO | 245 W Polycrystalline Module | UL 1703 | 245 | 220 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.8 | 37.1 | 8.23 | 30.1 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.65 | 29.7783 | 6.6 | 27.0236 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20055
REC Solar | REC245PE(BLK) ECO | 245 W Polycrystalline Module | UL 1703 | 245 | 220 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.8 | 37.1 | 8.23 | 30.1 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.65 | 29.7783 | 6.6 | 27.0236 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20055
REC Solar | REC245PE-US | 245 W Polycrystalline Module | UL 1703 | 245 | 222.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.68 | 37.2 | 8.12 | 30.2 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.6636 | 29.2963 | 6.5059 | 26.6646 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19893
REC Solar | REC245PE-US ECO | 245 W Polycrystalline Module | UL 1703 | 245 | 220 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.8 | 37.1 | 8.23 | 30.1 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.65 | 29.7783 | 6.6 | 27.0236 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20055
REC Solar | REC245PE-US(BLK) ECO | 245 W Polycrystalline Module | UL 1703 | 245 | 220 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.8 | 37.1 | 8.23 | 30.1 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.65 | 29.7783 | 6.6 | 27.0236 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.20055
REC Solar | REC250PE | 250 W Polycrystalline Module | UL 1703 | 250 | 227.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.76 | 37.5 | 8.2 | 30.5 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.68 | 29.5873 | 6.57 | 26.9295 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19883
REC Solar | REC250PE BLK2 | 250 W Polycrystalline Module | UL 1703 | 250 | 228.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.86 | 37.4 | 8.3 | 30.2 | 45.7 | -0.4 | 0.05 | -0.31 | -0.002 | -0.4 | 1.63 | 29.05 | 6.65 | 27.76 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.18941
REC Solar | REC250PE ECO | 250 W Polycrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.86 | 37.4 | 8.3 | 30.2 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.664 | 29.8772 | 6.6561 | 27.1134 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19887
REC Solar | REC250PE Q2 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.76 | 37.5 | 8.2 | 30.5 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.68 | 29.5873 | 6.57 | 26.9295 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19883
REC Solar | REC250PE Q2 ECO | 250 W Polycrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.86 | 37.4 | 8.3 | 30.2 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.664 | 29.8772 | 6.6561 | 27.1134 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19887
REC Solar | REC250PE Q3 | 250 W Polycrystalline Module | UL 1703 | 250 | 227.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.76 | 37.5 | 8.2 | 30.5 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.68 | 29.5873 | 6.57 | 26.9295 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19883
REC Solar | REC250PE Q3 ECO | 250 W Polycrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.86 | 37.4 | 8.3 | 30.2 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.664 | 29.8772 | 6.6561 | 27.1134 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19887
REC Solar | REC250PE Z-LINK | 250 W Polycrystalline Module | UL 1703 | 250 | 227.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.86 | 37.4 | 8.3 | 30.2 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.7 | 28.4 | 6.63 | 26.79 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19312
REC Solar | REC250PE Z-Link-S | 250 W Polycrystalline Module | UL 1703 | 250 | 227.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.9 | 37.5 | 8.31 | 30.1 | 46.5 | -0.39592 | 0.04888 | -0.29741 | -0.00689 | -0.38988 | 1.6422 | 28.8499 | 6.648 | 27.3769 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18951
REC Solar | REC250PE(BLK) ECO | 250 W Polycrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.86 | 37.4 | 8.3 | 30.2 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.664 | 29.8772 | 6.6561 | 27.1134 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19887
REC Solar | REC250PE-US | 250 W Polycrystalline Module | UL 1703 | 250 | 227.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.76 | 37.5 | 8.2 | 30.5 | 45.5 | -0.425 | 0.0249 | -0.297 | -0.0235 | -0.388 | 1.68 | 29.5873 | 6.57 | 26.9295 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19883
REC Solar | REC250PE-US ECO | 250 W Polycrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.86 | 37.4 | 8.3 | 30.2 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.664 | 29.8772 | 6.6561 | 27.1134 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19887
REC Solar | REC250PE-US(BLK) ECO | 250 W Polycrystalline Module | UL 1703 | 250 | 224.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.86 | 37.4 | 8.3 | 30.2 | 46 | -0.465 | 0.047 | -0.344 | -0.0017 | -0.455 | 1.664 | 29.8772 | 6.6561 | 27.1134 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19887
REC Solar | REC255PE | 255 W Polycrystalline Module | UL 1703 | 255 | 229.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.95 | 37.6 | 8.42 | 30.5 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.6881 | 29.9133 | 6.6701 | 27.4753 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19803
REC Solar | REC255PE BLK2 | 255 W Polycrystalline Module | UL 1703 | 255 | 233 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 8.95 | 37.6 | 8.42 | 30.5 | 45.7 | -0.4 | 0.05 | -0.31 | -0.002 | -0.4 | 1.65 | 29.33 | 6.75 | 28.04 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.18978
REC Solar | REC255PE Q2 | 255 W Polycrystalline Module | UL 1703 | 255 | 229.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.95 | 37.6 | 8.42 | 30.5 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.6881 | 29.9133 | 6.6701 | 27.4753 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19803
REC Solar | REC255PE Q3 | 255 W Polycrystalline Module | UL 1703 | 255 | 229.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.95 | 37.6 | 8.42 | 30.5 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.6881 | 29.9133 | 6.6701 | 27.4753 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19803
REC Solar | REC255PE Z-LINK | 255 W Polycrystalline Module | UL 1703 | 255 | 231.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.95 | 37.6 | 8.42 | 30.5 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.72 | 28.68 | 6.73 | 27.05 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19345
REC Solar | REC255PE Z-Link-S | 255 W Polycrystalline Module | UL 1703 | 255 | 232.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 8.93 | 37.8 | 8.42 | 30.3 | 46.5 | -0.39592 | 0.04888 | -0.29741 | -0.00689 | -0.38988 | 1.664 | 29.0416 | 6.736 | 27.5588 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18951
REC Solar | REC255PE(BLK) | 255 W Polycrystalline Module | UL 1703 | 255 | 229.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.95 | 37.6 | 8.42 | 30.5 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.6881 | 29.9133 | 6.6701 | 27.4753 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19803
REC Solar | REC255PE-US | 255 W Polycrystalline Module | UL 1703 | 255 | 229.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.95 | 37.6 | 8.42 | 30.5 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.6881 | 29.9133 | 6.6701 | 27.4753 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19803
REC Solar | REC255PE-US(BLK) | 255 W Polycrystalline Module | UL 1703 | 255 | 229.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 8.95 | 37.6 | 8.42 | 30.5 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.6881 | 29.9133 | 6.6701 | 27.4753 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19803
REC Solar | REC260PE | 260 W Polycrystalline Module | UL 1703 | 260 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.01 | 37.8 | 8.5 | 30.7 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.7042 | 30.1094 | 6.7335 | 27.6555 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19735
REC Solar | REC260PE BLK2 | 260 W Polycrystalline Module | UL 1703 | 260 | 237.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.65 | 60 | 1 | N | 9.01 | 37.8 | 8.5 | 30.7 | 45.7 | -0.4 | 0.05 | -0.31 | -0.002 | -0.4 | 1.67 | 29.53 | 6.81 | 28.22 | Rack | Flat Plate | 0.991 | 1.665 | 1 | 0.18967
REC Solar | REC260PE Q2 | 260 W Polycrystalline Module | UL 1703 | 260 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.01 | 37.8 | 8.5 | 30.7 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.7042 | 30.1094 | 6.7335 | 27.6555 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19735
REC Solar | REC260PE Q3 | 260 W Polycrystalline Module | UL 1703 | 260 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.01 | 37.8 | 8.5 | 30.7 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.7042 | 30.1094 | 6.7335 | 27.6555 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19735
REC Solar | REC260PE Z-LINK | 260 W Polycrystalline Module | UL 1703 | 260 | 236.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.01 | 37.8 | 8.5 | 30.7 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.74 | 28.87 | 6.79 | 27.23 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19321
REC Solar | REC260PE Z-Link-S | 260 W Polycrystalline Module | UL 1703 | 260 | 237.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.04 | 38 | 8.47 | 30.7 | 46.5 | -0.39592 | 0.04888 | -0.29741 | -0.00689 | -0.38988 | 1.6738 | 29.425 | 6.776 | 27.9226 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18943
REC Solar | REC260PE(BLK) | 260 W Polycrystalline Module | UL 1703 | 260 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.01 | 37.8 | 8.5 | 30.7 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.7042 | 30.1094 | 6.7335 | 27.6555 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19735
REC Solar | REC260PE-US | 260 W Polycrystalline Module | UL 1703 | 260 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.01 | 37.8 | 8.5 | 30.7 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.7042 | 30.1094 | 6.7335 | 27.6555 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19735
REC Solar | REC260PE-US(BLK) | 260 W Polycrystalline Module | UL 1703 | 260 | 234.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.01 | 37.8 | 8.5 | 30.7 | 46.5 | -0.4469 | 0.0358 | -0.3369 | -0.0168 | -0.4388 | 1.7042 | 30.1094 | 6.7335 | 27.6555 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19735
REC Solar | REC260TP | 260 W Polycrystalline Module | UL 1703 | 260 | 238.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 2 | N | 9.13 | 38 | 8.45 | 30.8 | 45.05 | -0.4 | 0.05 | -0.03 | -0.01 | 0.039 | 1.6702 | 29.0116 | 6.76 | 28.2478 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.18637
REC Solar | REC265PE | 265 W Polycrystalline Module | UL 1703 | 265 | 241.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.08 | 38.1 | 8.58 | 30.9 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.76 | 30.08 | 6.86 | 27.41 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19978
REC Solar | REC265PE Q2 | 265 W Polycrystalline Module | UL 1703 | 265 | 241.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.08 | 38.1 | 8.58 | 30.9 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.76 | 30.08 | 6.86 | 27.41 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19978
REC Solar | REC265PE Q3 | 265 W Polycrystalline Module | UL 1703 | 265 | 241.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.08 | 38.1 | 8.58 | 30.9 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.76 | 30.08 | 6.86 | 27.41 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19978
REC Solar | REC265PE Z-LINK | 265 W Polycrystalline Module | UL 1703 | 265 | 241.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.08 | 38.1 | 8.58 | 30.9 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.76 | 29.06 | 6.86 | 27.41 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.193
REC Solar | REC265PE Z-Link-S | 265 W Polycrystalline Module | UL 1703 | 265 | 241.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.09 | 38.2 | 8.55 | 31 | 46.5 | -0.39592 | 0.04888 | -0.29741 | -0.00689 | -0.38988 | 1.6896 | 29.7125 | 6.84 | 28.1954 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18945
REC Solar | REC265PE-US | 265 W Polycrystalline Module | UL 1703 | 265 | 241.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.08 | 38.1 | 8.58 | 30.9 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.76 | 30.08 | 6.86 | 27.41 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19978
REC Solar | REC265TP | 265 W Polycrystalline Module | UL 1703 | 265 | 245 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.21 | 38.3 | 8.53 | 31.1 | 44.4 | -0.38 | 0.04 | -0.29 | -0.01 | -0.37 | 1.68 | 29.51 | 6.82 | 28.72 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.18708
REC Solar | REC270PE | 270 W Polycrystalline Module | UL 1703 | 270 | 246 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.18 | 38.4 | 8.66 | 31.3 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.77 | 30.46 | 6.92 | 27.76 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19968
REC Solar | REC270PE Q2 | 270 W Polycrystalline Module | UL 1703 | 270 | 246 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.18 | 38.4 | 8.66 | 31.3 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.77 | 30.46 | 6.92 | 27.76 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19968
REC Solar | REC270PE Q3 | 270 W Polycrystalline Module | UL 1703 | 270 | 246 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.18 | 38.4 | 8.66 | 31.3 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.77 | 30.46 | 6.92 | 27.76 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19968
REC Solar | REC270PE Z-LINK | 270 W Polycrystalline Module | UL 1703 | 270 | 246 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.18 | 38.4 | 8.66 | 31.3 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.77 | 29.43 | 6.92 | 27.76 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19293
REC Solar | REC270PE Z-Link-S | 270 W Polycrystalline Module | UL 1703 | 270 | 246.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.6269 | 60 | 1 | N | 9.15 | 38.4 | 8.63 | 31.3 | 46.5 | -0.39592 | 0.04888 | -0.29741 | -0.00689 | -0.38988 | 1.7055 | 30 | 6.904 | 28.4683 | Rack | Flat Plate | 0.992 | 1.64 | 1 | 0.18949
REC Solar | REC270PE-US | 270 W Polycrystalline Module | UL 1703 | 270 | 246 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.18 | 38.4 | 8.66 | 31.3 | 44.6 | -0.4464 | 0.0389 | -0.3422 | -0.0139 | -0.4482 | 1.77 | 30.46 | 6.92 | 27.76 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.19968
REC Solar | REC270TP | 270 W Polycrystalline Module | UL 1703 | 270 | 249.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.29 | 38.6 | 8.66 | 31.2 | 44.3 | -0.37924 | 0.040874 | -0.28721 | -0.009732 | -0.37041 | 1.7083 | 29.6058 | 6.9221 | 28.8135 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.18732
REC Solar | REC270TP2 | 270 W Polycrystalline Module | UL 1703 | 270 | 248.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 2 | N | 9.29 | 38.6 | 8.66 | 31.2 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.7083 | 29.6058 | 6.9221 | 28.8135 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18732
REC Solar | REC270TP2 BLK | 270 W Polycrystalline Module | UL 1703 | 270 | 248.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 2 | N | 9.29 | 38.6 | 8.66 | 31.2 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.7083 | 29.6058 | 6.9221 | 28.8135 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18732
REC Solar | REC270TP2 BLK2 | 270 W Polycrystalline Module | UL 1703 | 270 | 243.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 2 | N | 9.18 | 38 | 8.61 | 31.4 | 46.88 | -0.442 | 0.055 | -0.34 | -0.007 | -0.436 | 1.6965 | 29.5454 | 6.8939 | 28.4603 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18564
REC Solar | REC270TP2M BLK2 | 270 W Monocrystalline Module | UL 1703 | 270 | 245.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 2 | N | 9.02 | 38.2 | 8.5 | 31.8 | 47.31 | -0.394 | 0.05 | -0.309 | -0.001 | -0.393 | 1.6766 | 29.9247 | 6.8624 | 28.5582 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18582
REC Solar | REC275PE Z-Link-M | 275 W Monocrystalline Module | UL 1703 | 275 | 250.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6467 | 60 | 1 | N | 9.29 | 38 | 8.79 | 31.3 | 46.52 | -0.405 | 0.047 | -0.301 | -0.004 | -0.402 | 1.7302 | 30.2303 | 7.0668 | 28.4519 | Rack | Flat Plate | 0.992 | 1.66 | 1 | 0.19019
REC Solar | REC275TP | 275 W Polycrystalline Module | UL 1703 | 275 | 254.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.4 | 38.8 | 8.76 | 31.4 | 44.3 | -0.37924 | 0.040874 | -0.28721 | -0.009732 | -0.37041 | 1.728 | 29.7955 | 7.002 | 28.9982 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.18723
REC Solar | REC275TP2 | 275 W, 120 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 275 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.52 | 38.2 | 8.74 | 31.5 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.7247 | 29.565 | 7.0255 | 28.667 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18542 |  | 2019-04-02
REC Solar | REC275TP2 BLK | 275 W, 120 half cut cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 275 | 253.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.52 | 38.2 | 8.74 | 31.5 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.7094 | 29.7238 | 6.963 | 28.821 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18476 |  | 2019-05-01
REC Solar | REC275TP2 BLK2 | 275 W Polycrystalline Module | UL 1703 | 275 | 247.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 2 | N | 9.28 | 38.2 | 8.71 | 31.6 | 46.88 | -0.442 | 0.055 | -0.34 | -0.007 | -0.436 | 1.7162 | 29.7336 | 6.974 | 28.6415 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18556
REC Solar | REC275TP2M BLK2 | 275 W Monocrystalline Module | UL 1703 | 275 | 250.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 2 | N | 9.11 | 38.4 | 8.6 | 32 | 47.31 | -0.394 | 0.05 | -0.309 | -0.001 | -0.393 | 1.6963 | 30.1129 | 6.9431 | 28.7378 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18575
REC Solar | REC280PE Z-Link-M | 280 W Monocrystalline Module | UL 1703 | 280 | 255.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6467 | 60 | 1 | N | 9.34 | 38.3 | 8.84 | 31.7 | 46.52 | -0.405 | 0.047 | -0.301 | -0.004 | -0.402 | 1.74 | 30.6167 | 7.107 | 28.8155 | Rack | Flat Plate | 0.992 | 1.66 | 1 | 0.19026
REC Solar | REC280TP | 280 W Polycrystalline Module | UL 1703 | 280 | 259.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.44 | 39.2 | 8.78 | 31.9 | 44.3 | -0.37924 | 0.040874 | -0.28721 | -0.009732 | -0.37041 | 1.732 | 30.27 | 7.018 | 29.46 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.18724
REC Solar | REC280TP2 | 280 W, 120 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 280 | 258.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.61 | 38.4 | 8.84 | 31.7 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.7287 | 30.0358 | 7.0416 | 29.1235 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18543 |  | 2019-04-02
REC Solar | REC280TP2 BLK | 280 W, 120 half cut cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 280 | 258.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.61 | 38.4 | 8.84 | 31.7 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.7289 | 29.9126 | 7.0427 | 29.004 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.1847 |  | 2019-05-01
REC Solar | REC280TP2 BLK2 | 280 W Polycrystalline Module | UL 1703 | 280 | 252.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 2 | N | 9.39 | 38.4 | 8.82 | 31.8 | 46.88 | -0.442 | 0.055 | -0.34 | -0.007 | -0.436 | 1.7379 | 29.9218 | 7.062 | 28.8228 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18572
REC Solar | REC280TP2M BLK2 | 280 W Monocrystalline Module | UL 1703 | 280 | 254.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 2 | N | 9.2 | 38.6 | 8.71 | 32.2 | 47.31 | -0.394 | 0.05 | -0.309 | -0.001 | -0.393 | 1.718 | 30.3011 | 7.0319 | 28.9174 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18592
REC Solar | REC285PE Z-Link-M | 285 W Monocrystalline Module | UL 1703 | 285 | 259.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6467 | 60 | 1 | N | 9.39 | 38.6 | 8.88 | 32.1 | 46.52 | -0.405 | 0.047 | -0.301 | -0.004 | -0.402 | 1.7479 | 31.003 | 7.1392 | 29.1791 | Rack | Flat Plate | 0.992 | 1.66 | 1 | 0.19014
REC Solar | REC285PE72 | 285 W Polycrystalline Module | UL 1703 | 285 | 260.3 | Formerly REC Solar REC285PE | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8808 | 72 | 1 | N | 8.66 | 43.9 | 8.06 | 35.4 | 46.6 | -0.383 | 0.013 | -0.274 | 0.035 | -0.353 | 1.63 | 34.39 | 6.37 | 32.08 | Rack | Flat Plate | 0.968 | 1.943 | 1 | 0.19669 |  | 2018-04-02
REC Solar | REC285PE72 Q2 | 285 W Polycrystalline Module | UL 1703 | 285 | 260.3 | Formerly REC Solar REC285PE Q2 | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8808 | 72 | 1 | N | 8.66 | 43.9 | 8.06 | 35.4 | 46.6 | -0.383 | 0.013 | -0.274 | 0.035 | -0.353 | 1.63 | 34.39 | 6.37 | 32.08 | Rack | Flat Plate | 0.968 | 1.943 | 1 | 0.19669 |  | 2018-04-02
REC Solar | REC285PE72 Q3 | 285 W Polycrystalline Module | UL 1703 | 285 | 260.3 | Formerly REC Solar REC285PE Q3 | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8808 | 72 | 1 | N | 8.66 | 43.9 | 8.06 | 35.4 | 46.6 | -0.383 | 0.013 | -0.274 | 0.035 | -0.353 | 1.63 | 34.39 | 6.37 | 32.08 | Rack | Flat Plate | 0.968 | 1.943 | 1 | 0.19669 |  | 2018-04-02
REC Solar | REC285TP | 285 W Polycrystalline Module | UL 1703 | 285 | 264.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.54 | 39.5 | 8.9 | 32.1 | 44.3 | -0.37924 | 0.040874 | -0.28721 | -0.009732 | -0.37041 | 1.7547 | 30.4598 | 7.1099 | 29.6447 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.18753
REC Solar | REC285TP2 | 285 W, 120 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 285 | 263.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.66 | 38.6 | 8.95 | 31.9 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.7523 | 30.2241 | 7.1378 | 29.3061 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18583 |  | 2019-04-02
REC Solar | REC285TP2 BLK | 285 W, 120 half cut cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 285 | 263.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.66 | 38.6 | 8.95 | 31.9 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.7504 | 30.1013 | 7.1303 | 29.187 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18488 |  | 2019-05-01
REC Solar | REC285TP2 BLK2 | 285 W Polycrystalline Module | UL 1703 | 285 | 257 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 2 | N | 9.4 | 38.6 | 8.92 | 32 | 46.88 | -0.442 | 0.055 | -0.34 | -0.007 | -0.436 | 1.7576 | 30.11 | 7.1421 | 29.0041 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18569
REC Solar | REC285TP2M BLK2 | 285 W Monocrystalline Module | UL 1703 | 285 | 259.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 2 | N | 9.32 | 38.8 | 8.81 | 32.4 | 47.31 | -0.394 | 0.05 | -0.309 | -0.001 | -0.393 | 1.7378 | 30.4893 | 7.1127 | 29.097 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.1859
REC Solar | REC290PE Z-Link-M | 290 W Monocrystalline Module | UL 1703 | 290 | 264.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.6467 | 60 | 1 | N | 9.45 | 39 | 8.93 | 32.5 | 46.52 | -0.405 | 0.047 | -0.301 | -0.004 | -0.402 | 1.7577 | 31.3893 | 7.1794 | 29.5427 | Rack | Flat Plate | 0.992 | 1.66 | 1 | 0.19025
REC Solar | REC290PE72 | 290 W Polycrystalline Module | UL 1703 | 290 | 264.9 | Formerly REC Solar REC290PE | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8808 | 72 | 1 | N | 8.75 | 44.2 | 8.17 | 35.6 | 46.6 | -0.383 | 0.013 | -0.274 | 0.035 | -0.353 | 1.66 | 34.59 | 6.46 | 32.26 | Rack | Flat Plate | 0.968 | 1.943 | 1 | 0.198 |  | 2018-04-02
REC Solar | REC290PE72 Q2 | 290 W Polycrystalline Module | UL 1703 | 290 | 264.9 | Formerly REC Solar REC290PE Q2 | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8808 | 72 | 1 | N | 8.75 | 44.2 | 8.17 | 35.6 | 46.6 | -0.383 | 0.013 | -0.274 | 0.035 | -0.353 | 1.66 | 34.59 | 6.46 | 32.26 | Rack | Flat Plate | 0.968 | 1.943 | 1 | 0.198 |  | 2018-04-02
REC Solar | REC290PE72 Q3 | 290 W Polycrystalline Module | UL 1703 | 290 | 264.9 | Formerly REC Solar REC290PE Q3 | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.8808 | 72 | 1 | N | 8.75 | 44.2 | 8.17 | 35.6 | 46.6 | -0.383 | 0.013 | -0.274 | 0.035 | -0.353 | 1.66 | 34.59 | 6.46 | 32.26 | Rack | Flat Plate | 0.968 | 1.943 | 1 | 0.198 |  | 2018-04-02
REC Solar | REC290TP | 290 W Polycrystalline Module | UL 1703 | 290 | 268.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.5868 | 60 | 1 | N | 9.62 | 39.7 | 8.98 | 32.3 | 44.3 | -0.37924 | 0.040874 | -0.28721 | -0.009732 | -0.37041 | 1.7714 | 30.6496 | 7.1779 | 29.8294 | Rack | Flat Plate | 0.967 | 1.641 | 1 | 0.18722
REC Solar | REC290TP2 | 290 W, 120 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 290 | 267.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.71 | 38.8 | 9.05 | 32.1 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.768 | 30.4124 | 7.202 | 29.4887 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18541 |  | 2019-04-02
REC Solar | REC290TP2 BLK | 290 W, 120 half cut cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 290 | 267.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.71 | 38.8 | 9.05 | 32.1 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.77 | 30.29 | 7.21 | 29.37 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18487 |  | 2019-05-01
REC Solar | REC290TP2 BLK2 | 290 W Polycrystalline Module | UL 1703 | 290 | 261.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.67 | 60 | 2 | N | 9.51 | 38.8 | 9.02 | 32.2 | 46.88 | -0.442 | 0.055 | -0.34 | -0.007 | -0.436 | 1.7773 | 30.2981 | 7.2222 | 29.1854 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18568
REC Solar | REC290TP2M | 290 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 290 | 266.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.45 | 39 | 8.9 | 32.6 | 45.68 | -0.395 | 0.039 | -0.291 | -0.024 | -0.375 | 1.7761 | 30.4267 | 7.153 | 29.3204 | [6 empty] | 2018-09-04 | 2019-05-01
REC Solar | REC290TP2M BLK2 | 290 W Monocrystalline Module | UL 1703 | 290 | 264.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.67 | 60 | 2 | N | 9.45 | 39 | 8.9 | 32.6 | 47.31 | -0.394 | 0.05 | -0.309 | -0.001 | -0.393 | 1.7555 | 30.6775 | 7.1853 | 29.2766 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18571
REC Solar | REC295NP | 295 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 295 | 275.3 |  | 2018-12-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.76 | 39.4 | 9.04 | 32.7 | 44.11 | -0.351 | 0.04 | -0.266 | 1.7767 | 31.1399 | 1.7767 | 31.1399 | 7.1938 | 30.3263 | [6 empty] | 2018-09-04 | 2019-04-02
REC Solar | REC295PE72 | 295 W Polycrystalline Module | UL 1703 | 295 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.71 | 44.5 | 8.18 | 36.1 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6103 | 34.5744 | 6.5598 | 32.7184 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18873 |  | 2018-04-02
REC Solar | REC295PE72 Q2 | 295 W Polycrystalline Module | UL 1703 | 295 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.71 | 44.5 | 8.18 | 36.1 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6103 | 34.5744 | 6.5598 | 32.7184 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18873 |  | 2018-04-02
REC Solar | REC295PE72 Q3 | 295 W Polycrystalline Module | UL 1703 | 295 | 267.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.71 | 44.5 | 8.18 | 36.1 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6103 | 34.5744 | 6.5598 | 32.7184 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18873 |  | 2018-04-02
REC Solar | REC295TP2 | 295 W, 120 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 295 | 272.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.76 | 39 | 9.14 | 32.3 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.7936 | 30.5066 | 7.3062 | 29.58 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18548 |  | 2019-04-02
REC Solar | REC295TP2 BLK | 295 W, 120 half cut cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 295 | 272.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.76 | 39 | 9.14 | 32.3 | 45.38 | -0.373 | 0.043 | -0.288 |  |  | 1.7876 | 30.4787 | 7.2817 | 29.553 | [6 empty] | 2019-05-01
REC Solar | REC295TP2M | 295 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 295 | 271 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.58 | 39.2 | 9 | 32.8 | 45.68 | -0.395 | 0.039 | -0.291 | -0.024 | -0.375 | 1.7961 | 30.6133 | 7.2334 | 29.5003 | [6 empty] | 2018-09-04 | 2019-05-01
REC Solar | REC300NP | 300 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 300 | 280.1 |  | 2018-12-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.85 | 39.6 | 9.1 | 33 | 44.11 | -0.351 | 0.04 | -0.266 | 1.7885 | 31.4256 | 1.7885 | 31.4256 | 7.2416 | 30.6046 | [6 empty] | 2018-09-04 | 2019-04-02
REC Solar | REC300PE72 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.76 | 44.9 | 8.22 | 36.5 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6182 | 34.9575 | 6.5919 | 33.0809 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18856 |  | 2018-04-02
REC Solar | REC300PE72 Q2 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.76 | 44.9 | 8.22 | 36.5 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6182 | 34.9575 | 6.5919 | 33.0809 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18856 |  | 2018-04-02
REC Solar | REC300PE72 Q3 | 300 W Polycrystalline Module | UL 1703 | 300 | 272.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.76 | 44.9 | 8.22 | 36.5 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6182 | 34.9575 | 6.5919 | 33.0809 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18856 |  | 2018-04-02
REC Solar | REC300TP2 | 300 W, 120 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 300 | 277.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.82 | 39.2 | 9.24 | 32.5 | 45.38 | -0.373 | 0.043 | -0.288 | -0.006 | -0.368 | 1.8133 | 30.6949 | 7.3864 | 29.7626 | Rack | Flat Plate | 0.997 | 1.675 | 1 | 0.18553 |  | 2019-04-02
REC Solar | REC300TP2 BLK | 300 W, 120 half cut cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 300 | 277.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.62 | 60 | 2 | N | 9.82 | 39.2 | 9.24 | 32.5 | 45.38 | -0.373 | 0.043 | -0.288 |  |  | 1.8072 | 30.6674 | 7.3614 | 29.736 | [6 empty] | 2019-05-01
REC Solar | REC300TP2M | 300 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 300 | 275.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.7 | 39.5 | 9.1 | 33 | 45.68 | -0.395 | 0.039 | -0.291 | -0.024 | -0.375 | 1.816 | 30.8 | 7.3137 | 29.6802 | [6 empty] | 2018-09-04 | 2019-05-01
REC Solar | REC305NP | 305 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 305 | 284.8 |  | 2018-12-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.93 | 39.9 | 9.17 | 33.3 | 44.11 | -0.351 | 0.04 | -0.266 | 1.8022 | 31.7113 | 1.8022 | 31.7113 | 7.2973 | 30.8828 | [6 empty] | 2018-09-04 | 2019-04-02
REC Solar | REC305NP Black | 305 W, 120 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 305 | 284.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.06 | 39.3 | 9.17 | 33.3 | 44.45 | -0.352 | 0.036 | -0.267 |  |  | 1.8015 | 31.9876 | 7.2749 | 30.7421 | [6 empty] | 2019-05-01 | 2021-09-13
REC Solar | REC305PE72 | 305 W Polycrystalline Module | UL 1703 | 305 | 276.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.82 | 45.2 | 8.27 | 36.9 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.628 | 35.3406 | 6.632 | 33.4434 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18864 |  | 2018-04-02
REC Solar | REC305PE72 Q2 | 305 W Polycrystalline Module | UL 1703 | 305 | 276.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.82 | 45.2 | 8.27 | 36.9 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.628 | 35.3406 | 6.632 | 33.4434 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18864 |  | 2018-04-02
REC Solar | REC305PE72 Q3 | 305 W Polycrystalline Module | UL 1703 | 305 | 276.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.82 | 45.2 | 8.27 | 36.9 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.628 | 35.3406 | 6.632 | 33.4434 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18864 |  | 2018-04-02
REC Solar | REC305TP2M | 305 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 305 | 280.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.8 | 39.7 | 9.17 | 33.3 | 45.68 | -0.395 | 0.039 | -0.291 | -0.024 | -0.375 | 1.83 | 31.08 | 7.37 | 29.95 | [6 empty] | 2018-09-04 | 2019-05-01
REC Solar | REC310NP | 310 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 310 | 289.6 |  | 2018-12-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.01 | 40.2 | 9.24 | 33.6 | 44.11 | -0.351 | 0.04 | -0.266 | 1.816 | 31.997 | 1.816 | 31.997 | 7.353 | 31.161 | [6 empty] | 2018-09-04 | 2019-04-02
REC Solar | REC310NP Black | 310 W, 120 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 310 | 289.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.12 | 39.7 | 9.24 | 33.6 | 44.45 | -0.352 | 0.036 | -0.267 |  |  | 1.8152 | 32.2758 | 7.3305 | 31.019 | [6 empty] | 2019-05-01 | 2021-09-13
REC Solar | REC310PE72 | 310 W Polycrystalline Module | UL 1703 | 310 | 281.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.88 | 45.5 | 8.34 | 37.2 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6418 | 35.6279 | 6.6881 | 33.7153 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18869 |  | 2018-04-02
REC Solar | REC310PE72 Q2 | 310 W Polycrystalline Module | UL 1703 | 310 | 281.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.88 | 45.5 | 8.34 | 37.2 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6418 | 35.6279 | 6.6881 | 33.7153 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18869 |  | 2018-04-02
REC Solar | REC310PE72 Q3 | 310 W Polycrystalline Module | UL 1703 | 310 | 281.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.88 | 45.5 | 8.34 | 37.2 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6418 | 35.6279 | 6.6881 | 33.7153 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18869 |  | 2018-04-02
REC Solar | REC310PE72XV | 310 W Polycrystalline Module | UL 1703 | 310 | 281.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 9.02 | 45.3 | 8.53 | 36.7 | 46.2 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.68 | 35.15 | 6.84 | 33.26 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.19049 |  | 2018-04-02
REC Solar | REC310TP2M | 310 W, 120 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 310 | 285.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 9.9 | 39.8 | 9.26 | 33.5 | 45.68 | -0.395 | 0.039 | -0.291 | -0.024 | -0.375 | 1.848 | 31.2667 | 7.4423 | 30.1299 | [6 empty] | 2018-09-04 | 2019-05-01
REC Solar | REC315NP | 315 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 315 | 294.4 |  | 2018-12-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.09 | 40.5 | 9.31 | 33.9 | 44.11 | -0.351 | 0.04 | -0.266 | 1.8298 | 32.2827 | 1.8298 | 32.2827 | 7.4087 | 31.4392 | [6 empty] | 2018-09-04 | 2019-04-02
REC Solar | REC315NP Black | 315 W, 120 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 315 | 294 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.09 | 40.5 | 9.31 | 33.9 | 44.45 | -0.352 | 0.036 | -0.267 |  |  | 1.829 | 32.564 | 7.386 | 31.296 | [6 empty] | 2019-05-01 | 2020-04-21
REC Solar | REC315PE72 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.93 | 45.8 | 8.4 | 37.5 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6536 | 35.9152 | 6.7362 | 33.9872 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18854 |  | 2018-04-02
REC Solar | REC315PE72 Q2 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.93 | 45.8 | 8.4 | 37.5 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6536 | 35.9152 | 6.7362 | 33.9872 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18854 |  | 2018-04-02
REC Solar | REC315PE72 Q3 | 315 W Polycrystalline Module | UL 1703 | 315 | 286.1 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.9503 | 72 | 1 | N | 8.93 | 45.8 | 8.4 | 37.5 | 46.18 | -0.42 | 0.06 | -0.32 | -0.001 | -0.42 | 1.6536 | 35.9152 | 6.7362 | 33.9872 | Rack | Flat Plate | 0.991 | 1.968 | 1 | 0.18854 |  | 2018-04-02
REC Solar | REC315TP2M | 315 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 315 | 292.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.05 | 39.9 | 9.36 | 33.7 | 44.57 | -0.37 | 0.04 | -0.286 | -0.024 | -0.375 | 1.852 | 31.597 | 7.473 | 30.574 | [6 empty] | 2018-09-04 | 2019-08-01
REC Solar | REC315TP2SB 72 XV | 315 W, 144 Half-Cell Polycrystalline Module | UL 1703 | 315 | 290.8 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.93 | 144 |  | N | 9 | 45.8 | 8.5 | 37.1 | 44.15 | -0.389 | 0.06 | -0.306 | 0.013 | -0.401 | 1.682 | 35.7 | 6.904 | 34.518 | [6 empty] | 2018-01-02 | 2018-02-01
REC Solar | REC315TP3M | 315 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 315 | 294.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.29 | 38.7 | 9.38 | 33.6 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8068 | 32.2168 | 1.8068 | 32.2168 | 7.3967 | 31.2108 | [6 empty] | 2020-09-11
REC Solar | REC315TP3M Black | 315 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 315 | 294.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.29 | 38.7 | 9.38 | 33.6 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8068 |  | 1.8068 | 32.2168 | 7.3967 | 31.2108 | [6 empty] | 2020-09-11
REC Solar | REC320NP | 320 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 320 | 299.2 |  | 2018-12-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.18 | 40.8 | 9.37 | 34.2 | 44.11 | -0.351 | 0.04 | -0.266 | 1.8415 | 32.5684 | 1.8415 | 32.5684 | 7.4565 | 31.7174 | [6 empty] | 2018-09-04 | 2019-04-02
REC Solar | REC320NP Black | 320 W, 120 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 1703 | 320 | 298.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.18 | 40.8 | 9.37 | 34.2 | 44.45 | -0.352 | 0.036 | -0.267 |  |  | 1.8408 | 32.8522 | 7.4336 | 31.573 | [6 empty] | 2019-05-01
REC Solar | REC320PEM 72 | 320 W Monocrystalline Module | UL 1703 | 320 | 288.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.27 | 45.4 | 8.58 | 37.3 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.7092 | 36.1128 | 6.8503 | 33.9171 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19288
REC Solar | REC320TP2M | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 320 | 297.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.1 | 40 | 9.45 | 33.9 | 44.57 | -0.37 | 0.04 | -0.286 | -0.024 | -0.375 | 1.8698 | 31.7845 | 7.5449 | 30.7554 | [6 empty] | 2018-09-04 | 2019-08-01
REC Solar | REC320TP2M BLK | 320 W, 120 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730, UL 1703 | 320 | 297.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.1 | 40 | 9.45 | 33.9 | 44.57 | -0.37 | 0.04 | -0.286 |  |  | 1.8698 | 31.7845 | 7.5449 | 30.7554 | [6 empty] | 2019-08-01
REC Solar | REC320TP2SB 72 XV | 320 W, 144 Half-Cell Polycrystalline Module | UL 1703 | 320 | 295.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.933 | 144 |  | N | 9.09 | 46.1 | 8.56 | 37.4 | 44.15 | -0.389 | 0.06 | -0.306 | 0.013 | -0.401 | 1.682 | 35.7 | 6.904 | 34.518 | [6 empty] | 2018-01-02 | 2018-02-01
REC Solar | REC320TP3M | 320 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 320 | 299.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.32 | 39.1 | 9.46 | 33.8 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8222 | 32.4086 | 1.8222 | 32.4086 | 7.4598 | 31.3966 | [6 empty] | 2020-09-11
REC Solar | REC320TP3M Black | 320 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 320 | 299.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.32 | 39.1 | 9.46 | 33.8 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8222 |  | 1.8222 | 32.4086 | 7.4598 | 31.3966 | [6 empty] | 2020-09-11
REC Solar | REC325NP | 325 W, 120 half cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 325 | 304 |  | 2018-12-20 | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.27 | 41 | 9.46 | 34.4 | 44.11 | -0.351 | 0.04 | -0.266 | 1.8592 | 32.7588 | 1.8592 | 32.7588 | 7.5281 | 31.9029 | [6 empty] | 2018-09-04 | 2019-04-02
REC Solar | REC325NP Black | 325 W, 120 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 325 | 303.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.28 | 40.7 | 9.46 | 34.4 | 44.45 | -0.352 | 0.036 | -0.267 |  |  | 1.8585 | 33.0443 | 7.505 | 31.7576 | [6 empty] | 2019-05-01 | 2021-09-13
REC Solar | REC325PEM 72 | 325 W Monocrystalline Module | UL 1703 | 325 | 292.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.32 | 45.6 | 8.67 | 37.5 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.7271 | 36.3064 | 6.9222 | 34.099 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19294
REC Solar | REC325TP 72 | 325 W Polycrystalline Module | UL 1703 | 325 | 295.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.007 | 72 | 2 | N | 9.19 | 45.9 | 8.56 | 38 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.6809 | 36.0442 | 6.8402 | 34.6514 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18642
REC Solar | REC325TP 72 Q2 | 325 W Polycrystalline Module | UL 1703 | 325 | 295.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.007 | 72 | 2 | N | 9.19 | 45.9 | 8.56 | 38 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.6809 | 36.0442 | 6.8402 | 34.6514 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18642
REC Solar | REC325TP2M | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 325 | 302.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.12 | 40.4 | 9.56 | 34 | 44.57 | -0.37 | 0.04 | -0.286 |  |  | 1.8916 | 31.8783 | 7.6327 | 30.8462 | [6 empty] | 2019-08-01
REC Solar | REC325TP2M BLK | 325 W, 120 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730, UL 1703 | 325 | 302.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.12 | 40.4 | 9.56 | 34 | 44.57 | -0.37 | 0.04 | -0.286 |  |  | 1.8916 | 31.8783 | 7.6327 | 30.8462 | [6 empty] | 2019-08-01
REC Solar | REC325TP2S 72 | 325 W, 144 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 325 | 295.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.19 | 45.9 | 8.56 | 38 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.6752 | 36.0161 | 6.817 | 34.6244 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18564 |  | 2019-02-01
REC Solar | REC325TP2S 72 XV | 325 W, 144 half cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 325 | 295.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.19 | 45.9 | 8.56 | 38 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.6752 | 36.0161 | 6.817 | 34.6244 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18564 |  | 2019-02-01
REC Solar | REC325TP2SB 72 XV | 325 W, 144 Half-Cell Polycrystalline Module | UL 1703 | 325 | 300.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.933 | 144 |  | N | 9.213 | 45.813 | 8.65 | 37.382 | 44.15 | -0.389 | 0.06 | -0.306 | 0.013 | -0.401 | 1.682 | 35.7 | 6.904 | 34.518 | [6 empty] | 2018-01-02 | 2018-02-01
REC Solar | REC325TP2SM | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 325 | 302.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.12 | 40.4 | 9.56 | 34 | 44.57 | -0.37 | 0.04 | -0.286 |  |  | 1.8916 | 31.8783 | 7.6327 | 30.8462 | [6 empty] | 2019-08-01
REC Solar | REC325TP2SM BLK | 325 W, 120 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 1703 | 325 | 302.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.12 | 40.4 | 9.56 | 34 | 44.57 | -0.37 | 0.04 | -0.286 |  |  | 1.8916 | 31.8783 | 7.6327 | 30.8462 | [6 empty] | 2019-08-01
REC Solar | REC325TP3M | 325 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 325 | 304 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.36 | 39.5 | 9.54 | 34.1 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8376 | 32.6962 | 1.8376 | 32.6962 | 7.5229 | 31.6752 | [6 empty] | 2020-09-11
REC Solar | REC325TP3M Black | 325 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 325 | 304 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.36 | 39.5 | 9.54 | 34.1 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8376 |  | 1.8376 | 32.6962 | 7.5229 | 31.6752 | [6 empty] | 2020-09-11
REC Solar | REC330NP | 330W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 330 | 309.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.33 | 41 | 9.55 | 34.6 | 44.26 | -0.342 | 0.036 | -0.263 |  |  | 1.893 | 32.936 | 7.628 | 32.072 | [6 empty] | 2020-04-21 | 2021-03-11
REC Solar | REC330NP Black | 330 W, 120 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 330 | 308.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.62 | 60 | 2 | N | 10.33 | 41 | 9.55 | 34.6 | 44.45 | -0.352 | 0.036 | -0.267 |  |  | 1.8761 | 33.2364 | 7.5764 | 31.9422 | [6 empty] | 2019-05-01 | 2021-09-13
REC Solar | REC330PEM 72 | 330 W Monocrystalline Module | UL 1703 | 330 | 297.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.36 | 45.8 | 8.76 | 37.7 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.745 | 36.5 | 6.994 | 34.2808 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19301
REC Solar | REC330TP 72 | 330 W Polycrystalline Module | UL 1703 | 330 | 300 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.007 | 72 | 1 | N | 9.22 | 46 | 8.67 | 38.1 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7025 | 36.139 | 6.9281 | 34.7426 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18645
REC Solar | REC330TP2M | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 330 | 307.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.22 | 40.6 | 9.62 | 34.3 | 44.57 | -0.37 | 0.04 | -0.286 |  |  | 1.9034 | 32.1596 | 7.6806 | 31.1183 | [6 empty] | 2019-08-01
REC Solar | REC330TP2M BLK | 330 W, 120 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730, UL 1703 | 330 | 307.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.22 | 40.6 | 9.62 | 34.3 | 44.57 | -0.37 | 0.04 | -0.286 |  |  | 1.9034 | 32.1596 | 7.6806 | 31.1183 | [6 empty] | 2019-08-01
REC Solar | REC330TP2S 72 | 330 W, 144 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 330 | 300.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.44 | 46 | 8.67 | 38.1 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.6967 | 36.1109 | 6.9046 | 34.7155 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18567 |  | 2019-02-01
REC Solar | REC330TP2S 72 XV | 330 W, 144 half cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 330 | 300.2 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.44 | 46 | 8.67 | 38.1 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.6967 | 36.1109 | 6.9046 | 34.7155 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18567 |  | 2019-02-01
REC Solar | REC330TP2SB 72 XV | 330 W, 144 Half-Cell Polycrystalline Module | UL 1703 | 330 | 305 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.933 | 144 |  | N | 9.28 | 46.6 | 8.67 | 38.1 | 44.15 | -0.389 | 0.06 | -0.306 | 0.013 | -0.401 | 1.682 | 35.7 | 6.904 | 34.518 | [6 empty] | 2018-01-02 | 2018-02-01
REC Solar | REC330TP2SM | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 1703 | 330 | 307.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.22 | 40.6 | 9.62 | 34.3 | 44.57 | -0.37 | 0.04 | -0.286 |  |  | 1.9034 | 32.1596 | 7.6806 | 31.1183 | [6 empty] | 2019-08-01
REC Solar | REC330TP2SM BLK | 330 W, 120 half-cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 1703 | 330 | 307.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.617 | 60 | 2 | N | 10.22 | 40.6 | 9.62 | 34.3 | 44.57 | -0.37 | 0.04 | -0.286 |  |  | 1.9034 | 32.1596 | 7.6806 | 31.1183 | [6 empty] | 2019-08-01
REC Solar | REC330TP3M | 330 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 330 | 308.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.39 | 39.9 | 9.62 | 34.3 | 44.95 | -0.336 | 0.038 | -0.264 | 1.853 | 32.888 | 1.853 | 32.888 | 7.586 | 31.861 | [6 empty] | 2020-09-11
REC Solar | REC330TP3M Black | 330 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 330 | 308.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.39 | 39.9 | 9.62 | 34.3 | 44.95 | -0.336 | 0.038 | -0.264 | 1.853 |  | 1.853 | 32.888 | 7.586 | 31.861 | [6 empty] | 2020-09-11
REC Solar | REC335NP | 335W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 335 | 314 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.38 | 41.3 | 9.64 | 34.8 | 44.26 | -0.342 | 0.036 | -0.263 |  |  | 1.9108 | 33.1264 | 7.6999 | 32.2574 | [6 empty] | 2021-03-11
REC Solar | REC335PEM 72 | 335 W Monocrystalline Module | UL 1703 | 335 | 302.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.4 | 46 | 8.84 | 37.9 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.761 | 36.6937 | 7.0579 | 34.4627 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19288
REC Solar | REC335TP 72 | 335 W Polycrystalline Module | UL 1703 | 335 | 304.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.007 | 72 | 1 | N | 9.27 | 46.2 | 8.75 | 38.3 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7182 | 36.3287 | 6.9921 | 34.925 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18633
REC Solar | REC335TP2S 72 | 335 W, 144 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 335 | 304.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.52 | 46.2 | 8.75 | 38.3 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7124 | 36.3004 | 6.9683 | 34.8978 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18555 |  | 2019-02-01
REC Solar | REC335TP2S 72 XV | 335 W, 144 half cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 335 | 304.9 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.52 | 46.2 | 8.75 | 38.3 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7124 | 36.3004 | 6.9683 | 34.8978 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18555 |  | 2019-02-01
REC Solar | REC335TP2SB 72 XV | 335 W, 144 Half-Cell Polycrystalline Module | UL 1703 | 335 | 309.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.933 | 144 |  | N | 9.36 | 46.8 | 8.74 | 38.4 | 44.15 | -0.389 | 0.06 | -0.306 | 0.013 | -0.401 | 1.682 | 35.7 | 6.904 | 34.518 | [6 empty] | 2018-01-02 | 2018-02-01
REC Solar | REC335TP3M | 335 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 335 | 313.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.42 | 40.2 | 9.69 | 34.6 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8665 | 33.1757 | 1.8665 | 33.1757 | 7.6412 | 32.1397 | [6 empty] | 2020-09-11
REC Solar | REC335TP3M Black | 335 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 335 | 313.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.42 | 40.2 | 9.69 | 34.6 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8665 |  | 1.8665 | 33.1757 | 7.6412 | 32.1397 | [6 empty] | 2020-09-11
REC Solar | REC340AA | 340 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 340 | 322.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 60 | 2 | N | 10.09 | 43.1 | 9.34 | 36.4 | 44.01 | -0.279 | 0.037 | -0.241 |  |  | 1.8542 | 34.0496 | 7.4189 | 33.8481 | [6 empty] | 2019-07-15 | 2019-10-01
REC Solar | REC340AA Black | 340 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 340 | 321 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.09 | 43.1 | 9.34 | 36.4 | 45.55 | -0.282 | 0.038 | -0.24 |  |  | 1.8344 | 34.6153 | 7.3821 | 34.1866 | [6 empty] | 2019-08-15 | 2019-10-01
REC Solar | REC340PEM 72 | 340 W Polycrystalline Module | UL 1703 | 340 | 306.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.6 | 46.8 | 9 | 37.8 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.7961 | 36.3178 | 7.1842 | 33.9032 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19185
REC Solar | REC340TP 72 | 340 W, 144 half cell polycrystalline module, white backsheet | UL 1703 | 340 | 309.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.58 | 46.3 | 8.84 | 38.5 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.73 | 36.49 | 7.04 | 35.08 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18567 |  | 2019-02-01
REC Solar | REC340TP2S 72 | 340 W, 144 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 340 | 309.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.58 | 46.3 | 8.84 | 38.5 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.73 | 36.49 | 7.04 | 35.08 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18567 |  | 2019-02-01
REC Solar | REC340TP2S 72 XV | 340 W, 144 half cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 340 | 309.6 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.58 | 46.3 | 8.84 | 38.5 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.73 | 36.49 | 7.04 | 35.08 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18567 |  | 2019-02-01
REC Solar | REC340TP2SB 72 XV | 340 W, 144 Half-Cell Polycrystalline Module | UL 1703 | 340 | 314.5 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.933 | 144 |  | N | 9.44 | 47 | 8.82 | 38.6 | 44.15 | -0.389 | 0.06 | -0.306 | 0.013 | -0.401 | 1.682 | 35.7 | 6.904 | 34.518 | [6 empty] | 2018-01-02 | 2018-02-01
REC Solar | REC340TP3M | 340 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 340 | 318.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.45 | 40.6 | 9.79 | 34.7 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8857 | 33.2715 | 1.8857 | 33.2715 | 7.7201 | 32.2326 | [6 empty] | 2020-09-11
REC Solar | REC340TP3M Black | 340 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 340 | 318.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.61 | 60 | 2 | N | 10.45 | 40.6 | 9.79 | 34.7 | 44.95 | -0.336 | 0.038 | -0.264 | 1.8857 |  | 1.8857 | 33.2715 | 7.7201 | 32.2326 | [6 empty] | 2020-09-11
REC Solar | REC345AA | 345 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 345 | 327.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 60 | 2 | N | 10.12 | 43.4 | 9.39 | 36.7 | 44.01 | -0.279 | 0.037 | -0.241 |  |  | 1.8642 | 34.3302 | 7.4586 | 34.1271 | [6 empty] | 2019-07-15 | 2019-10-01
REC Solar | REC345AA Black | 345 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 345 | 325.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.12 | 43.4 | 9.39 | 36.7 | 45.55 | -0.282 | 0.038 | -0.24 |  |  | 1.8442 | 34.9006 | 7.4216 | 34.4683 | [6 empty] | 2019-08-15 | 2019-10-01
REC Solar | REC345PEM 72 | 345 W Polycrystalline Module | UL 1703 | 345 | 311.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.65 | 47.1 | 9.1 | 38 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.816 | 36.51 | 7.264 | 34.0826 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19218
REC Solar | REC345TP 72 | 345 W Polycrystalline Module | UL 1703 | 345 | 314 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.007 | 72 | 1 | N | 9.36 | 46.5 | 8.92 | 38.7 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7516 | 36.7082 | 7.1279 | 35.2897 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18637
REC Solar | REC345TP2S 72 | 345 W, 144 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 345 | 314.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.64 | 46.5 | 8.92 | 38.7 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7457 | 36.6796 | 7.1037 | 35.2622 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18559 |  | 2019-02-01
REC Solar | REC345TP2S 72 XV | 345 W, 144 half cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 345 | 314.3 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.64 | 46.5 | 8.92 | 38.7 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7457 | 36.6796 | 7.1037 | 35.2622 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18559 |  | 2019-02-01
REC Solar | REC350AA | 350 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 350 | 332.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 60 | 2 | N | 10.16 | 43.8 | 9.45 | 37.1 | 44.01 | -0.279 | 0.037 | -0.241 |  |  | 1.8761 | 34.7044 | 7.5063 | 34.499 | [6 empty] | 2019-07-15 | 2019-10-01
REC Solar | REC350AA Black | 350 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 350 | 331.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.44 | 43.2 | 9.73 | 36 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.8057 | 34.6483 | 7.3523 | 34.2359 | [6 empty] | 2019-08-15 | 2020-12-11
REC Solar | REC350PEM 72 | 350 W Polycrystalline Module | UL 1703 | 350 | 316.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.73 | 47.2 | 9.2 | 38.1 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.836 | 36.6061 | 7.3439 | 34.1723 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19202
REC Solar | REC350TP 72 | 350 W Polycrystalline Module | UL 1703 | 350 | 318.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.007 | 72 | 2 | N | 9.4 | 46.7 | 9 | 38.9 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7673 | 36.8979 | 7.1918 | 35.4721 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18631
REC Solar | REC350TP2M 72 | 350 W Monocrystalline Module | UL 1703 | 350 | 323.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 2 | N | 9.55 | 47 | 8.98 | 39 | 44.99 | -0.37 | 0.04 | -0.28 | 0 | -0.37 | 1.7852 | 37.2221 | 7.2096 | 36.0591 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18985
REC Solar | REC350TP2S 72 | 350 W, 144 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 350 | 319 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.72 | 46.7 | 9 | 38.9 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7613 | 36.8691 | 7.1674 | 35.4445 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18554 |  | 2019-02-01
REC Solar | REC350TP2S 72 XV | 350 W, 144 half cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 350 | 319 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.72 | 46.7 | 9 | 38.9 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7613 | 36.8691 | 7.1674 | 35.4445 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18554 |  | 2019-02-01
REC Solar | REC350TP2SM 72 | 350W, 144 Half-Cell Mono c-Si module, white backsheet, 1000V max system Vdc | UL 1703 | 350 | 324.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.55 | 47 | 8.98 | 39 | 44.99 | -0.37 | 0.04 | -0.28 | 0 | -0.37 | 1.7629 | 37.3198 | 7.1197 | 36.1538 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18797 |  | 2019-01-02
REC Solar | REC355AA | 355 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 355 | 337.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 60 | 2 | N | 10.19 | 44 | 9.5 | 37.4 | 44.01 | -0.279 | 0.037 | -0.241 |  |  | 1.886 | 34.985 | 7.546 | 34.778 | [6 empty] | 2019-07-15 | 2019-10-01
REC Solar | REC355AA Black | 355 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 355 | 336.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.47 | 43.6 | 9.77 | 36.4 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.8132 | 35.0333 | 7.3825 | 34.6163 | [6 empty] | 2019-08-15 | 2020-12-11
REC Solar | REC355NP2 | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 355 | 334.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.27 | 40.7 | 10.6 | 33.5 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0426 |  | 2.0426 | 32.4496 | 8.2884 | 31.7178 | [6 empty] | 2021-10-01
REC Solar | REC355NP2 Black | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 355 | 334.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.27 | 40.7 | 10.6 | 33.5 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0426 |  | 2.0426 | 32.4496 | 8.2884 | 31.7178 | [6 empty] | 2021-10-01
REC Solar | REC355PEM 72 | 355 W Polycrystalline Module | UL 1703 | 355 | 320.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.78 | 47.4 | 9.3 | 38.2 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.8559 | 36.7022 | 7.4237 | 34.262 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19188
REC Solar | REC355TP 72 | 355 W Polycrystalline Module | UL 1703 | 355 | 323.4 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 2.007 | 72 | 2 | N | 9.44 | 46.8 | 9.08 | 39.1 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.783 | 37.0876 | 7.2558 | 35.6545 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18628
REC Solar | REC355TP2M 72 | 355 W Monocrystalline Module | UL 1703 | 355 | 328.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 2 | N | 9.65 | 47.2 | 9.06 | 39.2 | 44.99 | -0.37 | 0.04 | -0.28 | 0 | -0.37 | 1.8011 | 37.413 | 7.2739 | 36.244 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18981
REC Solar | REC355TP2S 72 | 355 W, 144 half cell polycrystalline module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 355 | 323.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.78 | 46.8 | 9.09 | 39.1 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7789 | 37.0587 | 7.2391 | 35.6267 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.1857 |  | 2019-02-01
REC Solar | REC355TP2S 72 XV | 355 W, 144 half cell polycrystalline module, white backsheet, 1500V max system Vdc | UL 61730, UL 1703 | 355 | 323.7 |  | No Information Submitted | No Information Submitted | Polycrystalline | Multi-c-Si | 1.95 | 72 | 2 | N | 9.78 | 46.8 | 9.09 | 39.1 | 44.26 | -0.46 | 0.05 | -0.35 | -0.01 | -0.45 | 1.7789 | 37.0587 | 7.2391 | 35.6267 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.1857 |  | 2019-02-01
REC Solar | REC355TP2SM 72 | 355W, 144 Half-Cell Mono c-Si module, white backsheet, 1000V max system Vdc | UL 1703 | 355 | 328.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 9.65 | 47.2 | 9.06 | 39.2 | 44.99 | -0.37 | 0.04 | -0.28 | 0 | -0.37 | 1.7786 | 37.5112 | 7.1831 | 36.3392 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18794 |  | 2019-01-02
REC Solar | REC355TP4 | 355 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 355 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.19 | 40.5 | 10.6 | 33.5 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.0451 | 32.5503 | 8.3103 | 31.5977 | [6 empty] | 2021-07-01
REC Solar | REC355TP4 Black | 355 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 355 | 331.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.19 | 40.5 | 10.6 | 33.5 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.0451 | 32.5503 | 8.3103 | 31.5977 | [6 empty] | 2021-07-01
REC Solar | REC360AA | 360 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 360 | 342.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 60 | 2 | N | 10.23 | 44.1 | 9.55 | 37.7 | 44.01 | -0.279 | 0.037 | -0.241 |  |  | 1.8959 | 35.2656 | 7.5857 | 35.057 | [6 empty] | 2019-07-15 | 2019-10-01
REC Solar | REC360AA Black | 360 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 341 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.49 | 43.9 | 9.82 | 36.7 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.8224 | 35.322 | 7.4203 | 34.9016 | [6 empty] | 2019-08-15 | 2020-12-11
REC Solar | REC360NP2 | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 360 | 338.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.31 | 40.8 | 10.62 | 33.9 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0464 |  | 2.0464 | 32.8371 | 8.3041 | 32.0966 | [6 empty] | 2021-10-01
REC Solar | REC360NP2 Black | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 338.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.31 | 40.8 | 10.62 | 33.9 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0464 |  | 2.0464 | 32.8371 | 8.3041 | 32.0966 | [6 empty] | 2021-10-01
REC Solar | REC360PEM 72 | 360 W Polycrystalline Module | UL 1703 | 360 | 325.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.84 | 47.6 | 9.38 | 38.4 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.8719 | 36.8943 | 7.4875 | 34.4413 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19184
REC Solar | REC360TP2M 72 | 360 W Monocrystalline Module | UL 1703 | 360 | 333.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 2 | N | 9.74 | 47.4 | 9.14 | 39.4 | 44.99 | -0.37 | 0.04 | -0.28 | 0 | -0.37 | 1.817 | 37.6039 | 7.3381 | 36.4289 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18979
REC Solar | REC360TP2SM 72 | 360 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730, UL 1703 | 360 | 337.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.74 | 47.4 | 9.14 | 39.4 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.797 | 36.9715 | 7.2635 | 36.2001 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18455 |  | 2019-05-15
REC Solar | REC360TP2SM 72 BLK | 360 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 360 | 337.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.74 | 47.4 | 9.14 | 39.4 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.797 | 36.9715 | 7.2635 | 36.2001 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18455 |  | 2021-09-13
REC Solar | REC360TP2SM 72 XV | 360 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 360 | 337.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.74 | 47.4 | 9.14 | 39.4 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.797 | 36.9715 | 7.2635 | 36.2001 | [6 empty] | 2019-01-02 | 2021-09-13
REC Solar | REC360TP2SM 72 XV BLK | 360 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 360 | 337.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.74 | 47.4 | 9.14 | 39.4 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.797 | 36.9715 | 7.2635 | 36.2001 | [6 empty] | 2019-01-02 | 2021-09-13
REC Solar | REC360TP4 | 360 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 360 | 336 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.26 | 40.6 | 10.62 | 33.9 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.049 | 32.939 | 8.326 | 31.975 | [6 empty] | 2021-07-01
REC Solar | REC360TP4 Black | 360 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 360 | 336 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.26 | 40.6 | 10.62 | 33.9 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.049 | 32.939 | 8.326 | 31.975 | [6 empty] | 2021-07-01
REC Solar | REC365AA | 365 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730, UL 1703 | 365 | 346.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.68 | 60 | 2 | N | 10.26 | 44.3 | 9.6 | 38 | 44.01 | -0.279 | 0.037 | -0.241 |  |  | 1.9059 | 35.5463 | 7.6254 | 35.3359 | [6 empty] | 2019-07-15 | 2019-10-01
REC Solar | REC365AA Black | 365 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 345.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.52 | 44 | 9.85 | 37.1 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.828 | 35.707 | 7.443 | 35.282 | [6 empty] | 2019-08-15 | 2020-12-11
REC Solar | REC365NP 72 | 365 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 365 | 340.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.12 | 47.4 | 9.35 | 39.1 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.8147 | 38.5937 | 7.3577 | 37.3278 | [6 empty] | 2020-04-13
REC Solar | REC365NP 72 XV | 365 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 365 | 340.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.12 | 47.4 | 9.35 | 39.1 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.8147 | 38.5937 | 7.3577 | 37.3278 | [6 empty] | 2020-04-13
REC Solar | REC365NP2 | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 365 | 343.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.36 | 40.9 | 10.65 | 34.3 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0522 |  | 2.0522 | 33.2245 | 8.3275 | 32.4753 | [6 empty] | 2021-10-01
REC Solar | REC365NP2 Black | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 343.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.36 | 40.9 | 10.65 | 34.3 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0522 |  | 2.0522 | 33.2245 | 8.3275 | 32.4753 | [6 empty] | 2021-10-01
REC Solar | REC365PEM 72 | 365 W Polycrystalline Module | UL 1703 | 365 | 330.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.9 | 47.9 | 9.44 | 38.7 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.8839 | 37.1825 | 7.5354 | 34.7104 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19191
REC Solar | REC365TP2M 72 | 365 W Monocrystalline Module | UL 1703 | 365 | 338.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 2 | N | 9.82 | 47.6 | 9.22 | 39.6 | 44.99 | -0.37 | 0.04 | -0.28 | 0 | -0.37 | 1.8329 | 37.7947 | 7.4023 | 36.6138 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18979
REC Solar | REC365TP2SM 72 | 365 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730, UL 1703 | 365 | 342.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.82 | 47.6 | 9.22 | 39.6 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8127 | 37.1591 | 7.3271 | 36.3839 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18454 |  | 2019-05-15
REC Solar | REC365TP2SM 72 BLK | 365 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 365 | 342.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.82 | 47.6 | 9.22 | 39.6 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8127 | 37.1591 | 7.3271 | 36.3839 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18454 |  | 2021-09-13
REC Solar | REC365TP2SM 72 XV | 365 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 365 | 342.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.82 | 47.6 | 9.22 | 39.6 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8127 | 37.1591 | 7.3271 | 36.3839 | [6 empty] | 2019-01-02 | 2021-09-13
REC Solar | REC365TP2SM 72 XV BLK | 365 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 365 | 342.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.82 | 47.6 | 9.22 | 39.6 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8127 | 37.1591 | 7.3271 | 36.3839 | [6 empty] | 2019-01-02 | 2021-09-13
REC Solar | REC365TP4 | 365 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 365 | 340.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.32 | 40.8 | 10.65 | 34.3 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.0548 | 33.3277 | 8.3495 | 32.3523 | [6 empty] | 2021-07-01
REC Solar | REC365TP4 Black | 365 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 365 | 340.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.32 | 40.8 | 10.65 | 34.3 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.0548 | 33.3277 | 8.3495 | 32.3523 | [6 empty] | 2021-07-01
REC Solar | REC370AA | 370 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730 | 370 | 351.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.55 | 44.1 | 9.9 | 37.4 | 45.45 | -0.258 | 0.034 | -0.236 |  |  | 1.888 | 35.65 | 7.667 | 35.28 | [6 empty] | 2019-07-15 | 2020-06-22
REC Solar | REC370AA Black | 370 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 370 | 350.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.55 | 44.1 | 9.9 | 37.4 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.8373 | 35.9957 | 7.4808 | 35.5673 | [6 empty] | 2020-12-11
REC Solar | REC370NP 72 | 370 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 370 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.16 | 47.7 | 9.42 | 39.3 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.8282 | 38.7911 | 7.4127 | 37.5187 | [6 empty] | 2020-04-13
REC Solar | REC370NP 72 XV | 370 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 370 | 345.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.16 | 47.7 | 9.42 | 39.3 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.8282 | 38.7911 | 7.4127 | 37.5187 | [6 empty] | 2020-04-13
REC Solar | REC370NP2 | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 370 | 348.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.41 | 41.1 | 10.68 | 34.7 | 43.93 | -0.323 | 0.036 | -0.252 | 2.058 |  | 2.058 | 33.612 | 8.351 | 32.854 | [6 empty] | 2021-10-01
REC Solar | REC370NP2 Black | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 370 | 348.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.41 | 41.1 | 10.68 | 34.7 | 43.93 | -0.323 | 0.036 | -0.252 | 2.058 |  | 2.058 | 33.612 | 8.351 | 32.854 | [6 empty] | 2021-10-01
REC Solar | REC370PEM 72 | 370 W Polycrystalline Module | UL 1703 | 370 | 334.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 1 | N | 9.97 | 48.2 | 9.52 | 38.9 | 46.18 | -0.452 | 0.042 | -0.317 | -0.028 | -0.429 | 1.8998 | 37.3747 | 7.5993 | 34.8898 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.19191
REC Solar | REC370TP2M 72 | 370 W Monocrystalline Module | UL 1703 | 370 | 342.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 2 | N | 9.85 | 47.8 | 9.3 | 39.8 | 44.99 | -0.37 | 0.04 | -0.28 | 0 | -0.37 | 1.8488 | 37.9856 | 7.4666 | 36.7988 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.1898
REC Solar | REC370TP2SM 72 | 370 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730, UL 1703 | 370 | 347.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.85 | 47.8 | 9.3 | 39.8 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8284 | 37.3468 | 7.3907 | 36.5676 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18456 |  | 2019-05-15
REC Solar | REC370TP2SM 72 BLK | 370 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 370 | 347.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.85 | 47.8 | 9.3 | 39.8 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8284 | 37.3468 | 7.3907 | 36.5676 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18456 |  | 2021-09-13
REC Solar | REC370TP2SM 72 XV | 370 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730, UL 1703 | 370 | 347.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.85 | 47.8 | 9.3 | 39.8 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8284 | 37.3468 | 7.3907 | 36.5676 | [6 empty] | 2019-01-02 | 2019-05-15
REC Solar | REC370TP2SM 72 XV BLK | 370 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 370 | 347.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.85 | 47.8 | 9.3 | 39.8 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8284 | 37.3468 | 7.3907 | 36.5676 | [6 empty] | 2019-01-02 | 2021-09-13
REC Solar | REC370TP4 | 370 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 370 | 345.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.38 | 41 | 10.68 | 34.7 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.0606 | 33.7163 | 8.373 | 32.7296 | [6 empty] | 2021-07-01
REC Solar | REC370TP4 Black | 370 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 370 | 345.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.38 | 41 | 10.68 | 34.7 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.0606 | 33.7163 | 8.373 | 32.7296 | [6 empty] | 2021-07-01
REC Solar | REC375AA | 375 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730 | 375 | 356.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.58 | 44.2 | 9.94 | 37.8 | 45.45 | -0.258 | 0.034 | -0.236 |  |  | 1.8956 | 36.0313 | 7.698 | 35.6573 | [6 empty] | 2020-06-22
REC Solar | REC375AA Black | 375 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 375 | 355.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.58 | 44.2 | 9.94 | 37.8 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.8447 | 36.3807 | 7.511 | 35.9477 | [6 empty] | 2020-12-11
REC Solar | REC375NP 72 | 375 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 375 | 350.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.2 | 48.1 | 9.46 | 39.7 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.836 | 39.1859 | 7.4442 | 37.9006 | [6 empty] | 2020-04-13
REC Solar | REC375NP 72 XV | 375 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 375 | 350.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.2 | 48.1 | 9.46 | 39.7 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.836 | 39.1859 | 7.4442 | 37.9006 | [6 empty] | 2020-04-13
REC Solar | REC375NP2 | 375 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 375 | 353.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.46 | 41.3 | 10.72 | 35 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0657 |  | 2.0657 | 33.9026 | 8.3823 | 33.138 | [6 empty] | 2021-10-01
REC Solar | REC375NP2 Black | 375 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 375 | 353.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.46 | 41.3 | 10.72 | 35 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0657 |  | 2.0657 | 33.9026 | 8.3823 | 33.138 | [6 empty] | 2021-10-01
REC Solar | REC375TP2M 72 | 375 W Monocrystalline Module | UL 1703 | 375 | 347.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 2 | N | 9.96 | 48 | 9.36 | 40.1 | 44.99 | -0.37 | 0.04 | -0.28 | 0 | -0.37 | 1.8607 | 38.2719 | 7.5147 | 37.0761 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.1899
REC Solar | REC375TP2SM 72 | 375 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730, UL 1703 | 375 | 352.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.96 | 48 | 9.36 | 40.1 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8402 | 37.6283 | 7.4384 | 36.8432 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18465 |  | 2019-05-15
REC Solar | REC375TP2SM 72 BLK | 375 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 375 | 352.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.96 | 48 | 9.36 | 40.1 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8402 | 37.6283 | 7.4384 | 36.8432 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18465 |  | 2021-09-13
REC Solar | REC375TP2SM 72 XV | 375 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730 | 375 | 352.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.96 | 48 | 9.36 | 40.1 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8402 | 37.6283 | 7.4384 | 36.8432 | [6 empty] | 2019-01-02 | 2021-09-13
REC Solar | REC375TP2SM 72 XV BLK | 375 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 375 | 352.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 9.96 | 48 | 9.36 | 40.1 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.8402 | 37.6283 | 7.4384 | 36.8432 | [6 empty] | 2019-01-02 | 2021-09-13
REC Solar | REC375TP4 | 375 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 375 | 350.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.45 | 41.2 | 10.72 | 35 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.0683 | 34.0078 | 8.4044 | 33.0125 | [6 empty] | 2021-07-01
REC Solar | REC375TP4 Black | 375 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 375 | 350.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.45 | 41.2 | 10.72 | 35 | 45.51 | -0.339 | 0.037 | -0.266 |  |  | 2.0683 | 34.0078 | 8.4044 | 33.0125 | [6 empty] | 2021-07-01
REC Solar | REC380AA | 380 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730 | 380 | 361.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.61 | 44.3 | 9.98 | 38.1 | 45.45 | -0.258 | 0.034 | -0.236 |  |  | 1.9033 | 36.3172 | 7.729 | 35.9403 | [6 empty] | 2020-06-22
REC Solar | REC380AA Black | 380 W, 120 half-cut cell monocrystalline HJT module, black backsheet, 1000V max system Vdc | UL 61730 | 380 | 360.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.61 | 44.3 | 9.98 | 38.1 | 46.01 | -0.266 | 0.037 | -0.235 |  |  | 1.8521 | 36.6695 | 7.5412 | 36.233 | [6 empty] | 2020-12-11
REC Solar | REC380NP 72 | 380 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 380 | 355.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.24 | 48.5 | 9.56 | 39.8 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.8554 | 39.2846 | 7.5229 | 37.9961 | [6 empty] | 2020-04-13
REC Solar | REC380NP 72 XV | 380 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 355.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.24 | 48.5 | 9.56 | 39.8 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.8554 | 39.2846 | 7.5229 | 37.9961 | [6 empty] | 2020-04-13
REC Solar | REC380NP2 | 380 W, 120 half-cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 380 | 358.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.51 | 41.4 | 10.77 | 35.3 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0753 |  | 2.0753 | 34.1932 | 8.4214 | 33.4221 | [6 empty] | 2021-10-01
REC Solar | REC380NP2 Black | 380 W, 120 half-cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 380 | 358.2 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.77 | 60 | 2 | N | 11.51 | 41.4 | 10.77 | 35.3 | 43.93 | -0.323 | 0.036 | -0.252 | 2.0753 |  | 2.0753 | 34.1932 | 8.4214 | 33.4221 | [6 empty] | 2021-10-01
REC Solar | REC380TP2M 72 | 380 W Monocrystalline Module | UL 1703 | 380 | 352.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 2.007 | 72 | 2 | N | 10.05 | 48.2 | 9.43 | 40.3 | 44.99 | -0.37 | 0.04 | -0.28 | 0 | -0.37 | 1.8746 | 38.4628 | 7.5709 | 37.2611 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.18974
REC Solar | REC380TP2SM 72 | 380 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730, UL 1703 | 380 | 357.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.05 | 48.2 | 9.43 | 40.3 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.854 | 37.816 | 7.494 | 37.027 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.1845 |  | 2019-05-15
REC Solar | REC380TP2SM 72 BLK | 380 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730 | 380 | 357.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.05 | 48.2 | 9.43 | 40.3 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.854 | 37.816 | 7.494 | 37.027 | Rack | Flat Plate | 1.001 | 2.005 | 1 | 0.1845 |  | 2021-09-13
REC Solar | REC380TP2SM 72 XV | 380 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 61730, UL 1703 | 380 | 357.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.05 | 48.2 | 9.43 | 40.3 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.854 | 37.816 | 7.494 | 37.027 | [6 empty] | 2019-01-02 | 2019-08-01
REC Solar | REC380TP2SM 72 XV BLK | 380 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730 | 380 | 357.1 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.05 | 48.2 | 9.43 | 40.3 | 41.94 | -0.366 | 0.038 | -0.285 | 0 | -0.37 | 1.854 | 37.816 | 7.494 | 37.027 | [6 empty] | 2019-01-02 | 2021-09-13
REC Solar | REC380TP3SM 72 XV | 380 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 380 | 355 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.3 | 46.9 | 9.41 | 40.4 | 44.81 | -0.341 | 0.033 | -0.265 |  |  | 1.8567 | 38.6932 | 7.5621 | 37.4529 | [6 empty] | 2020-11-23
REC Solar | REC385AA | 385 W, 120 half-cut cell monocrystalline HJT module, white backsheet, 1000V max system Vdc | UL 61730 | 385 | 366.4 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.69 | 60 | 2 | N | 10.64 | 44.4 | 10.03 | 38.4 | 45.45 | -0.258 | 0.034 | -0.236 |  |  | 1.9128 | 36.6032 | 7.7677 | 36.2233 | [6 empty] | 2020-06-22
REC Solar | REC385AA Pure | 385 W, 132 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 385 | 366.5 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.794 | 66 | 2 | N | 10.1 | 48.5 | 9.35 | 41.2 | 45.01 | -0.256 | 0.034 | -0.233 |  |  | 1.8163 | 38.9722 | 7.3726 | 38.6297 | [6 empty] | 2021-07-21
REC Solar | REC385NP 72 | 385 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 385 | 359.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.28 | 48.9 | 9.63 | 40 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.869 | 39.482 | 7.578 | 38.187 | [6 empty] | 2020-04-13
REC Solar | REC385NP 72 XV | 385 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 359.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.28 | 48.9 | 9.63 | 40 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.869 | 39.482 | 7.578 | 38.187 | [6 empty] | 2020-04-13
REC Solar | REC385TP2M 72 | 385 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 385 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.4 | 9.51 | 40.5 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8697 | 38.0037 | 7.5576 | 37.2108 | [6 empty] | 2019-08-01
REC Solar | REC385TP2M 72 BLK | 385 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 385 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.4 | 9.51 | 40.5 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8697 | 38.0037 | 7.5576 | 37.2108 | [6 empty] | 2019-08-01
REC Solar | REC385TP2M 72 XV | 385 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 1703 | 385 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.4 | 9.51 | 40.5 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8697 | 38.0037 | 7.5576 | 37.2108 | [6 empty] | 2019-08-01
REC Solar | REC385TP2M 72 XV BLK | 385 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 1703 | 385 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.4 | 9.51 | 40.5 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8697 | 38.0037 | 7.5576 | 37.2108 | [6 empty] | 2019-08-01
REC Solar | REC385TP2SM 72 | 385 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730, UL 1703 | 385 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.4 | 9.51 | 40.5 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8697 | 38.0037 | 7.5576 | 37.2108 | [6 empty] | 2019-08-01
REC Solar | REC385TP2SM 72 BLK | 385 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730, UL 1703 | 385 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.4 | 9.51 | 40.5 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8697 | 38.0037 | 7.5576 | 37.2108 | [6 empty] | 2019-08-01
REC Solar | REC385TP2SM 72 XV | 385 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 1703 | 385 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.4 | 9.51 | 40.5 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8697 | 38.0037 | 7.5576 | 37.2108 | [6 empty] | 2019-08-01
REC Solar | REC385TP2SM 72 XV BLK | 385 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730, UL 1703 | 385 | 361.9 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.1 | 48.4 | 9.51 | 40.5 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8697 | 38.0037 | 7.5576 | 37.2108 | [6 empty] | 2019-08-01
REC Solar | REC385TP3SM 72 XV | 385 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 385 | 359.8 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.33 | 47.2 | 9.47 | 40.7 | 44.81 | -0.341 | 0.033 | -0.265 |  |  | 1.8685 | 38.9806 | 7.6103 | 37.7311 | [6 empty] | 2020-11-23
REC Solar | REC390AA Pure | 390 W, 132 half cut cell monocrystalline module, black backsheet, 1000V max system Vdc | UL 61730 | 390 | 371.3 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.794 | 66 | 2 | N | 10.15 | 48.6 | 9.4 | 41.5 | 45.01 | -0.256 | 0.034 | -0.233 |  |  | 1.826 | 39.256 | 7.412 | 38.911 | [6 empty] | 2021-07-21
REC Solar | REC390NP 72 | 390 W, 144 half cut cell monocrystalline module, white backsheet, 1000V max system Vdc | UL 61730 | 390 | 364.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.32 | 49.1 | 9.72 | 40.2 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.8865 | 39.6794 | 7.6488 | 38.3779 | [6 empty] | 2020-04-13
REC Solar | REC390NP 72 XV | 390 W, 144 half cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 364.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.32 | 49.1 | 9.72 | 40.2 | 44.37 | -0.348 | 0.031 | -0.266 |  |  | 1.8865 | 39.6794 | 7.6488 | 38.3779 | [6 empty] | 2020-04-13
REC Solar | REC390TP2M 72 | 390 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 1703 | 390 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.13 | 48.6 | 9.58 | 40.7 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8835 | 38.1913 | 7.6132 | 37.3945 | [6 empty] | 2019-08-01
REC Solar | REC390TP2M 72 BLK | 390 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 1703 | 390 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.13 | 48.6 | 9.58 | 40.7 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8835 | 38.1913 | 7.6132 | 37.3945 | [6 empty] | 2019-08-01
REC Solar | REC390TP2M 72 XV | 390 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 1703 | 390 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.13 | 48.6 | 9.58 | 40.7 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8835 | 38.1913 | 7.6132 | 37.3945 | [6 empty] | 2019-08-01
REC Solar | REC390TP2M 72 XV BLK | 390 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 1703 | 390 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.13 | 48.6 | 9.58 | 40.7 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8835 | 38.1913 | 7.6132 | 37.3945 | [6 empty] | 2019-08-01
REC Solar | REC390TP2SM 72 | 390 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1000V max system Vdc | UL 61730, UL 1703 | 390 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.13 | 48.6 | 9.58 | 40.7 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8835 | 38.1913 | 7.6132 | 37.3945 | [6 empty] | 2019-08-01
REC Solar | REC390TP2SM 72 BLK | 390 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1000V max system Vdc | UL 61730, UL 1703 | 390 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.13 | 48.6 | 9.58 | 40.7 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8835 | 38.1913 | 7.6132 | 37.3945 | [6 empty] | 2019-08-01
REC Solar | REC390TP2SM 72 XV | 390 W, 144 half cut cell monocrystalline module, white backsheet, silver frame, 1500V max system Vdc | UL 1703 | 390 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.13 | 48.6 | 9.58 | 40.7 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8835 | 38.1913 | 7.6132 | 37.3945 | [6 empty] | 2019-08-01
REC Solar | REC390TP2SM 72 XV BLK | 390 W, 144 half cut cell monocrystalline module, white backsheet, black frame, 1500V max system Vdc | UL 61730, UL 1703 | 390 | 366.7 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.947 | 72 | 2 | N | 10.13 | 48.6 | 9.58 | 40.7 | 41.94 | -0.366 | 0.038 | -0.285 |  |  | 1.8835 | 38.1913 | 7.6132 | 37.3945 | [6 empty] | 2019-08-01
REC Solar | REC390TP3SM 72 XV | 390 W, 144 half-cut cell monocrystalline module, white backsheet, 1500V max system Vdc | UL 61730 | 390 | 364.6 |  | No Information Submitted | No Information Submitted | Monocrystalline | Mono-c-Si | 1.95 | 72 | 2 | N | 10.35 | 47.6 | 9.54 | 40.9 | 44.81 | -0.341 | 0.033 | -0.265 |  |  | 1.8823 | 39.1721 | 7.6665 | 37.9165 | [6 empty] | 2020-11-23