{"text_format":"1","workbook":"xlsx","n_sheets":4,"sheets":["List","Form Instructions","Reporting Instructions","HVAC 1"],"not_rendered":{"charts":0,"images":13,"macros":1,"external_links":0,"defined_names":269,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"List","index":0,"n_rows":23,"n_cols":3,"rows_kept":23,"cut":false,"hidden":true,"merged":[]}
["AHRI Unit List","Manufacturer","Economizer Controller"]
["SP - Single-Package Air-Conditioner","Aaon","Aaon VCCX2 "]
["RCU – Remote Condensing Unit (Split System) ","Amana","Bard LC6000 "]
["HSP – Single-Package Heat Pump","Bard","Belimo ZIP "]
["HRCU – Heat Pump with Remote Condensing Unit (Split System)","Bryant Heating & Cooling Systems ","Carrier ComfortLink "]
["SPVA – Single Package Vertical Air Conditioner (Wall Mount)","Carrier Corporation","Carrier i-Vu RTU-Open "]
["SPVHP – Single Package Vertical Heat Pump (Wall Mount)","Daikin","Daikin WattMaster OE377-26B-00001 "]
["Other","Day & Night ","Honeywell W7220 (Jade) "]
[null,"Friedrich","Johnson Controls IPU "]
[null,"Fujitsu","Johnson Controls PK-ECO1011-0 (PEAK) "]
[null,"Johnson Controls ","Johnson Controls Simplicity SE Unit Controller "]
[null,"Lennox","Johnson Controls Smart Equipment  "]
[null,"Marvair ","OEM CTRL I/O Flex 6126 "]
[null,"Rheem","OEM CTRL I/O Pro 812u "]
[null,"Trane","Pelican PEARL "]
[null,"York","Prodigy Control System "]
[null,"Other","Siemens Climatix ECO, POL224.00  "]
[null,null,"Trane Intellipak "]
[null,null,"Trane ReliaTel Microporcessor "]
[null,null,"Trane Symbio 700 "]
[null,null,"Trane Symbio 800 "]
[null,null,"Trane Tracer UC600 "]
[null,null,"Other (Specify) "]

{"sheet":"Form Instructions","index":1,"n_rows":29,"n_cols":12,"rows_kept":29,"cut":false,"hidden":false,"merged":[[0,0,0,8]]}
[]
[null,null,null,null,null,null,null,null,null,null,"Error Table","HVAC 1"]
[null,null,null,null,null,null,null,null,null,null,"Section"]
[null,null,null,null,null,null,null,null,null,null,"Guidance and Worksheet Section",14]
[null,null,null,null,null,null,null,null,null,null,"Licensed Professional Recommendations",2]
[null,null,null,null,null,null,null,null,null,null,"Deficiencies",1]
[null,null,null,null,null,null,null,null,null,null,"1.1 HVAC Equipment Details",18]
[null,null,null,null,null,null,null,null,null,null,"2.1 Filter Data",7]
[null,null,null,null,null,null,null,null,null,null,"2.2 Supply Fan Motor Nameplate Data",10]
[null,null,null,null,null,null,null,null,null,null,"2.3 Fan and Motor Sheave Data",0]
[null,null,null,null,null,null,null,null,null,null,"2.4 Airflow Data",23]
[null,null,null,null,null,null,null,null,null,null,"2.5 Summary Data for Powered Exhaust Test",7]
[null,null,null,null,null,null,null,null,null,null,"2.6 Minor Repairs and Adjustments",0]
[null,null,null,null,null,null,null,null,null,null,"2.7 Remaining Deficiencies",0]
[null,null,null,null,null,null,null,null,null,null,"3.1 Minimum Required Outside Air (OSA) for HVAC System",6]
[null,null,null,null,null,null,null,null,null,null,"3.2 Outside Air Measurements"]
[null,null,null,null,null,null,null,null,null,null,"3.3 Minor Repairs and Adjustments"]
[null,null,null,null,null,null,null,null,null,null,"3.4 Outside Air Deficiencies"]
[null,null,null,null,null,null,null,null,null,null,"4.1  Economizer and DCV Information"]
[null,null,null,null,null,null,null,null,null,null,"4.2 Economizer Configuration and Testing"]
[null,null,null,null,null,null,null,null,null,null,"4.3 Demand Controlled Ventilation"]
[null,null,null,null,null,null,null,null,null,null,"4.4 Minor Repairs and Adjustments"]
[null,null,null,null,null,null,null,null,null,null,"4.5 Remaining Deficiencies"]
[null,null,null,null,null,null,null,null,null,null,"5.1 Operational Controls"]
[null,null,null,null,null,null,null,null,null,null,"5.2 Minor_Repairs_and_Adjustments"]
[null,null,null,null,null,null,null,null,null,null,"5.3 Remaining Deficiencies"]
[null,null,null,null,null,null,null,null,null,null,"6.1 General Maintenance"]
[null,null,null,null,null,null,null,null,null,null,"6.2 Minor Repairs and Adjustments"]
[null,null,null,null,null,null,null,null,null,null,"6.3 Remaining Deficiencies"]

{"sheet":"Reporting Instructions","index":2,"n_rows":7,"n_cols":17,"rows_kept":7,"cut":false,"hidden":false,"merged":[[0,0,0,14],[0,15,0,26],[1,15,9,15],[1,22,1,26],[2,16,3,26],[4,16,5,26],[6,16,7,26]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"This document contains links to resources.  See below."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Links:"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CA Climate Zone Information: https://www.energy.ca.gov/programs-and-topics/programs/building-energy-efficiency-standards/climate-zone-tool-maps-and"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AHRI Database: https://www.ahridirectory.org/Search/SearchHome?ReturnUrl=%2f"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Informational Video on Filter Performance: https://youtu.be/ycgLBUfIM_c"]

{"sheet":"HVAC 1","index":3,"n_rows":231,"n_cols":56,"rows_kept":231,"cut":false,"hidden":false,"merged":[[224,0,224,62],[225,0,229,30],[225,31,225,46],[225,47,225,62],[226,31,226,46],[226,47,226,62],[230,0,230,62],[231,0,231,62],[232,0,244,62],[227,31,227,46],[227,47,227,62],[228,31,228,46],[228,47,228,62],[229,31,229,46],[229,47,229,62],[219,31,219,46],[219,47,219,62],[220,31,220,46],[220,47,220,62],[221,31,221,46],[221,47,221,62],[214,0,214,62],[215,0,223,30],[215,31,215,46],[215,47,215,62],[216,31,216,46],[216,47,216,62],[217,31,217,46],[217,47,217,62],[218,31,218,46],[218,47,218,62],[222,31,222,46],[222,47,222,62],[223,31,223,46],[223,47,223,62],[212,0,212,30],[212,31,212,54],[212,55,212,62],[213,0,213,30],[213,31,213,54],[213,55,213,62],[208,0,208,62],[209,0,209,62],[210,0,210,30],[210,31,210,54],[210,55,210,62],[211,0,211,30],[211,31,211,54],[211,55,211,62],[204,31,204,46],[204,47,204,62],[205,31,205,46],[205,47,205,62],[206,0,206,62],[207,0,207,62],[199,31,199,46],[199,47,199,62],[200,0,200,62],[201,0,205,30],[201,31,201,46],[201,47,201,62],[202,31,202,46],[202,47,202,62],[203,31,203,46],[203,47,203,62],[194,0,194,62],[195,0,199,30],[195,31,195,46],[195,47,195,62],[196,31,196,46],[196,47,196,62],[197,31,197,46],[197,47,197,62],[198,31,198,46],[198,47,198,62],[192,0,192,30],[192,31,192,54],[192,55,192,62],[193,0,193,30],[193,31,193,54],[193,55,193,62],[189,0,189,30],[189,31,189,62],[190,0,190,30],[190,31,190,54],[190,55,190,62],[191,0,191,30],[191,31,191,54],[191,55,191,62],[185,0,185,62],[186,0,186,62],[187,0,187,30],[187,31,187,62],[188,0,188,30],[188,31,188,62],[181,30,181,44],[181,45,181,62],[182,30,182,44],[182,45,182,62],[183,0,183,62],[184,0,184,62],[178,30,178,44],[178,45,178,62],[179,30,179,44],[179,45,179,62],[180,30,180,44],[180,45,180,62],[173,0,173,62],[174,0,182,29],[174,30,174,44],[174,45,174,62],[175,30,175,44],[175,45,175,62],[176,30,176,44],[176,45,176,62],[177,30,177,44],[177,45,177,62],[162,0,162,30],[162,31,162,62],[163,0,163,30],[163,31,163,62],[164,0,164,62],[165,0,172,29],[165,30,165,44],[165,45,165,62],[166,30,166,44],[166,45,166,62],[170,30,170,44],[170,45,170,62],[171,30,171,44],[171,45,171,62],[172,30,172,44],[172,45,172,62],[167,30,167,44],[167,45,167,62],[168,30,168,44],[168,45,168,62],[169,30,169,44],[169,45,169,62],[158,0,158,30],[158,31,158,62],[159,0,159,30],[159,31,159,62],[160,0,160,62],[161,0,161,30],[161,31,161,62],[155,0,155,30],[155,31,155,62],[156,0,156,30],[156,31,156,62],[157,0,157,30],[157,31,157,62],[151,0,151,62],[152,0,153,30],[152,31,152,62],[153,31,153,44],[153,45,153,62],[154,0,154,30],[154,31,154,62],[148,0,148,30],[148,31,148,62],[149,0,149,30],[149,31,149,62],[150,0,150,30],[150,31,150,62],[144,0,144,62],[145,0,145,62],[146,0,146,62],[147,0,147,62],[140,30,140,44],[140,45,140,62],[141,30,141,44],[141,45,141,62],[142,30,142,44],[142,45,142,62],[137,30,137,44],[137,45,137,62],[138,30,138,44],[138,45,138,62],[139,30,139,44],[139,45,139,62],[132,0,132,62],[133,0,143,29],[133,30,133,44],[133,45,133,62],[134,30,134,44],[134,45,134,62],[135,30,135,44],[135,45,135,62],[136,30,136,44],[136,45,136,62],[143,30,143,44],[143,45,143,62],[129,30,129,44],[129,45,129,62],[130,30,130,44],[130,45,130,62],[131,30,131,44],[131,45,131,62],[125,0,125,38],[125,39,125,45],[125,46,125,54],[125,55,125,62],[126,0,126,62],[127,0,131,29],[127,30,127,44],[127,45,127,62],[128,30,128,44],[128,45,128,62],[123,0,123,38],[123,39,123,45],[123,46,123,54],[123,55,123,62],[124,0,124,38],[124,39,124,45],[124,46,124,54],[124,55,124,62],[121,0,121,38],[121,39,121,45],[121,46,121,54],[121,55,121,62],[122,0,122,38],[122,39,122,45],[122,46,122,54],[122,55,122,62],[118,0,118,62],[119,0,119,38],[119,39,119,45],[119,46,119,54],[119,55,119,62],[120,0,120,38],[120,39,120,45],[120,46,120,54],[120,55,120,62],[115,0,115,34],[115,35,115,62],[116,0,116,34],[116,35,116,62],[117,0,117,34],[117,35,117,62],[112,0,112,34],[112,35,112,62],[113,0,114,34],[113,35,113,62],[114,35,114,47],[114,48,114,62],[107,0,107,62],[108,0,108,62],[109,0,109,62],[110,0,110,62],[111,0,111,34],[111,35,111,62],[103,30,103,44],[103,45,103,62],[104,30,104,44],[104,45,104,62],[105,0,105,62],[106,0,106,62],[93,30,93,44],[93,45,93,62],[94,0,94,62],[95,0,104,29],[95,30,95,44],[95,45,95,62],[96,30,96,44],[96,45,96,62],[100,30,100,44],[100,45,100,62],[101,30,101,44],[101,45,101,62],[102,30,102,44],[102,45,102,62],[97,30,97,44],[97,45,97,62],[98,30,98,44],[98,45,98,62],[99,30,99,44],[99,45,99,62],[81,0,81,62],[82,0,93,29],[82,30,82,44],[82,45,82,62],[83,30,83,44],[83,45,83,62],[84,30,84,44],[84,45,84,62],[85,30,85,44],[85,45,85,62],[89,30,89,44],[89,45,89,62],[90,30,90,44],[90,45,90,62],[91,30,91,44],[91,45,91,62],[86,30,86,44],[86,45,86,62],[87,30,87,44],[87,45,87,62],[88,30,88,44],[88,45,88,62],[92,30,92,44],[92,45,92,62],[79,0,79,29],[79,30,79,44],[79,45,79,62],[80,0,80,29],[80,30,80,44],[80,45,80,62],[77,0,77,29],[77,30,77,44],[77,45,77,62],[78,0,78,29],[78,30,78,44],[78,45,78,62],[73,0,73,30],[73,31,73,44],[73,45,73,62],[74,0,74,62],[75,0,75,62],[76,0,76,29],[76,30,76,62],[71,0,71,30],[71,31,71,44],[71,45,71,62],[72,0,72,30],[72,31,72,44],[72,45,72,62],[69,0,69,30],[69,31,69,44],[69,45,69,62],[70,0,70,30],[70,31,70,44],[70,45,70,62],[67,0,67,30],[67,31,67,44],[67,45,67,62],[68,0,68,30],[68,31,68,44],[68,45,68,62],[65,0,65,30],[65,31,65,44],[65,45,65,62],[66,0,66,30],[66,31,66,44],[66,45,66,62],[63,0,63,30],[63,31,63,44],[63,45,63,62],[64,0,64,30],[64,31,64,44],[64,45,64,62],[60,0,60,62],[61,0,61,30],[61,31,61,44],[61,45,61,62],[62,0,62,30],[62,31,62,44],[62,45,62,62],[58,0,58,17],[58,18,58,30],[58,31,58,47],[58,48,58,62],[59,0,59,17],[59,18,59,62],[56,0,56,17],[56,18,56,30],[56,31,56,47],[56,48,56,62],[57,0,57,17],[57,18,57,30],[57,31,57,47],[57,48,57,62],[53,0,53,17],[53,18,53,30],[53,31,53,47],[53,48,53,62],[54,0,54,62],[55,0,55,17],[55,18,55,30],[55,31,55,47],[55,48,55,62],[51,0,51,17],[51,18,51,30],[51,31,51,47],[51,48,51,62],[52,0,52,17],[52,18,52,30],[52,31,52,47],[52,48,52,62],[47,0,47,62],[48,0,48,17],[48,18,48,62],[49,0,49,17],[49,18,49,62],[50,0,50,17],[50,18,50,30],[50,31,50,47],[50,48,50,62],[45,55,45,62],[46,0,46,11],[46,12,46,20],[46,21,46,30],[46,31,46,38],[46,39,46,46],[46,47,46,54],[46,55,46,62],[45,0,45,11],[45,12,45,20],[45,21,45,30],[45,31,45,38],[45,39,45,46],[45,47,45,54],[43,0,43,62],[44,0,44,11],[44,12,44,20],[44,21,44,30],[44,31,44,38],[44,39,44,46],[44,47,44,54],[44,55,44,62],[39,0,39,24],[39,25,39,62],[40,0,40,24],[40,25,40,62],[41,0,41,62],[42,0,42,62],[36,0,37,24],[36,25,36,62],[37,25,37,42],[37,43,37,62],[38,0,38,24],[38,25,38,62],[33,0,35,24],[33,25,33,42],[33,43,33,62],[34,25,34,42],[34,43,34,62],[35,25,35,42],[35,43,35,62],[29,0,32,24],[29,25,29,42],[29,43,29,62],[30,25,30,42],[30,43,30,62],[31,25,31,42],[31,43,31,62],[32,25,32,42],[32,43,32,62],[27,0,27,24],[27,25,27,62],[28,0,28,24],[28,25,28,62],[23,0,23,24],[23,25,23,62],[24,0,24,24],[24,25,24,62],[25,0,25,24],[25,25,25,62],[20,0,20,24],[20,25,20,62],[21,0,21,24],[21,25,21,62],[22,0,22,24],[22,25,22,62],[19,0,19,62],[26,0,26,24],[26,25,26,62],[15,0,15,62],[16,0,17,24],[16,25,16,62],[17,25,17,42],[17,43,17,62],[18,0,18,62],[11,0,11,62],[12,0,13,24],[12,25,12,62],[13,25,13,42],[13,43,13,62],[14,0,14,62],[10,0,10,62],[7,0,7,10],[7,11,7,37],[7,38,7,49],[7,50,7,64],[7,65,7,67],[8,0,8,10],[8,11,8,37],[8,38,8,49],[8,50,8,64],[8,65,8,67],[6,0,6,10],[6,11,6,37],[6,38,6,49],[6,50,6,64],[6,65,6,67],[9,0,9,10],[9,11,9,37],[9,38,9,49],[9,50,9,64],[9,65,9,67],[4,0,4,10],[4,11,4,37],[4,38,4,49],[4,50,4,64],[4,65,4,67],[5,0,5,10],[5,11,5,37],[5,38,5,49],[5,50,5,64],[5,65,5,67],[0,0,0,67],[1,0,1,67],[2,0,2,10],[2,11,2,37],[2,38,2,49],[2,50,2,64],[2,65,2,67],[3,0,3,10],[3,11,3,37],[3,38,3,49],[3,50,3,64],[3,65,3,67]]}
["California Schools Healthy Air, Plumbing, and Efficiency Ventilation Program\nHVAC Assessment and Maintenance Pathway\nHVAC Assessment Report Worksheets March 2024"]
["1. System Overview\n2. Filtration System\n3. Ventilation Rate\n4. Economizer Operation\n5. Demand Control Ventilation\n6. Air Distribution and Building Pressure\n7. General Maintenance\n8. Operational Controls\n9. CO2 Monitoring\nThese worksheets are made available to help Program participants gather information for an HVAC Assessment Report as part of the California Schools Healthy Air, Plumbing, and Efficiency (CalSHAPE) Ventilation Program Assessment and Maintenance Grant. These worksheets are intended to be used for optional information gathering purposes only since completion of these worksheets does not constitute an HVAC Assessment Report. To comply with grant requirements and be eligible for funding, participants must submit an HVAC Assessment Report electronically by entering the required information through the CalSHAPE Online System as set forth in the most recent CalSHAPE Ventilation Program Guidelines.\nThese worksheets were designed and offered with a technician in mind that may not always have an electronic device to use when recording data. These worksheets can be printed out and then written on in the field. The information can later be typed into the required HVAC Assessment Report submitted electronically to the CalSHAPE Online System.\nThe CalSHAPE Ventilation Program Guidelines, these worksheets, and other program requirements such as a data reporting and processes are subject to change by the California Energy Commission, including but not limited to any changes to data reporting requirements from the California Public Utilities Commission. It is the participant’s responsibility to use the most recent version of these worksheets and otherwise comply with the current requirements of the CalSHAPE Ventilation Program."]
["Worksheet #",null,null,null,null,null,null,null,null,null,null,"Guidance and Worksheet Section",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Name of Qualified Testing Technician",null,null,null,null,null,null,null,null,null,null,null,"Name of Qualified Adjusting Technician"]
[1,null,null,null,null,null,null,null,null,null,null,"HVAC Equipment Details"]
[2,null,null,null,null,null,null,null,null,null,null,"Filtration, Airflow Distribution, and Building Pressurization"]
[3,null,null,null,null,null,null,null,null,null,null,"Minimum Outside Air"]
[4,null,null,null,null,null,null,null,null,null,null,"Ventilation System Operation\n     Economizer\n     Demand Control Ventilation"]
[5,null,null,null,null,null,null,null,null,null,null,"Operational Controls"]
[6,null,null,null,null,null,null,null,null,null,null,"General Maintenance"]
[7,null,null,null,null,null,null,null,null,null,null,"Exhaust Only System"]
[]
["Licensed Professional Recommendations"]
["Does this HVAC Unit require repairs or replacement?"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If Repair or Replace is selected, describe required repairs/replacement:"]
[]
["Deficiencies"]
["Does the unit have deficiencies? "]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes', describe overall unit deficiencies: "]
[]
["1.1 HVAC Equipment Details (Based on Nameplate)"]
["HVAC Unit Name (District ID)"]
["AHRI Unit Type"]
["AHRI Unit Type: Other - Please Specify"]
["Manufacturer"]
["Manufacturer: Other - Please Specify"]
["Model Number (outdoor unit)"]
["Serial Number (outdoor unit)"]
["Model Number (indoor unit)\nRequired for split systems only"]
["Serial Number (indoor unit)\nRequired for split systems only"]
["Heating type (select yes for all that apply)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No Heat"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Gas Heat"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Heat Pump"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Electric Resistance Heat"]
["Cooling type (select yes for all that apply)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No cooling"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Compressor air conditioning "]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Evaporative cooling"]
["Refrigerant Type\nRequired for compressor air conditioning systems only"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Refrigerant Type: Other - Specify refrigerant type"]
["Heating Output Capacity (kBtuh)\nRequired for heating systems only"]
["Heating Input Capacity (kBtuh)\nRequired for gas heat systems only"]
["Cooling Output Capacity (kBtuh)\nRequired for cooling systems only"]
[]
["2.1 Filter Data"]
["Document filters as the system was found (as-found) and as the system was adjusted (as-left). Enter MERV rating of “0” if the system was found with no existing filters."]
["Filter Length (in)",null,null,null,null,null,null,null,null,null,null,null,"Filter Width (in)",null,null,null,null,null,null,null,null,"Quantity",null,null,null,null,null,null,null,null,null,"Filter Depth\n(in) As- found",null,null,null,null,null,null,null,"Filter Depth (in) As-left",null,null,null,null,null,null,null,"MERV\nAs-found",null,null,null,null,null,null,null,"MERV\nAs-Left"]
[]
[]
["2.2 Supply Fan Motor Nameplate Data"]
["Variable Speed\nDrive on Motor"]
["Drive Assembly"]
["Manufacturer",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"RPM"]
["HP",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Phase"]
["Amps",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Service Factor"]
["Volts",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Frame Size"]
["2.3 Fan and Motor Sheave Data. Required for belt driven systems only."]
["Fan Sheave Model",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Motor Sheave Model"]
["Shaft Diameter (in)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Shaft Diameter (in)"]
["Pitch Diameter (in)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Pitch Diameter (As-Found) (in)"]
["Shaft Centerline (in)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Pitch Diameter (As-Left) (in)"]
["Grooves (# Belts)"]
["2.4 Summary data for airflow, fan performance, and building pressurization at full airflow (if applicable, power exhaust disabled). Provide a complete TAB report as an attachment with the supporting data for as-found and as-left measurements. The TAB report must include individual register return and supply readings. If drawings specifying supply, return and outside air design rates are not available, see instructions\nfor guidance. Outside air results are in form 3."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"As-Found",null,null,null,null,null,null,null,null,null,null,null,null,null,"As-Left"]
["Supply Airflow Design (CFM)"]
["Supply Airflow Tested (Sum Terminals) (CFM)"]
["Supply Airflow Tested (Pitot-Traverse) (CFM)"]
["Return Airflow Design (CFM)"]
["Return Airflow Tested (Sum Terminals) (CFM)"]
["Return Airflow Tested (Pitot-Traverse) (CFM)"]
["Measured Motor Speed (RPM)"]
["Measured Fan Speed (RPM)"]
["Measured Motor Input Power (BHP)"]
["Total Static Pressure (Fan) (inwc)"]
["External Static Pressure (Ductwork) (inwc)"]
["Building Pressurization (inwc)"]
[]
["2.5 Summary Data for Powered Exhaust Test. Required only for systems with powered exhaust. Provide a complete TAB report as an attachment with the supporting data."]
["Powered Exhaust Present"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"As-Found",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"As-Left"]
["Supply Airflow (Sum Terminals) (CFM)"]
["Exhaust Airflow (Sum Terminals) (CFM)"]
["Building Pressurization (in WC)"]
["2.6 Minor Repairs and Adjustments"]
["Minor Repairs and Adjustments. Select yes to all types of adjustments and/or minor repairs that were made  to the fan, motor, and airflow system (meaning, document what changed in the system between the “as found”\nand “as-left” condition).",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Fan Sheave Replaced",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Motor Sheave Replaced",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Motor Sheave Adjusted",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Belt Replaced",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Belt Tension Aligned or Adjusted",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Variable frequency Drive Speed Adjusted",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply Air Distribution Adjusted",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Return Air Distribuion Adjusted",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Power Exhaust Repaired or Adjusted",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Modifications to Reduce Filter Bypass",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, describe any other types of minor repairs/adjustments:"]
["2.7 Remaining Deficiencies. "]
["Remaining Deficiencies: Select 'Yes' to any deficiencies remaining",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Fan/motor system could not be adjusted to use MERV13 filtration ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Return duct leakage suspected (greater than 10% of flow) ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply duct leakage suspected (greater than 10% of flow) ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Airflow distribution problem that could not be corrected",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Building pressurization exceeds 0.05 inwc (insufficient exhaust) ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Building pressurization less than 0 inwc (insufficient outside air supply)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Cooling coil exceeds 500 ft/min and may have moisture carry over",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Significant filter bypass that could not be corrected",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, specify remaining deficiencies:"]
["2.8 Remaining Deficiencies Notes. If deficiencies remaining, describe and provide notes to inform future repairs and/or replacements. Lack of access to the building, rooftop, or control system is not an acceptable\nreason to leave the system with a deficiency."]
[]
["2.9 Measurement Notes. Provide notes here for reasons that specific measurements could not be made. Lack of access to the building, rooftop, or control system is not an acceptable reason."]
[]
[]
["3.1 Minimum Required Outside Air (OSA) for HVAC System. Provide a complete TAB report as an attachment with the supporting data for as-found and as-left measurements. If drawings specifying outside air\ndesign rates are not available, see instructions for guidance."]
["Actual occupancy for space served by HVAC system\n(number of people)"]
["Floor area for space served by HVAC system (ft2)"]
["Primary Occupancy Category (use)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If 'Other' selected for primary occupancy category, please specify:"]
["Does the system use demand-controlled ventilation (DCV)?"]
["Minimum Outside Air Requirement (CFM)"]
["System Type"]
["3.2 Outside Air Measurements"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"As-found",null,null,null,null,null,null,"Adjusted (As-Left)",null,null,null,null,null,null,null,null,"Units"]
["High Speed: Minimum damper position as a percent of full open. Mark physical damper position on unit.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%"]
["High Speed: Measured outdoor airflow reading for CAV and high speed VAV (cfm).",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CFM"]
["High Speed: %OAFA = Measured outdoor airflow reading/Required outdoor airflow (%). Note: This field will be populated when calculated by validation macro",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,0,null,null,null,null,null,null,null,null,"%"]
["VAV Low Speed: Minimum damper position as a percent of full open. VAV systems only. Mark physical damper position on unit.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%"]
["VAV Low Speed: Measured outdoor airflow reading for low\nspeed (30% airflow) VAV (cfm). VAV systems only.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CFM"]
["VAV Low Speed: %OAFA = Measured outdoor airflow\nreading/Required outdoor airflow (%).VAV systems only. Note: This field will be populated when calculated by validation macro",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,0,null,null,null,null,null,null,null,null,"%"]
["3.3 Minor Repairs and Adjustments."]
["Minor Repairs and Adjustments. Select 'yes' to all types of adjustments and/or minor repairs that were made to the outdoor air system (meaning, document what changed in the system between the “as found” and “as-left” condition).",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Adjusted manual outdoor damper setting",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Adjusted economizer minimum position setting",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Clear or unblock outdoor air intake",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, describe any other types of minor repairs/adjustments:"]
["3.4 Outside Air Deficiencies. "]
["Outside Air Deficiencies. Select 'yes' to reason(s) that system can not be adjusted to meet the outside air requirement. Lack of access (to buildings, systems, control systems) is not a valid reason.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No outdoor air intake",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor intake is at maximum setting, but outdoor air is still too low",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor intake is at minimum setting, but outdoor air is still too high",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air damper assembly is broken ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air actuator is broken",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air controller is broken (no power or has fault) ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air controller is not communicating with BAS",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outside air intake has exhaust discharge outlets or vents that do not meet distance requirements",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outside air intake is covered or blocked by debris",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, specify remaining deficiencies: "]
["3.5 Remaining Deficiencies Notes. If deficiencies remaining, describe and provide notes to inform future repairs and/or replacements.  Lack of access to the building, rooftop, or control system is not an acceptable\nreason to leave the system with a deficiency."]
[]
[]
["4.1 Economizer and DCV Information"]
["Economizer present in system"]
["Does the system use demand-controlled ventilation (DCV)?"]
["The 2013 Building Energy Efficiency Standards require an economizer for systems with cooling capacity greater than 54,000 btu/hr. For systems greater than 54,000 btu/hr without economizers, select the reason."]
["4.2 Economizer Configuration and Testing (For systems with economizers)"]
["Model of the Economizer Controller"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If Other selected for model, please specify:"]
["California Climate Zone"]
["Economizer High Limit Type"]
["Economizer High Limit Setting"]
["Economizer Minimum Damper Position (%)"]
["Economizer Passed all Functional Testing (As-Found)"]
["Economizer Passed all Functional Testing (As-Left)"]
["4.3 Demand Controlled Ventilation"]
["Carbon Dioxide (CO2) Setpoint (ppm)"]
["DCV Passed all Functional Testing (As-Found)"]
["DCV Passed all Functional Testing (As-Left)"]
["4.4 Minor Repairs and Adjustments. "]
["Minor Repairs and Adjustments. Select 'yes' to all types of adjustments and/or minor repairs that were made to the economizer and/or DCV system (meaning, document what changed in the system between the “as found” and “as-left” condition).",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Configured economizer settings",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Configured DCV settings",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Repaired or replaced temperature, humidity, or enthalpy sensor ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Repaired or replaced carbon dioxide sensor",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Repaired damaged or incorrect signal wiring",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Repaired or adjusted outside air assembly",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, describe any other types of minor repairs/adjustments:"]
["4.5 Remaining Deficiencies. "]
["Remaining Deficiencies. Select 'yes' to any deficiencies remaining.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air economizer controller is broken",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air actuator is broken",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air damper assembly is broken",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air assembly does not achieve 100% outdoor air position ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air assembly does not achieve fully closed outdoor air position ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Outdoor air assembly does not close when unit is turned off ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"DCV is present but is not working correctly ",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, specify remaining deficiencies: "]
["4.6 Remaining Deficiencies Notes. If deficiencies remaining, describe and provide notes to inform future\nrepairs and/or replacements.  Lack of access to the building, rooftop, or control system is not an acceptable reason to leave the system with a deficiency."]
[]
[]
["5.1 Operational Controls"]
["Control Type"]
["Ventilation System Start Time (hh:mm)\nTypical occupied day"]
["Ventilation System End Time (hh:mm)\nTypical occupied day"]
["Occupied Cooling Setpoint (°F)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F"]
["Occupied Heating Setpoint (°F)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F"]
["Unoccupied Cooling Setpoint (°F)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F"]
["Unoccupied Heating Setpoint (°F)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F"]
["5.2 Minor Repairs and Adjustments."]
["Minor Repairs and Adjustments. Select 'yes' to all types of adjustments and/or minor repairs that were made to the economizer (meaning, document what changed in the system between the “as found” and “as-left”\ncondition).",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Reprogrammed Thermostat",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Reprogrammed Building Automation System",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Replaced Thermostat",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, describe any other types of minor repairs/adjustments:"]
["5.3 Remaining Deficiencies. "]
["Remaining Deficiencies. Select 'yes' to any deficiencies remaining.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Existing controls do not support programming a ventilation schedule",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Existing controls do not support programming a setpoint schedule",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Existing controls are pneumatic and not working correctly",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, specify remaining deficiencies: "]
["5.4 Remaining Deficiencies Notes. If deficiencies remaining, describe and provide notes to inform future repairs and/or replacements.  Lack of access to the building, rooftop, or control system is not an acceptable\nreason to leave the system with a deficiency."]
[]
[]
["6.1 General Maintenance"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Temperature",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Units"]
["Outside Air Temperature During Testing (°F)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F"]
["Air Temperature Split – Cooling (°F)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F"]
["Air Temperature Split – Heating (°F)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"°F"]
["6.2 Minor Repairs and Adjustments"]
["Minor Repairs and Adjustments. Select 'yes' to all types of adjustments and/or minor repairs that were made to the economizer (meaning, document what changed in the system between the “as found” and “as-left”\ncondition).",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Cleaned Indoor Coil",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Cleaned Outdoor Coil",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Repaired Condensate Pump",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Replaced Condensate Pump",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Repaired Condensate Drain",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Replaced Condensate Drain",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Capped service ports (i.e. Shrader valves) to prevent leaks",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, describe any other types of minor repairs/adjustments:"]
["6.3 Remaining Deficiencies."]
["Remaining Deficiencies. Select 'yes' to any deficiencies remaining.",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Air temperature split is lower than expected, possible refrigerant leak",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Standing water, mold, or mildew on HVAC system",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Mechanical room shows unsanitary conditions, such as leaks and spills",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Other",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"No"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"If selected 'yes' for Other, specify remaining deficiencies: "]
["6.4 Remaining Deficiencies Notes. If deficiencies remaining, describe and provide notes to inform future repairs and/or replacements.  Lack of access to the building, rooftop, or control system is not an acceptable\nreason to leave the system with a deficiency."]